## Sheet1
Florida Power & Light Company
Docket No. 20190015-EG
Staff's First Set of Interrogatories
Interrogatory No. 11
Attachment No. 1
Tab 1 of 1
Schedule 9
Status Report and Specifications of Proposed Generating Facilities
| -1 | Plant Name and Unit Number: |  | Unsited 3x1 Combined Cycle
| -2 | Capacity
|  | a. Summer | 1886 | MW
|  | b. Winter | 1880 | MW
| -3 | Technology Type: | Combined Cycle
| -4 | Anticipated Construction Timing
|  | a. Field construction start-date: |  | 2024
|  | b. Commercial In-service date: |  | 2026
| -5 | Fuel
|  | a. Primary Fuel |  |  | Natural Gas
|  | b. Alternate Fuel |  |  | Ultra-low sulfur distillate
| -6 | Air Pollution and Control Strategy: |  |  | Dry Low NOx Burners, SCR, Natural Gas,
0.0015% S. Distillate and Water Injection
| -7 | Cooling Method: |  |  | Mechanical Draft Cooling Towers
| -8 | Total Site Area: |  | TBD | Acres
| -9 | Construction Status: |  | P | (Planned Unit)
| -10 | Certification Status: |  | ---
| -11 | Status with Federal Agencies: |  | ---
| -12 | Projected Unit Performance Data:
|  | Planned Outage Factor (POF): |  |  | 3.5%
|  | Forced Outage Factor (FOF): |  |  | 1%
|  | Equivalent Availability Factor (EAF): |  |  | 95.5%
|  | Resulting Capacity Factor (%): |  |  | Approx. 80% | (First Full Year Base Operation)
|  | Average Net Operating Heat Rate (ANOHR): |  |  | 6134
Base Operation 75F,100%
|  | Average Net Incremental Heat Rate (ANIHR): |  |  | 8045
Wet Compression 75F,100%
| -13 | Projected Unit Financial Data *,**
|  | Book Life (Years): |  |  | 40 | years
|  | Total Installed Cost (2026 $/kW): |  |  | 673.7396
|  | Direct Construction Cost (2026 $/kW): |  |  | 605.7396
|  | AFUDC Amount (2026 $/kW): |  |  | 68
|  | Escalation ($/kW): |  |  | Accounted for in Direct Construction Cost
|  | Fixed O&M (2026 $/kW-Yr.): |  |  | 23.0407
|  | Variable O&M (2026 $/MWH): |  |  | 0.17008
|  | K Factor: |  |  | 1.53
* $/kW values are based on Summer capacity.
** Levelized value for Fixed O&M also includes Capital Replacement
Note: Total installed cost includes transmission interconnection and integration, escalation, and AFUDC.