## Exec Summary
FPL 003532
20190015-EG
FLORIDA POWER & LIGHT COMPANY
LINE LOSS STUDY - 2017 ACTUALS
Summary of Loss Expansion Factors and Loss Percentages
Variance - Year Ended December 2017 vs. Year Ended December 2016
| Demand - 12 CP Expansion Factor |  |  | Energy Expansion Factor
Voltage Level | 2017 | 2016 | Variance | 2017 | 2016 | Variance
Transmission | 1.0214 | 1.0219 | -0.00051798 | 1.0172 | 1.0177 | -0.00051016
Primary | 1.0369 | 1.037 | -0.00012488 | 1.0292 | 1.0294 | -0.00024666
Secondary | 1.0654 | 1.0614 | 0.0039521 | 1.0511 | 1.0483 | 0.0028342
| Demand Loss % |  |  | Energy Loss %
Voltage Level | 2017 | 2016 | Variance | 2017 | 2016 | Variance
Transmission | 2.093% | 2.143% | -0.04963% | 1.691% | 1.74% | -0.04928%
Primary | 3.554% | 3.566% | -0.01161% | 2.834% | 2.857% | -0.02328%
Secondary | 6.136% | 5.787% | 0.3495% | 4.864% | 4.606% | 0.2572%

## LLS_Expansion_Factors_Energy_B
FPL 003533
20190015-EG
ENERGY FLOW THROUGH SYSTEM | FLOW MWH | LOSS % | LOSS MULTIPLIER | EXPANSION FACTOR | CUMULATIVE LOSS %
Net Energy to Transmission | 128438432 | 0% | 0 | 0 | 0%
Generation Step-up Transformer Losses | -254662.7 | 0.1983% | 1.002 | 0 | 0%
Flow to Transmission | 128183769.3 | 0% | 0 | 0 | 0%
Transmission Line & Substation Losses | -1959812.6035 | 0% | 0 | 0 | 0%
Remove Southern JEA/ LP, NF & STF Wheeling Losses (a) | 43199 | 0% | 0 | 0 | 0%
Adjusted Transmission Line & Substation Losses | -1916613.6035 | 1.495% | 1.0152 | 0 | 0%
Flow on Transmission | 126267155.6965 | 0% | 0 | 0 | 0%
Delivered Sales at Transmission | -8049650.6908 | 0 | 0 | 1.0172 | 1.691%
Seminole & Firm Power Wheeled for Others | -7693314 | 0% | 0 | 0 | 0%
Include Southern JEA/LP, NF & STF Wheeling Losses (a) | -43199 | 0% | 0 | 0 | 0%
Flow to Distribution | 110480992.0056 | 0% | 0 | 0 | 0%
Distribution Substation Losses | -476293.608 | 0.4311% | 1.0043 | 0 | 0%
Flow to Primary Lines | 110004698.3976 | 0% | 0 | 0 | 0%
Primary Line Losses | -808674.3381 | 0.7351% | 1.0074 | 0 | 0%
Flow on Primary | 109196024.0596 | 0% | 0 | 0 | 0%
Delivered Sales at Primary | -2579339.3792 | 0 | 0 | 1.0292 | 2.834%
Flow to Secondary | 106616684.6804 | 0% | 0 | 0 | 0%
Transformer Losses | -1557362.4413 | 1.461% | 1.0148 | 0 | 0%
Flow on Secondary | 105059322.2391 | 0% | 0 | 0 | 0%
Secondary Line & Service Losses | -669633.625 | 0.6374% | 1.0064 | 0 | 0%
Balance For Use | 104389688.614 | 0% | 0 | 0 | 0%
Company Use | -126388 | 0% | 0 | 0 | 0%
Delivered Sales at Secondary | -104263300.614 | 0 | 0 | 1.0511 | 4.864%
(a) JEA/Southern loss payback and the non-firm and short-term wheeling losses are excluded from the transmission loss percentage calculation because the
flows that create these losses are not in the flow to transmission. However, because these are real losses, they are included in the flow to distribution.

## LLS_Expansion_Factors_Demand_B
FPL 003534
20190015-EG
DEMAND FLOW THROUGH SYSTEM | LOAD FACTOR | ENERGY LOSS % DIVIDED BY (.3 + (.7* LF)) (a) | FLOW MW | LOSS FACTOR | EXPANSION FACTOR
Net Demand to Transmission | 0 | 0 | 20303.7731 | 0 | 0
Generation Step-up Transformer Losses | 0 | 0.24608 | -49.9639 | 1.0025 | 0
Flow to Transmission | 0.72247 | 0 | 20253.8091 | 0 | 0
Transmission Line & Substation Losses | 0 | 1.8515 | -374.9983 | 1.0189 | 0
Flow on Transmission | 0.7251 | 0 | 19878.8108 | 0 | 0
Delivered Demand at Transmission (b) | 0 | 0 | -1385.4388 | 0 | 1.0214
Flow to Distribution | 0 | 0 | 18493.372 | 0 | 0
Distribution Substation Losses | 0 | 0.55414 | -102.4801 | 1.0056 | 0
Flow to Primary Lines | 0.68282 | 0 | 18390.892 | 0 | 0
Primary Line Losses | 0 | 0.94371 | -173.5561 | 1.0095 | 0
Flow on Primary | 0.68425 | 0 | 18217.3359 | 0 | 0
Delivered Demand at Primary (c) | 0 | 0 | -358.801 | 0 | 1.0369
Flow to Secondary | 0 | 0 | 17858.5349 | 0 | 0
Transformer Losses | 0 | 1.8749 | -334.8355 | 1.0191 | 0
Flow on Secondary | 0.68439 | 0 | 17523.6993 | 0 | 0
Secondary Line & Service Losses | 0 | 0.81722 | -143.2075 | 1.0082 | 0
Balance For Use | 0.68563 | 0 | 17380.4919 | 0 | 0
Company Use | 0 | 0 | -20.0848 | 0 | 0
Delivered Demand at Secondary (d) | 0 | 0 | 17360.4071 | 0 | 1.0654
(a) Westinghouse Formula
(b) Total Company average 12-month coincident peak MWs at meter for transmission voltage level.
(c) Total Company average 12-month coincident peak MWs at meter for primary voltage level.
(d) Total Company average 12-month coincident peak MWs at meter for secondary voltage level.

## LLS_Energy_Losses_Sales_Compan
FPL 003535
20190015-EG
LINE NO. | ENERGY LOSSES, SALES, COMPANY USE AND WHEELING | LOSSES (MWH) | SALES (MWH) | NET ENERGY (MWH)
1
2 | NET ENERGY TO TRANSMISSION | 0 | 0 | 128438432
3 |  | 0 | 0 | 0
4 | LOSSES & UNACCOUNTED FOR ENERGY: | 0 | 0 | 0
5 | Generation Step-Up Transformer Losses (a) | 254662.7 | 0 | -254662.7
6 |  | 0 | 0 | 0
7 | Southern JEA/LP, NF & STF Wheeling Losses (a) | 43199 | 0 | 0
8 | Adjusted Transmission Line Losses (a) | 1916613.6035 | 0 | 0
9 | Transmission Line Losses (a) | 1959812.6035 | 0 | -1959812.6035
10 |  | 0 | 0 | 0
11 | Distribution Substation Losses (a) | 476293.608 | 0 | -476293.608
12 |  | 0 | 0 | 0
13 | Other Distribution Losses & Unaccounted For Energy:
14 | Primary Line Losses (b) | 808674.3381 | 0 | 0
15 |  | 0 | 0 | 0
16 | Transformer Losses (b) | 1557362.4413 | 0 | 0
17 |  | 0 | 0 | 0
18 | Secondary Losses & Unaccounted for Energy (c) | 669633.625 | 0 | 0
19 |  | 0 | 0 | 0
20 | SUBTOTAL - Other Distribution Losses | 3035670.4045 | 0 | -3035670.4045
21 |  | 0 | 0 | 0
22 | TOTAL LOSSES & UNACCOUNTED FOR ENERGY | 5726439.316 | 0 | 0
23 |  | 0 | 0 | 0
24 | SYSTEM - NET OF LOSSES AND UNACCOUNTED FOR ENERGY | 16448361.64 | 0 | 122711992.684
25
26 | DELIVERED SALES:
27 | Retail: | 0 | 0 | 0
28 | Transmission | 0 | 1670954.3658 | 0
29 | Primary | 0 | 2579339.3792 | 0
30 | Secondary | 0 | 104263300.614 | 0
31 | Total Retail | 0 | 108513594.359 | 0
32
33 | Wholesale: | 0 | 0 | 0
34 | Transmission | 0 | 6378696.325 | 0
35 | Total Wholesale | 0 | 6378696.325 | 0
36
37 | TOTAL DELIVERED SALES | 0 | 0 | -114892290.684
38 |  | 0 | 0 | 0
39 | COMPANY USE | 0 | 0 | -126388
40 |  | 0 | 0 | 0
41 | FIRM POWER WHEELED FOR OTHERS - SOUTHERN JEA/LP - NF/STF (a) | 0 | 0 | -7693314
42 |  | 0 | 0 | 0
43 | TOTAL | 16448361.64 | 229784581.368 | 1.4901e-08
44
45
46 | (a) GSU, transmission and distribution substation losses provided by Power Supply.
47 | (b) Specifications provided by Distribution Engineering.
48 | (c) Secondary losses include electricity theft and unknown usage.

## LLS_Expansion_Factors_Summary_
FPL 003536
20190015-EG
LINE NO. | VOLTAGE LEVEL |  | DEMAND EXPANSION FACTOR | ENERGY EXPANSION FACTOR | ENERGY LOSS %
1
2 | TRANSMISSION | 0 | 1.0214 | 1.0172 | 1.691%
3 |  | 0 | 0 | 0 | 0%
4 | PRIMARY | 0 | 1.0369 | 1.0292 | 2.834%
5 |  | 0 | 0 | 0 | 0%
6 | SECONDARY | 0 | 1.0654 | 1.0511 | 4.864%
7 |  | 0 | 0 | 0 | 0%
8 |  | 0 | 0 | 0 | 0
9
10
11 | COMPANY USE - DEMAND: | 0 | 0 | 0 | 0%
12 | GSD-1 Delivered Sales (MWH) / | 26293906.4251 | 0 | 0 | 0%
13 | Hours in Year / | 8760 | 0 | 0 | 0%
14 | GSD-1 12CP (MW) | 4178.4651 | 0 | 0 | 0%
15 | GSD-1 Load Factor | 0.71835 | 0 | 0 | 0
16 |  | 0 | 0 | 0 | 0%
17 | Company Use - MWH / | 126388 | 0 | 0 | 0%
18 | Hours in Year / | 8760 | 0 | 0 | 0%
19 | GSD-1 Load Factor | 0.71835 | 0 | 0 | 0%
20 | COMPANY USE - 12CP DEMAND (MW) | 20.0848 | 0 | 0 | 0
21 |  | 0 | 0 | 0 | 0%
22
23
24
25 | CALCULATION OF NET ENERGY TO TRANSMISSION:
26 | Net Energy for Load (NEL) | 120745118 | 0 | 0 | 0%
27 |  | 0 | 0 | 0 | 0%
28 | + Seminole Load Received | 2355310 | 0 | 0 | 0%
29 | + St. Lucie Entitlement Received | 551508 | 0 | 0 | 0%
30 | + Power Wheeled for Others | 4829695 | 0 | 0 | 0%
31 | - Southern JEA / Transfers Loss Payback | -19728 | 0 | 0 | 0%
32 | - Non-Firm Wheeling Losses | -14104 | 0 | 0 | 0%
33 | - Short Term Firm Wheeling Losses | -9367 | 0 | 0 | 0%
34 | SUBTOTAL: Firm Power Wheeled for Others - Southern JEA/LP - NF/STF: | 7693314 | 0 | 0 | 0
35 |  | 0 | 0 | 0 | 0%
36 | NET ENERGY TO TRANSMISSION (MWH) | 128438432 | 0 | 0 | 0
37 |  | 0 | 0 | 0 | 0%
38
39
40
41 | LINE LOSS TOTALS USING BILLED SALES: | 0 | 0 | 0 | 0%
42 | NEL | 120745118 | 0 | 0 | 0
43 | Prior Month Unbilled | 4773600 | 0 | 0 | 0%
44 | SUBTOTAL | 125518718 | 0 | 0 | 0%
45 | Billed Sales | -115276852.684 | 0 | 0 | 0%
46 | Company Use | -126388 | 0 | 0 | 0%
47 | Current Month Unbilled | -4389038 | 0 | 0 | 0%
48 | ENERGY LOST OR UNACCOUNTED FOR | 5726439.316 | 0 | 0 | 0%
49 | % LOST OR UNACCOUNTED FOR | 4.743% | 0 | 0 | 0
50 |  | 0 | 0 | 0 | 0%
51
52
53
54 | TOTAL DELIVERED TO BILLED SALES RATIO: | 0 | 0 | 0 | 0%
55 | Total Delivered MWH | 114892290.684 | 0 | 0 | 0
56 | Total Billed MWH | 115276852.684 | 0 | 0 | 0%
57 | TOTAL DELIVERED TO BILLED SALES RATIO | 0.99666 | 0 | 0 | 0
58 |  | 0 | 0 | 0 | 0%
59

## LLS_12CP_Demand_Losses_by_Rate
FPL 003537
20190015-EG
RATE CLASS | 12 CP DEMAND @ MTR | LOSS EXPANSION FACTORS | 12 CP DEMAND @ GEN | DELIVERED EFFICIENCY | LOSSES | COST RECOVERY MULTIPLIER
CILC-1D
Primary | 138560.2199 | 1.0369 | 143666.7127 | 0.96446 | 5106.4928 | 0
Secondary | 199809.4468 | 1.0654 | 212871.4272 | 0.93864 | 13061.9805 | 0
TOTAL | 338369.6667 | 1.0537 | 356538.14 | 0.94904 | 18168.4733 | 0.99251
CILC-1G
Primary | 288.9197 | 1.0369 | 299.5676 | 0.96446 | 10.6478 | 0
Secondary | 13464.4969 | 1.0654 | 14344.7006 | 0.93864 | 880.2036 | 0
TOTAL | 13753.4167 | 1.0648 | 14644.2681 | 0.93917 | 890.8514 | 1.0029
CILC-1T
Transmission | 162803 | 1.0214 | 166283.3455 | 0.97907 | 3480.3455 | 0
TOTAL | 162803 | 1.0214 | 166283.3455 | 0.97907 | 3480.3455 | 0.96207
GS(T)-1
Secondary | 1145468.1667 | 1.0654 | 1220349.9256 | 0.93864 | 74881.7589 | 0
TOTAL | 1145468.1667 | 1.0654 | 1220349.9256 | 0.93864 | 74881.7589 | 1.0035
GSCU-1
Secondary | 7982.1667 | 1.0654 | 8503.9784 | 0.93864 | 521.8117 | 0
TOTAL | 7982.1667 | 1.0654 | 8503.9784 | 0.93864 | 521.8117 | 1.0035
GSD(T)-1
Primary | 11648.6416 | 1.0369 | 12077.9402 | 0.96446 | 429.2986 | 0
Secondary | 4166816.4417 | 1.0654 | 4439210.3442 | 0.93864 | 272393.9025 | 0
TOTAL | 4178465.0833 | 1.0653 | 4451288.2844 | 0.93871 | 272823.2011 | 1.0034
GSLD(T)-1
Primary | 63347.2252 | 1.0369 | 65681.8213 | 0.96446 | 2334.5961 | 0
Secondary | 1584662.0248 | 1.0654 | 1688254.8466 | 0.93864 | 103592.8218 | 0
TOTAL | 1648009.25 | 1.0643 | 1753936.6679 | 0.93961 | 105927.4179 | 1.0025
GSLD(T)-2
Primary | 131260.7711 | 1.0369 | 136098.2503 | 0.96446 | 4837.4792 | 0
Secondary | 212233.0622 | 1.0654 | 226107.2016 | 0.93864 | 13874.1394 | 0
TOTAL | 343493.8333 | 1.0545 | 362205.4519 | 0.94834 | 18711.6186 | 0.99324
GSLD(T)-3
Transmission | 26251 | 1.0214 | 26812.1847 | 0.97907 | 561.1847 | 0
TOTAL | 26251 | 1.0214 | 26812.1847 | 0.97907 | 561.1847 | 0.96207
MET
Primary | 11498.1667 | 1.0369 | 11921.9196 | 0.96446 | 423.753 | 0
TOTAL | 11498.1667 | 1.0369 | 11921.9196 | 0.96446 | 423.753 | 0.97665
OS-2
Primary | 716 | 1.0369 | 742.3874 | 0.96446 | 26.3874 | 0
TOTAL | 716 | 1.0369 | 742.3874 | 0.96446 | 26.3874 | 0.97665
RS(T)-1
Secondary | 10026385.5 | 1.0654 | 10681832.2452 | 0.93864 | 655446.7452 | 0
TOTAL | 10026385.5 | 1.0654 | 10681832.2452 | 0.93864 | 655446.7452 | 1.0035
SL-1M
Secondary | 0.25 | 1.0654 | 0.26634 | 0.93864 | 0.016343 | 0
TOTAL | 0.25 | 1.0654 | 0.26634 | 0.93864 | 0.016343 | 1.0035
SL-2
Secondary | 3575.3333 | 1.0654 | 3809.0607 | 0.93864 | 233.7274 | 0
TOTAL | 3575.3333 | 1.0654 | 3809.0607 | 0.93864 | 233.7274 | 1.0035
SL-2M
Secondary | 10.1667 | 1.0654 | 10.8313 | 0.93864 | 0.66462 | 0
TOTAL | 10.1667 | 1.0654 | 10.8313 | 0.93864 | 0.66462 | 1.0035
SST-DST
Primary | 1481.0833 | 1.0369 | 1535.6671 | 0.96446 | 54.5838 | 0
TOTAL | 1481.0833 | 1.0369 | 1535.6671 | 0.96446 | 54.5838 | 0.97665
SST-TST
Transmission | 13395.5833 | 1.0214 | 13681.9494 | 0.97907 | 286.3661 | 0
TOTAL | 13395.5833 | 1.0214 | 13681.9494 | 0.97907 | 286.3661 | 0.96207
TOTAL FPSC
TOTAL | 17921657.6667 | 1.0643 | 19074096.5736 | 0.93958 | 1152438.907 | 1.0025
BLOUNTSTOWN
Transmission | 1798.5 | 1.0214 | 1836.9477 | 0.97907 | 38.4477 | 0
TOTAL | 1798.5 | 1.0214 | 1836.9477 | 0.97907 | 38.4477 | 0.96207
FKEC
Transmission | 125005.5 | 1.0214 | 127677.8238 | 0.97907 | 2672.3238 | 0
TOTAL | 125005.5 | 1.0214 | 127677.8238 | 0.97907 | 2672.3238 | 0.96207
HOMESTEAD
Transmission | 20000 | 1.0214 | 20427.553 | 0.97907 | 427.553 | 0
TOTAL | 20000 | 1.0214 | 20427.553 | 0.97907 | 427.553 | 0.96207
LCEC
Transmission | 757215.3333 | 1.0214 | 773402.8176 | 0.97907 | 16187.4843 | 0
TOTAL | 757215.3333 | 1.0214 | 773402.8176 | 0.97907 | 16187.4843 | 0.96207
MOORE HAVEN
Transmission | 2975.1667 | 1.0214 | 3038.7687 | 0.97907 | 63.6021 | 0
TOTAL | 2975.1667 | 1.0214 | 3038.7687 | 0.97907 | 63.6021 | 0.96207
NEW SMRYNA BCH
Transmission | 35416.6667 | 1.0214 | 36173.7918 | 0.97907 | 757.1251 | 0
TOTAL | 35416.6667 | 1.0214 | 36173.7918 | 0.97907 | 757.1251 | 0.96207
NEW SMRYNA BCH (PEAK)
Transmission | 1250 | 1.0214 | 1276.7221 | 0.97907 | 26.7221 | 0
TOTAL | 1250 | 1.0214 | 1276.7221 | 0.97907 | 26.7221 | 0.96207
QUINCY
Transmission | 11500 | 1.0214 | 11745.843 | 0.97907 | 245.843 | 0
TOTAL | 11500 | 1.0214 | 11745.843 | 0.97907 | 245.843 | 0.96207
SEMINOLE
Transmission | 166666.6667 | 1.0214 | 170229.6083 | 0.97907 | 3562.9416 | 0
TOTAL | 166666.6667 | 1.0214 | 170229.6083 | 0.97907 | 3562.9416 | 0.96207
WAUCHULA
Transmission | 11856.9167 | 1.0214 | 12110.3897 | 0.97907 | 253.473 | 0
TOTAL | 11856.9167 | 1.0214 | 12110.3897 | 0.97907 | 253.473 | 0.96207
WINTER PARK
Transmission | 49304.4167 | 1.0214 | 50358.4292 | 0.97907 | 1054.0126 | 0
TOTAL | 49304.4167 | 1.0214 | 50358.4292 | 0.97907 | 1054.0126 | 0.96207
TOTAL FERC
TOTAL | 1182989.1667 | 1.0214 | 1208278.6948 | 0.97907 | 25289.5282 | 0.96207
TOTAL COMPANY
TOTAL | 19104646.8333 | 1.0616 | 20282375.2685 | 0.94193 | 1177728.4352 | 1
COMPANY USE
TOTAL | 20084.7997 | 1.0654 | 21397.787 | 0.93864 | 1312.9873 | 0
TOTAL FPL
TOTAL | 19124731.6331 | 1.0617 | 20303773.0555 | 0.94193 | 1179041.4224 | 0

## LLS_Energy_Losses_by_Rate_Clas
FPL 003538
20190015-EG
RATE CLASS | DELIVERED MWH @ MTR | LOSS EXPANSION FACTORS | DELIVERED MWH @ GEN | DELIVERED EFFICIENCY | LOSSES | COST RECOVERY MULTIPLIER
CILC-1D
Primary | 1046652.8611 | 1.0292 | 1077179.307 | 0.97166 | 30526.4459 | 0
Secondary | 1552431.3327 | 1.0511 | 1631793.9102 | 0.95136 | 79362.5775 | 0
TOTAL | 2599084.1938 | 1.0423 | 2708973.2172 | 0.95944 | 109889.0234 | 0.9943
CILC-1G
Primary | 2139.044 | 1.0292 | 2201.4308 | 0.97166 | 62.3869 | 0
Secondary | 101931.7675 | 1.0511 | 107142.6697 | 0.95136 | 5210.9022 | 0
TOTAL | 104070.8115 | 1.0507 | 109344.1005 | 0.95177 | 5273.2891 | 1.0023
CILC-1T
Transmission | 1377840.4271 | 1.0172 | 1401533.6216 | 0.98309 | 23693.1944 | 0
TOTAL | 1377840.4271 | 1.0172 | 1401533.6216 | 0.98309 | 23693.1944 | 0.97037
GS(T)-1
Secondary | 6226810.903 | 1.0511 | 6545134.6525 | 0.95136 | 318323.7496 | 0
TOTAL | 6226810.903 | 1.0511 | 6545134.6525 | 0.95136 | 318323.7496 | 1.0027
GSCU-1
Secondary | 68852.2332 | 1.0511 | 72372.0608 | 0.95136 | 3519.8276 | 0
TOTAL | 68852.2332 | 1.0511 | 72372.0608 | 0.95136 | 3519.8276 | 1.0027
GSD(T)-1
Primary | 71650.5962 | 1.0292 | 73740.3417 | 0.97166 | 2089.7454 | 0
Secondary | 26222255.8289 | 1.0511 | 27562776.1895 | 0.95136 | 1340520.3606 | 0
TOTAL | 26293906.4251 | 1.0511 | 27636516.5312 | 0.95142 | 1342610.1061 | 1.0027
GSLD(T)-1
Primary | 367510.0557 | 1.0292 | 378228.7727 | 0.97166 | 10718.717 | 0
Secondary | 9866969.8345 | 1.0511 | 10371383.8729 | 0.95136 | 504414.0385 | 0
TOTAL | 10234479.8901 | 1.0503 | 10749612.6456 | 0.95208 | 515132.7555 | 1.002
GSLD(T)-2
Primary | 988939.4553 | 1.0292 | 1017782.6447 | 0.97166 | 28843.1895 | 0
Secondary | 1602894.0204 | 1.0511 | 1684836.3248 | 0.95136 | 81942.3044 | 0
TOTAL | 2591833.4756 | 1.0427 | 2702618.9696 | 0.95901 | 110785.4939 | 0.99474
GSLD(T)-3
Transmission | 196919.1779 | 1.0172 | 200305.3787 | 0.98309 | 3386.2008 | 0
TOTAL | 196919.1779 | 1.0172 | 200305.3787 | 0.98309 | 3386.2008 | 0.97037
MET
Primary | 82758.1965 | 1.0292 | 85171.9038 | 0.97166 | 2413.7073 | 0
TOTAL | 82758.1965 | 1.0292 | 85171.9038 | 0.97166 | 2413.7073 | 0.98179
OL-1
Secondary | 98627.6116 | 1.0511 | 103669.6005 | 0.95136 | 5041.9888 | 0
TOTAL | 98627.6116 | 1.0511 | 103669.6005 | 0.95136 | 5041.9888 | 1.0027
OS-2
Primary | 10908.6923 | 1.0292 | 11226.8528 | 0.97166 | 318.1605 | 0
TOTAL | 10908.6923 | 1.0292 | 11226.8528 | 0.97166 | 318.1605 | 0.98179
RS(T)-1
Secondary | 57965912.3766 | 1.0511 | 60929215.2393 | 0.95136 | 2963302.8627 | 0
TOTAL | 57965912.3766 | 1.0511 | 60929215.2393 | 0.95136 | 2963302.8627 | 1.0027
SL-1
Secondary | 524367.2447 | 1.0511 | 551173.6709 | 0.95136 | 26806.4263 | 0
TOTAL | 524367.2447 | 1.0511 | 551173.6709 | 0.95136 | 26806.4263 | 1.0027
SL-1M
Secondary | 935.7772 | 1.0511 | 983.6155 | 0.95136 | 47.8383 | 0
TOTAL | 935.7772 | 1.0511 | 983.6155 | 0.95136 | 47.8383 | 1.0027
SL-2
Secondary | 31177.7261 | 1.0511 | 32771.5774 | 0.95136 | 1593.8513 | 0
TOTAL | 31177.7261 | 1.0511 | 32771.5774 | 0.95136 | 1593.8513 | 1.0027
SL-2M
Secondary | 133.9578 | 1.0511 | 140.806 | 0.95136 | 6.8481 | 0
TOTAL | 133.9578 | 1.0511 | 140.806 | 0.95136 | 6.8481 | 1.0027
SST-DST
Primary | 8780.4782 | 1.0292 | 9036.5676 | 0.97166 | 256.0895 | 0
TOTAL | 8780.4782 | 1.0292 | 9036.5676 | 0.97166 | 256.0895 | 0.98179
SST-TST
Transmission | 96194.7607 | 1.0172 | 97848.9154 | 0.98309 | 1654.1547 | 0
TOTAL | 96194.7607 | 1.0172 | 97848.9154 | 0.98309 | 1654.1547 | 0.97037
TOTAL FPSC
TOTAL | 108513594.359 | 1.0501 | 113947649.9268 | 0.95231 | 5434055.5678 | 1.0017
FKEC
Transmission | 903640.6922 | 1.0172 | 919179.5995 | 0.98309 | 15538.9073 | 0
TOTAL | 903640.6922 | 1.0172 | 919179.5995 | 0.98309 | 15538.9073 | 0.97037
LCEC
Transmission | 580664.5817 | 1.0172 | 590649.6268 | 0.98309 | 9985.0451 | 0
TOTAL | 580664.5817 | 1.0172 | 590649.6268 | 0.98309 | 9985.0451 | 0.97037
MDCSWM
Transmission | 4894391.0511 | 1.0172 | 4978554.4683 | 0.98309 | 84163.4172 | 0
TOTAL | 4894391.0511 | 1.0172 | 4978554.4683 | 0.98309 | 84163.4172 | 0.97037
TOTAL FERC
TOTAL | 6378696.325 | 1.0172 | 6488383.6946 | 0.98309 | 109687.3696 | 0.97037
TOTAL COMPANY
TOTAL | 114892290.684 | 1.0483 | 120436033.6214 | 0.95397 | 5543742.9374 | 1
COMPANY USE
TOTAL | 126388 | 1.0511 | 132849.1408 | 0.95136 | 6461.1408 | 0
TOTAL FPL
TOTAL | 115018678.684 | 1.0483 | 120568882.7622 | 0.95397 | 5550204.0782 | 0

## LLS_GNCP_Demand_Losses_by_Rate
FPL 003539
20190015-EG
RATE CLASS | GNCP DEMAND @ MTR | LOSS EXPANSION FACTORS | GNCP DEMAND @ GEN | DELIVERED EFFICIENCY | LOSSES | COST RECOVERY MULTIPLIER
CILC-1D
Primary | 152357.8345 | 1.0426 | 158844.8713 | 0.95916 | 6487.0369 | 0
Secondary | 219706.1655 | 1.0756 | 236308.7622 | 0.92974 | 16602.5967 | 0
TOTAL | 372064 | 1.0621 | 395153.6336 | 0.94157 | 23089.6336 | 0.98801
CILC-1G
Primary | 354.0541 | 1.0426 | 369.1288 | 0.95916 | 15.0748 | 0
Secondary | 16499.9459 | 1.0756 | 17746.8019 | 0.92974 | 1246.856 | 0
TOTAL | 16854 | 1.0749 | 18115.9308 | 0.93034 | 1261.9308 | 0.99993
GS(T)-1
Secondary | 1344014 | 1.0756 | 1445577.4784 | 0.92974 | 101563.4784 | 0
TOTAL | 1344014 | 1.0756 | 1445577.4784 | 0.92974 | 101563.4784 | 1.0006
GSCU-1
Secondary | 11346 | 1.0756 | 12203.3863 | 0.92974 | 857.3863 | 0
TOTAL | 11346 | 1.0756 | 12203.3863 | 0.92974 | 857.3863 | 1.0006
GSD(T)-1
Primary | 13112.2036 | 1.0426 | 13670.4903 | 0.95916 | 558.2867 | 0
Secondary | 4690344.7964 | 1.0756 | 5044781.3815 | 0.92974 | 354436.5851 | 0
TOTAL | 4703457 | 1.0755 | 5058451.8718 | 0.92982 | 354994.8718 | 1.0005
GSLD(T)-1
Primary | 74513.9849 | 1.0426 | 77686.6144 | 0.95916 | 3172.6295 | 0
Secondary | 1864004.0151 | 1.0756 | 2004861.7231 | 0.92974 | 140857.708 | 0
TOTAL | 1938518 | 1.0743 | 2082548.3375 | 0.93084 | 144030.3375 | 0.9994
GSLD(T)-2
Primary | 151966.7811 | 1.0426 | 158437.1679 | 0.95916 | 6470.3867 | 0
Secondary | 245712.2189 | 1.0756 | 264280.0222 | 0.92974 | 18567.8033 | 0
TOTAL | 397679 | 1.063 | 422717.1901 | 0.94077 | 25038.1901 | 0.98885
MET
Primary | 13844 | 1.0426 | 14433.4448 | 0.95916 | 589.4448 | 0
TOTAL | 13844 | 1.0426 | 14433.4448 | 0.95916 | 589.4448 | 0.96989
OL-1
Secondary | 27062 | 1.0756 | 29107.0017 | 0.92974 | 2045.0017 | 0
TOTAL | 27062 | 1.0756 | 29107.0017 | 0.92974 | 2045.0017 | 1.0006
OS-2
Primary | 11676 | 1.0426 | 12173.1365 | 0.95916 | 497.1365 | 0
TOTAL | 11676 | 1.0426 | 12173.1365 | 0.95916 | 497.1365 | 0.96989
RS(T)-1
Secondary | 13259240 | 1.0756 | 14261204.6637 | 0.92974 | 1001964.6637 | 0
TOTAL | 13259240 | 1.0756 | 14261204.6637 | 0.92974 | 1001964.6637 | 1.0006
SL-1
Secondary | 224314 | 1.0756 | 241264.7982 | 0.92974 | 16950.7982 | 0
TOTAL | 224314 | 1.0756 | 241264.7982 | 0.92974 | 16950.7982 | 1.0006
SL-1M
Secondary | 577 | 1.0756 | 620.6023 | 0.92974 | 43.6023 | 0
TOTAL | 577 | 1.0756 | 620.6023 | 0.92974 | 43.6023 | 1.0006
SL-2
Secondary | 4197 | 1.0756 | 4514.1559 | 0.92974 | 317.1559 | 0
TOTAL | 4197 | 1.0756 | 4514.1559 | 0.92974 | 317.1559 | 1.0006
SL-2M
Secondary | 49 | 1.0756 | 52.7028 | 0.92974 | 3.7028 | 0
TOTAL | 49 | 1.0756 | 52.7028 | 0.92974 | 3.7028 | 1.0006
SST-DST
Primary | 3396 | 1.0426 | 3540.5937 | 0.95916 | 144.5937 | 0
TOTAL | 3396 | 1.0426 | 3540.5937 | 0.95916 | 144.5937 | 0.96989
TOTAL FPSC
TOTAL | 22328287 | 1.0749 | 24001678.928 | 0.93028 | 1673391.928 | 1
TOTAL COMPANY
TOTAL | 22328287 | 1.0749 | 24001678.928 | 0.93028 | 1673391.928 | 1
COMPANY USE
TOTAL | 22608.2999 | 1.0756 | 24316.7476 | 0.92974 | 1708.4477 | 0
TOTAL FPL
TOTAL | 22350895.2999 | 1.0749 | 24025995.6756 | 0.93028 | 1675100.3757 | 0