## Table Staff-36
Florida Power & Light Company
Docket No. 150196-EI
Staff's Second Set of Interrogatories
Interrogatory No. 36
Attachment No. 1
Tab 1 of 1
Table Staff-36
| Plant Specifications for Generation Options in Exhibit SRS-3 | [13 empty] | Plant Specifications for Generation Options in Exhibit SRS-3 (cont)
[16 empty] | Emission Rates |  |  |  | Linear Facilities
| Site | Manufacturer | Model of CT | Generating Technology1 | Capacity Summer Peak (95oF) MW | Capacity Winter Peak (35oF) MW | Planned Outage Factor (%) | Forced Outage Factor (%) | Equivalent Availability Factor (%) | Resulting Capacity Factor (Approx. %) | Heat Rate (Base @ 75oF, 100%) BTU/kWh | Annual Fixed O&M2 (2019$) | Annual Variable O&M3 ($/MWh) | Primary Fuel | Backup Fuel | NOx Emission Rates (lb/mmbtu) | CO Emission Rates (lb/mmbtu) | SO2 Emission Rates (lb/mmbtu) | Primary Water Source | Gas | Transmission
1 | Okeechobee | GE | 7HA.02 | 3x3x1 | 1523 | 1577 | 3.5 | 1 | 95.5 | 80 | 6419 | 22.266 | 0.26457 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
2 | Okeechobee | Mitsubishi | J | 4x4x1 | 1749 | 1954 | 3.5 | 1 | 95.5 | 80 | 6340 | 25.4093 | 0.26828 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
3 | Okeechobee | GE | 7HA.02 | 3x3x1 | 1424 | 1477 | 3.5 | 1 | 95.5 | 80 | 6391 | 23.814 | 0.28297 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
4 | Okeechobee | Mitsubishi | J | 3x3x1 | 1411 | 1561 | 3.5 | 1 | 95.5 | 80 | 6370 | 24.8506 | 0.26153 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
5 | Okeechobee | Mitsubishi | J | 3x3x1 | 1311 | 1465 | 3.5 | 1 | 95.5 | 80 | 6342 | 26.7462 | 0.28148 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
6 | Okeechobee | GE | 7FA.05 | 7x0x0 | 1419 | 1557 | 3 | 1 | 96 | 5 | 10071 | 8.8141 | 0.23062 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
7 | Okeechobee | GE | 7FA.05 | 6x0x0 | 1216 | 1334 | 3 | 1 | 96 | 5 | 10071 | 8.4989 | 0.26286 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | Floridan Aquifer | New Pipeline Lateral | See Note 4
8 | Putnam | GE | 7HA.02 | 3x3x1 | 1524 | 1577 | 3.5 | 1 | 95.5 | 80 | 6419 | 22.266 | 0.20394 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | St. Johns River | New Pipeline and Compression | See Note 4
9 | Putnam | GE | 7HA.02 | 3x3x1 | 1424 | 1496 | 3.5 | 1 | 95.5 | 80 | 6391 | 23.814 | 0.21826 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | St. Johns River | New Pipeline and Compression | See Note 4
10 | Putnam | Siemens | H | 3x3x1 | 1321 | 1435 | 3.5 | 1 | 95.5 | 80 | 6501 | 20.0488 | 0.23528 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | St. Johns River | New Pipeline and Compression | See Note 4
11 | Putnam | Siemens | H | 3x3x1 | 1220 | 1338 | 3.5 | 1 | 95.5 | 80 | 6473 | 21.7085 | 0.25476 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | St. Johns River | New Pipeline and Compression | See Note 4
12 | Putnam | Mitsubishi | J | 3x3x1 | 1312 | 1465 | 3.5 | 1 | 95.5 | 80 | 6342 | 29.0614 | 0.23689 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | St. Johns River | New Pipeline and Compression | See Note 4
13 | Putnam | GE | 7FA.05 | 5x0x0 | 1014 | 1112 | 3 | 1 | 96 | 5 | 10071 | 8.6058 | 0.075053 | Natural Gas | Light Fuel Oil | 0.01 | 0.011 | 0.006 | St. Johns River | New Pipeline and Compression | See Note 4
Notes:
1 Generating technology provided describes the number of advanced combustion turbines followed by the number of heat recovery
steam generators followed by the number of steam turbines (e.g., Row 1 is an Okeechobee generating technology with three (3)
advanced combustion turbines, three (3) heat recovery steam generators, and a single (1) steam turbine)
2 Annual fixed O&M value includes capital replacement costs and fixed O&M presented as a levelized value in 2019 $
3 Variable O&M represents the value for 2019
4 No new linear transmission facilities