## 2015 Annual Cable Losses Energy
OPC 012911
FPL RC-16
2015 FCST (RC2016) - ESTIMATED PRIMARY LINE (CABLE) ENERGY LOSSES
[10 empty] | 2015 FCST NEL = | 119951.959 | GWH |  | 1989 NEL = | 69956 | GWH
|  |  | Estimated Annual Cable Losses (GWH) = |  |  |  | 655.2042 |  |  | Cable Losses % NEL = | 0.54622 |  |  | Cable Losses % NEL = | 1.2994
CL = Conductor losses at peak (hour, day, month - mW); conductor losses are proportional to the square of the load current (load). Conductor losses vary with load over time.
CLE = mwh associated to conductor losses: 1 mW at peak = 1 mW p.u. = 1 mWh at the peak hour, varying over time.
CLEF = Hourly factor for energy on conductors. Changes with time over a daily/monthly load cycle. CLEF is the square of the p.u. load.
More generally:
| HL (Hourly Load p.u.) | CLEF (HL^2) | CLEF*CL (Mwh)
| 1 | 1 | 1*CL
| 0.98814 | 0.97642 | 0.9764*CL | [10 empty] | CONDUCTOR LOSSES (CL MW)
| 0.96386 | 0.92902 | 0.9290*CL | [10 empty] | Total | 196
| 0.91823 | 0.84314 | 0.8431*CL
| . | . | .
| . | . | .
| . | . | .
Hourly Energy (CLE) = CLEF*CL
Peak = Summer Peak (April to October)
Hourly Energy
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | MWH/Day
2015-01-01 | 38.1988 | 35.4699 | 31.8934 | 29.5619 | 28.5744 | 29.0559 | 30.5872 | 31.8791 | 37.926 | 48.5465 | 59.6735 | 67.9541 | 73.1094 | 75.187 | 74.5639 | 72.6672 | 70.7311 | 72.3875 | 79.5873 | 75.2637 | 68.947 | 62.2377 | 53.8507 | 44.153 | 1292.0062
2015-01-02 | 35.9454 | 31.1275 | 28.0836 | 26.6823 | 26.2922 | 27.9098 | 34.5431 | 40.4484 | 50.0812 | 62.7269 | 73.9326 | 82.1432 | 88.2759 | 92.6734 | 94.6786 | 93.6611 | 89.9214 | 88.359 | 95.0477 | 87.9439 | 78.8228 | 69.241 | 59.2449 | 48.5289 | 1506.3148
2015-01-03 | 39.2601 | 33.2341 | 29.7477 | 28.1237 | 27.9899 | 29.8718 | 35.7488 | 41.7522 | 49.3419 | 56.2784 | 60.4469 | 61.8297 | 61.8396 | 60.7025 | 59.5662 | 58.8663 | 58.5082 | 64.2367 | 73.3689 | 70.8268 | 65.7541 | 59.8688 | 52.3319 | 44.2537 | 1223.749
2015-01-04 | 37.6077 | 33.4603 | 31.0923 | 30.0932 | 30.218 | 31.7366 | 35.1022 | 39.8002 | 47.618 | 55.1094 | 59.7418 | 60.7813 | 59.8004 | 58.2476 | 56.2879 | 54.4922 | 54.8659 | 60.5353 | 65.7234 | 62.1978 | 57.8433 | 52.7165 | 46.6208 | 39.9039 | 1161.5959
2015-01-05 | 33.5773 | 29.3768 | 26.8718 | 25.4823 | 25.2025 | 26.3959 | 29.3289 | 32.9072 | 40.4564 | 48.5553 | 58.1705 | 64.5408 | 67.975 | 69.073 | 68.9785 | 67.694 | 65.9386 | 67.4137 | 75.9227 | 71.5302 | 65.6006 | 57.1155 | 47.9323 | 38.9678 | 1205.0077
2015-01-06 | 30.9024 | 26.8587 | 24.5849 | 23.7958 | 24.4223 | 28.2109 | 36.9137 | 43.0105 | 48.9434 | 57.5171 | 67.0719 | 73.5096 | 78.7779 | 81.663 | 80.7637 | 77.3604 | 74.2044 | 78.9574 | 87.2463 | 82.4297 | 72.1834 | 60.5058 | 51.4855 | 42.3667 | 1353.6855
2015-01-07 | 35.9909 | 32.683 | 31.8648 | 32.5171 | 35.6582 | 43.2926 | 59.5369 | 72.6241 | 78.8228 | 82.6133 | 81.1046 | 76.9388 | 73.0446 | 69.2831 | 66.3908 | 66.2056 | 70.1692 | 83.6152 | 100.2528 | 101.4453 | 97.0907 | 86.2932 | 73.6938 | 62.2177 | 1613.3491
2015-01-08 | 54.0548 | 50.0097 | 48.5993 | 47.9761 | 49.4751 | 56.4776 | 70.8268 | 78.3413 | 77.5717 | 77.5717 | 76.6178 | 72.7965 | 67.7252 | 63.0876 | 59.2254 | 57.7377 | 58.8275 | 65.529 | 73.7915 | 71.1248 | 65.1104 | 55.9283 | 46.1476 | 36.8447 | 1481.3979
2015-01-09 | 30.0516 | 26.8129 | 25.3486 | 24.8234 | 25.8664 | 30.4198 | 40.8349 | 48.4937 | 51.0333 | 55.7584 | 59.1185 | 60.9784 | 61.1462 | 60.2506 | 59.1185 | 58.721 | 59.4297 | 65.1817 | 74.335 | 72.5596 | 66.9684 | 58.5468 | 49.2 | 39.4345 | 1204.4321
2015-01-10 | 31.6868 | 27.2266 | 24.8172 | 23.9377 | 24.4597 | 28.2378 | 37.7473 | 44.8693 | 50.664 | 58.1416 | 64.4292 | 68.6013 | 70.9757 | 72.7857 | 72.8504 | 72.452 | 71.8939 | 72.7534 | 80.6161 | 76.1761 | 69.3778 | 61.334 | 53.499 | 45.1915 | 1304.7241
2015-01-11 | 36.3708 | 31.3323 | 28.1371 | 26.6496 | 26.344 | 27.7898 | 31.1698 | 35.7261 | 47.0444 | 60.7911 | 71.3594 | 78.3524 | 83.7539 | 87.1166 | 88.5016 | 87.7426 | 84.0085 | 81.025 | 85.9298 | 79.6211 | 71.7762 | 63.0174 | 54.5388 | 45.7622 | 1413.8607
2015-01-12 | 37.1752 | 31.63 | 28.3924 | 26.591 | 25.7124 | 26.2468 | 28.4193 | 31.4313 | 39.4265 | 48.5817 | 55.6547 | 59.9177 | 63.8021 | 66.3187 | 67.0305 | 66.1953 | 64.2671 | 62.9372 | 70.5294 | 67.8188 | 61.8099 | 53.8599 | 45.4892 | 36.6456 | 1165.8827
2015-01-13 | 30.0516 | 26.6757 | 25.1708 | 25.0189 | 26.4089 | 31.9862 | 43.9182 | 51.9579 | 55.3253 | 59.9861 | 64.2569 | 67.5382 | 70.6037 | 73.0122 | 74.5749 | 75.7027 | 75.0447 | 76.3747 | 86.1407 | 83.9274 | 75.4501 | 64.4393 | 53.3789 | 42.1367 | 1359.0811
2015-01-14 | 33.4676 | 28.6758 | 26.2727 | 25.0822 | 25.5525 | 29.8028 | 40.1276 | 47.0011 | 52.9001 | 61.5123 | 69.1675 | 73.824 | 76.2643 | 76.3857 | 75.3404 | 72.5596 | 71.8083 | 75.187 | 84.4838 | 81.9944 | 74.4985 | 64.3785 | 52.8266 | 41.638 | 1360.7514
2015-01-15 | 33.0959 | 28.7502 | 26.4414 | 25.6804 | 26.2016 | 30.9938 | 42.2516 | 49.5996 | 52.3411 | 56.089 | 58.0838 | 58.2283 | 56.6391 | 55.0907 | 53.3882 | 52.5881 | 53.4251 | 59.5174 | 67.975 | 66.0207 | 60.9192 | 53.3605 | 44.4388 | 35.5451 | 1146.6646
2015-01-16 | 29.5757 | 26.617 | 25.7701 | 26.0853 | 27.9699 | 34.7662 | 49.3863 | 60.2016 | 62.148 | 62.8571 | 62.837 | 60.9685 | 58.1608 | 55.2596 | 52.7899 | 51.5943 | 52.8174 | 60.5353 | 78.6883 | 82.4526 | 81.5831 | 76.3857 | 68.3609 | 59.947 | 1307.7576
2015-01-17 | 54.3338 | 52.195 | 52.5057 | 54.3338 | 58.5178 | 69.8204 | 92.2483 | 107.3171 | 105.1039 | 94.4206 | 83.3152 | 72.6457 | 64.338 | 57.9876 | 53.7395 | 51.4674 | 51.876 | 58.4599 | 69.8732 | 69.01 | 66.2467 | 60.9488 | 55.1094 | 48.4322 | 1604.2459
2015-01-18 | 42.4242 | 39.8799 | 39.1415 | 39.4583 | 41.2071 | 45.3445 | 52.7899 | 63.1177 | 70.5825 | 71.4341 | 68.7793 | 63.4896 | 58.1512 | 53.5544 | 49.6352 | 47.5657 | 47.5919 | 53.1576 | 66.504 | 68.9995 | 68.989 | 67.8604 | 64.9168 | 60.8207 | 1345.3951
2015-01-19 | 57.9683 | 57.0105 | 57.7473 | 59.9666 | 63.6206 | 69.7571 | 79.8241 | 92.8681 | 100.7594 | 94.5803 | 81.7658 | 70.1692 | 61.542 | 55.5511 | 50.9521 | 47.3916 | 46.3538 | 49.3863 | 60.6336 | 59.8883 | 57.0773 | 51.5853 | 46.2764 | 39.2918 | 1511.9668
2015-01-20 | 34.5431 | 32.4019 | 31.9219 | 32.5315 | 35.1396 | 40.6173 | 50.4663 | 60.7222 | 64.6829 | 62.8871 | 60.4862 | 58.2187 | 55.5981 | 53.6192 | 52.1311 | 51.3134 | 51.4583 | 54.9876 | 65.5494 | 64.6728 | 59.0603 | 51.2953 | 42.4819 | 33.9517 | 1200.7377
2015-01-21 | 28.1573 | 25.3359 | 24.2167 | 24.2105 | 25.4823 | 30.9446 | 43.0105 | 50.9882 | 52.799 | 53.3605 | 53.9341 | 53.9156 | 53.6932 | 52.7073 | 51.8487 | 50.9792 | 51.3134 | 55.9472 | 65.6517 | 65.2838 | 59.9666 | 51.9306 | 43.1597 | 35.0274 | 1103.8638
2015-01-22 | 29.2059 | 27.1542 | 26.826 | 27.8564 | 31.036 | 39.6092 | 57.431 | 70.2539 | 68.2669 | 70.7311 | 68.989 | 65.5596 | 61.7503 | 57.4597 | 54.5295 | 52.9736 | 54.0362 | 61.4825 | 79.6098 | 84.9839 | 84.8209 | 79.6775 | 71.9582 | 63.2483 | 1389.4495
2015-01-23 | 58.2861 | 57.1155 | 58.3537 | 61.1561 | 66.5247 | 80.6275 | 107.6183 | 122.0556 | 113.7445 | 100.5312 | 88.7156 | 76.4851 | 66.9581 | 59.4979 | 54.7349 | 52.3685 | 52.5607 | 58.2187 | 72.9151 | 75.7687 | 73.3905 | 66.9168 | 57.364 | 48.5729 | 1730.4806
2015-01-24 | 42.6055 | 40.5931 | 40.4644 | 41.5647 | 44.9032 | 54.7443 | 74.3786 | 85.8595 | 85.7425 | 81.9487 | 77.2049 | 70.5719 | 64.927 | 60.2604 | 56.5536 | 54.4642 | 55.0063 | 60.0547 | 72.1083 | 72.409 | 69.178 | 63.8929 | 57.5459 | 50.0991 | 1477.0806
2015-01-25 | 44.2874 | 41.4914 | 40.3921 | 40.7059 | 42.1942 | 45.7537 | 52.3411 | 61.2253 | 70.148 | 69.62 | 64.4191 | 58.9632 | 54.7723 | 51.5671 | 49.1646 | 47.3829 | 46.6122 | 48.9169 | 57.1823 | 56.2974 | 52.5332 | 48.0987 | 42.3584 | 36.249 | 1222.6763
2015-01-26 | 31.3676 | 28.3385 | 27.0884 | 26.5649 | 26.9636 | 28.8587 | 32.6324 | 38.1988 | 46.733 | 51.4493 | 53.6377 | 53.4066 | 53.2774 | 53.1576 | 52.4508 | 51.7033 | 51.558 | 54.1942 | 62.9673 | 62.6669 | 57.211 | 49.8936 | 42.0056 | 33.6505 | 1069.976
2015-01-27 | 27.4578 | 24.0801 | 22.6694 | 22.2981 | 23.5622 | 28.3116 | 39.5853 | 46.6726 | 49.7866 | 53.5544 | 57.9972 | 61.008 | 63.5198 | 65.621 | 66.5968 | 67.8396 | 68.4027 | 69.4409 | 78.0062 | 76.9942 | 69.136 | 58.1994 | 47.1484 | 36.4089 | 1224.2973
2015-01-28 | 28.4597 | 24.5097 | 22.6875 | 21.983 | 22.8563 | 27.3454 | 37.7706 | 45.183 | 48.6874 | 53.6099 | 58.9244 | 62.817 | 66.535 | 69.7043 | 72.0761 | 73.9 | 74.5312 | 74.826 | 82.4182 | 81.0477 | 73.6938 | 62.2277 | 51.3044 | 40.4082 | 1277.5067
2015-01-29 | 31.9362 | 27.597 | 25.5973 | 24.899 | 25.8535 | 30.8884 | 41.9893 | 50.3497 | 54.1849 | 59.6344 | 63.8323 | 67.4137 | 51.7669 | 66.8031 | 65.3961 | 65.9592 | 68.0479 | 73.6721 | 81.0591 | 79.2046 | 74.1718 | 65.1715 | 54.9314 | 44.2958 | 1294.6552
2015-01-30 | 37.1983 | 33.2341 | 31.3323 | 30.9235 | 32.3803 | 38.3473 | 52.1585 | 61.5519 | 66.5143 | 71.3914 | 74.1391 | 73.7806 | 72.2049 | 70.3704 | 68.3504 | 67.1961 | 67.975 | 72.7103 | 81.4577 | 80.0613 | 73.8349 | 65.1817 | 54.0177 | 43.5507 | 1419.8626
2015-01-31 | 36.4623 | 32.6396 | 31.1346 | 30.5034 | 31.4809 | 37.0367 | 49.7153 | 58.1897 | 61.7602 | 66.4834 | 70.0317 | 72.0332 | 72.452 | 71.9154 | 70.9225 | 71.4982 | 70.678 | 71.9904 | 78.3077 | 75.8347 | 69.2726 | 61.3538 | 52.744 | 43.5757 | 1388.016
2015-02-01 | 35.8244 | 30.9938 | 28.1371 | 26.6888 | 26.4284 | 27.6966 | 31.191 | 36.615 | 47.4264 | 58.8372 | 67.1132 | 71.8725 | 75.4831 | 77.6941 | 79.0922 | 79.5873 | 78.3748 | 75.4282 | 78.8677 | 75.7907 | 68.0479 | 59.8102 | 51.4946 | 42.721 | 1331.216
2015-02-02 | 34.878 | 30.0308 | 27.1212 | 25.5525 | 25.0126 | 25.5142 | 27.69 | 31.6868 | 42.9939 | 54.8939 | 62.9573 | 68.3295 | 75.3076 | 80.4348 | 84.1475 | 85.8829 | 85.6724 | 82.3379 | 82.2806 | 74.7604 | 68.0166 | 64.0546 | 58.8759 | 47.1571 | 1345.5893
2015-02-03 | 37.6697 | 30.5942 | 28.0367 | 26.9833 | 27.6567 | 32.2439 | 42.556 | 49.5551 | 56.3827 | 65.6927 | 75.7027 | 83.0502 | 88.9895 | 93.7345 | 97.265 | 98.7156 | 96.2585 | 92.9777 | 98.1015 | 95.5657 | 85.0887 | 73.7589 | 60.7813 | 48.1512 | 1585.5121
2015-02-04 | 38.5353 | 33.3654 | 30.4337 | 29.0559 | 29.3562 | 33.5041 | 44.0104 | 50.889 | 57.3257 | 67.2686 | 76.8612 | 84.3098 | 90.3652 | 94.2734 | 96.9414 | 98.4898 | 97.0533 | 93.0752 | 98.2893 | 97.3024 | 88.0268 | 75.8787 | 63.4393 | 50.601 | 1618.6511
2015-02-05 | 40.8753 | 35.0274 | 32.0648 | 30.5523 | 30.8112 | 35.5451 | 46.9145 | 54.0548 | 60.7517 | 71.4875 | 81.5603 | 89.5027 | 94.6663 | 98.3645 | 100.6706 | 99.6087 | 95.4422 | 92.0179 | 96.7176 | 94.1385 | 84.9955 | 73.3364 | 60.3585 | 47.8362 | 1647.3006
2015-02-06 | 38.3395 | 32.4955 | 29.6307 | 28.2109 | 28.6149 | 32.8131 | 43.6507 | 50.592 | 57.3353 | 65.6108 | 73.2607 | 79.1034 | 84.0085 | 88.7037 | 90.7018 | 91.921 | 90.7619 | 89.2996 | 94.4697 | 93.1605 | 84.2286 | 72.818 | 60.1428 | 47.27 | 1547.1436
2015-02-07 | 37.6077 | 32.2439 | 28.8044 | 27.286 | 27.5174 | 31.7437 | 42.2927 | 49.5107 | 54.3897 | 61.0179 | 67.6421 | 74.0956 | 78.0508 | 78.7107 | 83.9737 | 85.4854 | 85.0538 | 83.9506 | 84.4955 | 80.1065 | 73.9 | 64.0647 | 55.5322 | 45.7879 | 1433.2636
2015-02-08 | 37.6853 | 32.0863 | 28.9606 | 27.4446 | 27.3322 | 28.5744 | 32.1579 | 37.5226 | 48.5729 | 61.3538 | 71.8618 | 78.6995 | 83.4305 | 85.7776 | 87.2817 | 86.3401 | 84.2518 | 81.2184 | 83.1193 | 79.2608 | 71.5302 | 63.2483 | 54.7443 | 46.2163 | 1418.6711
2015-02-09 | 38.0117 | 32.4883 | 29.3494 | 27.7765 | 27.4313 | 28.4867 | 31.0501 | 35.207 | 43.484 | 51.8032 | 57.6993 | 60.8699 | 63.8727 | 65.7234 | 66.5453 | 65.8566 | 64.2266 | 63.7314 | 69.7254 | 70.6568 | 63.8929 | 55.3629 | 46.8799 | 37.1906 | 1197.3219
2015-02-10 | 30.0101 | 26.2922 | 24.8234 | 24.5911 | 25.7765 | 31.0149 | 42.7292 | 50.3856 | 53.8599 | 58.344 | 63.5098 | 66.9891 | 70.2962 | 72.9259 | 74.0304 | 75.187 | 75.3953 | 74.5639 | 80.5821 | 82.1088 | 74.1826 | 63.5803 | 52.0946 | 40.8995 | 1334.1726
2015-02-11 | 32.9 | 28.3453 | 26.2598 | 25.5909 | 26.4609 | 31.4455 | 43.2261 | 50.871 | 54.9876 | 60.7419 | 66.1542 | 71.3274 | 75.8237 | 79.9032 | 82.4182 | 85.0538 | 85.8244 | 84.3214 | 88.918 | 89.5027 | 82.1088 | 68.7165 | 55.815 | 43.4257 | 1440.1417
2015-02-12 | 33.9443 | 29.1854 | 26.4479 | 25.3422 | 25.9242 | 30.2667 | 41.118 | 47.775 | 53.259 | 60.7025 | 67.5798 | 73.3905 | 77.8612 | 81.606 | 82.5788 | 81.0705 | 79.0585 | 79.4296 | 86.9398 | 85.0421 | 77.2271 | 66.3085 | 52.4234 | 39.9917 | 1404.4726
2015-02-13 | 32.0076 | 27.4181 | 25.3995 | 24.635 | 25.5206 | 30.2597 | 41.638 | 49.5551 | 53.9898 | 56.9152 | 59.5954 | 60.555 | 61.087 | 60.9291 | 60.388 | 59.5467 | 58.7113 | 58.7306 | 65.7541 | 68.5804 | 64.2873 | 57.2014 | 48.3443 | 39.1257 | 1190.1748
2015-02-14 | 32.5459 | 29.5139 | 28.5271 | 28.8587 | 31.0289 | 38.5274 | 55.1376 | 67.2375 | 66.9891 | 63.8828 | 61.4231 | 57.3927 | 54.2779 | 52.195 | 50.898 | 50.853 | 50.8169 | 51.776 | 58.4502 | 59.8004 | 55.6076 | 50.1617 | 44.3631 | 37.9027 | 1178.1671
2015-02-15 | 32.7046 | 29.5963 | 28.01 | 27.4379 | 27.6833 | 29.6444 | 33.6725 | 39.7843 | 46.9838 | 51.8942 | 54.7817 | 55.0813 | 53.7395 | 52.3959 | 51.223 | 50.7899 | 50.5471 | 51.1959 | 56.3353 | 57.5746 | 53.6377 | 48.6346 | 43.1016 | 36.4318 | 1062.8812
2015-02-16 | 31.2404 | 28.4732 | 28.117 | 28.4395 | 29.0967 | 32.0505 | 37.6 | 45.8221 | 53.0472 | 55.2502 | 54.1942 | 51.776 | 50.4304 | 49.4573 | 49.0141 | 49.1735 | 49.7153 | 50.7359 | 56.5821 | 58.6919 | 54.0641 | 48.1337 | 42.2188 | 34.9153 | 1068.2395
2015-02-17 | 29.6032 | 26.9111 | 26.053 | 26.3246 | 28.0434 | 33.0305 | 42.1532 | 51.404 | 56.9247 | 59.1088 | 60.1036 | 60.3389 | 60.7025 | 61.3736 | 62.0783 | 63.1077 | 63.6508 | 63.9535 | 69.094 | 70.8374 | 63.9636 | 54.9033 | 44.6412 | 35.5376 | 1213.8424
2015-02-18 | 28.4934 | 24.7731 | 23.5316 | 23.214 | 24.491 | 29.5963 | 41.402 | 49.7242 | 53.0932 | 56.4871 | 59.7418 | 62.4771 | 64.9067 | 67.5382 | 70.0422 | 72.4627 | 73.3364 | 72.0118 | 75.5709 | 77.3271 | 69.736 | 58.8275 | 48.2828 | 37.2831 | 1264.3501
2015-02-19 | 29.6169 | 25.4377 | 23.6543 | 22.9469 | 23.7958 | 28.3654 | 39.268 | 46.2936 | 50.7179 | 56.0039 | 61.6015 | 66.5865 | 70.6249 | 74.6185 | 78.5315 | 82.3494 | 83.2921 | 80.9909 | 83.1078 | 84.0664 | 76.3085 | 65.1511 | 53.3236 | 41.6543 | 1348.3074
2015-02-20 | 32.7552 | 28.0903 | 25.6484 | 24.3911 | 24.7417 | 29.1717 | 39.7843 | 47.0617 | 53.5729 | 61.7106 | 69.8838 | 75.7247 | 81.2867 | 85.7542 | 88.9657 | 91.7878 | 92.1755 | 89.4907 | 92.5883 | 94.1875 | 86.5045 | 75.7907 | 62.9673 | 50.925 | 1504.9604
2015-02-21 | 40.9399 | 34.5208 | 31.3676 | 29.8511 | 29.9409 | 34.0327 | 45.0048 | 52.7532 | 62.9072 | 74.4985 | 85.0654 | 93.2215 | 99.0296 | 102.8753 | 103.35 | 102.2612 | 95.986 | 90.9546 | 93.1361 | 90.3652 | 81.8001 | 71.3167 | 61.7304 | 50.8079 | 1657.7168
2015-02-22 | 41.337 | 34.5802 | 31.1698 | 29.0763 | 28.5406 | 29.2263 | 32.3947 | 38.191 | 51.8851 | 66.0823 | 77.2938 | 86.0235 | 93.1483 | 97.1405 | 98.7156 | 99.4197 | 96.8667 | 90.4253 | 89.3593 | 86.8692 | 77.5272 | 68.1104 | 58.5565 | 48.3179 | 1550.2573
2015-02-23 | 39.4186 | 33.5115 | 29.9686 | 27.9899 | 27.1147 | 27.4313 | 29.3973 | 34.1655 | 46.6553 | 60.7813 | 72.9798 | 82.8661 | 95.0354 | 97.0658 | 98.816 | 100.4046 | 98.904 | 94.8015 | 94.7523 | 95.06 | 86.2463 | 72.7318 | 61.1363 | 48.3179 | 1555.5518
2015-02-24 | 38.0117 | 32.9725 | 29.858 | 28.1371 | 28.3453 | 32.5387 | 41.8421 | 49.4751 | 57.4884 | 67.9646 | 78.3413 | 86.0938 | 94.016 | 99.6214 | 103.1446 | 105.8954 | 103.4399 | 99.6214 | 103.2857 | 104.0317 | 92.1755 | 78.129 | 63.2684 | 49.484 | 1667.1813
2015-02-25 | 38.8417 | 32.9 | 29.5619 | 27.7964 | 27.9298 | 32.1436 | 42.6302 | 49.1912 | 56.4586 | 65.3348 | 73.8132 | 81.2526 | 88.6442 | 95.3435 | 100.734 | 103.9416 | 102.9907 | 97.4645 | 98.565 | 98.6027 | 88.2522 | 74.4658 | 60.9784 | 47.2613 | 1615.0978
2015-02-26 | 36.9829 | 31.1416 | 27.7898 | 26.2922 | 26.4024 | 29.9755 | 39.7444 | 46.6639 | 52.8082 | 60.084 | 70.4022 | 77.7052 | 84.5187 | 89.3235 | 92.4547 | 93.0996 | 90.3052 | 88.3947 | 93.4167 | 93.2581 | 84.7395 | 73.4446 | 60.5746 | 48.2565 | 1517.7786
2015-02-27 | 38.6766 | 33.6066 | 31.036 | 29.8649 | 30.2319 | 34.4244 | 45.2764 | 51.8396 | 55.9472 | 61.2549 | 67.31 | 66.0105 | 72.2371 | 73.1094 | 72.7857 | 71.9904 | 70.275 | 73.0878 | 78.4195 | 79.3846 | 72.8504 | 62.2177 | 50.7809 | 40.4644 | 1363.082
2015-02-28 | 32.6108 | 28.4867 | 26.6692 | 26.1111 | 26.9374 | 31.8506 | 43.609 | 51.1416 | 53.6192 | 55.1657 | 56.4017 | 56.7818 | 56.858 | 57.4788 | 58.1608 | 59.1185 | 59.7223 | 58.9341 | 61.7106 | 63.389 | 58.0645 | 51.413 | 44.0271 | 36.3099 | 1154.5714
2015-03-01 | 30.0308 | 26.3764 | 24.4785 | 23.6727 | 23.9872 | 25.9629 | 29.9893 | 35.8773 | 44.0104 | 49.8044 | 53.6377 | 55.6735 | 57.6514 | 59.6344 | 61.1265 | 63.0676 | 63.3086 | 61.6709 | 61.8099 | 64.1051 | 57.9779 | 51.4674 | 44.4641 | 36.6609 | 1106.4457
2015-03-02 | 30.3919 | 26.728 | 24.7543 | 23.0499 | 22.8019 | 23.7465 | 26.1369 | 30.5593 | 40.1356 | 49.0761 | 55.1469 | 59.7516 | 63.3991 | 67.0719 | 69.6938 | 72.0332 | 72.7965 | 70.997 | 71.7226 | 74.3568 | 66.9684 | 57.5842 | 47.6965 | 37.8638 | 1184.4629
2015-03-03 | 31.2757 | 26.2986 | 23.765 | 22.8502 | 23.3725 | 27.5307 | 37.0059 | 43.6841 | 50.1438 | 57.8337 | 65.4472 | 71.306 | 77.2826 | 83.2921 | 87.2227 | 90.8221 | 91.9089 | 89.2041 | 89.1683 | 90.8582 | 80.6615 | 67.6837 | 54.7256 | 41.9075 | 1425.251
2015-03-04 | 32.7625 | 27.5042 | 24.8234 | 23.5193 | 23.802 | 27.6501 | 37.1752 | 44.1194 | 50.2422 | 57.8433 | 65.1206 | 71.37 | 77.2493 | 82.8891 | 87.8373 | 91.5943 | 92.5154 | 89.6701 | 89.9574 | 91.051 | 82.1088 | 70.54 | 57.4597 | 44.9201 | 1443.7247
2015-03-05 | 35.2895 | 30.2736 | 27.5373 | 26.4414 | 26.8849 | 30.9938 | 41.7359 | 49.0141 | 55.0532 | 64.0647 | 72.366 | 79.8693 | 86.3871 | 90.7138 | 92.4668 | 93.0386 | 90.786 | 87.8847 | 89.8855 | 90.8944 | 83.1308 | 71.819 | 59.1671 | 46.4571 | 1522.1545
2015-03-06 | 36.9905 | 31.9433 | 28.9674 | 27.7565 | 27.9498 | 31.9648 | 42.1696 | 49.4218 | 57.9299 | 67.2789 | 74.6076 | 80.934 | 85.2753 | 84.3794 | 82.3609 | 70.7418 | 65.3859 | 66.257 | 72.3767 | 73.6505 | 67.8396 | 59.0311 | 49.5195 | 39.6967 | 1374.4285
2015-03-07 | 32.0434 | 27.7099 | 25.995 | 25.2216 | 25.9371 | 30.2945 | 40.722 | 47.8537 | 54.763 | 60.7911 | 65.9489 | 68.34 | 69.5989 | 69.7149 | 69.6094 | 69.7043 | 68.7898 | 66.3599 | 67.5901 | 68.4758 | 63.4192 | 55.1282 | 46.9405 | 37.368 | 1258.3192
2015-03-08 | 31.5022 | 27.4644 | 25.6932 | 25.0569 | 25.5398 | 27.2068 | 31.6513 | 38.4021 | 46.0961 | 50.7989 | 52.1858 | 52.0764 | 51.8487 | 51.7578 | 52.46 | 53.5082 | 54.0734 | 53.5544 | 55.1469 | 58.0164 | 53.1208 | 47.496 | 41.0046 | 34.9302 | 1040.5915
2015-03-09 | 28.6352 | 0 | 25.355 | 23.6604 | 23.0742 | 23.839 | 26.0595 | 29.4453 | 34.7438 | 41.8502 | 48.1074 | 50.9882 | 55.0157 | 57.3066 | 59.0117 | 61.5321 | 64.1861 | 65.4778 | 63.55 | 64.1051 | 67.1754 | 59.6735 | 50.5471 | 38.8181 | 1062.1574
2015-03-10 | 30.2597 | 25.1645 | 22.8623 | 22.167 | 22.9833 | 26.8391 | 36.2414 | 44.0691 | 46.5518 | 51.6125 | 58.0357 | 62.0683 | 66.7722 | 69.9894 | 74.9244 | 79.858 | 84.0432 | 84.333 | 80.8545 | 79.937 | 81.3209 | 69.8626 | 58.1223 | 44.8863 | 1323.7584
2015-03-11 | 34.1286 | 28.1908 | 25.1455 | 23.6973 | 23.6912 | 27.4512 | 36.8524 | 44.4136 | 46.5691 | 52.5332 | 58.1319 | 63.5803 | 68.5072 | 73.185 | 77.7164 | 82.9466 | 87.4825 | 88.8346 | 85.7074 | 84.1706 | 85.7308 | 75.516 | 62.6869 | 47.8012 | 1384.6702
2015-03-12 | 37.5458 | 31.2263 | 28.1774 | 26.8784 | 27.1673 | 31.2192 | 41.6543 | 41.199 | 51.5127 | 59.07 | 68.968 | 77.4271 | 84.3098 | 89.1445 | 91.7999 | 97.0284 | 100.2401 | 98.7407 | 93.4778 | 91.3285 | 92.2483 | 81.3095 | 68.4758 | 54.2314 | 1564.3802
2015-03-13 | 42.5148 | 35.4699 | 31.5731 | 29.5894 | 29.0831 | 32.2009 | 41.1666 | 47.3568 | 49.2444 | 55.025 | 59.5369 | 62.2576 | 63.792 | 64.7643 | 65.437 | 66.144 | 67.5278 | 67.1961 | 63.4393 | 62.9873 | 65.5085 | 57.8049 | 48.2214 | 37.8094 | 1245.6505
2015-03-14 | 30.0378 | 26.0402 | 23.9377 | 23.4275 | 24.4597 | 29.1376 | 41.0694 | 50.871 | 53.2037 | 55.3159 | 56.9533 | 57.3544 | 57.1823 | 57.613 | 58.1705 | 59.1963 | 60.6828 | 60.5943 | 58.3054 | 58.1127 | 60.231 | 54.3897 | 46.7589 | 38.6844 | 1141.7294
2015-03-15 | 30.6501 | 26.2922 | 23.7958 | 22.7116 | 22.9167 | 24.4098 | 27.6833 | 33.6286 | 40.9965 | 48.3706 | 54.3897 | 57.9876 | 60.6435 | 62.9072 | 65.6108 | 68.4445 | 71.5729 | 72.119 | 68.6327 | 65.3348 | 66.0823 | 59.0991 | 51.5853 | 41.8584 | 1167.7229
2015-03-16 | 34.0769 | 29.1376 | 26.1757 | 24.5849 | 23.9563 | 24.3599 | 26.4609 | 29.9133 | 37.4762 | 48.5113 | 57.1155 | 63.8424 | 69.4304 | 73.8566 | 78.2742 | 81.3665 | 82.8201 | 82.315 | 78.2965 | 76.7948 | 79.4746 | 71.242 | 61.4924 | 48.9611 | 1309.935
2015-03-17 | 39.1257 | 33.2269 | 30.1278 | 29.0422 | 29.6307 | 34.0474 | 44.1026 | 52.46 | 57.2492 | 67.2893 | 79.081 | 87.6716 | 94.1262 | 97.4894 | 99.2686 | 100.5312 | 100.9116 | 98.1266 | 94.9984 | 96.8543 | 96.7176 | 86.5751 | 75.2747 | 61.0179 | 1684.946
2015-03-18 | 49.6085 | 42.7705 | 39.4821 | 37.9416 | 37.7008 | 41.1909 | 50.7539 | 56.858 | 55.7961 | 59.2643 | 62.747 | 64.6829 | 66.3599 | 68.7165 | 71.8511 | 75.2528 | 78.9125 | 80.0613 | 76.9055 | 75.3624 | 77.2271 | 67.9541 | 56.1932 | 43.1763 | 1436.7693
2015-03-19 | 33.1395 | 27.7698 | 25.0885 | 23.9377 | 24.2416 | 28.117 | 37.6465 | 44.8609 | 48.0111 | 54.4642 | 61.2154 | 66.432 | 69.9894 | 74.444 | 78.9574 | 83.419 | 86.2697 | 86.4458 | 81.8572 | 78.8116 | 80.9227 | 71.6799 | 60.133 | 46.9318 | 1374.7857
2015-03-20 | 36.9445 | 30.9867 | 28.0434 | 26.4414 | 26.5389 | 30.218 | 39.7046 | 47.2265 | 50.6819 | 57.0391 | 64.0748 | 69.5884 | 74.0521 | 78.8452 | 83.3152 | 86.9516 | 89.3713 | 88.5135 | 84.3678 | 81.0364 | 82.7856 | 72.0225 | 59.7613 | 46.9751 | 1435.4858
2015-03-21 | 36.1198 | 29.8649 | 26.2986 | 24.4285 | 24.3848 | 27.2794 | 34.7587 | 42.0548 | 46.9751 | 54.8284 | 63.3488 | 70.4552 | 76.3636 | 82.4756 | 88.4897 | 93.5267 | 95.5286 | 93.5633 | 86.7162 | 81.8115 | 82.2119 | 72.8935 | 63.379 | 52.4508 | 1450.2075
2015-03-22 | 42.3913 | 36.2338 | 32.287 | 30.0308 | 29.1444 | 30.0862 | 33.0741 | 37.1675 | 44.6074 | 57.4118 | 67.975 | 73.9 | 79.2721 | 83.4651 | 86.3988 | 89.6342 | 93.869 | 93.7834 | 88.4065 | 82.0974 | 81.3779 | 71.8939 | 61.2549 | 49.5462 | 1475.3089
2015-03-23 | 39.6728 | 32.9145 | 29.1444 | 27.0424 | 26.0659 | 26.4804 | 28.3991 | 31.4809 | 38.826 | 51.0784 | 63.0174 | 72.8073 | 82.7396 | 91.8362 | 98.2643 | 103.7871 | 106.2206 | 105.9474 | 101.1401 | 95.4299 | 96.3453 | 84.3794 | 71.4448 | 56.7437 | 1561.2079
2015-03-24 | 45.0896 | 37.5535 | 32.8927 | 31.036 | 30.7972 | 33.9517 | 41.2558 | 48.1688 | 53.342 | 61.0771 | 67.5071 | 72.1298 | 73.9435 | 73.7372 | 71.819 | 70.5719 | 70.6993 | 71.4661 | 71.338 | 72.1083 | 70.9757 | 62.3673 | 53.1116 | 42.1532 | 1359.0922
2015-03-25 | 33.8634 | 28.3116 | 25.0569 | 23.913 | 24.2416 | 27.3256 | 35.1696 | 42.0794 | 46.526 | 53.4713 | 58.6145 | 63.9737 | 68.3191 | 71.4127 | 74.335 | 76.6952 | 78.7555 | 78.9238 | 75.7907 | 72.1083 | 73.4554 | 63.8828 | 51.9944 | 39.7444 | 1287.9638
2015-03-26 | 30.2667 | 25.355 | 22.7778 | 21.9179 | 22.5913 | 26.2922 | 35.3646 | 44.0942 | 49.5462 | 52.4417 | 54.791 | 54.8097 | 53.6839 | 52.3228 | 51.4493 | 50.9611 | 51.8396 | 52.4508 | 52.1402 | 55.1282 | 59.6832 | 53.9341 | 45.4551 | 36.9829 | 1056.2795
2015-03-27 | 30.0447 | 26.2727 | 24.4223 | 23.9996 | 24.8297 | 28.6352 | 37.5535 | 44.5652 | 48.2565 | 53.6839 | 56.4491 | 57.8337 | 58.4792 | 59.0117 | 58.9438 | 58.8178 | 59.0311 | 58.8856 | 58.1512 | 60.801 | 63.2985 | 57.1728 | 48.7933 | 39.49 | 1137.4223
2015-03-28 | 31.8862 | 27.1937 | 24.8864 | 23.6973 | 24.167 | 27.3983 | 34.9601 | 41.8993 | 47.2352 | 54.9688 | 63.2583 | 68.4131 | 72.0761 | 74.2588 | 76.0549 | 77.1827 | 76.9831 | 74.6076 | 71.1781 | 71.21 | 72.6241 | 66.3599 | 58.7113 | 49.2178 | 1310.4282
2015-03-29 | 40.8188 | 35.4473 | 32.1507 | 30.5034 | 30.1625 | 31.3111 | 34.4466 | 39.268 | 47.0271 | 58.6919 | 69.6727 | 77.7386 | 81.4007 | 83.3844 | 82.9696 | 80.9681 | 78.3748 | 75.7027 | 71.605 | 70.4552 | 67.6317 | 59.3227 | 52.0035 | 43.251 | 1374.3082
2015-03-30 | 35.237 | 30.0447 | 26.6431 | 25.0316 | 24.4535 | 25.0569 | 27.5373 | 30.7831 | 37.1906 | 46.3882 | 53.3236 | 56.9819 | 58.6822 | 59.9764 | 61.2154 | 62.2676 | 63.3387 | 63.0977 | 60.5648 | 58.8081 | 62.1082 | 54.6509 | 45.3955 | 35.1621 | 1103.9389
2015-03-31 | 27.524 | 23.8143 | 21.5645 | 20.8605 | 21.6761 | 26.5584 | 36.5386 | 43.6758 | 46.2249 | 49.8758 | 53.7858 | 57.0105 | 59.3713 | 62.2377 | 64.8151 | 66.9995 | 68.0375 | 66.9168 | 65.6313 | 67.2168 | 70.1586 | 61.334 | 50.655 | 38.9599 | 1171.4425
2015-04-01 | 30.218 | 25.5525 | 23.3237 | 22.4414 | 23.0439 | 27.1805 | 38.2301 | 45.8563 | 48.7492 | 52.8174 | 56.9152 | 60.5648 | 63.5702 | 67.559 | 72.5165 | 78.2854 | 83.7192 | 85.7074 | 82.6937 | 77.4604 | 78.6771 | 68.685 | 55.1282 | 41.9975 | 1310.8925
2015-04-02 | 32.287 | 26.9242 | 24.2105 | 22.8683 | 23.214 | 27.3784 | 37.4762 | 43.8011 | 46.8886 | 52.9276 | 58.2765 | 63.3287 | 66.8858 | 71.3914 | 78.4979 | 85.1353 | 90.2932 | 92.4911 | 88.3709 | 82.9006 | 84.0085 | 73.6288 | 59.4103 | 45.6341 | 1378.2289
2015-04-03 | 35.0648 | 29.0899 | 25.95 | 24.704 | 24.9747 | 29.322 | 38.8024 | 45.0642 | 49.5107 | 56.5821 | 63.6609 | 69.8204 | 75.5709 | 81.264 | 89.3832 | 94.9246 | 98.9165 | 97.3149 | 92.9046 | 86.6338 | 89.8855 | 78.7667 | 63.7819 | 49.2266 | 1491.1192
2015-04-04 | 37.9805 | 31.7153 | 28.117 | 26.4284 | 26.2404 | 30.0724 | 40.4243 | 46.4915 | 51.4493 | 59.7809 | 68.3295 | 75.7467 | 81.6859 | 87.9913 | 94.2611 | 99.8863 | 104.5348 | 104.0962 | 98.4397 | 88.9657 | 87.0105 | 77.4604 | 65.7234 | 53.1669 | 1565.9982
2015-04-05 | 42.2681 | 35.222 | 30.9797 | 28.4799 | 27.4975 | 27.8431 | 30.7621 | 34.6397 | 44.7594 | 57.8433 | 68.968 | 78.5315 | 86.7515 | 95.4916 | 101.7254 | 106.4421 | 108.2483 | 107.0686 | 99.2812 | 89.419 | 88.359 | 78.3077 | 67.0098 | 55.025 | 1590.9236
2015-04-06 | 43.8262 | 36.3861 | 31.4455 | 28.6555 | 27.5307 | 27.6966 | 29.6444 | 32.4883 | 42.8201 | 56.6106 | 68.9051 | 78.4531 | 87.6243 | 96.0355 | 104.0833 | 109.3815 | 111.9998 | 111.8127 | 105.5188 | 97.2775 | 97.5643 | 85.3219 | 71.1781 | 55.2783 | 1637.5381
2015-04-07 | 44.321 | 37.4143 | 33.8634 | 32.2009 | 32.6541 | 37.3834 | 48.2126 | 54.9595 | 61.3143 | 73.9326 | 87.5179 | 100.1896 | 111.2524 | 121.5258 | 129.9099 | 136.4109 | 140.4686 | 138.8413 | 130.9342 | 124.1862 | 122.1952 | 106.5333 | 88.5848 | 71.6478 | 2066.4538
2015-04-08 | 58.6726 | 49.7509 | 43.6507 | 40.6092 | 40.6575 | 45.0642 | 57.2492 | 64.2873 | 70.3492 | 79.3396 | 90.4253 | 100.139 | 106.0515 | 109.1967 | 108.5639 | 105.2464 | 107.0294 | 99.9747 | 87.093 | 81.1615 | 81.9487 | 71.2847 | 57.6034 | 44.5652 | 1799.9138
2015-04-09 | 35.613 | 30.1764 | 27.2266 | 25.7958 | 25.6996 | 29.3562 | 39.0388 | 44.0691 | 46.7503 | 52.3776 | 56.9628 | 59.4785 | 60.9981 | 62.2775 | 64.3785 | 66.9891 | 69.5252 | 71.1674 | 69.3988 | 66.9374 | 70.7099 | 62.4871 | 50.287 | 38.8102 | 1226.5109
2015-04-10 | 30.364 | 25.8664 | 23.4153 | 22.5373 | 22.9591 | 26.898 | 36.8524 | 42.7292 | 45.6597 | 50.7089 | 55.5887 | 59.2546 | 61.7999 | 64.7846 | 68.0896 | 71.7654 | 74.3568 | 74.2915 | 71.744 | 69.9788 | 73.7047 | 64.7439 | 53.1484 | 41.0937 | 1232.3351
2015-04-11 | 32.3516 | 27.0292 | 24.441 | 23.3786 | 23.7281 | 27.3388 | 37.0136 | 43.0768 | 47.5222 | 55.1751 | 62.527 | 67.7876 | 71.5409 | 75.3733 | 78.9462 | 80.2762 | 80.6956 | 78.6546 | 74.9462 | 72.1512 | 74.0848 | 67.4033 | 58.6242 | 48.3179 | 1332.3841
2015-04-12 | 39.1336 | 33.2196 | 29.3083 | 27.1739 | 26.2986 | 26.9701 | 30.1209 | 34.2763 | 44.3967 | 56.9152 | 67.4656 | 76.1651 | 82.3036 | 87.9557 | 91.4251 | 94.6417 | 95.8499 | 94.5066 | 87.5061 | 79.7226 | 79.6662 | 72.2908 | 61.4627 | 51.2139 | 1469.9889
2015-04-13 | 41.9975 | 35.4247 | 31.5802 | 29.1104 | 28.1037 | 28.4732 | 30.6012 | 33.7459 | 42.6962 | 54.8846 | 65.039 | 72.7857 | 79.8806 | 84.7395 | 86.8103 | 88.4897 | 88.9299 | 88.098 | 84.159 | 82.9926 | 86.5515 | 77.8501 | 66.1851 | 52.845 | 1461.9735
2015-04-14 | 42.3584 | 36.135 | 32.8855 | 31.0923 | 31.2545 | 35.2895 | 45.8648 | 52.4691 | 60.0644 | 72.538 | 85.0188 | 96.5686 | 106.3509 | 116.3596 | 124.5947 | 131.7739 | 135.6006 | 134.3385 | 126.3778 | 116.6733 | 115.3534 | 101.458 | 83.6383 | 65.4983 | 1979.5565
2015-04-15 | 51.7124 | 43.6925 | 39.0388 | 35.9757 | 35.4022 | 39.1889 | 50.1259 | 56.4301 | 65.9489 | 80.4801 | 93.6366 | 106.4291 | 116.1825 | 123.385 | 126.2784 | 128.5313 | 126.8895 | 117.1513 | 112.3075 | 105.7395 | 106.2206 | 94.1017 | 77.0607 | 60.388 | 1992.2974
2015-04-16 | 48.0811 | 40.4725 | 36.0212 | 33.8193 | 33.3654 | 36.8677 | 46.6467 | 51.876 | 55.7867 | 62.0783 | 67.5901 | 71.4982 | 75.6698 | 80.6161 | 84.2866 | 87.0812 | 88.7989 | 88.1691 | 85.2403 | 84.5535 | 87.7663 | 80.5254 | 67.5901 | 53.3974 | 1547.798
2015-04-17 | 43.1846 | 37.0751 | 33.7165 | 32.0219 | 32.2583 | 36.4394 | 46.8972 | 53.4343 | 59.5174 | 69.1885 | 78.263 | 84.391 | 86.481 | 88.1098 | 88.7275 | 87.79 | 86.3753 | 83.4536 | 80.775 | 79.1709 | 81.1843 | 75.2089 | 65.0492 | 53.038 | 1561.7509
2015-04-18 | 43.2344 | 36.9445 | 33.125 | 31.1134 | 30.8042 | 34.0032 | 41.0451 | 47.4612 | 56.6486 | 69.2095 | 80.3215 | 88.1454 | 93.1483 | 98.7281 | 101.4962 | 101.0004 | 99.8989 | 98.6027 | 93.2215 | 87.0459 | 87.3762 | 80.2536 | 70.5825 | 59.9764 | 1663.3867
2015-04-19 | 49.3952 | 42.9276 | 38.6766 | 36.0212 | 35.1396 | 35.9606 | 37.5613 | 40.0477 | 47.6267 | 61.5915 | 74.2697 | 83.6383 | 91.5822 | 97.6142 | 100.9877 | 103.2986 | 102.9266 | 98.3018 | 89.5983 | 79.4746 | 77.7386 | 69.1675 | 59.6735 | 47.5657 | 1600.7854
2015-04-20 | 37.7706 | 31.1839 | 27.0555 | 25.0189 | 24.1856 | 24.6225 | 26.6692 | 29.1922 | 36.9291 | 45.9076 | 51.2953 | 55.9189 | 59.1282 | 61.4924 | 63.1077 | 64.3886 | 65.2225 | 64.3481 | 62.1679 | 60.939 | 65.294 | 60.4371 | 51.2501 | 40.2798 | 1133.8049
2015-04-21 | 31.7153 | 26.6562 | 24.1359 | 22.953 | 23.3176 | 27.0818 | 35.9379 | 41.199 | 45.7879 | 52.0035 | 58.1608 | 63.0676 | 68.2252 | 72.5273 | 77.5494 | 81.6402 | 85.0072 | 84.7046 | 82.1203 | 78.5986 | 81.2981 | 71.9368 | 58.9341 | 46.2335 | 1340.7916
2015-04-22 | 35.7337 | 29.4659 | 26.6431 | 24.981 | 25.0126 | 29.2468 | 38.8811 | 43.5006 | 48.4761 | 54.9407 | 62.0783 | 69.5568 | 75.4501 | 80.4121 | 85.6957 | 92.309 | 97.016 | 97.9139 | 94.2856 | 88.8942 | 91.3043 | 80.8432 | 65.4063 | 50.1975 | 1488.2448
2015-04-23 | 39.1494 | 32.842 | 29.1513 | 27.0227 | 26.6888 | 30.2528 | 39.2285 | 34.0474 | 50.4125 | 57.9779 | 65.6824 | 71.7013 | 79.2046 | 88.7037 | 99.3567 | 107.7232 | 113.9602 | 115.557 | 110.6669 | 101.598 | 100.6706 | 91.2078 | 75.0447 | 55.749 | 1643.5993
2015-04-24 | 44.1362 | 37.0982 | 31.0994 | 28.6893 | 28.7638 | 30.9938 | 39.8162 | 45.5318 | 52.2497 | 62.577 | 73.8023 | 83.9043 | 93.6733 | 102.7857 | 110.7466 | 118.7978 | 123.5816 | 122.9504 | 115.9648 | 105.4279 | 104.5736 | 92.9899 | 75.9007 | 59.4979 | 1785.552
2015-04-25 | 46.5173 | 38.1208 | 33.2706 | 30.6082 | 30.0032 | 33.4092 | 42.4572 | 48.0374 | 55.4569 | 66.4423 | 79.1259 | 91.0631 | 102.108 | 112.8034 | 122.4327 | 130.8619 | 135.5859 | 134.2946 | 124.5242 | 110.8397 | 107.1732 | 95.6645 | 80.3668 | 65.0492 | 1916.2159
2015-04-26 | 51.223 | 41.8993 | 36.2947 | 32.871 | 30.9797 | 31.1064 | 33.2269 | 37.5768 | 49.5462 | 64.6728 | 80.0161 | 94.4206 | 106.4812 | 116.06 | 121.9997 | 127.4023 | 130.2268 | 128.5456 | 119.294 | 105.7784 | 102.1335 | 91.7636 | 78.5762 | 65.1919 | 1877.2869
2015-04-27 | 53.3236 | 44.8101 | 38.889 | 35.5376 | 33.4603 | 33.1032 | 34.2763 | 37.693 | 50.9792 | 68.3922 | 84.7744 | 99.2183 | 111.1591 | 121.3031 | 128.2736 | 134.3678 | 136.8243 | 135.1744 | 126.6762 | 115.0145 | 113.3676 | 101.4326 | 83.9621 | 67.9958 | 1990.0081
2015-04-28 | 55.3817 | 47.4612 | 42.721 | 39.8799 | 39.641 | 44.153 | 54.5015 | 61.0672 | 70.3492 | 84.2054 | 101.1783 | 116.4823 | 128.6602 | 139.4971 | 148.7777 | 156.0921 | 158.0553 | 157.278 | 148.6391 | 135.9981 | 132.4709 | 116.7688 | 95.8252 | 76.7726 | 2351.8567
2015-04-29 | 62.7269 | 53.6469 | 48.0987 | 45.0218 | 44.5146 | 48.7404 | 58.9147 | 65.5903 | 77.0607 | 92.6491 | 109.3948 | 124.5102 | 136.1897 | 145.9255 | 152.8734 | 157.8965 | 156.8506 | 153.2172 | 146.124 | 134.8368 | 130.6452 | 115.9104 | 95.7139 | 76.6952 | 2433.7473
2015-04-30 | 62.2875 | 53.9898 | 48.8904 | 46.1476 | 45.9761 | 50.2064 | 60.7714 | 67.4863 | 78.6883 | 94.4083 | 111.0526 | 125.0605 | 135.9097 | 145.651 | 151.7509 | 156.0132 | 153.7963 | 141.9096 | 133.3447 | 124.4115 | 123.8063 | 110.9062 | 92.0058 | 74.1609 | 2388.6313
2015-05-01 | 60.1134 | 51.6851 | 46.3968 | 43.6758 | 42.9194 | 47.4264 | 58.3537 | 65.2736 | 75.2747 | 90.8221 | 108.0906 | 121.9997 | 133.5636 | 143.7969 | 150.4775 | 153.8746 | 152.1713 | 143.2823 | 130.1692 | 120.4281 | 119.5425 | 105.7914 | 88.4659 | 71.7333 | 2325.3281
2015-05-02 | 58.8275 | 50.5292 | 45.5147 | 42.5725 | 41.8175 | 46.0275 | 56.4207 | 63.4192 | 72.2049 | 85.8829 | 98.4271 | 108.3534 | 114.3111 | 121.3727 | 126.5625 | 129.3202 | 127.602 | 122.4746 | 114.7843 | 104.7157 | 104.5219 | 90.9546 | 78.2071 | 65.5085 | 2070.3325
2015-05-03 | 54.0455 | 46.0447 | 41.0289 | 38.1208 | 36.6762 | 37.4684 | 40.2317 | 44.7425 | 54.2593 | 67.1132 | 78.4755 | 86.6926 | 90.5935 | 92.4911 | 91.4251 | 86.6221 | 76.0108 | 72.0761 | 68.5386 | 67.5798 | 69.9683 | 65.6006 | 58.5275 | 50.1348 | 1514.4676
2015-05-04 | 42.1696 | 36.3784 | 32.987 | 30.7831 | 30.107 | 30.1209 | 30.9375 | 31.9433 | 39.7843 | 49.6619 | 58.1127 | 64.5306 | 71.37 | 77.4938 | 82.9811 | 89.3115 | 94.3838 | 97.0036 | 94.74 | 86.8338 | 84.2286 | 74.5749 | 62.8971 | 48.2302 | 1441.5649
2015-05-05 | 37.965 | 30.7691 | 28.1774 | 26.3829 | 26.4349 | 30.225 | 38.4099 | 43.935 | 50.88 | 60.7123 | 71.6371 | 81.4235 | 91.2198 | 100.6579 | 109.7253 | 117.6167 | 124.7358 | 125.7537 | 119.9988 | 102.1463 | 102.632 | 90.0892 | 68.4549 | 55.683 | 1735.6655
2015-05-06 | 43.1348 | 36.0591 | 31.6584 | 29.1785 | 28.6082 | 31.9862 | 40.5127 | 46.1991 | 53.5082 | 64.5611 | 76.5514 | 89.0968 | 101.6872 | 111.7192 | 121.6233 | 130.4864 | 136.2782 | 135.895 | 128.7462 | 110.5739 | 112.7363 | 99.9242 | 81.8801 | 63.5702 | 1906.1746
2015-05-07 | 50.655 | 42.6467 | 38.3082 | 35.5527 | 34.9676 | 38.5039 | 47.679 | 53.7395 | 62.9873 | 75.0228 | 89.2519 | 101.8528 | 113.6772 | 125.004 | 135.6595 | 141.0681 | 145.1178 | 143.9787 | 135.1744 | 122.8244 | 119.9157 | 108.485 | 89.228 | 71.21 | 2122.5102
2015-05-08 | 56.8389 | 48.6082 | 43.7008 | 40.2878 | 39.5059 | 43.0022 | 52.3594 | 58.209 | 68.3713 | 81.4007 | 95.5533 | 107.9331 | 118.9494 | 129.7659 | 138.41 | 146.2614 | 151.1135 | 149.7655 | 142.0601 | 128.5456 | 123.5394 | 110.7599 | 92.564 | 75.0447 | 2242.55
2015-05-09 | 58.8081 | 49.5818 | 44.7087 | 41.1504 | 40.2959 | 43.9601 | 53.3697 | 59.4005 | 69.1045 | 82.3265 | 96.0727 | 107.9856 | 118.7428 | 128.7175 | 137.9794 | 145.0113 | 148.5929 | 145.0418 | 134.2507 | 119.736 | 113.8928 | 102.5041 | 88.5491 | 74.2371 | 2204.0196
2015-05-10 | 61.1759 | 52.6431 | 47.2613 | 43.584 | 41.8666 | 42.3009 | 44.1026 | 48.9788 | 63.2483 | 79.6437 | 92.7342 | 103.3371 | 114.6219 | 122.265 | 127.3311 | 131.1221 | 130.9052 | 128.1163 | 120.3173 | 107.0817 | 108.3271 | 98.8663 | 87.0459 | 73.7155 | 2070.5918
2015-05-11 | 61.5123 | 53.2406 | 47.5222 | 44.0104 | 42.342 | 41.9156 | 42.5807 | 45.5318 | 56.5441 | 71.4127 | 84.3446 | 94.9861 | 104.8062 | 113.4618 | 120.0264 | 123.3429 | 124.5947 | 121.164 | 114.1491 | 104.367 | 104.5478 | 98.1015 | 84.275 | 68.2147 | 1966.9942
2015-05-12 | 54.7817 | 46.8021 | 42.1532 | 39.8082 | 39.6092 | 43.7342 | 53.3143 | 59.3811 | 68.3295 | 82.1088 | 97.1654 | 110.0431 | 121.1084 | 130.0971 | 136.8391 | 142.8441 | 145.1026 | 143.2218 | 136.9722 | 127.7876 | 125.2866 | 111.4256 | 92.4547 | 74.979 | 2225.3498
2015-05-13 | 61.0968 | 52.9552 | 47.5309 | 44.3462 | 43.6674 | 47.7663 | 57.5459 | 63.5299 | 72.3015 | 86.2228 | 100.3034 | 111.5991 | 122.3209 | 129.6364 | 135.1597 | 139.8255 | 142.2559 | 139.5568 | 131.7884 | 121.5537 | 119.9988 | 109.3551 | 91.558 | 73.5313 | 2245.4058
2015-05-14 | 60.9784 | 52.8909 | 47.2005 | 44.0355 | 43.4423 | 45.0896 | 58.3826 | 63.2081 | 72.9259 | 88.3234 | 102.568 | 116.646 | 127.1601 | 134.0166 | 138.9456 | 138.7967 | 137.3568 | 134.2653 | 126.0372 | 116.605 | 117.2744 | 106.3248 | 89.9095 | 72.366 | 2234.7492
2015-05-15 | 58.7016 | 50.4753 | 45.2764 | 42.5395 | 42.4407 | 46.4312 | 56.2405 | 62.0484 | 70.1057 | 84.4258 | 98.0265 | 105.4928 | 108.3271 | 107.7625 | 103.2472 | 98.1015 | 96.7176 | 96.5189 | 93.8935 | 89.6581 | 89.6581 | 83.0962 | 70.2115 | 57.1346 | 1856.5315
2015-05-16 | 46.3366 | 40.0477 | 36.2338 | 33.9149 | 33.57 | 37.662 | 46.854 | 51.1959 | 54.5482 | 60.8601 | 66.504 | 70.6356 | 72.5165 | 73.8132 | 76.5293 | 78.1066 | 79.8919 | 78.0285 | 73.2499 | 67.2582 | 64.8354 | 59.732 | 51.5399 | 41.9484 | 1395.8124
2015-05-17 | 33.6799 | 28.7096 | 25.5079 | 23.7835 | 23.2749 | 23.8513 | 25.7188 | 29.4521 | 38.152 | 48.3531 | 57.498 | 64.9881 | 70.7205 | 76.1651 | 81.5717 | 85.9532 | 88.7632 | 88.2285 | 83.0847 | 74.6076 | 72.1512 | 67.4863 | 58.0549 | 48.3531 | 1318.1091
2015-05-18 | 39.7444 | 33.7899 | 29.934 | 27.4446 | 26.357 | 26.578 | 27.2398 | 30.3293 | 39.7843 | 52.1767 | 63.2081 | 72.2049 | 80.0839 | 86.7397 | 92.9655 | 97.6017 | 101.0004 | 100.2275 | 93.9058 | 85.2636 | 84.2982 | 78.1736 | 65.7644 | 52.3319 | 1487.1471
2015-05-19 | 41.7767 | 35.1771 | 31.3252 | 29.507 | 29.5894 | 33.1977 | 41.5647 | 46.8886 | 55.3629 | 66.2467 | 77.1716 | 87.0459 | 95.8623 | 104.9874 | 111.3057 | 117.5619 | 121.0111 | 120.4559 | 114.7708 | 104.0962 | 100.4553 | 91.2198 | 75.8127 | 59.2838 | 1791.6761
2015-05-20 | 46.9838 | 39.371 | 35.2745 | 32.8855 | 32.2152 | 35.3796 | 43.434 | 49.8936 | 58.5082 | 69.9154 | 82.0173 | 92.5762 | 101.4071 | 109.0251 | 114.5814 | 119.1285 | 121.8184 | 120.6223 | 115.7744 | 104.7675 | 101.4962 | 91.244 | 75.4172 | 59.5174 | 1853.2539
2015-05-21 | 47.1831 | 39.4583 | 34.9004 | 32.1221 | 31.3818 | 34.5134 | 42.7457 | 48.9611 | 56.4681 | 66.669 | 77.4827 | 87.577 | 96.4197 | 106.2988 | 116.06 | 122.9084 | 127.1316 | 125.3856 | 118.2065 | 106.6377 | 101.4835 | 92.4182 | 76.7062 | 60.182 | 1849.3009
2015-05-22 | 46.6035 | 38.6766 | 33.5334 | 31.0219 | 30.5872 | 33.9075 | 42.1614 | 47.9323 | 56.6296 | 67.8396 | 80.7523 | 93.9547 | 106.9118 | 120.0956 | 130.371 | 139.3181 | 145.057 | 143.2823 | 135.1744 | 121.3866 | 113.8254 | 104.2896 | 85.2169 | 66.7722 | 2015.301
2015-05-23 | 52.0399 | 43.1265 | 37.4762 | 34.3281 | 33.0959 | 35.9303 | 43.3425 | 50.8349 | 61.5321 | 75.6038 | 91.4976 | 108.4587 | 123.8204 | 140.1693 | 152.608 | 161.0071 | 163.7436 | 160.0467 | 148.8393 | 130.2845 | 122.8104 | 112.5486 | 95.541 | 78.5538 | 2257.2391
2015-05-24 | 63.8222 | 53.7024 | 46.3624 | 41.6217 | 39.1494 | 38.4883 | 39.1178 | 44.1278 | 58.8178 | 77.2715 | 95.8375 | 114.5002 | 131.3682 | 143.6152 | 151.2999 | 155.4614 | 155.2725 | 151.7353 | 139.8853 | 125.1594 | 119.1147 | 108.7088 | 93.7345 | 78.5203 | 2266.6945
2015-05-25 | 65.437 | 55.269 | 48.1249 | 43.6591 | 41.037 | 40.0636 | 40.4725 | 43.6591 | 55.269 | 71.4661 | 90.9185 | 107.7887 | 123.7501 | 134.8661 | 141.6539 | 145.6052 | 146.9344 | 141.4735 | 130.2845 | 117.9046 | 114.1356 | 104.9356 | 89.7538 | 75.6038 | 2170.0655
2015-05-26 | 62.1281 | 53.3697 | 47.3134 | 43.534 | 41.524 | 41.5565 | 42.4407 | 46.7071 | 61.3044 | 80.9909 | 100.772 | 116.1825 | 129.9099 | 139.7658 | 145.4071 | 148.3773 | 148.4697 | 143.8878 | 132.8783 | 120.3173 | 117.74 | 107.0294 | 90.3172 | 72.7965 | 2234.7195
2015-05-27 | 59.5564 | 50.7989 | 45.421 | 42.2763 | 41.2477 | 45.1405 | 53.7487 | 61.8595 | 73.5854 | 89.3115 | 105.7654 | 121.5119 | 133.7242 | 143.4487 | 149.2403 | 151.9999 | 147.609 | 136.3962 | 126.1932 | 116.5914 | 115.5027 | 105.7005 | 89.2519 | 70.997 | 2276.8784
2015-05-28 | 57.7185 | 49.3685 | 44.422 | 41.4507 | 40.7462 | 44.5484 | 53.4713 | 60.5353 | 71.338 | 85.3686 | 100.9877 | 118.0692 | 130.8763 | 141.8193 | 147.9314 | 149.6882 | 149.5182 | 143.6 | 134.5289 | 124.7781 | 121.7208 | 110.9461 | 93.6122 | 75.9337 | 2292.9779
2015-05-29 | 61.4924 | 52.0308 | 46.7416 | 43.6424 | 42.5725 | 46.0961 | 54.8846 | 61.9589 | 71.1461 | 83.4536 | 97.1778 | 107.4611 | 113.8793 | 118.1791 | 115.1771 | 111.9062 | 109.8445 | 107.2648 | 104.9227 | 97.9765 | 97.3149 | 90.8462 | 78.129 | 63.7113 | 1977.8093
2015-05-30 | 50.8079 | 42.4078 | 38.551 | 36.249 | 35.8319 | 39.181 | 47.0877 | 53.8507 | 63.9434 | 79.9032 | 95.3682 | 108.8801 | 120.0541 | 129.0187 | 134.4264 | 137.9497 | 136.9574 | 129.5933 | 116.878 | 106.8726 | 103.9673 | 95.5163 | 83.0387 | 70.4658 | 2056.8
2015-05-31 | 58.9729 | 49.9025 | 44.0271 | 40.3841 | 39.023 | 38.7866 | 40.3841 | 45.7451 | 60.4174 | 78.9799 | 97.265 | 112.562 | 122.9224 | 129.7515 | 130.9052 | 129.8523 | 126.0372 | 117.8771 | 108.7483 | 99.4827 | 98.2643 | 92.2847 | 81.9258 | 69.4199 | 2013.9213
2015-06-01 | 58.905 | 50.1885 | 44.844 | 41.272 | 39.3789 | 39.2839 | 40.0157 | 43.7677 | 55.8811 | 72.5058 | 89.3474 | 102.9907 | 114.8655 | 123.3289 | 127.7733 | 126.662 | 121.3309 | 112.3878 | 102.8241 | 96.4941 | 96.3701 | 92.1027 | 80.8772 | 67.0615 | 1940.4588
2015-06-02 | 55.6453 | 48.3443 | 44.3631 | 42.2106 | 42.4736 | 47.2005 | 56.1932 | 62.6269 | 68.8736 | 76.4409 | 84.02 | 88.454 | 92.8925 | 95.9118 | 97.964 | 97.864 | 97.3896 | 95.0477 | 92.6734 | 90.0892 | 90.9064 | 85.8947 | 73.5854 | 60.1918 | 1787.2565
2015-06-03 | 49.0761 | 42.1696 | 38.152 | 35.8319 | 35.6959 | 39.6648 | 48.2477 | 54.1105 | 59.9959 | 68.8003 | 78.1848 | 86.5515 | 92.8681 | 97.5643 | 99.5583 | 100.2148 | 97.7765 | 95.1709 | 90.786 | 87.0459 | 88.2641 | 81.9258 | 70.2009 | 56.6486 | 1694.5053
2015-06-04 | 45.5062 | 38.7001 | 34.7141 | 32.7191 | 32.6902 | 36.3937 | 44.3715 | 45.6256 | 57.431 | 69.2305 | 79.7677 | 88.5372 | 94.7769 | 102.4785 | 108.1826 | 112.1068 | 115.1364 | 115.7472 | 111.8261 | 102.9266 | 98.6403 | 91.5943 | 78.4307 | 62.9974 | 1800.5307
2015-06-05 | 50.4574 | 42.7705 | 37.9105 | 35.0498 | 34.1581 | 37.2831 | 44.279 | 52.2497 | 64.095 | 78.3636 | 94.347 | 109.6459 | 122.0416 | 133.9434 | 142.4217 | 148.6391 | 151.2688 | 150.1058 | 142.7988 | 128.4024 | 120.5807 | 108.6561 | 90.9908 | 72.0547 | 2192.5135
2015-06-06 | 58.3344 | 48.5993 | 42.4654 | 38.7866 | 37.129 | 39.6569 | 45.3445 | 53.4897 | 67.6629 | 84.9024 | 104.4315 | 123.8345 | 140.4087 | 153.4988 | 162.9525 | 168.3175 | 170.0922 | 166.8457 | 156.5501 | 140.6932 | 130.6741 | 119.8051 | 102.5425 | 85.9532 | 2442.9705
2015-06-07 | 70.997 | 60.2408 | 53.038 | 48.7139 | 45.8306 | 44.8355 | 45.6683 | 51.4221 | 67.4656 | 86.7279 | 108.3797 | 128.9469 | 143.1916 | 153.4831 | 159.6794 | 161.3599 | 155.5874 | 146.9344 | 135.7183 | 124.6229 | 117.2607 | 107.579 | 93.0874 | 78.2965 | 2389.0672
2015-06-08 | 65.4574 | 55.7207 | 49.1469 | 43.7342 | 42.0794 | 41.4507 | 41.5647 | 45.132 | 58.2379 | 78.0843 | 99.2183 | 118.8116 | 131.0498 | 133.9142 | 130.6885 | 128.6889 | 124.9334 | 120.9694 | 113.5021 | 104.7416 | 99.9242 | 92.637 | 77.9727 | 64.7846 | 2062.4446
2015-06-09 | 52.3137 | 44.3378 | 39.1415 | 36.5845 | 36.2338 | 39.4741 | 45.805 | 53.2314 | 64.9067 | 80.5368 | 99.2434 | 119.8604 | 136.6471 | 151.1912 | 159.1849 | 156.7715 | 152.5143 | 141.9096 | 129.8091 | 119.4183 | 113.731 | 104.1993 | 87.6007 | 70.9119 | 2235.5578
2015-06-10 | 57.2588 | 48.5201 | 43.4673 | 40.4082 | 39.633 | 42.9359 | 49.564 | 58.6919 | 72.6026 | 88.7275 | 105.0003 | 120.7056 | 133.4322 | 140.6783 | 140.289 | 130.8041 | 122.4886 | 118.6464 | 117.6441 | 110.5473 | 108.2351 | 98.1141 | 82.1661 | 66.5762 | 2137.1367
2015-06-11 | 54.6228 | 46.5949 | 41.2801 | 38.5274 | 37.9105 | 40.7542 | 47.5396 | 55.4852 | 67.8292 | 85.112 | 102.0186 | 117.1377 | 127.0034 | 133.228 | 127.0034 | 116.3733 | 111.1192 | 109.5005 | 107.2124 | 100.4173 | 97.2276 | 90.7379 | 77.1383 | 62.9974 | 1994.7711
2015-06-12 | 51.3949 | 43.5923 | 38.9126 | 36.135 | 35.5226 | 38.1598 | 44.5821 | 50.5381 | 57.2396 | 66.638 | 79.4183 | 94.2979 | 111.3723 | 127.545 | 138.7521 | 141.2632 | 134.2214 | 123.3991 | 115.4077 | 107.4087 | 103.2472 | 94.5311 | 78.4531 | 63.5299 | 1975.5622
2015-06-13 | 51.5036 | 43.6341 | 38.8181 | 35.8319 | 35.282 | 37.8716 | 43.459 | 51.549 | 64.4089 | 79.1147 | 94.5434 | 110.4942 | 123.5675 | 130.4287 | 130.2701 | 122.7824 | 115.2992 | 107.5397 | 100.8101 | 91.3405 | 85.801 | 80.3781 | 70.4446 | 58.8081 | 1903.9805
2015-06-14 | 48.7933 | 41.6788 | 36.9905 | 34.3059 | 33.1395 | 33.6066 | 35.2445 | 40.0956 | 52.049 | 68.1313 | 85.1586 | 101.6999 | 115.1771 | 126.662 | 132.0931 | 131.6724 | 124.7217 | 117.9046 | 107.5528 | 96.7425 | 92.7464 | 86.0821 | 75.2966 | 63.6911 | 1881.2359
2015-06-15 | 53.4251 | 46.3796 | 41.0937 | 38.0428 | 37.1829 | 37.9494 | 39.3472 | 44.1026 | 57.4693 | 75.4282 | 93.1605 | 110.534 | 125.4705 | 135.3801 | 141.2332 | 139.02 | 131.3392 | 121.9579 | 112.3075 | 102.6064 | 100.7213 | 96.2957 | 83.7077 | 70.5825 | 2034.7372
2015-06-16 | 57.7473 | 49.9025 | 45.166 | 42.3091 | 41.3532 | 44.4136 | 50.655 | 57.5076 | 66.9271 | 79.5084 | 97.2526 | 115.6249 | 128.9469 | 141.1882 | 149.9356 | 155.1938 | 158.3731 | 156.1237 | 144.9809 | 126.6762 | 118.3989 | 108.2614 | 91.0631 | 74.1718 | 2301.6807
2015-06-17 | 60.1232 | 51.3406 | 45.1915 | 41.7604 | 40.577 | 43.1763 | 49.5373 | 56.9533 | 66.7309 | 77.995 | 89.5624 | 100.7087 | 110.72 | 119.8051 | 122.9504 | 122.8944 | 120.4836 | 118.3164 | 113.9467 | 106.8726 | 102.7472 | 97.4146 | 81.0932 | 65.6415 | 2006.5424
2015-06-18 | 52.7532 | 45.0557 | 40.4082 | 37.5768 | 37.1213 | 40.0397 | 46.828 | 54.25 | 65.1308 | 78.2742 | 93.6978 | 109.2495 | 118.0967 | 121.3031 | 119.2113 | 113.6098 | 107.3956 | 102.2101 | 97.2276 | 92.3575 | 90.4974 | 85.801 | 73.1418 | 59.6539 | 1880.8909
2015-06-19 | 48.3179 | 41.5565 | 37.631 | 35.3947 | 34.8258 | 37.7085 | 44.1194 | 51.2049 | 62.6669 | 77.1162 | 93.8568 | 108.0643 | 120.3727 | 129.6364 | 130.3999 | 122.3349 | 114.9874 | 107.6707 | 100.5059 | 93.9058 | 90.4853 | 83.3959 | 71.6264 | 58.1512 | 1895.9355
2015-06-20 | 47.0791 | 40.1436 | 35.9076 | 33.6579 | 33.0959 | 35.5376 | 41.2801 | 48.617 | 60.4272 | 76.3636 | 92.8438 | 109.0383 | 122.1393 | 129.8523 | 127.602 | 116.5778 | 109.818 | 103.9287 | 99.0422 | 92.7829 | 89.1564 | 84.7511 | 74.4767 | 62.537 | 1866.6561
2015-06-21 | 51.3225 | 44.1026 | 39.268 | 36.5539 | 35.3872 | 35.847 | 36.9982 | 42.8532 | 58.4212 | 77.8501 | 95.3805 | 112.7899 | 127.3881 | 136.2044 | 133.5344 | 124.158 | 116.3051 | 110.0696 | 102.7088 | 95.2448 | 91.6063 | 87.3526 | 77.2493 | 64.8253 | 1933.4213
2015-06-22 | 53.5729 | 46.733 | 41.5403 | 38.4334 | 36.7145 | 36.615 | 37.0674 | 42.8697 | 57.6514 | 77.5272 | 96.0974 | 111.319 | 126.321 | 137.8013 | 145.3462 | 146.5213 | 141.5787 | 130.703 | 117.4797 | 106.5073 | 102.1846 | 95.9118 | 83.2921 | 68.1 | 2077.888
2015-06-23 | 55.2408 | 48.0549 | 43.2427 | 40.4564 | 39.864 | 43.0436 | 49.5462 | 58.0164 | 71.4127 | 87.719 | 106.716 | 124.9052 | 141.8795 | 156.1079 | 164.4556 | 166.3728 | 163.0331 | 155.8712 | 145.6662 | 132.006 | 123.3008 | 112.1068 | 95.2572 | 76.5404 | 2400.8153
2015-06-24 | 62.1978 | 52.9093 | 47.1658 | 43.5923 | 42.4325 | 45.2254 | 51.6942 | 60.1526 | 74.4985 | 91.6547 | 112.2138 | 131.1366 | 148.4081 | 164.3746 | 174.1192 | 179.5451 | 180.5282 | 173.836 | 165.1854 | 150.741 | 143.0707 | 130.2124 | 110.3614 | 89.9454 | 2625.2011
2015-06-25 | 73.7047 | 62.5969 | 54.9876 | 50.4753 | 48.8198 | 51.4402 | 57.9299 | 66.6793 | 81.7087 | 101.5216 | 124.0736 | 142.4669 | 159.855 | 174.0359 | 183.066 | 183.9731 | 176.4272 | 166.7967 | 155.005 | 140.1394 | 131.3247 | 120.2618 | 103.7871 | 84.5884 | 2695.6647
2015-06-26 | 69.3778 | 58.4309 | 51.5308 | 47.3134 | 45.7195 | 47.9149 | 54.4083 | 62.807 | 77.8724 | 98.3394 | 120.1095 | 138.41 | 153.2328 | 163.3074 | 173.4697 | 176.8469 | 176.9309 | 171.6278 | 162.1954 | 147.3175 | 137.0609 | 125.004 | 106.403 | 86.5045 | 2652.1349
2015-06-27 | 70.4976 | 60.3193 | 53.462 | 49.3242 | 47.9936 | 50.7899 | 56.2784 | 64.5712 | 79.5986 | 98.8788 | 117.932 | 136.0128 | 147.8853 | 158.23 | 167.3519 | 168.3503 | 164.8284 | 156.3289 | 141.4735 | 126.5909 | 118.6327 | 107.8543 | 94.863 | 79.2383 | 2517.2861
2015-06-28 | 64.3278 | 54.4642 | 48.2477 | 43.8011 | 41.199 | 39.1415 | 44.8863 | 48.5201 | 64.6017 | 85.7659 | 104.4574 | 125.0605 | 142.6932 | 154.1255 | 161.2957 | 166.7315 | 166.0796 | 162.2759 | 151.2222 | 136.4552 | 128.4024 | 118.8116 | 103.6455 | 86.6338 | 2442.8454
2015-06-29 | 72.0976 | 61.8794 | 54.763 | 49.974 | 47.3047 | 46.285 | 45.959 | 50.1169 | 66.8444 | 89.7299 | 113.1525 | 135.895 | 154.5021 | 163.8729 | 164.2937 | 158.0235 | 153.1703 | 145.5138 | 130.8185 | 117.7948 | 110.2951 | 102.8497 | 89.1564 | 73.4988 | 2397.791
2015-06-30 | 60.9192 | 52.2041 | 46.6726 | 43.5423 | 43.1597 | 46.5518 | 53.0748 | 60.1722 | 72.8612 | 91.0751 | 109.5798 | 126.7615 | 141.2932 | 154.2039 | 162.3081 | 166.3402 | 162.759 | 149.3947 | 136.7652 | 125.5271 | 119.4873 | 110.6403 | 96.4197 | 79.3846 | 2411.0976
2015-07-01 | 65.294 | 56.1742 | 50.862 | 47.7663 | 47.0444 | 50.5741 | 58.0068 | 64.4596 | 73.0554 | 85.8829 | 99.9116 | 114.9468 | 124.8063 | 129.3346 | 133.8119 | 135.7478 | 139.1392 | 137.0313 | 131.4406 | 126.3352 | 123.6658 | 113.2062 | 96.3949 | 79.4409 | 2284.3326
2015-07-02 | 64.4292 | 55.7773 | 50.3677 | 47.5309 | 46.6381 | 49.5107 | 56.2689 | 63.5903 | 76.5514 | 94.4697 | 115.462 | 131.0643 | 140.8281 | 142.045 | 136.3077 | 130.9631 | 129.5501 | 127.5164 | 123.5956 | 116.5641 | 114.0276 | 108.4324 | 95.1832 | 78.2518 | 2294.9256
2015-07-03 | 66.031 | 56.9819 | 51.9397 | 48.6786 | 48.16 | 51.0062 | 57.7761 | 65.3552 | 78.5986 | 98.3394 | 121.2057 | 140.3638 | 154.5649 | 164.8933 | 173.5363 | 178.379 | 176.4272 | 163.8244 | 150.555 | 137.9794 | 130.4576 | 122.0137 | 106.9249 | 89.4668 | 2633.4588
2015-07-04 | 74.8916 | 63.8828 | 56.2689 | 51.3768 | 48.8639 | 48.8021 | 49.8312 | 53.1761 | 67.6421 | 91.051 | 115.0687 | 135.4242 | 148.3466 | 154.8006 | 157.0247 | 156.4553 | 140.9181 | 122.9084 | 110.6403 | 100.1263 | 93.71 | 85.8478 | 81.6174 | 73.0446 | 2281.7193
2015-07-05 | 61.9987 | 53.1761 | 47.6354 | 44.1278 | 42.4736 | 42.5395 | 43.5673 | 46.5777 | 57.9106 | 72.0654 | 90.1372 | 103.9029 | 115.8968 | 127.8305 | 129.3489 | 120.4975 | 112.5754 | 107.2124 | 102.0314 | 96.7176 | 93.429 | 88.4303 | 79.1709 | 67.5694 | 1946.8222
2015-07-06 | 57.5171 | 49.9025 | 44.9201 | 41.6462 | 40.6253 | 40.7946 | 41.5077 | 44.7425 | 57.6034 | 72.044 | 86.2345 | 92.0543 | 98.089 | 103.6841 | 108.8933 | 109.7253 | 108.2088 | 104.2122 | 97.9389 | 88.5967 | 86.8338 | 83.1769 | 73.1094 | 60.9094 | 1792.9701
2015-07-07 | 51.5127 | 45.132 | 41.4182 | 39.6251 | 39.5376 | 42.9525 | 49.3597 | 56.7152 | 68.3818 | 81.4007 | 95.4916 | 105.2464 | 109.9107 | 113.5694 | 114.8655 | 118.6327 | 118.6327 | 118.0143 | 115.2856 | 111.7726 | 109.1043 | 102.8881 | 89.061 | 73.6396 | 2012.15
2015-07-08 | 60.5746 | 51.8032 | 46.2335 | 43.1431 | 42.2845 | 44.954 | 51.4221 | 59.3324 | 71.7333 | 90.1972 | 109.9901 | 129.0187 | 144.8136 | 152.3272 | 150.8496 | 142.1203 | 133.3009 | 125.7679 | 118.0967 | 108.2614 | 100.392 | 91.921 | 79.0023 | 65.4778 | 2213.0175
2015-07-09 | 53.8692 | 46.7848 | 42.4325 | 38.363 | 38.7001 | 42.556 | 49.2887 | 56.4966 | 69.3147 | 87.9676 | 106.2727 | 125.513 | 138.633 | 142.4971 | 130.8041 | 121.7348 | 117.466 | 111.3057 | 104.0446 | 99.8989 | 96.3081 | 99.4323 | 78.0062 | 64.8253 | 2062.5149
2015-07-10 | 52.7532 | 45.4296 | 41.2558 | 38.9678 | 38.3004 | 41.199 | 47.8624 | 55.7867 | 68.4967 | 85.2986 | 99.3693 | 109.4344 | 119.0183 | 126.0088 | 125.7254 | 121.0806 | 114.1895 | 106.8857 | 100.9751 | 94.9492 | 93.3069 | 88.2403 | 77.0829 | 64.1658 | 1955.7822
2015-07-11 | 52.5423 | 45.387 | 41.0775 | 38.889 | 38.3786 | 41.0289 | 46.7589 | 54.8097 | 69.4093 | 87.1284 | 105.8824 | 124.0032 | 138.4249 | 150.5085 | 157.7854 | 159.5677 | 158.0235 | 152.5924 | 143.903 | 131.0498 | 123.708 | 115.8968 | 101.5598 | 85.8244 | 2364.1394
2015-07-12 | 71.9796 | 62.3074 | 55.3817 | 51.1959 | 48.0286 | 48.0549 | 48.8727 | 52.9093 | 66.6484 | 87.7663 | 106.6377 | 124.8628 | 140.3638 | 149.1786 | 151.7975 | 151.2688 | 148.8856 | 141.0681 | 130.5009 | 116.5914 | 109.818 | 100.7213 | 88.3115 | 75.0775 | 2328.2283
2015-07-13 | 65.0187 | 57.5938 | 52.4783 | 48.6258 | 46.1562 | 45.2 | 45.3955 | 49.7509 | 65.0696 | 84.3446 | 102.2101 | 119.4735 | 132.7327 | 139.6165 | 145.3614 | 149.4256 | 148.6699 | 143.1463 | 134.2946 | 123.2307 | 117.3428 | 111.1458 | 97.265 | 81.8001 | 2305.3482
2015-07-14 | 68.5909 | 59.4297 | 52.9552 | 49.5373 | 48.6434 | 51.3225 | 57.8145 | 65.3144 | 79.779 | 98.4773 | 118.5914 | 136.4995 | 150.1058 | 153.859 | 151.0359 | 149.5337 | 148.9164 | 148.6237 | 144.7832 | 132.3837 | 121.6512 | 110.4676 | 94.3593 | 77.6718 | 2470.3462
2015-07-15 | 64.0748 | 55.2783 | 49.6174 | 46.1304 | 45.3274 | 48.0636 | 54.9314 | 61.9788 | 73.4338 | 90.8462 | 106.8073 | 121.2614 | 130.3854 | 130.4576 | 126.5198 | 119.5149 | 114.7572 | 111.4657 | 110.0564 | 104.8062 | 103.0548 | 97.5643 | 84.4722 | 70.0634 | 2120.8688
2015-07-16 | 58.4116 | 50.0722 | 44.7003 | 42.1449 | 41.7849 | 45.3445 | 53.8692 | 61.3934 | 75.3514 | 92.929 | 108.6956 | 121.2335 | 129.2771 | 123.2027 | 116.3324 | 110.8131 | 105.9734 | 101.5216 | 98.6278 | 93.8079 | 94.4697 | 91.0149 | 79.8693 | 66.7515 | 2007.5918
2015-07-17 | 55.5887 | 48.5641 | 43.3841 | 40.9319 | 40.6978 | 43.9434 | 51.0152 | 57.4214 | 72.4735 | 88.5848 | 105.6615 | 121.3587 | 121.7487 | 119.1561 | 115.9648 | 121.1779 | 128.3452 | 129.1909 | 127.5735 | 120.9833 | 115.7201 | 108.2614 | 91.9452 | 76.6731 | 2146.3653
2015-07-18 | 62.0783 | 53.2314 | 47.7052 | 44.2201 | 42.9276 | 45.4636 | 51.2772 | 58.6145 | 73.2607 | 93.1605 | 113.3003 | 132.9074 | 149.9511 | 163.0976 | 171.3797 | 175.9912 | 176.008 | 167.2539 | 151.3154 | 135.3213 | 125.6545 | 115.5978 | 100.2022 | 84.7976 | 2534.7173
2015-07-19 | 70.5188 | 60.1428 | 53.2774 | 49.0938 | 46.5001 | 46.3366 | 47.2179 | 51.667 | 68.5281 | 90.2572 | 111.3323 | 130.8185 | 146.4295 | 158.1506 | 163.1299 | 164.8447 | 168.9244 | 165.7867 | 153.3892 | 140.4835 | 133.0677 | 121.9021 | 105.9344 | 90.4613 | 2538.1946
2015-07-20 | 75.9998 | 65.621 | 58.0742 | 53.0288 | 50.1885 | 48.9964 | 49.1292 | 51.9761 | 67.5175 | 90.0772 | 111.0127 | 133.228 | 151.098 | 163.4851 | 169.5818 | 166.0634 | 162.9363 | 158.0077 | 147.4709 | 134.8368 | 129.6796 | 120.7472 | 105.8434 | 88.015 | 2552.6144
2015-07-21 | 73.0878 | 63.1479 | 56.3543 | 52.3411 | 51.3677 | 54.1105 | 61.1462 | 67.9854 | 80.7183 | 99.0925 | 119.9434 | 138.633 | 150.9893 | 153.1547 | 145.9866 | 138.8711 | 131.4261 | 124.8769 | 118.3302 | 111.239 | 109.8709 | 100.2401 | 86.9045 | 72.4735 | 2362.2909
2015-07-22 | 59.5857 | 51.3315 | 46.8626 | 43.7844 | 43.3342 | 47.1831 | 53.9712 | 61.1956 | 74.5639 | 91.1595 | 107.4349 | 120.4559 | 128.6172 | 133.2863 | 139.8255 | 143.706 | 140.7532 | 132.1222 | 124.7076 | 116.6596 | 114.4192 | 106.1165 | 91.4855 | 76.6731 | 2249.2345
2015-07-23 | 64.3684 | 55.8716 | 50.296 | 46.9145 | 46.0704 | 48.8727 | 56.7913 | 63.389 | 76.7837 | 91.7999 | 106.0515 | 118.1104 | 127.7162 | 137.1348 | 146.5518 | 151.4864 | 153.358 | 151.782 | 150.5705 | 139.8404 | 133.476 | 124.1017 | 105.8434 | 88.4184 | 2435.5992
2015-07-24 | 73.2715 | 62.4471 | 55.5699 | 51.5036 | 50.0991 | 52.6614 | 58.6242 | 65.8156 | 80.0952 | 100.0631 | 119.8189 | 102.6064 | 150.4775 | 158.1824 | 162.7912 | 167.2375 | 173.4365 | 169.8451 | 164.3099 | 151.1756 | 139.6314 | 128.7032 | 108.3009 | 89.1683 | 2635.8357
2015-07-25 | 74.4222 | 63.1278 | 56.2405 | 51.7396 | 49.6352 | 52.1585 | 58.0742 | 65.6108 | 82.1661 | 102.632 | 122.7404 | 142.4066 | 154.8792 | 161.8417 | 168.3339 | 174.5195 | 175.3717 | 169.1215 | 156.4869 | 141.5637 | 133.9434 | 122.5865 | 106.8465 | 90.8101 | 2677.2584
2015-07-26 | 77.605 | 67.2893 | 60.8995 | 55.7112 | 52.6431 | 52.1402 | 53.4435 | 57.0105 | 71.2634 | 92.6248 | 114.3111 | 129.8091 | 136.6323 | 140.4536 | 139.3181 | 135.1303 | 135.1744 | 132.0931 | 125.3715 | 116.2915 | 113.9602 | 104.9486 | 91.6184 | 79.8806 | 2335.6233
2015-07-27 | 67.9958 | 59.2449 | 53.5175 | 49.4929 | 47.409 | 46.8194 | 47.296 | 50.3497 | 67.2893 | 89.3951 | 109.9504 | 129.8379 | 146.7201 | 160.3185 | 169.3516 | 175.4888 | 177.5701 | 175.2044 | 164.7798 | 149.9047 | 143.2823 | 132.5145 | 114.5408 | 96.5189 | 2624.7924
2015-07-28 | 80.0952 | 69.8098 | 62.507 | 58.1319 | 56.9247 | 60.0155 | 66.7618 | 73.7372 | 89.2161 | 110.9195 | 131.7449 | 152.5768 | 167.4336 | 181.6842 | 194.9085 | 202.458 | 205.2175 | 202.1526 | 194.4678 | 179.6974 | 170.9004 | 156.993 | 132.8929 | 109.5269 | 3110.7734
2015-07-29 | 90.6777 | 78.3972 | 70.0951 | 65.2225 | 63.1177 | 65.4676 | 71.8725 | 78.2518 | 94.114 | 114.1086 | 134.7341 | 154.3765 | 167.9407 | 177.4354 | 182.2124 | 178.4802 | 174.8535 | 162.759 | 148.5005 | 136.3519 | 131.3826 | 121.3448 | 103.9158 | 88.2047 | 2853.8171
2015-07-30 | 73.7047 | 64.7236 | 58.2283 | 54.6042 | 53.1945 | 56.089 | 63.7314 | 70.0634 | 84.6232 | 102.3379 | 118.0967 | 137.6383 | 155.1623 | 171.2474 | 179.9685 | 180.681 | 170.3394 | 153.906 | 142.5725 | 131.8319 | 125.2866 | 115.7744 | 98.565 | 82.5329 | 2644.9031
2015-07-31 | 68.2878 | 58.9632 | 52.9828 | 49.5729 | 48.4146 | 50.9611 | 58.0357 | 63.7516 | 75.9998 | 95.3805 | 117.8497 | 139.6463 | 154.7691 | 165.1205 | 168.7439 | 164.6663 | 152.2181 | 140.9331 | 131.7159 | 121.7069 | 118.7565 | 110.4411 | 95.6151 | 79.8919 | 2484.4243
2015-08-01 | 67.4656 | 58.7791 | 52.1858 | 49.3597 | 47.8362 | 50.646 | 56.6676 | 64.6017 | 79.3058 | 99.9747 | 120.151 | 139.0945 | 154.1725 | 165.1854 | 174.603 | 179.7482 | 179.0038 | 169.0065 | 154.6906 | 141.2632 | 135.8803 | 125.117 | 107.4087 | 91.244 | 2663.391
2015-08-02 | 77.0163 | 66.1748 | 59.0505 | 54.3338 | 51.7851 | 51.558 | 53.0472 | 56.4112 | 71.9582 | 93.3435 | 114.1626 | 131.3103 | 145.3005 | 153.4831 | 160.975 | 160.6386 | 158.0553 | 151.502 | 140.1095 | 128.9326 | 124.7499 | 116.5505 | 101.6999 | 87.6598 | 2509.8082
2015-08-03 | 74.444 | 64.927 | 58.2283 | 53.962 | 51.4855 | 51.1868 | 52.2771 | 53.9249 | 65.8156 | 82.4297 | 96.0231 | 111.559 | 119.3906 | 121.7627 | 122.6285 | 124.7781 | 126.5767 | 124.3411 | 118.5226 | 112.951 | 108.13 | 99.3442 | 85.2169 | 70.8055 | 2150.7109
2015-08-04 | 58.3923 | 50.6999 | 45.9847 | 43.3009 | 43.1182 | 46.733 | 54.1013 | 59.9079 | 71.8618 | 88.3115 | 106.0515 | 122.3908 | 127.0461 | 124.9193 | 117.5482 | 110.2685 | 103.2601 | 95.7139 | 91.051 | 87.5889 | 89.9095 | 84.3214 | 74.0087 | 63.1077 | 1959.5969
2015-08-05 | 53.2406 | 46.9665 | 43.4673 | 41.5973 | 41.4996 | 44.6496 | 52.4234 | 59.1865 | 72.323 | 90.5575 | 107.5135 | 124.5665 | 138.886 | 147.7932 | 145.9713 | 144.5857 | 145.956 | 147.2255 | 142.286 | 131.5709 | 126.8184 | 115.0145 | 97.0409 | 80.6048 | 2341.7445
2015-08-06 | 65.6108 | 56.5916 | 50.5022 | 46.8367 | 46.1562 | 48.7845 | 55.6735 | 62.7069 | 77.6718 | 97.8889 | 117.8908 | 140.7832 | 157.5633 | 172.2407 | 181.6161 | 182.383 | 174.3193 | 165.7054 | 154.3294 | 143.3731 | 138.5141 | 127.0888 | 106.3509 | 88.7751 | 2659.3564
2015-08-07 | 72.9151 | 62.807 | 56.4681 | 52.4417 | 50.9972 | 53.7487 | 60.8995 | 67.4863 | 83.9159 | 105.4409 | 126.5909 | 148.2543 | 166.1285 | 178.9362 | 181.6331 | 180.0532 | 177.4691 | 173.0042 | 161.376 | 148.5005 | 137.1348 | 122.0416 | 100.6706 | 82.7741 | 2751.6874
2015-08-08 | 68.1209 | 57.9491 | 52.2223 | 48.8992 | 47.4438 | 52.799 | 57.2205 | 63.4796 | 74.2371 | 91.5096 | 108.9328 | 129.1048 | 148.5313 | 165.4941 | 174.5362 | 175.0874 | 172.0915 | 159.4879 | 144.5857 | 131.2958 | 126.662 | 116.1281 | 100.8355 | 87.5534 | 2554.2075
2015-08-09 | 72.162 | 62.3773 | 55.504 | 51.2863 | 49.2798 | 49.2798 | 50.619 | 54.7817 | 71.8939 | 94.9615 | 116.7824 | 137.4309 | 153.7806 | 165.0718 | 173.0707 | 177.8732 | 177.1999 | 167.0579 | 150.9427 | 135.9981 | 130.5009 | 119.0872 | 103.3628 | 89.7299 | 2610.0341
2015-08-10 | 75.8677 | 66.0721 | 58.5565 | 53.962 | 51.2682 | 50.3228 | 50.7539 | 53.2314 | 69.3252 | 92.0421 | 114.1221 | 137.5642 | 154.9892 | 168.6782 | 175.4219 | 176.763 | 175.5725 | 170.9004 | 158.5957 | 143.4033 | 136.6176 | 122.7544 | 103.7742 | 85.8712 | 2646.4297
2015-08-11 | 70.6886 | 60.5353 | 53.9898 | 50.1796 | 48.9788 | 52.2497 | 59.3421 | 64.8965 | 78.7219 | 100.139 | 122.1533 | 146.0934 | 165.5266 | 178.4127 | 181.7693 | 180.8338 | 181.3268 | 178.1429 | 168.711 | 154.6277 | 149.1169 | 132.2238 | 112.8034 | 92.1755 | 2783.6384
2015-08-12 | 75.8237 | 65.5085 | 57.8049 | 53.3143 | 51.876 | 54.6789 | 61.9191 | 68.1 | 82.4411 | 103.0163 | 123.357 | 143.2521 | 158.4208 | 170.6033 | 175.1543 | 174.8034 | 177.5364 | 175.7064 | 169.368 | 155.887 | 147.7932 | 132.1512 | 111.7326 | 93.1605 | 2783.4089
2015-08-13 | 76.4962 | 66.8444 | 59.7809 | 54.2314 | 52.8266 | 55.8056 | 63.4293 | 69.8732 | 85.7308 | 107.0033 | 128.2593 | 152.1402 | 170.4878 | 183.7504 | 190.6115 | 194.2037 | 194.1861 | 185.811 | 173.2369 | 157.4999 | 151.1446 | 136.7948 | 115.7201 | 96.5065 | 2922.3742
2015-08-14 | 80.7183 | 70.6568 | 63.9535 | 59.7613 | 57.9299 | 60.28 | 67.8917 | 73.9435 | 89.5505 | 111.8127 | 134.0751 | 152.8578 | 169.8945 | 179.2405 | 180.5621 | 168.5962 | 151.5486 | 139.0498 | 128.9756 | 120.6917 | 119.032 | 108.2088 | 94.2611 | 78.0173 | 2661.5093
2015-08-15 | 65.1919 | 57.1155 | 51.2049 | 48.5993 | 47.9236 | 51.404 | 59.5174 | 66.7515 | 82.0402 | 100.2907 | 119.3768 | 134.0897 | 145.7577 | 143.2672 | 123.1326 | 111.026 | 103.2601 | 98.0515 | 91.7152 | 85.8361 | 86.6221 | 80.6275 | 72.538 | 62.787 | 2088.1265
2015-08-16 | 53.4251 | 47.618 | 43.8513 | 41.4182 | 40.1997 | 40.6414 | 42.9028 | 46.7244 | 61.2846 | 84.8325 | 107.0817 | 124.8487 | 142.5423 | 145.7882 | 155.0679 | 148.0236 | 135.6448 | 123.3149 | 112.1201 | 102.9779 | 100.5186 | 93.5022 | 83.5575 | 70.9119 | 2148.7982
2015-08-17 | 60.28 | 52.9368 | 47.7489 | 44.2706 | 42.8449 | 42.9111 | 44.4557 | 47.4786 | 61.3044 | 83.6615 | 106.6899 | 127.0461 | 145.0874 | 160.991 | 163.6951 | 160.6386 | 162.1954 | 161.6007 | 154.5335 | 143.237 | 139.7508 | 127.4879 | 107.8675 | 86.9634 | 2475.6767
2015-08-18 | 72.6887 | 62.2576 | 55.683 | 51.9033 | 51.0965 | 56.3068 | 65.7951 | 70.2433 | 81.4919 | 102.965 | 125.5413 | 147.7164 | 165.3641 | 180.2058 | 187.0875 | 192.7628 | 193.6759 | 189.9493 | 181.9908 | 168.1372 | 162.7912 | 143.7212 | 118.4264 | 98.2017 | 2926.0028
2015-08-19 | 80.3781 | 69.4093 | 62.0086 | 57.498 | 56.1647 | 60.6041 | 70.6886 | 74.8369 | 87.0812 | 108.3666 | 129.1909 | 151.2378 | 169.878 | 183.049 | 190.978 | 200.6825 | 205.7245 | 200.5751 | 191.0478 | 174.937 | 168.5962 | 150.3535 | 124.6794 | 102.8881 | 3070.8541
2015-08-20 | 84.9373 | 73.4988 | 66.031 | 60.673 | 58.9826 | 62.9773 | 72.6887 | 61.7701 | 88.2997 | 109.8709 | 130.6019 | 154.1098 | 170.0757 | 186.1383 | 192.8505 | 194.1861 | 193.6583 | 188.4723 | 177.4691 | 164.2937 | 158.5162 | 142.9045 | 120.1787 | 98.7658 | 3011.9504
2015-08-21 | 83.4421 | 72.2478 | 64.8049 | 60.231 | 58.4212 | 62.6569 | 72.9367 | 77.7609 | 90.4613 | 110.3083 | 132.2529 | 154.9578 | 172.0584 | 187.4851 | 196.3928 | 205.6158 | 205.942 | 192.5173 | 178.8517 | 160.7988 | 156.8031 | 139.706 | 118.3577 | 97.2027 | 3052.2133
2015-08-22 | 79.7903 | 69.3778 | 62.3074 | 58.026 | 56.3258 | 60.2506 | 70.3916 | 74.9681 | 87.2345 | 108.722 | 129.6077 | 151.0669 | 168.9901 | 182.383 | 187.4678 | 198.5763 | 201.4886 | 193.5177 | 180.9018 | 162.7107 | 153.2328 | 135.6006 | 116.4687 | 98.6528 | 2988.0596
2015-08-23 | 82.2463 | 71.5409 | 63.4192 | 58.103 | 54.922 | 54.6415 | 56.0985 | 59.2838 | 75.198 | 100.2907 | 123.9751 | 146.7354 | 165.0718 | 177.9406 | 183.8531 | 188.6979 | 191.4846 | 187.5889 | 175.4721 | 158.3095 | 150.4 | 136.2634 | 119.7775 | 101.5471 | 2882.8608
2015-08-24 | 84.6 | 72.969 | 64.4799 | 58.905 | 55.6264 | 54.3897 | 54.5388 | 56.5156 | 73.2499 | 97.6766 | 119.8604 | 144.6313 | 165.4616 | 181.0207 | 190.6813 | 195.809 | 196.3397 | 193.4474 | 182.0249 | 166.9273 | 160.5426 | 141.8945 | 119.5563 | 99.319 | 2930.4669
2015-08-25 | 84.6465 | 72.9906 | 66.6174 | 62.9372 | 62.7269 | 68.3818 | 79.5084 | 84.0895 | 92.9412 | 111.9196 | 131.8464 | 150.1367 | 162.0667 | 166.8457 | 167.908 | 167.6135 | 168.5798 | 164.8122 | 153.8276 | 143.9636 | 141.5035 | 125.2301 | 106.5073 | 87.0341 | 2824.6344
2015-08-26 | 74.1718 | 65.5494 | 59.8004 | 56.5061 | 55.9189 | 60.9291 | 71.6799 | 75.8017 | 85.182 | 103.9029 | 121.7069 | 139.0051 | 151.7353 | 163.4366 | 171.512 | 178.1091 | 181.531 | 178.5984 | 168.7275 | 154.2353 | 149.1015 | 132.3255 | 108.6561 | 89.5027 | 2797.6249
2015-08-27 | 72.7103 | 62.4471 | 55.4569 | 51.4311 | 49.974 | 54.092 | 64.0242 | 67.5901 | 77.9281 | 97.6766 | 116.455 | 135.7919 | 152.1869 | 166.0796 | 177.1158 | 185.1744 | 189.9842 | 186.9838 | 177.0654 | 161.1995 | 156.171 | 138.8562 | 115.5435 | 96.1965 | 2808.1343
2015-08-28 | 79.8467 | 69.3988 | 62.0883 | 57.4214 | 55.5416 | 59.8883 | 70.7524 | 74.9462 | 85.427 | 101.7126 | 115.3941 | 127.6591 | 142.3614 | 157.96 | 172.6554 | 182.1101 | 186.3107 | 179.1559 | 164.8933 | 153.6397 | 146.9344 | 129.1191 | 108.9196 | 90.7981 | 2774.9345
2015-08-29 | 74.6731 | 65.1511 | 59.0214 | 54.9595 | 53.897 | 58.2861 | 69.073 | 74.6294 | 86.6338 | 108.1563 | 129.9387 | 147.3788 | 160.6066 | 173.5862 | 182.9977 | 188.403 | 186.5867 | 174.8201 | 160.2706 | 146.3378 | 141.1731 | 125.9237 | 109.1307 | 94.4083 | 2826.0428
2015-08-30 | 80.741 | 70.8055 | 63.9434 | 59.1574 | 57.125 | 59.0603 | 59.7613 | 62.2377 | 75.7687 | 99.1428 | 121.164 | 143.5395 | 159.3603 | 172.0418 | 181.7012 | 185.9316 | 185.3464 | 175.2713 | 158.1347 | 144.0545 | 138.9753 | 124.5383 | 109.2231 | 95.3312 | 2782.3562
2015-08-31 | 81.1956 | 70.4552 | 62.817 | 58.3826 | 55.3347 | 54.0269 | 54.8191 | 57.02 | 72.3875 | 97.2899 | 117.9732 | 137.7124 | 154.9421 | 167.1558 | 172.7218 | 174.5362 | 170.7518 | 163.4528 | 148.5005 | 134.9835 | 131.0787 | 117.836 | 102.6064 | 87.6125 | 2645.5924
2015-09-01 | 74.4767 | 66.0002 | 59.8297 | 55.4099 | 53.9991 | 54.8378 | 57.431 | 58.6242 | 73.1958 | 97.8889 | 120.886 | 144.768 | 158.7549 | 169.7957 | 179.5451 | 182.9293 | 180.2058 | 173.4365 | 162.1472 | 148.6853 | 144.6313 | 128.1878 | 107.579 | 89.9574 | 2743.2026
2015-09-02 | 74.7713 | 64.9067 | 58.344 | 54.6228 | 53.3882 | 57.7473 | 67.8396 | 72.0654 | 81.7315 | 100.9751 | 119.5702 | 140.0347 | 155.3984 | 165.1692 | 175.9577 | 182.3318 | 183.6819 | 177.8395 | 165.088 | 151.4398 | 143.6455 | 123.2588 | 101.2672 | 81.8001 | 2752.8747
2015-09-03 | 67.0719 | 57.8818 | 52.268 | 48.7404 | 47.8187 | 52.0035 | 62.4072 | 66.4525 | 75.0885 | 91.1716 | 103.2601 | 116.6596 | 130.0251 | 144.7528 | 155.7608 | 159.5198 | 161.8095 | 156.4869 | 147.2102 | 135.4977 | 131.9915 | 116.96 | 97.9139 | 79.1147 | 2457.8666
2015-09-04 | 65.1919 | 56.2121 | 50.7089 | 47.4525 | 46.5777 | 50.6729 | 61.3439 | 65.1919 | 71.3594 | 85.182 | 100.937 | 114.852 | 127.0604 | 139.02 | 144.1759 | 146.3684 | 149.0089 | 145.0265 | 137.9348 | 131.5709 | 129.7803 | 114.8249 | 95.7386 | 79.1933 | 2355.3853
2015-09-05 | 65.4574 | 56.8675 | 51.7124 | 48.6082 | 48.1249 | 52.46 | 63.8121 | 68.0375 | 77.3715 | 95.9489 | 115.557 | 134.4556 | 151.3621 | 164.7149 | 172.4895 | 172.971 | 165.4453 | 150.772 | 135.9392 | 126.2642 | 120.7472 | 107.3564 | 93.5022 | 80.7637 | 2520.7407
2015-09-06 | 68.3504 | 60.7222 | 55.1 | 51.3768 | 49.6263 | 49.5996 | 51.7851 | 55.4475 | 67.8084 | 85.8127 | 101.0258 | 113.3138 | 120.775 | 119.7913 | 117.425 | 114.3516 | 108.4981 | 103.9029 | 98.6528 | 95.986 | 96.0108 | 88.6918 | 80.05 | 70.7736 | 2024.8776
2015-09-07 | 61.0771 | 52.992 | 47.7925 | 44.3378 | 43.0602 | 43.2843 | 45.0387 | 47.3568 | 58.2765 | 74.0413 | 89.706 | 106.6377 | 121.4144 | 132.0205 | 137.0905 | 133.622 | 127.6163 | 119.5149 | 107.8806 | 104.1993 | 104.0317 | 93.5511 | 79.6775 | 66.1851 | 2040.4047
2015-09-08 | 56.0134 | 49.5729 | 44.8355 | 42.0958 | 41.9238 | 46.8713 | 57.1059 | 61.1561 | 68.0166 | 85.5204 | 105.078 | 123.6658 | 139.3181 | 151.7197 | 161.0872 | 165.088 | 164.6501 | 161.0552 | 148.1466 | 141.0231 | 136.1602 | 119.1975 | 99.697 | 81.9029 | 2450.9012
2015-09-09 | 67.8084 | 58.4502 | 52.9001 | 49.5018 | 48.1337 | 52.1676 | 62.6369 | 66.6174 | 73.824 | 90.0892 | 108.6166 | 126.4914 | 142.3915 | 156.8822 | 163.6789 | 170.9995 | 169.2037 | 161.4883 | 149.2712 | 139.6911 | 133.1843 | 114.6625 | 94.8507 | 77.7052 | 2531.2466
2015-09-10 | 64.8761 | 57.0391 | 52.049 | 48.6346 | 47.9149 | 52.5515 | 63.2684 | 66.9788 | 74.0848 | 88.4422 | 106.3248 | 121.8881 | 136.3519 | 149.3792 | 157.1672 | 160.8308 | 159.3922 | 152.8734 | 142.286 | 134.5289 | 129.9675 | 111.9329 | 93.1849 | 75.9227 | 2447.8699
2015-09-11 | 62.787 | 54.8659 | 49.5195 | 46.2936 | 45.5744 | 49.8579 | 60.496 | 64.5509 | 70.9438 | 86.1993 | 101.2927 | 115.0687 | 125.6687 | 133.4468 | 136.1602 | 137.0017 | 131.9189 | 122.1393 | 113.4752 | 108.7088 | 106.3509 | 94.3102 | 81.5033 | 67.31 | 2165.4438
2015-09-12 | 54.2872 | 48.2039 | 44.0691 | 42.0302 | 42.0302 | 46.6985 | 57.9587 | 61.4132 | 68.8003 | 81.8915 | 94.7892 | 106.2597 | 118.0967 | 129.8091 | 132.7909 | 131.6434 | 132.4709 | 133.4614 | 124.4397 | 114.6084 | 110.7466 | 99.634 | 87.8492 | 74.4331 | 2138.415
2015-09-13 | 61.0179 | 52.799 | 47.3308 | 43.1265 | 41.467 | 41.3126 | 43.5673 | 46.7244 | 56.8485 | 73.0014 | 91.9452 | 110.5074 | 125.7112 | 135.5418 | 139.5866 | 139.1243 | 133.403 | 125.4281 | 112.4548 | 106.0775 | 102.1591 | 90.2812 | 77.0496 | 64.4089 | 2060.8741
2015-09-14 | 55.0063 | 47.8974 | 43.0768 | 39.9598 | 38.1598 | 37.8638 | 39.0783 | 40.7946 | 52.4234 | 70.0845 | 88.6799 | 107.6314 | 122.7544 | 133.2863 | 138.7521 | 140.6034 | 140.8881 | 133.7535 | 121.4701 | 114.5002 | 110.8397 | 97.714 | 82.9121 | 67.3826 | 2065.5124
2015-09-15 | 56.6296 | 49.2887 | 44.9794 | 42.6384 | 42.5478 | 47.1051 | 57.3066 | 61.6114 | 69.2621 | 86.258 | 108.8274 | 127.2598 | 143.4336 | 158.1347 | 168.7931 | 176.0583 | 177.3681 | 172.5559 | 160.5906 | 151.7353 | 145.3005 | 125.8387 | 105.6745 | 83.9506 | 2563.1479
2015-09-16 | 68.6536 | 59.7711 | 53.3051 | 49.3774 | 48.3004 | 52.2315 | 62.787 | 66.8031 | 74.3024 | 90.3652 | 109.5005 | 128.3738 | 143.5092 | 155.1938 | 153.0921 | 146.6895 | 141.5336 | 135.6006 | 129.0187 | 126.463 | 121.484 | 105.7135 | 88.9418 | 72.818 | 2383.829
2015-09-17 | 59.2643 | 51.5671 | 46.4398 | 43.3425 | 43.0933 | 47.8012 | 58.7984 | 62.7369 | 68.8736 | 81.0932 | 97.7765 | 111.3723 | 121.679 | 127.3168 | 133.6366 | 133.2572 | 124.3551 | 114.4462 | 107.8281 | 108.9328 | 107.0686 | 95.5657 | 80.1518 | 64.8253 | 2091.2225
2015-09-18 | 54.1105 | 46.6553 | 42.9442 | 40.4725 | 40.2638 | 44.7594 | 55.5416 | 59.4297 | 65.6415 | 78.565 | 91.9573 | 106.7812 | 121.8184 | 136.2929 | 146.9344 | 153.0609 | 150.9893 | 151.9221 | 138.8711 | 131.3682 | 124.8769 | 108.8801 | 90.8342 | 73.5854 | 2256.556
2015-09-19 | 60.7222 | 52.2223 | 47.3568 | 44.3546 | 43.8178 | 48.1425 | 59.0505 | 63.9535 | 70.4128 | 84.9722 | 98.0265 | 106.5594 | 109.1571 | 104.8968 | 97.839 | 94.6171 | 91.7152 | 88.8942 | 85.5905 | 86.8338 | 85.4153 | 78.3189 | 68.6746 | 58.6435 | 1830.1873
2015-09-20 | 49.2976 | 43.3758 | 39.6569 | 37.6697 | 36.6762 | 37.662 | 40.7301 | 44.8778 | 53.1669 | 67.0615 | 80.6615 | 92.2119 | 101.191 | 107.2779 | 107.9856 | 98.6027 | 91.0872 | 87.4352 | 81.8229 | 83.0387 | 81.8229 | 73.6938 | 64.3684 | 55.1469 | 1656.5209
2015-09-21 | 47.0271 | 40.7784 | 36.9214 | 34.5208 | 33.5115 | 33.7679 | 35.6582 | 37.8716 | 46.9405 | 62.6769 | 78.9574 | 95.6274 | 110.0829 | 120.7472 | 128.1878 | 131.0498 | 130.6452 | 125.3432 | 113.8119 | 108.6693 | 103.1446 | 89.061 | 75.0228 | 60.5156 | 1880.5405
2015-09-22 | 49.965 | 43.2594 | 39.0783 | 37.3989 | 37.8094 | 43.0933 | 53.4251 | 58.4695 | 65.2838 | 78.4307 | 92.7586 | 106.2988 | 117.0283 | 119.3216 | 116.4278 | 112.7899 | 110.7466 | 106.7943 | 104.367 | 105.8304 | 100.8989 | 87.8492 | 73.023 | 59.3129 | 1919.6608
2015-09-23 | 48.8374 | 42.2352 | 38.074 | 35.9909 | 36.211 | 41.6869 | 53.1853 | 58.5468 | 61.334 | 69.6622 | 75.9778 | 83.8349 | 89.7538 | 91.051 | 91.7152 | 93.1971 | 95.2202 | 98.54 | 96.3577 | 99.256 | 96.7176 | 85.1353 | 71.7013 | 57.9587 | 1712.1803
2015-09-24 | 47.4786 | 41.1747 | 38.2222 | 35.9833 | 35.7563 | 41.0694 | 52.2406 | 57.4501 | 61.8198 | 70.2856 | 78.8564 | 87.8255 | 94.0895 | 101.9931 | 111.2923 | 118.8943 | 119.6116 | 116.4959 | 111.1192 | 111.026 | 108.025 | 96.0355 | 79.9257 | 66.0721 | 1882.7428
2015-09-25 | 55.1563 | 47.7838 | 43.2594 | 40.5287 | 40.3681 | 44.0523 | 52.7073 | 58.4792 | 65.7234 | 79.7 | 94.6663 | 105.1816 | 111.026 | 116.3188 | 123.5535 | 129.6077 | 125.2442 | 113.9062 | 106.4682 | 105.3112 | 101.3562 | 89.2996 | 75.1432 | 62.807 | 1987.6482
2015-09-26 | 52.4417 | 46.0018 | 42.0302 | 39.7524 | 39.7046 | 44.6749 | 55.4664 | 61.1166 | 65.9694 | 75.6258 | 88.9418 | 105.1816 | 118.2615 | 131.8029 | 136.6619 | 137.12 | 132.1802 | 122.8104 | 113.4214 | 111.9998 | 106.7551 | 96.0603 | 82.9236 | 78.9013 | 2085.8057
2015-09-27 | 64.8965 | 53.1853 | 48.7845 | 45.7281 | 44.5652 | 45.0727 | 47.6965 | 51.0604 | 62.6569 | 81.5489 | 99.3316 | 117.4113 | 132.5872 | 143.3882 | 151.1446 | 151.5331 | 141.8193 | 131.9189 | 119.0872 | 115.9648 | 108.7483 | 98.0515 | 84.9955 | 71.5088 | 2212.685
2015-09-28 | 60.496 | 53.0656 | 47.9061 | 44.4809 | 42.9359 | 43.1431 | 44.8778 | 47.9236 | 58.0838 | 76.1651 | 94.4697 | 112.7095 | 129.2053 | 141.5186 | 149.4719 | 151.9688 | 148.5313 | 138.7223 | 124.5102 | 124.2284 | 118.8805 | 104.6253 | 87.6125 | 71.2847 | 2216.8167
2015-09-29 | 60.0742 | 51.7669 | 47.2439 | 44.4809 | 44.4894 | 49.1735 | 60.0449 | 64.9983 | 71.4554 | 87.2817 | 105.7914 | 125.4988 | 138.3506 | 149.5491 | 155.3039 | 155.2567 | 151.331 | 140.9631 | 129.8091 | 125.3574 | 112.4548 | 97.739 | 80.8091 | 66.0105 | 2315.2336
2015-09-30 | 54.371 | 47.3047 | 43.168 | 40.7865 | 40.7623 | 45.6171 | 57.6322 | 61.9788 | 69.3988 | 84.6814 | 101.1274 | 116.1825 | 128.9039 | 133.2572 | 137.2828 | 130.992 | 130.1403 | 128.2593 | 121.3031 | 122.1393 | 116.7551 | 103.1702 | 86.1876 | 70.0634 | 2171.4651
2015-10-01 | 58.2669 | 50.5741 | 46.414 | 43.9601 | 43.559 | 48.7668 | 60.7911 | 65.2225 | 73.0338 | 88.6561 | 104.3799 | 120.9277 | 134.9541 | 145.7729 | 150.5395 | 158.8345 | 163.8083 | 158.7867 | 147.011 | 141.2932 | 133.7096 | 116.8371 | 96.085 | 86.1407 | 2438.3247
2015-10-02 | 67.31 | 56.5821 | 51.2139 | 47.9323 | 47.1051 | 51.5308 | 62.777 | 67.0098 | 75.1761 | 92.2604 | 111.1724 | 128.0305 | 142.5725 | 158.1824 | 166.9436 | 173.2369 | 176.9646 | 170.6858 | 156.7399 | 149.8583 | 141.0831 | 121.9858 | 102.2868 | 82.6133 | 2601.2532
2015-10-03 | 68.4549 | 59.4297 | 52.9001 | 49.3153 | 47.9498 | 51.9306 | 62.777 | 67.7876 | 76.9498 | 95.3188 | 115.0687 | 134.6608 | 148.7623 | 164.7636 | 173.1704 | 177.7721 | 177.5532 | 163.4205 | 144.0697 | 133.885 | 121.0667 | 106.2858 | 90.7138 | 76.3305 | 2560.3367
2015-10-04 | 63.9131 | 54.8846 | 49.484 | 45.882 | 44.1781 | 44.7679 | 47.4351 | 50.889 | 63.2985 | 81.5945 | 97.0409 | 111.5991 | 124.6653 | 132.8201 | 135.8655 | 134.0458 | 127.7733 | 118.6052 | 107.1994 | 105.2853 | 99.1428 | 87.9557 | 75.1651 | 62.8871 | 2066.3774
2015-10-05 | 51.3677 | 42.6714 | 36.6762 | 32.287 | 29.9824 | 29.3836 | 30.4128 | 31.4172 | 36.9137 | 45.8905 | 55.6076 | 63.0275 | 71.5302 | 79.4746 | 86.3988 | 91.6426 | 96.8667 | 94.8015 | 86.9398 | 86.3049 | 82.0173 | 70.9864 | 58.6919 | 46.8972 | 1438.1897
2015-10-06 | 38.3708 | 32.8493 | 29.6926 | 28.117 | 28.4867 | 33.3872 | 42.8118 | 47.27 | 51.8305 | 60.7911 | 70.5825 | 79.8806 | 90.1972 | 98.1766 | 106.5203 | 109.1835 | 112.1603 | 107.9987 | 103.8514 | 108.1694 | 101.5089 | 88.098 | 74.1935 | 60.1134 | 1704.2413
2015-10-07 | 48.9346 | 42.7788 | 39.0151 | 36.6915 | 36.1806 | 40.5529 | 51.4221 | 56.7818 | 59.3032 | 68.7793 | 79.7451 | 87.9439 | 94.9246 | 100.9751 | 104.0704 | 102.6576 | 102.4785 | 100.0379 | 98.1891 | 102.9907 | 97.5393 | 88.1691 | 72.9906 | 57.5746 | 1770.7265
2015-10-08 | 47.3482 | 41.2477 | 37.1367 | 35.1696 | 35.3947 | 40.36 | 51.3315 | 55.8622 | 60.7123 | 72.6026 | 87.1402 | 100.2528 | 113.26 | 123.7923 | 132.7036 | 136.8243 | 136.4699 | 132.0786 | 124.2706 | 124.3411 | 117.2744 | 102.4274 | 85.5672 | 70.0845 | 2063.6524
2015-10-09 | 57.2874 | 49.8401 | 44.9625 | 41.5321 | 41.0046 | 40.0716 | 55.3723 | 59.859 | 65.8156 | 80.7637 | 96.3825 | 111.319 | 123.1887 | 135.1303 | 143.5849 | 149.3175 | 150.338 | 144.8136 | 132.7764 | 130.198 | 121.679 | 105.8434 | 89.3832 | 71.9689 | 2242.4324
2015-10-10 | 58.6726 | 49.9293 | 45.0303 | 41.6625 | 41.0694 | 45.166 | 55.6547 | 60.7123 | 67.2375 | 82.51 | 99.0296 | 112.8168 | 125.697 | 136.8687 | 144.7224 | 150.1522 | 151.2378 | 143.6757 | 128.8466 | 123.8063 | 114.5273 | 101.1656 | 87.152 | 73.3364 | 2240.6789
2015-10-11 | 60.9291 | 52.579 | 47.5657 | 43.9685 | 42.0138 | 42.1122 | 44.4304 | 46.9145 | 57.7473 | 77.0053 | 94.9984 | 111.5457 | 125.1735 | 136.0128 | 143.6303 | 148.5775 | 149.5337 | 143.0556 | 127.3026 | 120.5113 | 111.2923 | 97.9264 | 85.4854 | 71.7333 | 2182.0447
2015-10-12 | 60.2898 | 51.7487 | 45.711 | 42.1122 | 40.4323 | 40.1196 | 41.7359 | 42.9773 | 54.3524 | 74.444 | 92.9655 | 110.0166 | 125.4988 | 136.0276 | 143.237 | 147.1948 | 147.6396 | 141.9397 | 128.7032 | 127.5878 | 118.4951 | 103.5555 | 89.0491 | 73.6071 | 2179.4408
2015-10-13 | 61.79 | 53.9341 | 49.2532 | 46.5777 | 46.6381 | 51.5762 | 62.0484 | 66.6999 | 73.1202 | 87.6835 | 105.5577 | 120.9138 | 132.2383 | 141.714 | 148.3004 | 152.686 | 152.0934 | 145.895 | 134.3678 | 133.8557 | 124.1299 | 109.0515 | 92.0785 | 75.4392 | 2367.6425
2015-10-14 | 62.6969 | 55.2314 | 50.88 | 48.0461 | 47.3829 | 52.524 | 64.5611 | 69.4936 | 76.0438 | 91.3768 | 107.4218 | 121.7905 | 132.3837 | 144.191 | 150.772 | 152.5768 | 148.9935 | 139.9151 | 132.006 | 133.9581 | 123.1466 | 107.2386 | 89.682 | 72.6564 | 2374.9689
2015-10-15 | 58.5855 | 50.296 | 45.6683 | 42.8863 | 42.9442 | 47.6354 | 58.75 | 64.1759 | 69.926 | 82.7396 | 95.7016 | 108.8274 | 95.2448 | 126.5056 | 128.7319 | 130.3566 | 126.4488 | 120.3311 | 113.0853 | 114.8114 | 105.4539 | 91.9937 | 75.5709 | 60.9685 | 2057.6386
2015-10-16 | 49.3597 | 42.3173 | 38.2301 | 35.5602 | 34.4022 | 37.6465 | 46.3108 | 49.5284 | 52.8541 | 61.4429 | 70.148 | 77.3049 | 85.0654 | 93.3191 | 101.0258 | 108.946 | 113.556 | 111.2124 | 102.0697 | 101.2291 | 92.9533 | 79.3396 | 64.5509 | 50.5292 | 1698.9016
2015-10-17 | 39.7524 | 33.1395 | 29.6788 | 27.7432 | 27.2728 | 30.7481 | 38.8654 | 42.7705 | 46.8626 | 54.9688 | 63.0475 | 70.8162 | 77.5828 | 85.7425 | 94.016 | 101.7636 | 105.6096 | 102.108 | 91.4251 | 87.8847 | 79.0697 | 67.6421 | 57.5651 | 47.0271 | 1503.102
2015-10-18 | 38.9284 | 32.3444 | 28.5406 | 26.4804 | 25.5717 | 26.3894 | 28.9674 | 31.7651 | 39.3552 | 50.4394 | 60.7025 | 69.8415 | 79.4859 | 88.3828 | 96.8295 | 103.5555 | 106.0645 | 102.1591 | 91.3768 | 88.5491 | 80.1065 | 69.073 | 59.42 | 48.8462 | 1473.1748
2015-10-19 | 40.36 | 34.2763 | 30.1764 | 27.8297 | 26.8784 | 26.9177 | 28.6622 | 30.3989 | 38.2301 | 50.108 | 61.7304 | 72.4843 | 84.4026 | 94.0895 | 102.2357 | 107.2255 | 108.9592 | 105.0651 | 96.6307 | 97.3273 | 89.6103 | 76.5735 | 64.1254 | 51.8487 | 1546.1457
2015-10-20 | 42.1367 | 35.7186 | 32.1651 | 30.3849 | 30.4895 | 34.5876 | 43.4174 | 48.3443 | 54.1756 | 66.4423 | 79.4859 | 91.3526 | 101.9804 | 110.6536 | 118.7703 | 121.1918 | 119.5149 | 113.9197 | 108.5245 | 110.4543 | 100.9116 | 86.8692 | 72.119 | 58.1897 | 1811.7995
2015-10-21 | 47.1658 | 41.0532 | 37.7008 | 35.6658 | 35.8168 | 40.4243 | 51.0965 | 56.9056 | 59.206 | 67.0098 | 76.2202 | 82.0631 | 86.1524 | 88.1691 | 88.6561 | 89.0849 | 88.181 | 86.4341 | 86.3753 | 91.4855 | 85.0305 | 75.198 | 62.7169 | 49.6263 | 1607.4378
2015-10-22 | 40.7704 | 35.267 | 32.2583 | 30.8252 | 31.1628 | 35.1546 | 46.1819 | 52.0308 | 54.5575 | 61.5024 | 70.8481 | 80.741 | 88.4065 | 95.2325 | 100.3667 | 103.3371 | 101.598 | 97.3024 | 95.3312 | 98.6152 | 91.5943 | 80.2989 | 66.432 | 53.0656 | 1642.8801
2015-10-23 | 43.1431 | 37.8483 | 34.4837 | 32.5243 | 32.3085 | 36.5463 | 47.2786 | 53.1024 | 54.5575 | 60.4567 | 67.5798 | 73.7915 | 79.1484 | 82.6592 | 85.9649 | 87.5061 | 86.6103 | 84.1359 | 82.3036 | 85.6256 | 82.5788 | 73.2066 | 61.3736 | 49.8758 | 1514.6095
2015-10-24 | 41.037 | 35.5451 | 32.5387 | 31.2545 | 31.6584 | 35.613 | 44.5737 | 50.592 | 54.4083 | 62.0484 | 68.7374 | 73.683 | 76.1981 | 78.9462 | 81.0819 | 83.0272 | 82.8201 | 80.2423 | 78.0843 | 79.2721 | 73.423 | 66.1748 | 58.2765 | 48.3004 | 1447.5363
2015-10-25 | 38.8496 | 32.6757 | 28.8994 | 26.6431 | 25.86 | 26.4544 | 28.9198 | 32.1436 | 38.9126 | 49.1292 | 58.4019 | 65.7132 | 72.323 | 78.6883 | 83.6037 | 87.2463 | 87.329 | 82.9581 | 75.2856 | 74.2697 | 67.6213 | 59.9372 | 52.1311 | 42.9773 | 1316.9732
2015-10-26 | 35.4849 | 30.3919 | 27.471 | 25.5142 | 24.7291 | 24.8864 | 26.4739 | 29.0082 | 35.0199 | 45.0472 | 54.6882 | 62.4371 | 69.3883 | 76.5072 | 82.4526 | 87.1284 | 89.2519 | 86.1993 | 79.3508 | 81.4235 | 74.2588 | 63.2985 | 51.6306 | 40.2237 | 1302.2658
2015-10-27 | 31.8934 | 27.0752 | 24.4535 | 23.3115 | 23.7096 | 27.7099 | 36.5005 | 41.9811 | 44.9709 | 52.992 | 61.6709 | 70 | 77.2604 | 85.2986 | 92.5154 | 99.3442 | 102.965 | 100.2401 | 94.7278 | 97.0409 | 87.6362 | 74.063 | 60.0938 | 46.6639 | 1484.1177
2015-10-28 | 37.2985 | 31.7509 | 28.4597 | 26.8522 | 26.9374 | 31.2122 | 40.7865 | 46.0104 | 49.4218 | 59.1574 | 68.8841 | 78.8228 | 87.4352 | 98.5776 | 106.9902 | 113.2197 | 116.2643 | 112.6961 | 105.3501 | 107.3171 | 97.0658 | 84.0316 | 68.8317 | 54.6976 | 1678.0707
2015-10-29 | 44.4725 | 37.9494 | 33.8781 | 31.7224 | 31.7153 | 35.7866 | 46.3624 | 51.223 | 54.5295 | 66.6999 | 77.5383 | 88.2878 | 98.9919 | 108.3929 | 116.1009 | 122.9224 | 124.2847 | 118.0006 | 108.4061 | 108.4324 | 98.7407 | 85.3336 | 70.0105 | 55.2783 | 1815.0601
2015-10-30 | 43.484 | 36.9291 | 32.8203 | 30.6082 | 30.3501 | 34.2911 | 44.0858 | 49.2976 | 52.4966 | 63.188 | 75.494 | 86.2932 | 95.9489 | 104.0962 | 108.946 | 112.7497 | 115.3941 | 110.3481 | 103.6584 | 105.0133 | 95.6398 | 83.9043 | 69.6832 | 55.8056 | 1740.5256
2015-10-31 | 44.4894 | 37.693 | 33.2778 | 31.1275 | 30.6781 | 34.5802 | 44.4472 | 49.9204 | 53.499 | 63.9434 | 74.2806 | 84.217 | 91.8968 | 97.4146 | 101.598 | 104.7933 | 105.4928 | 98.8788 | 87.4116 | 81.4235 | 70.6568 | 61.939 | 52.2406 | 42.3584 | 1578.2579
2015-11-01 | 33.5041 | 28.0501 | 25.1265 | 23.5683 | 23.0075 | 23.642 | 26.4089 | 29.3836 | 35.8319 | 44.4725 | 51.3134 | 54.6042 | 55.8811 | 55.8433 | 56.231 | 56.4871 | 55.6735 | 52.6981 | 50.664 | 53.5914 | 49.0141 | 43.5423 | 37.3525 | 31.3889 | 997.2805
2015-11-02 | 99.5835 | 21.9238 | 21.4122 | 21.3713 | 22.0541 | 24.1421 | 28.03 | 35.9076 | 43.5507 | 46.828 | 47.296 | 46.3882 | 45.5574 | 44.2621 | 43.6841 | 43.0685 | 43.3092 | 46.9751 | 54.6228 | 52.4051 | 48.5993 | 42.4325 | 35.1621 | 29.2059 | 987.7719
2015-11-03 | 24.6726 | 23.3176 | 22.5733 | 22.8563 | 24.5035 | 30.5174 | 41.7685 | 46.6898 | 48.0023 | 49.6975 | 51.776 | 53.3605 | 53.5452 | 53.8321 | 53.2314 | 52.3137 | 53.13 | 56.7437 | 64.7134 | 62.0385 | 56.9723 | 48.7845 | 39.9039 | 32.1221 | 1067.066
2015-11-04 | 27.1476 | 24.1732 | 22.5793 | 22.2742 | 23.0257 | 27.6302 | 35.9909 | 42.556 | 48.0811 | 52.5607 | 57.0677 | 61.1363 | 63.1177 | 64.9372 | 65.9181 | 66.7102 | 65.4472 | 67.5175 | 75.8237 | 73.1958 | 67.2271 | 57.1155 | 47.7139 | 38.9836 | 1197.9305
2015-11-05 | 32.4739 | 28.3318 | 26.2922 | 25.3295 | 25.9693 | 30.4476 | 39.3076 | 42.5395 | 51.1868 | 60.2016 | 67.4863 | 73.3905 | 77.416 | 79.4296 | 80.197 | 78.6883 | 76.1871 | 78.129 | 85.8244 | 81.9372 | 75.4831 | 65.8464 | 54.1105 | 43.3092 | 1379.5144
2015-11-06 | 35.515 | 30.7131 | 27.7898 | 26.2986 | 26.5259 | 31.0923 | 39.6648 | 46.5691 | 54.2314 | 63.3991 | 73.0338 | 81.5033 | 88.2878 | 93.4656 | 95.986 | 95.8004 | 91.558 | 87.5889 | 91.8241 | 85.4971 | 75.7797 | 63.9535 | 51.5671 | 41.1099 | 1498.7542
2015-11-07 | 33.1323 | 28.3924 | 25.5973 | 24.5473 | 24.7983 | 28.7096 | 37.4607 | 43.5757 | 50.6999 | 59.2351 | 67.3515 | 74.9681 | 81.3323 | 86.6691 | 89.0014 | 88.5016 | 83.7655 | 80.0161 | 82.4985 | 74.5858 | 66.7412 | 58.0068 | 49.6174 | 41.4264 | 1380.6301
2015-11-08 | 34.2172 | 29.3699 | 26.2339 | 24.9243 | 24.6601 | 25.7829 | 28.6014 | 34.5134 | 46.139 | 56.6106 | 64.3684 | 70.8374 | 76.5183 | 78.9462 | 78.5874 | 75.9667 | 72.2908 | 73.4771 | 76.121 | 69.5041 | 62.9974 | 55.7112 | 48.3882 | 40.4885 | 1275.2555
2015-11-09 | 34.232 | 29.3494 | 26.6496 | 25.285 | 24.7354 | 25.5079 | 27.4512 | 31.7509 | 40.7946 | 48.5377 | 53.1484 | 55.9472 | 56.2974 | 54.8939 | 53.4528 | 51.2139 | 50.7089 | 55.8528 | 60.555 | 57.1059 | 52.195 | 45.4381 | 38.7552 | 31.4738 | 1031.3319
2015-11-10 | 26.1692 | 23.4275 | 22.0245 | 21.4473 | 22.1611 | 25.4377 | 34.2615 | 42.1122 | 45.8905 | 50.6909 | 54.5202 | 57.9972 | 60.5943 | 62.9172 | 64.0748 | 65.0085 | 63.9535 | 65.6313 | 72.0332 | 67.3411 | 60.3095 | 51.2953 | 42.5313 | 34.1359 | 1135.9657
2015-11-11 | 27.3784 | 23.765 | 21.912 | 21.2431 | 21.7173 | 24.4785 | 30.4267 | 37.1521 | 43.584 | 49.7064 | 54.5388 | 58.1416 | 61.5717 | 64.8253 | 66.3702 | 67.8084 | 66.5556 | 67.2271 | 73.4663 | 69.0625 | 61.9291 | 52.8358 | 43.459 | 34.2467 | 1143.4015
2015-11-12 | 27.2794 | 23.5867 | 21.9771 | 21.313 | 22.1254 | 26.1047 | 35.1845 | 40.948 | 45.1915 | 50.898 | 57.0582 | 62.827 | 68.1104 | 73.7264 | 77.6162 | 79.036 | 76.9055 | 75.4721 | 80.8659 | 75.527 | 67.7772 | 58.1994 | 47.7052 | 37.8327 | 1253.2675
2015-11-13 | 30.6082 | 26.6431 | 24.3536 | 23.6666 | 24.2167 | 28.2445 | 37.3371 | 43.5507 | 49.4573 | 57.364 | 64.866 | 70.678 | 76.5514 | 81.9029 | 84.3446 | 84.6814 | 81.6402 | 79.9935 | 84.7279 | 79.1709 | 70.9757 | 60.6533 | 49.2178 | 39.3314 | 1354.1766
2015-11-14 | 31.7865 | 27.2134 | 24.836 | 23.6359 | 23.9192 | 27.5373 | 36.5081 | 42.9276 | 48.8992 | 55.683 | 61.939 | 66.2365 | 70.3916 | 73.4879 | 75.3295 | 75.3076 | 72.1083 | 71.0928 | 74.4767 | 68.4131 | 61.651 | 53.7487 | 46.371 | 38.6452 | 1252.1451
2015-11-15 | 32.2439 | 27.9298 | 25.6228 | 24.4098 | 24.3038 | 25.5717 | 28.7773 | 34.1728 | 43.409 | 51.9306 | 57.853 | 62.577 | 65.8054 | 68.6955 | 69.7782 | 69.1675 | 66.535 | 66.0105 | 69.7887 | 63.9939 | 57.9972 | 51.7669 | 45.5403 | 39.0941 | 1172.9747
2015-11-16 | 32.9362 | 29.1104 | 26.741 | 25.4632 | 25.0885 | 26.1176 | 28.0367 | 32.4595 | 43.7259 | 55.3065 | 64.4393 | 71.5195 | 77.7052 | 81.7087 | 83.4305 | 83.3267 | 80.1065 | 79.5084 | 84.4722 | 79.0473 | 71.1141 | 62.2377 | 53.3974 | 44.111 | 1341.1101
2015-11-17 | 37.0213 | 33.0015 | 30.8112 | 29.8787 | 31.0923 | 36.2338 | 46.6639 | 53.3974 | 61.79 | 73.9543 | 86.4458 | 96.5189 | 104.0317 | 108.2746 | 108.8405 | 107.0033 | 103.1702 | 103.2857 | 107.1601 | 99.1931 | 87.8847 | 74.15 | 61.334 | 48.6963 | 1729.8335
2015-11-18 | 39.7604 | 34.454 | 31.0078 | 29.3015 | 29.7132 | 33.6139 | 44.2201 | 50.898 | 56.6296 | 63.4091 | 68.1521 | 69.0625 | 66.7515 | 64.2772 | 61.0179 | 57.8433 | 57.9876 | 64.4089 | 71.1994 | 69.052 | 63.9434 | 56.4112 | 47.1137 | 39.0546 | 1269.283
2015-11-19 | 33.7679 | 31.5164 | 30.6221 | 30.7481 | 32.8638 | 39.5933 | 54.4736 | 61.6709 | 64.6931 | 66.1851 | 65.3757 | 62.3074 | 58.6822 | 56.0512 | 54.0269 | 53.2774 | 54.5388 | 62.0385 | 69.9894 | 68.685 | 64.7338 | 57.3161 | 48.3706 | 39.9438 | 1261.4712
2015-11-20 | 34.3503 | 31.701 | 31.0641 | 31.3323 | 33.57 | 40.2798 | 53.5822 | 59.4492 | 58.0838 | 58.0645 | 57.5651 | 56.9533 | 55.9945 | 55.025 | 53.462 | 52.7073 | 53.0472 | 59.8786 | 67.746 | 66.535 | 62.1878 | 55.0719 | 46.5001 | 38.2301 | 1212.3811
2015-11-21 | 32.3229 | 28.8994 | 27.7565 | 27.0818 | 28.0367 | 34.5728 | 44.7425 | 51.1597 | 53.499 | 55.8056 | 57.7761 | 58.2283 | 56.6201 | 55.504 | 54.157 | 52.946 | 53.6562 | 59.1185 | 62.6569 | 59.4882 | 55.3723 | 49.9025 | 43.8597 | 37.3448 | 1140.5075
2015-11-22 | 31.488 | 27.9699 | 26.0982 | 25.4505 | 25.6868 | 27.1871 | 30.8042 | 36.0136 | 45.6427 | 54.9033 | 60.5943 | 63.7718 | 63.9434 | 63.7415 | 62.7369 | 61.0376 | 60.732 | 65.6313 | 69.5252 | 66.8961 | 63.1378 | 57.7377 | 51.8669 | 44.3126 | 1186.9094
2015-11-23 | 37.6077 | 33.5334 | 30.5034 | 28.8384 | 28.5339 | 29.5207 | 31.6442 | 36.7681 | 49.9025 | 64.7643 | 75.4392 | 82.7511 | 87.5416 | 91.0992 | 91.7515 | 90.5334 | 85.9766 | 87.79 | 93.5511 | 89.6581 | 82.9811 | 73.5529 | 63.7314 | 54.6042 | 1522.578
2015-11-24 | 44.0355 | 38.152 | 35.0049 | 33.8266 | 34.7662 | 39.6887 | 49.5195 | 57.02 | 67.5278 | 80.1405 | 92.4425 | 106.0385 | 117.083 | 122.8804 | 125.6545 | 124.6088 | 118.1104 | 115.7608 | 120.4975 | 112.5218 | 102.3762 | 88.0268 | 75.8677 | 61.8595 | 1963.4104
2015-11-25 | 50.7989 | 43.7844 | 40.0716 | 38.6609 | 39.0072 | 44.1194 | 54.3804 | 61.9092 | 72.6564 | 84.7744 | 96.0603 | 103.9158 | 108.4981 | 111.8661 | 111.4523 | 109.1835 | 104.3541 | 105.9214 | 110.3481 | 104.4832 | 95.1462 | 84.6349 | 72.7103 | 61.7701 | 1910.5073
2015-11-26 | 51.8942 | 45.6597 | 41.793 | 39.8401 | 39.856 | 42.7953 | 49.484 | 56.2784 | 64.927 | 71.4021 | 71.8511 | 70.3068 | 67.9333 | 64.2974 | 60.0449 | 56.0228 | 53.897 | 58.3054 | 63.3488 | 60.4272 | 55.7395 | 51.0423 | 45.1151 | 38.0974 | 1320.359
2015-11-27 | 32.1722 | 28.5204 | 26.7475 | 26.3051 | 26.7672 | 28.913 | 33.1614 | 39.8799 | 48.3355 | 54.3059 | 58.0068 | 59.4882 | 59.3908 | 57.3735 | 55.1094 | 51.6579 | 47.296 | 45.5488 | 46.8021 | 43.5256 | 41.3451 | 39.4265 | 36.4928 | 32.4235 | 1018.9953
2015-11-28 | 28.757 | 26.6757 | 25.86 | 26.1369 | 27.6169 | 30.8533 | 36.3861 | 42.7045 | 49.1557 | 52.992 | 53.5175 | 51.7851 | 49.6797 | 47.81 | 46.1047 | 45.0133 | 45.0981 | 50.7899 | 57.6801 | 55.683 | 52.6706 | 50.862 | 44.9964 | 38.7709 | 1037.5992
2015-11-29 | 33.5627 | 30.8954 | 29.5207 | 29.3494 | 30.1556 | 31.8791 | 35.8092 | 41.1261 | 47.1831 | 50.0901 | 50.4663 | 50.2243 | 49.3597 | 48.4058 | 47.2526 | 46.1219 | 45.132 | 49.0407 | 54.3152 | 51.9124 | 48.2828 | 44.3042 | 39.2047 | 33.4092 | 1017.0031
2015-11-30 | 28.1304 | 24.9432 | 23.4092 | 22.8382 | 23.1167 | 24.3225 | 26.728 | 30.7621 | 38.2301 | 44.4472 | 48.5201 | 51.2772 | 53.3328 | 54.399 | 54.6135 | 53.897 | 52.8541 | 57.0773 | 64.8965 | 62.1281 | 57.6418 | 51.1326 | 43.7844 | 35.297 | 1027.7789
2015-12-01 | 29.3289 | 25.7252 | 24.0182 | 23.4887 | 24.3911 | 29.0422 | 38.6687 | 44.5737 | 49.9472 | 56.1932 | 63.1077 | 68.7479 | 71.4448 | 72.4735 | 71.1887 | 68.8841 | 66.7618 | 71.6478 | 79.9709 | 77.3604 | 71.3914 | 62.2476 | 52.195 | 41.581 | 1284.3795
2015-12-02 | 33.5041 | 28.8994 | 26.1434 | 25.0948 | 25.815 | 30.1417 | 40.2478 | 45.9847 | 50.3318 | 56.9247 | 63.6004 | 67.85 | 70.3598 | 71.9475 | 71.4021 | 69.5568 | 67.0822 | 72.4412 | 80.6161 | 77.605 | 71.7013 | 62.9172 | 52.3594 | 41.6706 | 1304.1971
2015-12-03 | 33.4018 | 28.5069 | 26.053 | 24.9243 | 25.4059 | 29.7546 | 40.7462 | 45.9933 | 51.3949 | 59.5272 | 66.1234 | 71.7013 | 76.0218 | 78.0843 | 79.7 | 80.4574 | 76.7837 | 78.4979 | 85.9532 | 81.9258 | 74.9462 | 65.2429 | 54.2779 | 42.7705 | 1378.1945
2015-12-04 | 34.2689 | 29.5139 | 26.9374 | 25.8664 | 26.4869 | 31.0571 | 41.0208 | 47.0531 | 52.3411 | 60.3291 | 67.0822 | 72.969 | 77.683 | 79.8128 | 81.2412 | 81.7772 | 77.7832 | 79.6775 | 87.6007 | 84.1822 | 77.6496 | 68.5281 | 56.8485 | 45.353 | 1413.0626
2015-12-05 | 36.4547 | 30.9024 | 28.0769 | 26.957 | 27.3916 | 31.872 | 41.9893 | 48.1425 | 54.6509 | 64.3582 | 72.0547 | 77.4604 | 80.5028 | 80.2197 | 79.9145 | 81.0364 | 79.531 | 81.5147 | 85.8127 | 80.5708 | 74.0087 | 66.1748 | 57.6705 | 47.8799 | 1435.1468
2015-12-06 | 39.023 | 33.2997 | 29.9409 | 27.9298 | 27.1344 | 28.0167 | 30.8813 | 35.7337 | 46.8194 | 59.0408 | 68.8422 | 75.6917 | 80.4801 | 83.4998 | 84.8675 | 83.7655 | 78.8564 | 76.7948 | 80.0726 | 72.5811 | 65.621 | 58.7016 | 50.5471 | 41.7033 | 1359.8444
2015-12-07 | 33.4749 | 28.7638 | 25.8535 | 24.0429 | 23.5499 | 24.2478 | 26.1111 | 29.6788 | 39.0467 | 49.5729 | 56.9342 | 61.9689 | 64.6829 | 66.1953 | 66.6484 | 64.6829 | 62.0385 | 65.1511 | 73.4554 | 67.9541 | 62.2676 | 54.4456 | 45.0387 | 35.6808 | 1151.487
2015-12-08 | 28.5609 | 24.6162 | 22.7477 | 22.1135 | 22.8442 | 27.0884 | 36.2947 | 41.9484 | 45.8905 | 50.7269 | 55.1 | 58.0453 | 59.9959 | 61.5915 | 62.3374 | 63.2382 | 62.8871 | 67.3515 | 76.3968 | 73.7806 | 66.7206 | 57.4118 | 47.27 | 36.5997 | 1171.5577
2015-12-09 | 29.0218 | 25.3422 | 23.5806 | 23.0985 | 23.8883 | 28.6893 | 39.9358 | 45.7793 | 48.9169 | 51.5308 | 53.1116 | 53.4528 | 53.3143 | 52.7073 | 51.7487 | 50.3587 | 51.0423 | 58.4599 | 68.6432 | 67.4967 | 63.1278 | 56.0985 | 46.6898 | 37.7396 | 1103.7748
2015-12-10 | 31.4809 | 28.9198 | 27.7565 | 28.4395 | 30.4337 | 38.5667 | 54.4549 | 64.3886 | 63.4594 | 60.3389 | 57.9299 | 55.0532 | 52.6523 | 51.0333 | 49.0761 | 48.3355 | 49.3863 | 57.9876 | 70.6356 | 70.6249 | 68.7374 | 62.3872 | 53.1853 | 43.8262 | 1219.0896
2015-12-11 | 38.1364 | 35.5753 | 34.99 | 35.1845 | 37.8327 | 46.6898 | 64.7643 | 74.1174 | 70.0845 | 66.0823 | 61.2747 | 58.1608 | 55.1469 | 52.9184 | 50.862 | 50.0097 | 51.1416 | 59.3908 | 69.9577 | 69.1045 | 66.4937 | 60.182 | 50.3497 | 41.3695 | 1299.8194
2015-12-12 | 35.3646 | 32.4379 | 31.4384 | 31.3181 | 33.8266 | 41.8911 | 57.0868 | 65.2429 | 65.8361 | 65.7234 | 63.6911 | 61.1265 | 58.0934 | 55.5793 | 53.0472 | 52.1676 | 53.5544 | 62.6769 | 71.8404 | 70.1163 | 68.0479 | 63.0977 | 56.1363 | 48.2565 | 1297.5975
2015-12-13 | 41.5891 | 38.8339 | 37.5613 | 37.7163 | 39.181 | 43.276 | 49.965 | 58.5178 | 63.8727 | 63.55 | 59.7613 | 56.3637 | 53.897 | 51.5036 | 49.4218 | 48.3443 | 48.0461 | 53.5637 | 60.6435 | 58.3344 | 55.9094 | 52.4142 | 47.3308 | 42.0056 | 1211.6027
2015-12-14 | 36.8677 | 33.8193 | 32.7986 | 32.8855 | 33.9149 | 36.9521 | 42.8118 | 50.664 | 58.3633 | 59.2643 | 56.089 | 53.7302 | 51.9306 | 50.4663 | 49.4929 | 48.6346 | 48.6698 | 54.5015 | 64.8049 | 63.4896 | 60.5058 | 55.1751 | 46.6726 | 39.023 | 1161.5276
2015-12-15 | 33.7092 | 31.1628 | 30.9727 | 31.5093 | 34.4837 | 42.6714 | 59.4005 | 69.052 | 68.2147 | 63.4293 | 60.0155 | 57.3544 | 56.7342 | 55.749 | 54.5762 | 54.399 | 54.6789 | 61.3835 | 72.5165 | 71.3594 | 66.9581 | 59.2838 | 49.4929 | 40.1036 | 1279.2105
2015-12-16 | 33.6212 | 30.7411 | 29.7201 | 30.0862 | 32.1507 | 39.5615 | 55.1188 | 63.1177 | 62.2576 | 59.07 | 57.001 | 55.9567 | 55.6076 | 55.7678 | 55.5793 | 55.8244 | 55.9661 | 61.0968 | 70.997 | 69.1255 | 63.7819 | 55.222 | 45.8306 | 36.5081 | 1229.7098
2015-12-17 | 29.5482 | 26.1822 | 24.9053 | 24.7605 | 26.4154 | 32.3516 | 44.4641 | 51.7487 | 52.5057 | 53.3974 | 54.2035 | 54.6789 | 55.6358 | 56.8199 | 58.0742 | 59.3519 | 58.721 | 63.4192 | 72.1512 | 69.3357 | 63.54 | 56.2121 | 46.5604 | 36.7451 | 1171.7279
2015-12-18 | 29.8649 | 26.3894 | 25.0253 | 24.9558 | 26.5064 | 32.0791 | 44.3126 | 51.876 | 54.6415 | 56.3068 | 57.0105 | 56.4301 | 56.3353 | 58.1319 | 59.2449 | 59.5272 | 58.9535 | 63.2784 | 72.044 | 69.2621 | 64.8558 | 57.2396 | 48.0023 | 38.5274 | 1190.8009
2015-12-19 | 31.6868 | 28.2445 | 26.6431 | 26.3959 | 27.8231 | 33.3216 | 44.4894 | 52.5698 | 55.5134 | 57.2205 | 58.7403 | 59.3421 | 59.274 | 59.8297 | 59.8199 | 59.5954 | 58.4792 | 61.8297 | 69.1675 | 65.2736 | 60.1624 | 54.0455 | 47.409 | 39.3076 | 1196.1841
2015-12-20 | 32.6613 | 28.5744 | 26.578 | 25.6868 | 25.5973 | 27.524 | 31.4101 | 36.9675 | 44.8863 | 51.4583 | 55.269 | 55.9661 | 58.8081 | 59.1477 | 59.4882 | 59.5857 | 58.4985 | 61.4627 | 67.9541 | 63.1077 | 57.9299 | 52.2954 | 45.6512 | 38.0662 | 1124.5744
2015-12-21 | 31.0853 | 26.5975 | 24.0182 | 22.8683 | 22.7116 | 23.5438 | 25.8022 | 29.8028 | 38.4726 | 48.1425 | 54.5668 | 58.0549 | 61.7701 | 62.8971 | 62.0484 | 60.4862 | 59.2254 | 64.1051 | 71.9904 | 68.7584 | 64.3278 | 58.0742 | 49.8758 | 40.2478 | 1129.4731
2015-12-22 | 32.3516 | 27.5904 | 24.9116 | 23.6359 | 24.0182 | 27.1805 | 33.1759 | 39.7444 | 49.3863 | 59.5662 | 68.6955 | 74.8041 | 79.0473 | 82.2577 | 84.5303 | 83.3959 | 79.5197 | 81.7772 | 90.5935 | 85.7659 | 78.7891 | 70.7843 | 60.5943 | 48.0023 | 1410.1182
2015-12-23 | 38.2613 | 32.0863 | 28.4328 | 26.6823 | 26.9177 | 30.2319 | 36.3251 | 43.0519 | 53.6932 | 65.621 | 75.1761 | 82.3265 | 87.6835 | 89.8496 | 85.0188 | 79.9709 | 75.6148 | 77.3049 | 85.2636 | 80.7069 | 74.3677 | 69.6622 | 63.0375 | 54.922 | 1462.2084
2015-12-24 | 45.7793 | 39.268 | 35.297 | 33.6139 | 33.2341 | 35.515 | 39.9677 | 45.9847 | 58.5565 | 74.3459 | 87.8018 | 97.3896 | 102.5553 | 103.4656 | 104.1477 | 101.6872 | 99.0548 | 101.4453 | 103.697 | 92.2968 | 82.1775 | 74.0848 | 66.6071 | 56.6011 | 1714.5739
2015-12-25 | 47.2526 | 40.6012 | 35.0797 | 31.1064 | 28.5136 | 28.0635 | 29.1172 | 32.1507 | 39.9358 | 48.7315 | 54.6976 | 57.8241 | 58.9341 | 58.1319 | 56.4396 | 52.9552 | 49.3597 | 50.889 | 55.2314 | 52.9552 | 51.1416 | 48.3619 | 43.5006 | 37.029 | 1088.0032
2015-12-26 | 30.8603 | 26.898 | 25.1772 | 24.2913 | 24.704 | 26.9964 | 31.1487 | 36.3404 | 43.4257 | 50.5831 | 56.4396 | 58.9438 | 58.8759 | 57.4022 | 56.5061 | 55.8716 | 56.4301 | 63.0074 | 70.4022 | 67.694 | 62.777 | 56.9437 | 50.278 | 41.9893 | 1133.9862
2015-12-27 | 34.3799 | 29.3289 | 26.221 | 24.8549 | 24.8612 | 25.8664 | 28.6014 | 31.8078 | 39.9837 | 50.9972 | 60.4272 | 66.9168 | 71.1141 | 72.5058 | 72.5596 | 70.3068 | 67.6109 | 70.7311 | 77.9504 | 73.3689 | 67.0098 | 60.496 | 52.4325 | 43.0602 | 1243.3925
2015-12-28 | 35.0498 | 29.6238 | 26.4219 | 24.6726 | 23.8328 | 24.2167 | 26.1692 | 28.8248 | 38.6216 | 50.8259 | 60.8207 | 68.8527 | 74.7167 | 78.9574 | 81.2412 | 81.1615 | 78.6883 | 77.9727 | 85.0654 | 79.5084 | 72.1834 | 64.1962 | 54.6322 | 43.7426 | 1309.9985
2015-12-29 | 35.3721 | 30.1417 | 27.1871 | 25.9371 | 26.0724 | 28.6014 | 34.232 | 39.9917 | 50.2691 | 63.2784 | 74.6403 | 82.487 | 86.7279 | 88.6561 | 90.0892 | 90.8221 | 87.9557 | 87.152 | 95.4669 | 89.1206 | 80.8545 | 70.2856 | 59.5759 | 47.4438 | 1492.3609
2015-12-30 | 37.6465 | 31.8435 | 28.5541 | 26.8391 | 26.6757 | 29.24 | 34.5282 | 40.1276 | 49.023 | 59.9568 | 70.6674 | 80.0161 | 86.129 | 90.5454 | 91.7636 | 90.2692 | 86.8103 | 86.775 | 94.9615 | 88.7156 | 81.264 | 71.1674 | 61.0376 | 49.6619 | 1494.2185
2015-12-31 | 40.1356 | 33.9075 | 30.364 | 28.5339 | 28.3789 | 30.6851 | 35.6808 | 41.7522 | 50.4663 | 60.2408 | 68.6327 | 73.7481 | 74.99 | 75.8017 | 75.5489 | 73.9761 | 74.4222 | 82.3609 | 89.4907 | 81.1274 | 71.6478 | 61.949 | 52.7899 | 45.805 | 1382.4354
[25 empty] | 655204.1522 | Annual MWHs
Note on L5: AJZ: Taken from Load Forecast (FNG)
Note on A13: AJZ: NOTES: Variable losses vary with the amount of electricity distributed and are, more precisely, proportional to the square of the current. Consequently, a 1% increase in current leads to an increase in losses of more than 1%. - Electrical Engineering Portal

## 2015 Hourly Load - RC2016
OPC 012912
FPL RC-16
2015 FORECASTED Hourly Loads - RC2016
BASED ON 2013 RAW DATA
FORECASTED |  |  |  | 23433.6356
SUMMER PEAK |  | 22861 |  | 23433.6356
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | MAX | 2014 Hourly Load | 116299005
2015-01-01 | 10092.347 | 9725.1651 | 9221.837 | 8878.3774 | 8728.823 | 8802.0531 | 9031.0261 | 9219.7742 | 10056.2477 | 11377.4839 | 12614.1445 | 13460.9322 | 13962.1974 | 14159.1967 | 14100.4064 | 13919.9096 | 13733.2244 | 13893.093 | 14567.6351 | 14166.4166 | 13558.9161 | 12882.3111 | 11982.9216 | 10850.4334 | 14567.6351 | 2015 Projected (FNG) NEL | 119951958.9966
2015-01-02 | 9790.1439 | 9110.4447 | 8653.5301 | 8434.8711 | 8372.9865 | 8626.7134 | 9597.2702 | 10385.2675 | 11555.9179 | 12932.8502 | 14040.5846 | 14799.7024 | 15342.224 | 15719.7201 | 15888.8713 | 15803.2643 | 15484.5586 | 15349.4439 | 15919.8136 | 15313.3446 | 14497.4992 | 13587.7956 | 12568.7625 | 11375.4211 | 15919.8136
2015-01-03 | 10231.5874 | 9413.6792 | 8906.2255 | 8659.7185 | 8639.0903 | 8924.7909 | 9763.3272 | 10551.3245 | 11470.3108 | 12250.0568 | 12695.6259 | 12840.0233 | 12841.0547 | 12722.4426 | 12602.799 | 12528.5375 | 12490.3753 | 13087.5617 | 13986.9513 | 13742.5071 | 13241.2418 | 12634.7727 | 11812.739 | 10862.8103 | 13986.9513 | Ratio 2013 to 2015 | 1.0314
2015-01-04 | 10013.9599 | 9445.653 | 9105.2877 | 8957.796 | 8976.3614 | 9199.146 | 9674.626 | 10301.7233 | 11268.1545 | 12122.162 | 12621.3644 | 12730.6939 | 12627.5529 | 12462.5273 | 12251.0882 | 12054.0889 | 12095.3453 | 12704.9086 | 13238.1476 | 12878.1855 | 12419.208 | 11856.0582 | 11149.5423 | 10315.1316 | 13238.1476
2015-01-05 | 9462.1555 | 8850.5294 | 8464.782 | 8243.0289 | 8197.6468 | 8389.4891 | 8843.3095 | 9367.2658 | 10386.2989 | 11378.5153 | 12454.276 | 13118.504 | 13462.995 | 13571.293 | 13562.0103 | 13435.1469 | 13259.8072 | 13407.2988 | 14228.3012 | 13810.5802 | 13225.7707 | 12340.8209 | 11305.2852 | 10193.4252 | 14228.3012 | Applied above ratio to 2013 historical hourly loads
2015-01-06 | 9077.4396 | 8462.7192 | 8096.5687 | 7965.5796 | 8069.752 | 8673.1269 | 9921.133 | 10709.1302 | 11423.8974 | 12384.1401 | 13373.2623 | 14000.3596 | 14493.3736 | 14756.3831 | 14674.9018 | 14362.3845 | 14066.3698 | 14509.8762 | 15252.4914 | 14825.4876 | 13873.4962 | 12701.8144 | 11716.8178 | 10628.6802 | 15252.4914
2015-01-07 | 9796.3324 | 9335.2921 | 9217.7113 | 9311.5697 | 9750.9503 | 10744.1982 | 12599.7048 | 13915.784 | 14497.4992 | 14841.9902 | 14705.8441 | 14323.1909 | 13956.009 | 13591.9212 | 13305.1892 | 13286.6239 | 13678.5597 | 14931.7229 | 16349.9116 | 16446.8642 | 16089.9963 | 15168.9472 | 14017.8936 | 12880.2483 | 16446.8642 | Resulting Total Hourly Load | 119951958.9966
2015-01-08 | 12005.6126 | 11547.6666 | 11383.6724 | 11310.4423 | 11485.782 | 12271.7164 | 13742.5071 | 14453.1486 | 14381.9813 | 14381.9813 | 14293.28 | 13932.2865 | 13438.2411 | 12969.981 | 12566.6997 | 12407.8625 | 12524.4119 | 13218.5508 | 14027.1763 | 13771.3866 | 13176.263 | 12211.8946 | 11092.8148 | 9911.8503 | 14453.1486
2015-01-09 | 8951.6076 | 8455.4993 | 8221.3693 | 8135.7622 | 8304.9135 | 9006.2723 | 10434.7752 | 11371.2955 | 11665.2473 | 12193.3292 | 12555.3542 | 12751.3221 | 12768.856 | 12674.9977 | 12555.3542 | 12513.0664 | 12588.3593 | 13183.4829 | 14078.7468 | 13909.5955 | 13362.9482 | 12494.501 | 11453.8083 | 10254.2784 | 14078.7468
2015-01-10 | 9191.9261 | 8520.4782 | 8134.7308 | 7989.302 | 8075.9405 | 8677.2525 | 10032.5253 | 10938.1033 | 11622.9595 | 12451.1818 | 13107.1585 | 13524.8796 | 13756.9468 | 13931.2551 | 13937.4436 | 13899.2814 | 13845.6481 | 13928.1609 | 14661.4934 | 14252.0236 | 13601.2039 | 12788.4528 | 11943.728 | 10977.2968 | 14661.4934
2015-01-11 | 9847.9029 | 9140.3556 | 8661.7813 | 8429.7141 | 8381.2378 | 8608.148 | 9116.6332 | 9760.233 | 11200.0814 | 12731.7253 | 13794.0776 | 14454.18 | 14944.0998 | 15241.1459 | 15361.8208 | 15295.8106 | 14966.7908 | 14698.6242 | 15136.9734 | 14570.7293 | 13834.3026 | 12962.7611 | 12059.2459 | 11046.4013 | 15361.8208
2015-01-12 | 9956.2009 | 9183.6748 | 8700.9749 | 8420.4314 | 8280.1596 | 8365.7667 | 8705.1006 | 9154.7953 | 10253.247 | 11381.6096 | 12181.9837 | 12639.9298 | 13043.2111 | 13297.9694 | 13369.1367 | 13285.5925 | 13090.656 | 12954.5098 | 13713.6276 | 13447.5238 | 12837.9605 | 11983.953 | 11013.3962 | 9885.0336 | 13713.6276
2015-01-13 | 8951.6076 | 8433.8397 | 8192.4898 | 8167.7359 | 8391.5519 | 9235.2453 | 10821.5539 | 11770.4511 | 12145.8844 | 12647.1497 | 13089.6246 | 13419.6758 | 13720.8475 | 13952.9147 | 14101.4378 | 14207.673 | 14145.7884 | 14270.589 | 15155.5388 | 14959.5709 | 14183.9506 | 13108.1899 | 11930.3197 | 10599.8008 | 15155.5388 | 2014 Historical Summer Peak | 22720
2015-01-14 | 9446.6844 | 8744.2941 | 8369.8923 | 8178.05 | 8254.3744 | 8914.4768 | 10344.0111 | 11194.9243 | 11876.6864 | 12807.0182 | 13580.5757 | 14030.2705 | 14260.2749 | 14271.6204 | 14173.6365 | 13909.5955 | 13837.3968 | 14159.1967 | 15009.0786 | 14786.294 | 14094.2179 | 13102.0015 | 11868.4351 | 10536.8848 | 15009.0786
2015-01-15 | 9394.0825 | 8755.6397 | 8396.709 | 8275.0026 | 8358.5468 | 9090.8479 | 10614.2405 | 11500.2217 | 11813.7704 | 12229.4286 | 12444.9933 | 12460.4644 | 12289.2504 | 12120.0991 | 11931.3511 | 11841.6184 | 11935.4767 | 12597.642 | 13462.995 | 13268.0585 | 12745.1336 | 11928.2569 | 10885.5013 | 9735.4792 | 13462.995 | Ratioed 2015 Projected Summer Peak | 23433.6356
2015-01-16 | 8880.4403 | 8424.557 | 8289.4423 | 8339.9814 | 8635.9961 | 9628.2125 | 11475.4679 | 12669.8407 | 12873.0285 | 12946.2586 | 12944.1957 | 12750.2907 | 12453.2446 | 12138.6645 | 11864.3095 | 11729.1947 | 11867.4037 | 12704.9086 | 14485.1223 | 14827.5504 | 14749.1633 | 14271.6204 | 13501.1572 | 12643.024 | 14827.5504
2015-01-17 | 12036.5549 | 11797.2678 | 11832.3357 | 12036.5549 | 12491.4067 | 13644.5231 | 15683.6208 | 16916.1557 | 16740.816 | 15867.2117 | 14904.9062 | 13917.8468 | 13097.8758 | 12434.6792 | 11970.5447 | 11714.755 | 11761.1685 | 12485.2183 | 13649.6802 | 13565.1046 | 13290.7495 | 12748.2278 | 12122.162 | 11364.0756 | 16916.1557 | FNG Projected Summer Peak | 22861
2015-01-18 | 10635.9001 | 10312.0374 | 10216.1162 | 10257.3726 | 10482.22 | 10995.8622 | 11864.3095 | 12973.0752 | 13718.7847 | 13801.2975 | 13542.4136 | 13011.2374 | 12452.2132 | 11949.9165 | 11504.3474 | 11261.966 | 11265.0602 | 11905.5659 | 13316.5348 | 13564.0732 | 13563.0418 | 13451.6495 | 13156.6662 | 12734.8195 | 13801.2975
2015-01-19 | 12432.6164 | 12329.4754 | 12408.8939 | 12645.0868 | 13024.6457 | 13638.3347 | 14589.2947 | 15736.2227 | 16391.168 | 15880.6201 | 14765.6658 | 13678.5597 | 12810.1124 | 12170.6382 | 11655.9646 | 11241.3378 | 11117.5686 | 11475.4679 | 12715.2227 | 12636.8356 | 12336.6952 | 11728.1633 | 11108.2859 | 10235.713 | 16391.168
2015-01-20 | 9597.2702 | 9295.0671 | 9225.9626 | 9313.6325 | 9679.783 | 10406.9271 | 11600.2685 | 12724.5054 | 13132.9438 | 12949.3528 | 12699.7516 | 12459.433 | 12175.7953 | 11957.1364 | 11790.0479 | 11697.221 | 11713.7236 | 12108.7536 | 13220.6136 | 13131.9124 | 12549.1657 | 11695.1582 | 10643.12 | 9514.7574 | 13220.6136
2015-01-21 | 8664.8756 | 8219.3064 | 8035.7155 | 8034.6841 | 8243.0289 | 9083.628 | 10709.1302 | 11660.0903 | 11865.3409 | 11928.2569 | 11992.2043 | 11990.1415 | 11965.3876 | 11855.0268 | 11758.0742 | 11659.0589 | 11697.221 | 12213.9574 | 13230.9277 | 13193.797 | 12645.0868 | 11767.3569 | 10727.6956 | 9664.3119 | 13230.9277
2015-01-22 | 8824.7441 | 8509.1327 | 8457.5622 | 8618.4621 | 9097.0364 | 10276.9694 | 12374.8574 | 13686.811 | 13491.8745 | 13733.2244 | 13563.0418 | 13221.645 | 12831.7721 | 12377.9516 | 12058.2145 | 11884.9377 | 12003.5498 | 12803.924 | 14569.6979 | 15053.4292 | 15038.9895 | 14575.8864 | 13851.8366 | 12986.4836 | 15053.4292
2015-01-23 | 12466.6529 | 12340.8209 | 12473.8728 | 12769.8874 | 13318.5976 | 14662.5248 | 16939.8782 | 18040.3926 | 17415.3582 | 16372.6026 | 15380.3862 | 14280.9031 | 13361.9168 | 12595.5792 | 12080.9056 | 11816.8646 | 11838.5242 | 12459.433 | 13943.6321 | 14213.8615 | 13989.0141 | 13357.7912 | 12367.6375 | 11380.5782 | 18040.3926
2015-01-24 | 10658.5911 | 10403.8329 | 10387.3303 | 10527.6021 | 10942.2289 | 12081.937 | 14082.8724 | 15130.785 | 15120.4709 | 14782.1684 | 14347.9448 | 13717.7533 | 13157.6976 | 12676.0291 | 12279.9677 | 12050.9947 | 12110.8164 | 12654.3695 | 13866.2763 | 13895.1558 | 13581.6071 | 13052.4938 | 12387.2343 | 11557.9807 | 15130.785
2015-01-25 | 10866.936 | 10518.3194 | 10378.0476 | 10418.2726 | 10607.0206 | 11045.3699 | 11813.7704 | 12777.1073 | 13676.4969 | 13624.9264 | 13106.1271 | 12538.8516 | 12085.0312 | 11726.1005 | 11449.6826 | 11240.3064 | 11148.5109 | 11420.8031 | 12348.0408 | 12252.1196 | 11835.43 | 11324.882 | 10627.6488 | 9831.4003 | 13676.4969
2015-01-26 | 9145.5126 | 8692.7236 | 8498.8186 | 8416.3058 | 8479.2218 | 8772.1422 | 9328.0722 | 10092.347 | 11162.9506 | 11712.6922 | 11959.1992 | 11933.4139 | 11918.9742 | 11905.5659 | 11826.1473 | 11741.5717 | 11725.0691 | 12021.0838 | 12957.6041 | 12926.6618 | 12351.135 | 11534.2582 | 10583.2982 | 9472.4696 | 12957.6041
2015-01-27 | 8556.5775 | 8013.0244 | 7774.7687 | 7710.8213 | 7926.386 | 8688.598 | 10273.8752 | 11155.7308 | 11521.8813 | 11949.9165 | 12435.7106 | 12754.4163 | 13014.3316 | 13227.8335 | 13325.8174 | 13449.5867 | 13505.2828 | 13607.3924 | 14422.2063 | 14328.348 | 13577.4815 | 12457.3702 | 11212.4583 | 9853.0599 | 14422.2063
2015-01-28 | 8711.289 | 8084.1917 | 7777.863 | 7656.1566 | 7806.7424 | 8539.0436 | 10035.6195 | 10976.2654 | 11393.9865 | 11956.1049 | 12534.726 | 12942.1329 | 13319.629 | 13633.1776 | 13863.1821 | 14037.4904 | 14097.3121 | 14125.1602 | 14824.4562 | 14700.687 | 14017.8936 | 12881.2797 | 11696.1896 | 10380.1104 | 14824.4562
2015-01-29 | 9228.0254 | 8578.2371 | 8261.5943 | 8148.1392 | 8302.8507 | 9075.3768 | 10581.2354 | 11586.8602 | 12020.0524 | 12610.0189 | 13046.3053 | 13407.2988 | 11748.7915 | 13346.4457 | 13205.1425 | 13261.87 | 13470.2149 | 14015.8308 | 14701.7184 | 14532.5672 | 14063.2756 | 13182.4515 | 12102.5652 | 10867.9674 | 14701.7184
2015-01-30 | 9959.2951 | 9413.6792 | 9140.3556 | 9080.5338 | 9291.9729 | 10111.9438 | 11793.1422 | 12811.1439 | 13317.5662 | 13797.1718 | 14060.1814 | 14026.1449 | 13875.559 | 13698.1565 | 13500.1257 | 13385.6392 | 13462.995 | 13924.0353 | 14737.8178 | 14610.9543 | 14031.3019 | 13183.4829 | 12001.487 | 10776.1719 | 14737.8178
2015-01-31 | 9860.2798 | 9329.1036 | 9111.4761 | 9018.6492 | 9162.0152 | 9937.6355 | 11513.63 | 12456.3388 | 12832.8035 | 13314.4719 | 13665.1513 | 13859.0564 | 13899.2814 | 13847.7109 | 13751.7898 | 13807.4859 | 13728.0674 | 13854.9308 | 14450.0544 | 14220.0499 | 13590.8898 | 12790.5156 | 11859.1524 | 10779.2661 | 14450.0544
2015-02-01 | 9773.6413 | 9090.8479 | 8661.7813 | 8435.9025 | 8394.6461 | 8593.7083 | 9119.7274 | 9880.908 | 11245.4634 | 12525.4433 | 13377.388 | 13843.5853 | 14187.0448 | 14393.3268 | 14522.2531 | 14567.6351 | 14456.2428 | 14181.8878 | 14501.6249 | 14215.9243 | 13470.2149 | 12628.5843 | 11717.8492 | 10673.0309 | 14567.6351
2015-02-02 | 9643.6837 | 8948.5133 | 8503.9756 | 8254.3744 | 8166.7045 | 8248.1859 | 8592.6769 | 9191.9261 | 10707.0674 | 12098.4395 | 12956.5727 | 13498.0629 | 14170.5423 | 14644.9909 | 14979.1677 | 15132.8478 | 15114.2824 | 14817.2363 | 14812.0793 | 14118.9718 | 13467.1206 | 13068.9964 | 12529.5689 | 11213.4897 | 15132.8478
2015-02-03 | 10022.2112 | 9032.0575 | 8646.3102 | 8482.316 | 8587.5198 | 9272.3761 | 10652.4027 | 11495.0647 | 12261.4023 | 13235.0534 | 14207.673 | 14881.1838 | 15404.1086 | 15809.4528 | 16104.436 | 16224.0796 | 16020.8918 | 15745.5054 | 16173.5405 | 15963.1329 | 15062.7119 | 14024.082 | 12730.6939 | 11331.0705 | 16224.0796
2015-02-04 | 10136.6977 | 9432.2446 | 9008.3351 | 8802.0531 | 8847.4351 | 9451.8414 | 10832.8994 | 11648.7448 | 12363.5119 | 13392.8591 | 14315.9711 | 14993.6075 | 15522.7208 | 15854.8348 | 16077.6194 | 16205.5142 | 16086.9021 | 15753.7566 | 16189.0117 | 16107.5303 | 15320.5644 | 14224.1756 | 13006.0803 | 11615.7396 | 16205.5142
2015-02-05 | 10439.9322 | 9664.3119 | 9246.5908 | 9025.8691 | 9064.0312 | 9735.4792 | 11184.6102 | 12005.6126 | 12727.5996 | 13806.4545 | 14747.1005 | 15448.4593 | 15887.8399 | 16195.2001 | 16383.9482 | 16297.3097 | 15952.8188 | 15664.024 | 16059.054 | 15843.4893 | 15054.4606 | 13983.857 | 12686.3432 | 11293.9397 | 16383.9482
2015-02-06 | 10110.9124 | 9308.4754 | 8888.6915 | 8673.1269 | 8735.0115 | 9353.8575 | 10788.5488 | 11614.7082 | 12364.5433 | 13226.8021 | 13976.6372 | 14523.2845 | 14966.7908 | 15379.3548 | 15551.6003 | 15655.7727 | 15556.7573 | 15430.9253 | 15871.3374 | 15760.9765 | 14986.3876 | 13934.3494 | 12663.6522 | 11226.8981 | 15871.3374
2015-02-07 | 10013.9599 | 9272.3761 | 8763.8909 | 8529.7609 | 8565.8602 | 9200.1774 | 10619.3976 | 11489.9076 | 12042.7434 | 12755.4477 | 13429.9899 | 14056.0557 | 14426.3319 | 14487.1851 | 14963.6966 | 15097.7799 | 15059.6177 | 14961.6337 | 15010.11 | 14615.08 | 14037.4904 | 13070.0278 | 12168.5754 | 11049.4955 | 15097.7799
2015-02-08 | 10024.274 | 9249.6851 | 8787.6134 | 8554.5147 | 8536.9807 | 8728.823 | 9259.9992 | 10002.6144 | 11380.5782 | 12790.5156 | 13842.5539 | 14486.1537 | 14915.2203 | 15123.5651 | 15255.5856 | 15173.0728 | 14988.4504 | 14716.1582 | 14887.3722 | 14537.7242 | 13810.5802 | 12986.4836 | 12081.937 | 11101.066 | 15255.5856
2015-02-09 | 10067.5932 | 9307.444 | 8846.4037 | 8606.0852 | 8552.4519 | 8715.4147 | 9099.0992 | 9689.0657 | 10767.9206 | 11752.9172 | 12403.7369 | 12739.9766 | 13050.431 | 13238.1476 | 13320.6604 | 13251.5559 | 13086.5303 | 13035.9912 | 13635.2405 | 13726.0045 | 13052.4938 | 12150.01 | 11180.4846 | 9958.2637 | 13726.0045
2015-02-10 | 8945.4191 | 8372.9865 | 8135.7622 | 8097.6001 | 8290.4737 | 9093.9421 | 10674.0623 | 11590.9858 | 11983.953 | 12472.8414 | 13013.3002 | 13365.011 | 13690.9366 | 13944.6635 | 14049.8673 | 14159.1967 | 14178.7935 | 14100.4064 | 14658.3992 | 14796.6081 | 14064.307 | 13020.5201 | 11785.9223 | 10443.0264 | 14796.6081
2015-02-11 | 9366.2344 | 8693.7551 | 8367.8295 | 8260.5628 | 8399.8032 | 9156.8582 | 10735.9469 | 11646.6819 | 12108.7536 | 12726.5682 | 13281.4668 | 13790.9834 | 14219.0185 | 14596.5146 | 14824.4562 | 15059.6177 | 15127.6908 | 14994.6389 | 15397.9202 | 15448.4593 | 14796.6081 | 13536.2251 | 12199.5177 | 10760.7007 | 15448.4593
2015-02-12 | 9513.726 | 8821.6499 | 8397.7404 | 8220.3379 | 8314.1962 | 8983.5813 | 10470.8745 | 11286.7198 | 11916.9114 | 12722.4426 | 13423.8014 | 13989.0141 | 14408.798 | 14751.2261 | 14838.8959 | 14702.7498 | 14519.1588 | 14553.1954 | 15225.6747 | 15058.5863 | 14350.0076 | 13296.938 | 11823.0531 | 10326.4771 | 15225.6747
2015-02-13 | 9238.3395 | 8550.3891 | 8229.6205 | 8104.8199 | 8249.2173 | 8982.5499 | 10536.8848 | 11495.0647 | 11998.3928 | 12319.1613 | 12605.8933 | 12706.9714 | 12762.6676 | 12746.165 | 12689.4375 | 12600.7362 | 12512.0349 | 12514.0978 | 13241.2418 | 13522.8168 | 13092.7188 | 12350.1036 | 11353.7615 | 10214.0534 | 13522.8168
2015-02-14 | 9315.6953 | 8871.1576 | 8721.6031 | 8772.1422 | 9096.005 | 10135.6663 | 12125.2562 | 13389.7649 | 13365.011 | 13051.4624 | 12797.7355 | 12370.7318 | 12030.3665 | 11797.2678 | 11649.7762 | 11644.6191 | 11640.4935 | 11749.8229 | 12484.1869 | 12627.5529 | 12176.8267 | 11565.2005 | 10876.2187 | 10053.1535 | 13389.7649
2015-02-15 | 9338.3863 | 8883.5345 | 8642.1846 | 8553.4833 | 8591.6455 | 8890.7544 | 9475.5638 | 10299.6605 | 11192.8615 | 11763.2313 | 12086.0626 | 12119.0677 | 11970.5447 | 11819.9588 | 11686.9069 | 11637.3992 | 11609.5512 | 11683.8127 | 12256.2453 | 12390.3286 | 11959.1992 | 11387.798 | 10720.4757 | 9856.1541 | 12390.3286
2015-02-16 | 9126.9473 | 8713.3518 | 8658.6871 | 8708.1948 | 8808.2416 | 9244.528 | 10012.9285 | 11053.6212 | 11893.1889 | 12137.6331 | 12021.0838 | 11749.8229 | 11596.1428 | 11483.7192 | 11432.1487 | 11450.714 | 11513.63 | 11631.2108 | 12283.0619 | 12509.9721 | 12006.644 | 11329.0077 | 10610.1149 | 9648.8407 | 12509.9721
2015-02-17 | 8884.5659 | 8470.9705 | 8334.8244 | 8378.1436 | 8647.3416 | 9384.7998 | 10601.8636 | 11707.5351 | 12320.1927 | 12554.3228 | 12659.5266 | 12684.2804 | 12722.4426 | 12792.5785 | 12865.8086 | 12972.0438 | 13027.74 | 13058.6823 | 13573.3559 | 13743.5385 | 13059.7137 | 12099.4709 | 10910.2552 | 9734.4478 | 13743.5385
2015-02-18 | 8716.4461 | 8127.511 | 7921.2289 | 7867.5956 | 8081.0975 | 8883.5345 | 10506.9739 | 11514.6615 | 11898.346 | 12272.7478 | 12621.3644 | 12907.065 | 13155.6348 | 13419.6758 | 13666.1828 | 13900.3128 | 13983.857 | 13856.9936 | 14195.2961 | 14359.2903 | 13636.2719 | 12524.4119 | 11346.5416 | 9970.6407 | 14359.2903
2015-02-19 | 8886.6287 | 8235.809 | 7941.8571 | 7822.2136 | 7965.5796 | 8696.8493 | 10232.6188 | 11110.3487 | 11629.148 | 12220.1459 | 12816.3009 | 13324.786 | 13722.9103 | 14105.5634 | 14470.6826 | 14818.2677 | 14902.8434 | 14695.53 | 14886.3408 | 14971.9478 | 14264.4006 | 13180.3886 | 11924.1312 | 10538.9476 | 14971.9478
2015-02-20 | 9345.6062 | 8654.5615 | 8269.8455 | 8064.5949 | 8122.3539 | 8819.5871 | 10299.6605 | 11202.1442 | 11951.9793 | 12827.6464 | 13650.7116 | 14209.7358 | 14722.3466 | 15121.5023 | 15402.0458 | 15644.4272 | 15677.4323 | 15447.4279 | 15712.5002 | 15847.6149 | 15187.5125 | 14215.9243 | 12957.6041 | 11652.8704 | 15847.6149
2015-02-21 | 10448.1835 | 9594.176 | 9145.5126 | 8921.6967 | 8935.105 | 9526.1029 | 10954.6058 | 11860.1838 | 12951.4156 | 14094.2179 | 15060.6491 | 15766.1336 | 16249.8649 | 16562.3821 | 16600.5443 | 16512.8744 | 15998.2008 | 15573.2599 | 15758.9137 | 15522.7208 | 14768.7601 | 13789.952 | 12829.7092 | 11639.4621 | 16600.5443
2015-02-22 | 10498.7226 | 9602.4273 | 9116.6332 | 8805.1473 | 8723.6659 | 8827.8384 | 9294.0357 | 10091.3156 | 11762.1999 | 13274.2469 | 14356.1961 | 15145.2247 | 15759.9451 | 16094.1219 | 16224.0796 | 16281.8386 | 16071.4309 | 15527.8778 | 15436.0823 | 15219.4862 | 14377.8557 | 13476.4033 | 12495.5324 | 11350.6673 | 16281.8386
2015-02-23 | 10252.2156 | 9452.8728 | 8939.2306 | 8639.0903 | 8502.9442 | 8552.4519 | 8853.6236 | 9544.6683 | 11153.6679 | 12730.6939 | 13949.8205 | 14864.6812 | 15918.7822 | 16087.9335 | 16232.3309 | 16362.2885 | 16239.5508 | 15899.1854 | 15895.0598 | 15920.8451 | 15164.8215 | 13926.0981 | 12767.8246 | 11350.6673 | 16362.2885
2015-02-24 | 10067.5932 | 9376.5485 | 8922.7281 | 8661.7813 | 8693.7551 | 9314.6639 | 10562.67 | 11485.782 | 12381.0459 | 13461.9636 | 14453.1486 | 15151.4132 | 15833.1752 | 16298.3411 | 16584.0417 | 16803.732 | 16607.7641 | 16298.3411 | 16595.3872 | 16655.209 | 15677.4323 | 14433.5518 | 12988.5464 | 11486.8134 | 16803.732
2015-02-25 | 10176.9227 | 9366.2344 | 8878.3774 | 8609.1794 | 8629.8076 | 9257.9363 | 10661.6854 | 11452.7769 | 12269.6536 | 13198.954 | 14029.2391 | 14719.2524 | 15374.1977 | 15944.5675 | 16389.1052 | 16647.9891 | 16571.6648 | 16120.9386 | 16211.7027 | 16214.7969 | 15340.1612 | 14091.1237 | 12751.3221 | 11225.8667 | 16647.9891
2015-02-26 | 9930.4157 | 9112.5075 | 8608.148 | 8372.9865 | 8390.5205 | 8940.262 | 10294.5034 | 11154.6994 | 11866.3723 | 12657.4638 | 13701.2507 | 14394.3582 | 15012.1728 | 15432.9881 | 15701.1547 | 15755.8195 | 15517.5637 | 15352.5381 | 15782.6361 | 15769.2278 | 15031.7696 | 13994.1711 | 12709.0343 | 11343.4474 | 15782.6361
2015-02-27 | 10155.2631 | 9466.2812 | 9097.0364 | 8923.7595 | 8978.4242 | 9580.7677 | 10987.6109 | 11757.0428 | 12213.9574 | 12780.2015 | 13396.9847 | 13267.0271 | 13878.6532 | 13962.1974 | 13931.2551 | 13854.9308 | 13688.8738 | 13960.1346 | 14460.3685 | 14549.0697 | 13937.4436 | 12880.2483 | 11636.3678 | 10387.3303 | 14549.0697
2015-02-28 | 9324.978 | 8715.4147 | 8432.8083 | 8344.1071 | 8475.0961 | 9215.6485 | 10783.3918 | 11677.6242 | 11957.1364 | 12128.3504 | 12263.4651 | 12304.7215 | 12312.9728 | 12380.0145 | 12453.2446 | 12555.3542 | 12619.3016 | 12535.7574 | 12827.6464 | 13000.9233 | 12442.9305 | 11708.5665 | 10834.9623 | 9839.6516 | 13000.9233
2015-03-01 | 8948.5133 | 8386.3949 | 8079.0347 | 7944.9514 | 7997.5533 | 8320.3846 | 8942.3249 | 9780.8612 | 10832.8994 | 11523.9441 | 11959.1992 | 12184.0466 | 12398.5798 | 12610.0189 | 12766.7932 | 12967.9182 | 12992.672 | 12823.5208 | 12837.9605 | 13074.1534 | 12433.6478 | 11714.755 | 10888.5956 | 9887.0964 | 13074.1534
2015-03-02 | 9002.1466 | 8442.091 | 8124.4167 | 7839.7476 | 7797.4597 | 7957.3283 | 8348.2327 | 9026.9005 | 10345.0425 | 11439.3685 | 12126.2876 | 12622.3958 | 13001.9547 | 13373.2623 | 13632.1462 | 13859.0564 | 13932.2865 | 13759.0097 | 13829.1455 | 14080.8096 | 13362.9482 | 12391.36 | 11277.4372 | 10047.9964 | 14080.8096
2015-03-03 | 9132.1043 | 8374.0179 | 7960.4225 | 7805.711 | 7894.4123 | 8567.923 | 9933.5099 | 10792.6744 | 11563.1377 | 12418.1766 | 13210.2995 | 13788.9205 | 14355.1646 | 14902.8434 | 15250.4285 | 15561.9144 | 15654.7413 | 15422.674 | 15419.5798 | 15565.0086 | 14665.6191 | 13434.1155 | 12079.8741 | 10570.9213 | 15654.7413
2015-03-04 | 9346.6376 | 8563.7974 | 8135.7622 | 7919.1661 | 7966.611 | 8586.4884 | 9956.2009 | 10846.3078 | 11574.4832 | 12419.208 | 13177.2944 | 13795.109 | 14352.0704 | 14866.744 | 15304.0619 | 15627.9246 | 15706.3118 | 15462.899 | 15487.6529 | 15581.5112 | 14796.6081 | 13714.659 | 12377.9516 | 10944.2917 | 15706.3118
2015-03-05 | 9700.4112 | 8984.6127 | 8568.9544 | 8396.709 | 8466.8448 | 9090.8479 | 10549.2617 | 11432.1487 | 12115.9735 | 13070.0278 | 13891.0301 | 14593.4204 | 15177.1984 | 15552.6317 | 15702.1861 | 15750.6624 | 15558.8201 | 15308.1875 | 15481.4644 | 15568.1028 | 14888.4036 | 13838.4282 | 12560.5112 | 11129.9455 | 15750.6624
2015-03-06 | 9931.4471 | 9229.0569 | 8788.6448 | 8602.991 | 8632.9019 | 9232.1511 | 10603.9264 | 11479.5935 | 12428.4907 | 13393.8905 | 14104.532 | 14690.3729 | 15079.2145 | 14999.7959 | 14819.2992 | 13734.2558 | 13204.1111 | 13291.7809 | 13892.0616 | 14013.7679 | 13449.5867 | 12546.0715 | 11490.939 | 10288.3149 | 15079.2145
2015-03-07 | 9243.4966 | 8595.7711 | 8325.5417 | 8200.7411 | 8316.259 | 8987.7069 | 10420.3354 | 11296.0025 | 12083.9998 | 12731.7253 | 13260.8386 | 13499.0943 | 13622.8635 | 13634.209 | 13623.8949 | 13633.1776 | 13543.445 | 13302.095 | 13424.8328 | 13512.5027 | 13004.0175 | 12124.2248 | 11187.7045 | 9981.9862 | 13634.209
2015-03-08 | 9165.1094 | 8557.6089 | 8277.0654 | 8173.9244 | 8252.3116 | 8517.3839 | 9186.769 | 10119.1637 | 11086.6263 | 11638.4307 | 11796.2364 | 11783.8595 | 11758.0742 | 11747.7601 | 11827.1787 | 11944.7594 | 12007.6754 | 11949.9165 | 12126.2876 | 12437.7734 | 11901.4402 | 11253.7147 | 10456.4348 | 9650.9036 | 12437.7734
2015-03-09 | 8738.1057 | 0 | 8222.4007 | 7942.8886 | 7843.8732 | 7972.7994 | 8335.8558 | 8860.8435 | 9625.1183 | 10563.7014 | 11325.9134 | 11660.0903 | 12111.8479 | 12361.4491 | 12544.0087 | 12809.081 | 13082.4047 | 13213.3938 | 13017.4259 | 13074.1534 | 13383.5764 | 12614.1445 | 11609.5512 | 10173.8284 | 13383.5764
2015-03-10 | 8982.5499 | 8191.4584 | 7807.7738 | 7688.1303 | 7828.402 | 8459.625 | 9830.3689 | 10840.1193 | 11141.291 | 11731.2576 | 12439.8362 | 12864.7772 | 13343.3514 | 13661.0257 | 14134.4429 | 14592.389 | 14969.885 | 14995.6703 | 14683.153 | 14599.6088 | 14725.4408 | 13648.6488 | 12449.1189 | 10940.1661 | 14995.6703
2015-03-11 | 9539.5113 | 8670.0326 | 8188.3641 | 7949.077 | 7948.0456 | 8555.5461 | 9912.8817 | 10882.4071 | 11143.3538 | 11835.43 | 12450.1503 | 13020.5201 | 13515.5969 | 13969.4173 | 14395.3896 | 14871.9011 | 15273.1196 | 15390.7003 | 15117.3767 | 14981.2305 | 15119.4395 | 14190.139 | 12928.7246 | 11289.8141 | 15390.7003
2015-03-12 | 10005.7086 | 9124.8844 | 8667.9698 | 8465.8134 | 8511.1955 | 9123.853 | 10538.9476 | 10481.1886 | 11719.912 | 12550.1971 | 13560.9789 | 14368.573 | 14993.6075 | 15417.517 | 15645.4586 | 16084.8393 | 16348.8802 | 16226.1424 | 15787.7932 | 15605.2336 | 15683.6208 | 14724.4094 | 13512.5027 | 12025.2094 | 16348.8802
2015-03-13 | 10647.2456 | 9725.1651 | 9175.4235 | 8882.5031 | 8806.1787 | 9266.1876 | 10477.063 | 11237.2122 | 11458.9653 | 12112.8793 | 12599.7048 | 12884.374 | 13042.1797 | 13141.1951 | 13209.2681 | 13280.4354 | 13418.6444 | 13385.6392 | 13006.0803 | 12959.6669 | 13216.488 | 12415.0824 | 11339.3218 | 10040.7765 | 13418.6444
2015-03-14 | 8949.5447 | 8332.7615 | 7989.302 | 7903.695 | 8075.9405 | 8814.43 | 10464.6861 | 11646.6819 | 11910.7229 | 12144.853 | 12323.2869 | 12366.6061 | 12348.0408 | 12394.4542 | 12454.276 | 12563.6054 | 12720.3798 | 12711.0971 | 12468.7157 | 12448.0875 | 12672.9349 | 12042.7434 | 11166.0449 | 10156.2945 | 12720.3798
2015-03-15 | 9040.3088 | 8372.9865 | 7965.5796 | 7781.9886 | 7817.0565 | 8067.6892 | 8591.6455 | 9469.3754 | 10455.4034 | 11356.8557 | 12042.7434 | 12434.6792 | 12716.2541 | 12951.4156 | 13226.8021 | 13509.4084 | 13814.7058 | 13867.3077 | 13527.9738 | 13198.954 | 13274.2469 | 12553.2913 | 11728.1633 | 10564.7328 | 13867.3077
2015-03-16 | 9532.2914 | 8814.43 | 8354.4212 | 8096.5687 | 7992.3962 | 8059.4379 | 8399.8032 | 8930.9794 | 9996.4259 | 11373.3583 | 12340.8209 | 13047.3367 | 13606.361 | 14033.3647 | 14446.9601 | 14729.5665 | 14860.5556 | 14815.1735 | 14449.023 | 14309.7826 | 14557.321 | 13782.7321 | 12804.9554 | 11425.9602 | 14860.5556
2015-03-17 | 10214.0534 | 9412.6478 | 8962.9531 | 8799.9903 | 8888.6915 | 9528.1658 | 10844.2449 | 11827.1787 | 12355.2606 | 13394.9219 | 14521.2217 | 15289.6221 | 15842.4579 | 16123.0014 | 16269.4616 | 16372.6026 | 16403.5449 | 16175.6033 | 15915.688 | 16070.3995 | 16059.054 | 15193.701 | 14167.448 | 12755.4477 | 16403.5449
2015-03-18 | 11501.2531 | 10679.2193 | 10260.4669 | 10058.3105 | 10026.3368 | 10480.1572 | 11633.2736 | 12312.9728 | 12197.4549 | 12570.8253 | 12934.9131 | 13132.9438 | 13302.095 | 13536.2251 | 13841.5225 | 14165.3852 | 14505.7505 | 14610.9543 | 14320.0967 | 14175.6993 | 14350.0076 | 13460.9322 | 12240.7741 | 10729.7584 | 14610.9543
2015-03-19 | 9400.2709 | 8605.0538 | 8179.0815 | 7989.302 | 8039.8411 | 8658.6871 | 10019.1169 | 10937.0718 | 11314.5679 | 12050.9947 | 12776.0759 | 13309.3149 | 13661.0257 | 14089.0609 | 14509.8762 | 14914.1889 | 15166.8843 | 15182.3555 | 14773.9171 | 14496.4678 | 14689.3415 | 13825.0199 | 12662.6208 | 11186.6731 | 15182.3555
2015-03-20 | 9925.2586 | 9089.8165 | 8647.3416 | 8396.709 | 8412.1801 | 8976.3614 | 10289.3464 | 11221.741 | 11625.0223 | 12332.5696 | 13071.0592 | 13621.8321 | 14051.9301 | 14499.5621 | 14904.9062 | 15226.7061 | 15437.1138 | 15362.8522 | 14998.7645 | 14699.6556 | 14857.4613 | 13858.025 | 12623.4272 | 11191.8301 | 15437.1138
2015-03-21 | 9813.8663 | 8923.7595 | 8374.0179 | 8070.7834 | 8063.5635 | 8528.7294 | 9627.1811 | 10589.4867 | 11191.8301 | 12091.2197 | 12996.7977 | 13706.4077 | 14269.5576 | 14829.6133 | 15360.7894 | 15791.9188 | 15960.0386 | 15795.013 | 15206.0779 | 14769.7915 | 14805.8908 | 13941.5692 | 12999.8919 | 11826.1473 | 15960.0386
2015-03-22 | 10631.7745 | 9829.3375 | 9278.5645 | 8948.5133 | 8815.4614 | 8956.7646 | 9390.9882 | 9955.1695 | 10906.1295 | 12372.7946 | 13462.995 | 14037.4904 | 14538.7556 | 14918.3145 | 15178.2298 | 15459.8048 | 15820.7983 | 15813.5784 | 15353.5695 | 14795.5767 | 14730.5979 | 13845.6481 | 12780.2015 | 11494.0333 | 15820.7983
2015-03-23 | 10285.2207 | 9368.2972 | 8815.4614 | 8491.5987 | 8336.8872 | 8402.8974 | 8702.0063 | 9162.0152 | 10174.8598 | 11670.4044 | 12962.7611 | 13933.318 | 14853.3357 | 15648.5528 | 16186.9488 | 16635.6122 | 16829.5173 | 16807.8577 | 16422.1103 | 15951.7874 | 16028.1117 | 14999.7959 | 13802.3289 | 12300.5959 | 16829.5173
2015-03-24 | 10964.9199 | 10006.74 | 9365.203 | 9097.0364 | 9061.9684 | 9514.7574 | 10488.4085 | 11333.1333 | 11926.1941 | 12761.6362 | 13416.5815 | 13868.3391 | 14041.616 | 14022.0192 | 13838.4282 | 13717.7533 | 13730.1302 | 13804.3917 | 13792.0148 | 13866.2763 | 13756.9468 | 12895.7195 | 11900.4088 | 10601.8636 | 14041.616
2015-03-25 | 9502.3805 | 8688.598 | 8173.9244 | 7985.1764 | 8039.8411 | 8535.9493 | 9683.9087 | 10592.5809 | 11138.1968 | 11940.6338 | 12501.7208 | 13060.7451 | 13497.0315 | 13799.2346 | 14078.7468 | 14300.4999 | 14491.3108 | 14506.7819 | 14215.9243 | 13866.2763 | 13995.2026 | 13051.4624 | 11774.5768 | 10294.5034 | 14506.7819
2015-03-26 | 8983.5813 | 8222.4007 | 7793.3341 | 7644.8111 | 7761.3604 | 8372.9865 | 9710.7253 | 10843.2135 | 11494.0333 | 11825.1159 | 12087.094 | 12089.1568 | 11964.3562 | 11811.7075 | 11712.6922 | 11656.996 | 11757.0428 | 11826.1473 | 11791.0793 | 12124.2248 | 12615.1759 | 11992.2043 | 11009.2705 | 9930.4157 | 12615.1759
2015-03-27 | 8950.5761 | 8369.8923 | 8069.752 | 7999.6161 | 8136.7936 | 8738.1057 | 10006.74 | 10900.9725 | 11343.4474 | 11964.3562 | 12268.6222 | 12418.1766 | 12487.2811 | 12544.0087 | 12536.7888 | 12523.3805 | 12546.0715 | 12530.6003 | 12452.2132 | 12732.7567 | 12991.6406 | 12347.0093 | 11406.3634 | 10261.4983 | 12991.6406
2015-03-28 | 9220.8056 | 8515.3211 | 8146.0763 | 7949.077 | 8027.4642 | 8547.2948 | 9655.0292 | 10569.8899 | 11222.7724 | 12106.6908 | 12987.515 | 13506.3142 | 13863.1821 | 14071.5269 | 14240.6781 | 14345.882 | 14327.3166 | 14104.532 | 13776.5436 | 13779.6379 | 13915.784 | 13302.095 | 12512.0349 | 11455.8711 | 14345.882
2015-03-29 | 10432.7123 | 9722.0708 | 9258.9677 | 9018.6492 | 8968.1101 | 9137.2614 | 9583.8619 | 10232.6188 | 11198.0186 | 12509.9721 | 13630.0834 | 14397.4525 | 14732.6607 | 14911.0946 | 14873.9639 | 14693.4671 | 14456.2428 | 14207.673 | 13817.8 | 13706.4077 | 13428.9585 | 12577.0138 | 11775.6082 | 10739.0411 | 14911.0946
2015-03-30 | 9693.1914 | 8950.5761 | 8428.6827 | 8169.7988 | 8074.909 | 8173.9244 | 8568.9544 | 9059.9056 | 9958.2637 | 11121.6942 | 11924.1312 | 12326.3811 | 12508.9407 | 12646.1182 | 12776.0759 | 12885.4054 | 12995.7662 | 12971.0124 | 12708.0028 | 12522.349 | 12868.9028 | 12071.6229 | 11002.0507 | 9682.8773 | 12995.7662
2015-03-31 | 8566.8916 | 7968.6738 | 7582.9265 | 7458.1258 | 7602.5233 | 8415.2743 | 9870.5939 | 10791.643 | 11102.0974 | 11532.1954 | 11975.7017 | 12329.4754 | 12582.1708 | 12882.3111 | 13146.3521 | 13366.0424 | 13469.1834 | 13357.7912 | 13228.8649 | 13387.7021 | 13677.5283 | 12788.4528 | 11621.9281 | 10192.3938 | 13677.5283
2015-04-01 | 8976.3614 | 8254.3744 | 7886.161 | 7735.5751 | 7838.7161 | 8513.2583 | 10096.4727 | 11057.7468 | 11401.2064 | 11867.4037 | 12319.1613 | 12708.0028 | 13019.4887 | 13421.7386 | 13905.4699 | 14447.9916 | 14941.0055 | 15117.3767 | 14849.21 | 14371.6672 | 14484.0909 | 13533.1309 | 12124.2248 | 10582.2668 | 15117.3767
2015-04-02 | 9278.5645 | 8473.0333 | 8034.6841 | 7808.8053 | 7867.5956 | 8544.2006 | 9996.4259 | 10807.1142 | 11181.516 | 11879.7806 | 12465.6215 | 12994.7348 | 13354.6969 | 13797.1718 | 14467.5883 | 15066.8376 | 15516.5323 | 15704.249 | 15350.4753 | 14867.7754 | 14966.7908 | 14011.7051 | 12586.2965 | 11030.9302 | 15704.249
2015-04-03 | 9669.4689 | 8807.2102 | 8318.3218 | 8116.1654 | 8160.5161 | 8842.2781 | 10171.7656 | 10961.8257 | 11489.9076 | 12283.0619 | 13028.7714 | 13644.5231 | 14195.2961 | 14720.2838 | 15438.1452 | 15909.4995 | 16240.5822 | 16108.5617 | 15739.3169 | 15198.858 | 15481.4644 | 14492.3422 | 13041.1483 | 11456.9025 | 16240.5822
2015-04-04 | 10063.4676 | 9196.0517 | 8658.6871 | 8394.6461 | 8364.7353 | 8954.7018 | 10382.1733 | 11134.0712 | 11712.6922 | 12625.49 | 13498.0629 | 14211.7987 | 14758.446 | 15317.4702 | 15853.8034 | 16320.0007 | 16695.434 | 16660.366 | 16201.3886 | 15402.0458 | 15231.8632 | 14371.6672 | 13238.1476 | 11906.5973 | 16695.434
2015-04-05 | 10616.3033 | 9691.1285 | 9088.7851 | 8714.3833 | 8562.766 | 8616.3993 | 9056.8114 | 9610.6786 | 10924.6949 | 12419.208 | 13560.9789 | 14470.6826 | 15209.1721 | 15956.9444 | 16469.5552 | 16847.0513 | 16989.3858 | 16896.5589 | 16270.4931 | 15441.2394 | 15349.4439 | 14450.0544 | 13367.0739 | 12112.8793 | 16989.3858
2015-04-06 | 10810.2084 | 9849.9657 | 9156.8582 | 8741.1999 | 8567.923 | 8593.7083 | 8890.7544 | 9307.444 | 10685.4078 | 12286.1562 | 13554.7905 | 14463.4627 | 15285.4965 | 16002.3265 | 16659.3346 | 17078.0871 | 17281.2749 | 17266.8351 | 16773.8211 | 16105.4675 | 16129.1899 | 15083.3401 | 13776.5436 | 12140.7273 | 17281.2749
2015-04-07 | 10871.0616 | 9988.1746 | 9502.3805 | 9266.1876 | 9331.1664 | 9984.049 | 11338.2903 | 12105.6594 | 12786.39 | 14040.5846 | 15276.2138 | 16344.7546 | 17223.5159 | 18001.1991 | 18611.7938 | 19071.8027 | 19353.3776 | 19240.9539 | 18685.0239 | 18197.167 | 18050.7067 | 16854.2711 | 15369.0407 | 13821.9257 | 19353.3776
2015-04-08 | 12507.9093 | 11517.7557 | 10788.5488 | 10405.8957 | 10412.0841 | 10961.8257 | 12355.2606 | 13092.7188 | 13696.0936 | 14544.9441 | 15527.8778 | 16340.6289 | 16816.109 | 17063.6474 | 17014.1397 | 16752.1615 | 16893.4647 | 16327.2206 | 15239.083 | 14711.0011 | 14782.1684 | 13786.8577 | 12393.4228 | 10900.9725 | 17063.6474
2015-04-09 | 9744.7619 | 8970.1729 | 8520.4782 | 8293.568 | 8278.0968 | 8847.4351 | 10202.7079 | 10840.1193 | 11165.0135 | 11817.896 | 12324.3183 | 12593.5163 | 12753.3849 | 12886.4368 | 13102.0015 | 13365.011 | 13615.6437 | 13775.5122 | 13603.2667 | 13359.854 | 13731.1616 | 12908.0964 | 11579.6403 | 10172.797 | 13775.5122
2015-04-10 | 8998.021 | 8304.9135 | 7901.6322 | 7752.0777 | 7824.2764 | 8468.9077 | 9912.8817 | 10674.0623 | 11034.0244 | 11628.1166 | 12174.7639 | 12569.7939 | 12836.9291 | 13143.2579 | 13474.3405 | 13833.2712 | 14080.8096 | 14074.6211 | 13831.2084 | 13659.9943 | 14018.925 | 13139.1322 | 11904.5344 | 10467.7803 | 14080.8096
2015-04-11 | 9287.8472 | 8489.5359 | 8072.8462 | 7895.4437 | 7954.2341 | 8538.0121 | 9934.5413 | 10717.3815 | 11256.809 | 12129.3818 | 12912.222 | 13444.4296 | 13811.6116 | 14176.7307 | 14508.8447 | 14630.5511 | 14668.7133 | 14482.0281 | 14136.5057 | 13870.4019 | 14055.0243 | 13406.2674 | 12502.7523 | 11350.6673 | 14668.7133
2015-04-12 | 10215.0848 | 9411.6164 | 8840.2153 | 8512.2269 | 8374.0179 | 8480.2532 | 8961.9217 | 9560.1395 | 10880.3443 | 12319.1613 | 13412.4559 | 14250.9922 | 14814.1421 | 15314.376 | 15613.4849 | 15885.7771 | 15986.8553 | 15874.4316 | 15275.1824 | 14580.012 | 14574.855 | 13883.8103 | 12801.8612 | 11685.8755 | 15986.8553
2015-04-13 | 10582.2668 | 9718.9766 | 9176.4549 | 8810.3044 | 8656.6243 | 8713.3518 | 9033.0889 | 9485.8779 | 10669.9367 | 12097.4081 | 13169.0431 | 13931.2551 | 14594.4518 | 15031.7696 | 15214.3292 | 15360.7894 | 15398.9516 | 15326.7529 | 14980.1991 | 14876.0267 | 15191.6382 | 14407.7666 | 13284.561 | 11870.4979 | 15398.9516
2015-04-14 | 10627.6488 | 9815.9292 | 9364.1716 | 9105.2877 | 9129.0101 | 9700.4112 | 11058.7782 | 11828.2101 | 12655.4009 | 13907.5327 | 15056.5235 | 16046.6771 | 16839.8314 | 17614.4203 | 18227.0779 | 18744.8457 | 19015.0751 | 18926.3739 | 18357.0355 | 17638.1427 | 17538.096 | 16447.8956 | 14933.7857 | 13215.4566 | 19015.0751
2015-04-15 | 11742.6031 | 10793.7059 | 10202.7079 | 9794.2695 | 9715.8824 | 10222.3047 | 11561.0749 | 12266.5594 | 13260.8386 | 14649.1165 | 15801.2015 | 16846.0198 | 17601.012 | 18138.3766 | 18349.8157 | 18512.7784 | 18394.1663 | 17674.2421 | 17304.9973 | 16791.3551 | 16829.5173 | 15840.3951 | 14334.5364 | 12689.4375 | 18512.7784
2015-04-16 | 11322.8192 | 10388.3617 | 9800.458 | 9496.192 | 9432.2446 | 9914.9445 | 11152.6365 | 11761.1685 | 12196.4235 | 12865.8086 | 13424.8328 | 13807.4859 | 14204.5788 | 14661.4934 | 14991.5446 | 15238.0516 | 15387.6061 | 15332.9413 | 15076.1203 | 15015.2671 | 15297.8734 | 14653.2421 | 13424.8328 | 11932.3825 | 15387.6061
2015-04-17 | 10730.7898 | 9942.7926 | 9481.7523 | 9240.4024 | 9274.4389 | 9857.1856 | 11182.5474 | 11936.5082 | 12597.642 | 13582.6385 | 14445.9287 | 15000.8273 | 15185.4497 | 15327.7843 | 15381.4176 | 15299.9362 | 15176.167 | 14917.2831 | 14675.9332 | 14529.4729 | 14713.0639 | 14161.2596 | 13170.0745 | 11892.1575 | 15381.4176
2015-04-18 | 10736.9783 | 9925.2586 | 9398.2081 | 9108.3819 | 9062.9998 | 9521.9773 | 10461.5918 | 11249.5891 | 12290.2818 | 13584.7014 | 14634.6768 | 15330.8785 | 15759.9451 | 16225.111 | 16450.9898 | 16410.7648 | 16321.0321 | 16214.7969 | 15766.1336 | 15234.9574 | 15263.8369 | 14628.4883 | 13718.7847 | 12646.1182 | 16450.9898
2015-04-19 | 11476.4993 | 10698.8161 | 10155.2631 | 9800.458 | 9679.783 | 9792.2067 | 10007.7714 | 10333.697 | 11269.1859 | 12815.2695 | 14072.5583 | 14933.7857 | 15626.8932 | 16133.3155 | 16409.7334 | 16596.4186 | 16566.5077 | 16190.0431 | 15456.7105 | 14557.321 | 14397.4525 | 13580.5757 | 12614.1445 | 11261.966 | 16596.4186
2015-04-20 | 10035.6195 | 9118.696 | 8493.6615 | 8167.7359 | 8030.5584 | 8102.7571 | 8432.8083 | 8822.6813 | 9923.1958 | 11063.9353 | 11695.1582 | 12210.8632 | 12556.3856 | 12804.9554 | 12972.0438 | 13103.0329 | 13187.6085 | 13098.9072 | 12875.0913 | 12747.1964 | 13194.8284 | 12694.5945 | 11690.0012 | 10363.6079 | 13194.8284
2015-04-21 | 9196.0517 | 8430.7455 | 8022.3071 | 7823.245 | 7885.1296 | 8497.7871 | 9789.1125 | 10481.1886 | 11049.4955 | 11775.6082 | 12453.2446 | 12967.9182 | 13487.7488 | 13906.5013 | 14379.9185 | 14754.3203 | 15055.4921 | 15028.6754 | 14797.6395 | 14476.871 | 14723.378 | 13849.7737 | 12535.7574 | 11103.1289 | 15055.4921
2015-04-22 | 9761.2644 | 8863.9377 | 8428.6827 | 8161.5475 | 8166.7045 | 8830.9326 | 10182.0797 | 10769.9834 | 11369.2326 | 12103.5966 | 12865.8086 | 13618.7379 | 14183.9506 | 14642.928 | 15116.3452 | 15688.7778 | 16083.8078 | 16158.0694 | 15855.8662 | 15395.8574 | 15603.1708 | 14682.1216 | 13206.1739 | 11569.3262 | 16158.0694
2015-04-23 | 10217.1477 | 9357.9831 | 8816.4928 | 8488.5045 | 8435.9025 | 8981.5184 | 10227.4618 | 9528.1658 | 11594.08 | 12433.6478 | 13234.022 | 13827.0827 | 14532.5672 | 15379.3548 | 16276.6815 | 16948.1294 | 17431.8607 | 17553.5671 | 17178.1339 | 16459.2411 | 16383.9482 | 15594.9195 | 14145.7884 | 12192.2978 | 17553.5671
2015-04-24 | 10848.3706 | 9945.8868 | 9106.3191 | 8746.357 | 8757.7025 | 9090.8479 | 10303.7861 | 11018.5532 | 11803.4563 | 12917.3791 | 14028.2077 | 14957.5081 | 15804.2957 | 16555.1622 | 17184.3223 | 17798.0113 | 18152.8163 | 18106.4029 | 17584.5094 | 16766.6013 | 16698.5282 | 15746.5368 | 14226.2384 | 12595.5792 | 18152.8163
2015-04-25 | 11137.1654 | 10082.0329 | 9418.8363 | 9034.1204 | 8944.3877 | 9438.4331 | 10640.0258 | 11317.6621 | 12160.3241 | 13310.3463 | 14525.3473 | 15582.5426 | 16500.4975 | 17343.1595 | 18068.2407 | 18679.8669 | 19014.0437 | 18923.2796 | 18221.9208 | 17191.5422 | 16904.8102 | 15971.3841 | 14638.8024 | 13170.0745 | 19014.0437
2015-04-26 | 11686.9069 | 10569.8899 | 9837.5888 | 9362.1087 | 9088.7851 | 9107.3505 | 9412.6478 | 10009.8342 | 11494.0333 | 13131.9124 | 14606.8287 | 15867.2117 | 16850.1455 | 17591.7293 | 18036.267 | 18431.297 | 18634.4848 | 18513.8098 | 17835.1421 | 16794.4493 | 16502.5603 | 15642.3644 | 14474.8082 | 13184.5143 | 18634.4848
2015-04-27 | 11924.1312 | 10930.8834 | 10183.1111 | 9734.4478 | 9445.653 | 9395.1139 | 9560.1395 | 10025.3054 | 11659.0589 | 13504.2514 | 15034.8639 | 16265.336 | 17216.296 | 17984.6965 | 18494.2131 | 18928.4367 | 19100.6821 | 18985.1642 | 18378.6951 | 17512.3107 | 17386.4787 | 16445.8328 | 14962.6652 | 13465.0578 | 19100.6821
2015-04-28 | 12152.0728 | 11249.5891 | 10673.0309 | 10312.0374 | 10281.0951 | 10850.4334 | 12055.1203 | 12760.6048 | 13696.0936 | 14984.3248 | 16425.2046 | 17623.703 | 18522.0611 | 19286.336 | 19917.5589 | 20401.2902 | 20529.185 | 20478.6459 | 19908.2762 | 19042.9232 | 18794.3534 | 17645.3626 | 15984.7925 | 14307.7198 | 20529.185
2015-04-29 | 12932.8502 | 11960.2306 | 11324.882 | 10956.6686 | 10894.784 | 11400.1749 | 12533.6946 | 13224.7393 | 14334.5364 | 15717.6573 | 17079.1185 | 18220.8894 | 19056.3315 | 19725.7166 | 20189.8511 | 20518.8709 | 20450.7979 | 20212.5421 | 19739.125 | 18961.4418 | 18664.3957 | 17580.3838 | 15975.5098 | 14300.4999 | 20518.8709
2015-04-30 | 12887.4682 | 11998.3928 | 11417.7089 | 11092.8148 | 11072.1866 | 11570.3576 | 12729.6625 | 13414.5187 | 14485.1223 | 15866.1803 | 17208.0448 | 18261.1144 | 19036.7347 | 19707.1512 | 20115.5896 | 20396.1331 | 20250.7043 | 19452.393 | 18856.238 | 18213.6695 | 18169.3189 | 17196.6993 | 15662.9926 | 14062.2442 | 20396.1331
2015-05-01 | 12660.558 | 11739.5088 | 11122.7256 | 10791.643 | 10697.7847 | 11245.4634 | 12473.8728 | 13192.7656 | 14167.448 | 15561.9144 | 16977.0089 | 18036.267 | 18871.7091 | 19581.3192 | 20031.014 | 20255.8614 | 20143.4377 | 19546.2513 | 18630.3592 | 17919.7177 | 17853.7074 | 16795.4808 | 15358.7266 | 13830.1769 | 20255.8614
2015-05-02 | 12524.4119 | 11607.4884 | 11016.4904 | 10654.4655 | 10559.5758 | 11078.375 | 12265.528 | 13004.0175 | 13875.559 | 15132.8478 | 16200.3572 | 16997.6371 | 17458.6774 | 17989.8536 | 18370.4439 | 18569.506 | 18445.7368 | 18071.3349 | 17494.7767 | 16709.8737 | 16694.4026 | 15573.2599 | 14440.7717 | 13216.488 | 18569.506
2015-05-03 | 12004.5812 | 11080.4378 | 10459.529 | 10082.0329 | 9889.1593 | 9995.3945 | 10357.4194 | 10922.6321 | 12028.3036 | 13377.388 | 14465.5255 | 15204.0151 | 15542.3176 | 15704.249 | 15613.4849 | 15197.8266 | 14236.5525 | 13863.1821 | 13518.6911 | 13423.8014 | 13658.9629 | 13225.7707 | 12492.4382 | 11562.1063 | 15704.249
2015-05-04 | 10603.9264 | 9848.9343 | 9378.6113 | 9059.9056 | 8959.8588 | 8961.9217 | 9082.5966 | 9229.0569 | 10299.6605 | 11507.4416 | 12448.0875 | 13117.4726 | 13795.109 | 14374.7614 | 14874.9953 | 15431.9567 | 15864.1175 | 16082.7764 | 15894.0284 | 15216.392 | 14986.3876 | 14101.4378 | 12950.3842 | 11340.3532 | 16082.7764
2015-05-05 | 10061.4047 | 9057.8428 | 8667.9698 | 8387.4263 | 8395.6776 | 8977.3928 | 10120.1951 | 10823.6167 | 11647.7133 | 12723.474 | 13820.8943 | 14734.7235 | 15595.9509 | 16382.9167 | 17104.9038 | 17709.31 | 18237.392 | 18311.6535 | 17887.744 | 16503.5917 | 16542.7853 | 15498.9984 | 13510.4398 | 12185.078 | 18311.6535
2015-05-06 | 10724.6014 | 9805.6151 | 9187.8005 | 8820.6185 | 8733.98 | 9235.2453 | 10393.5188 | 11099.0032 | 11944.7594 | 13120.5669 | 14287.0916 | 15413.3913 | 16466.461 | 17259.6153 | 18008.4189 | 18653.0502 | 19062.52 | 19035.7033 | 18528.2496 | 17170.914 | 17338.0024 | 16323.095 | 14775.9799 | 13019.4887 | 19062.52
2015-05-07 | 11621.9281 | 10663.7482 | 10106.7868 | 9736.5106 | 9656.0606 | 10132.572 | 11275.3743 | 11970.5447 | 12959.6669 | 14143.7256 | 15426.7997 | 16479.8693 | 17410.2011 | 18256.9888 | 19019.2008 | 19394.634 | 19671.0519 | 19593.6961 | 18985.1642 | 18097.1202 | 17881.5555 | 17007.9512 | 15424.7368 | 13779.6379 | 19671.0519
2015-05-08 | 12310.91 | 11384.7038 | 10794.7373 | 10364.6393 | 10263.5611 | 10708.0988 | 11815.8332 | 12458.4016 | 13502.1886 | 14732.6607 | 15962.1015 | 16964.632 | 17809.3568 | 18601.4797 | 19211.043 | 19748.4076 | 20073.3018 | 19983.5691 | 19462.7071 | 18513.8098 | 18149.7221 | 17185.3537 | 15710.4374 | 14145.7884 | 20073.3018
2015-05-09 | 12522.349 | 11498.1589 | 10918.5065 | 10475.0002 | 10365.6707 | 10826.711 | 11929.2883 | 12585.2651 | 13574.3873 | 14816.2049 | 16005.4207 | 16968.7576 | 17793.8857 | 18526.1868 | 19181.1321 | 19663.832 | 19905.182 | 19665.8948 | 18920.1854 | 17868.1472 | 17426.7037 | 16532.4712 | 15365.9465 | 14069.4641 | 19905.182
2015-05-10 | 12771.9503 | 11847.8069 | 11225.8667 | 10780.2975 | 10565.7642 | 10620.429 | 10844.2449 | 11428.023 | 12986.4836 | 14572.7922 | 15724.8772 | 16599.5129 | 17482.3998 | 18055.8638 | 18426.14 | 18698.4322 | 18682.9611 | 18482.8675 | 17911.4664 | 16897.5903 | 16995.5743 | 16236.4565 | 15234.9574 | 14019.9564 | 18698.4322
2015-05-11 | 12807.0182 | 11914.8485 | 11256.809 | 10832.8994 | 10625.586 | 10571.9527 | 10655.4969 | 11018.5532 | 12278.9363 | 13799.2346 | 14996.7017 | 15914.6566 | 16717.0936 | 17393.6986 | 17889.8068 | 18135.2824 | 18227.0779 | 17974.3824 | 17446.3005 | 16682.0257 | 16696.4654 | 16173.5405 | 14990.5132 | 13486.7174 | 18227.0779
2015-05-12 | 12086.0626 | 11171.2019 | 10601.8636 | 10302.7547 | 10276.9694 | 10798.8629 | 11923.0998 | 12583.2022 | 13498.0629 | 14796.6081 | 16096.1848 | 17129.6576 | 17970.2568 | 18625.2021 | 19101.7136 | 19516.3404 | 19670.0205 | 19542.1256 | 19110.9962 | 18459.1451 | 18277.617 | 17236.9242 | 15701.1547 | 14139.6 | 19670.0205
2015-05-13 | 12763.699 | 11882.8748 | 11257.8404 | 10874.1558 | 10790.6116 | 11285.6884 | 12387.2343 | 13015.363 | 13884.8417 | 15162.7587 | 16354.0373 | 17250.3326 | 18059.9894 | 18592.197 | 18984.1328 | 19309.027 | 19476.1154 | 19290.4616 | 18745.8771 | 18003.2619 | 17887.744 | 17076.0243 | 15624.8304 | 14002.4224 | 19476.1154
2015-05-14 | 12751.3221 | 11875.655 | 11218.6468 | 10835.9937 | 10762.7636 | 10964.9199 | 12476.967 | 12982.3579 | 13944.6635 | 15346.3497 | 16537.6283 | 17636.0799 | 18413.7631 | 18903.6828 | 19248.1738 | 19237.8597 | 19137.8129 | 18921.2168 | 18332.2817 | 17632.9857 | 17683.5248 | 16837.7686 | 15483.5272 | 13891.0301 | 19248.1738
2015-05-15 | 12511.0035 | 11601.2999 | 10987.6109 | 10650.3399 | 10637.9629 | 11126.8513 | 12245.9312 | 12862.7144 | 13672.3712 | 15003.9216 | 16167.3521 | 16771.7583 | 16995.5743 | 16951.2237 | 16592.293 | 16173.5405 | 16059.054 | 16042.5514 | 15822.8611 | 15461.8676 | 15461.8676 | 14885.3094 | 13682.6853 | 12342.8837 | 16995.5743
2015-05-16 | 11115.5058 | 10333.697 | 9829.3375 | 9509.6004 | 9461.1241 | 10021.1797 | 11177.3904 | 11683.8127 | 12060.2774 | 12738.9451 | 13316.5348 | 13723.9417 | 13905.4699 | 14029.2391 | 14285.0288 | 14431.489 | 14595.4832 | 14424.2691 | 13975.6058 | 13391.8277 | 13148.4149 | 12620.333 | 11723.0063 | 10576.0783 | 14595.4832
2015-05-17 | 9476.5953 | 8749.4512 | 8247.1545 | 7963.5168 | 7877.9097 | 7974.8623 | 8281.191 | 8861.8749 | 10086.1586 | 11354.7929 | 12382.0773 | 13163.8861 | 13732.193 | 14250.9922 | 14748.1319 | 15139.0363 | 15384.5118 | 15338.0984 | 14884.278 | 14104.532 | 13870.4019 | 13414.5187 | 12441.8991 | 11354.7929 | 15384.5118
2015-05-18 | 10294.5034 | 9492.0664 | 8934.0736 | 8554.5147 | 8383.3006 | 8418.3686 | 8522.541 | 8992.864 | 10299.6605 | 11795.205 | 12982.3579 | 13875.559 | 14613.0172 | 15208.1407 | 15744.4739 | 16132.2841 | 16410.7648 | 16347.8488 | 15823.8925 | 15078.1831 | 14992.576 | 14437.6775 | 13242.2732 | 11812.739 | 16410.7648
2015-05-19 | 10554.4187 | 9684.9401 | 9139.3242 | 8870.1262 | 8882.5031 | 9408.5222 | 10527.6021 | 11181.516 | 12150.01 | 13290.7495 | 14344.8505 | 15234.9574 | 15987.8867 | 16731.5333 | 17227.6416 | 17705.1844 | 17963.0369 | 17921.7805 | 17493.7453 | 16660.366 | 16366.4142 | 15595.9509 | 14217.9871 | 12572.8881 | 17963.0369
2015-05-20 | 11192.8615 | 10246.0271 | 9698.3484 | 9364.1716 | 9268.2504 | 9712.7882 | 10761.7321 | 11534.2582 | 12490.3753 | 13653.8058 | 14788.3569 | 15711.4688 | 16443.7699 | 17050.239 | 17479.3056 | 17822.7651 | 18022.8587 | 17934.1574 | 17570.0697 | 16713.9994 | 16450.9898 | 15598.0137 | 14180.8564 | 12597.642 | 18022.8587
2015-05-21 | 11216.584 | 10257.3726 | 9646.7779 | 9254.8421 | 9147.5755 | 9593.1446 | 10676.1251 | 11425.9602 | 12270.685 | 13333.0373 | 14373.73 | 15281.3708 | 16034.3002 | 16835.7057 | 17591.7293 | 18103.3087 | 18411.7003 | 18284.8368 | 17753.6607 | 16862.5224 | 16449.9584 | 15698.0605 | 14301.5313 | 12667.7779 | 18411.7003
2015-05-22 | 11147.4795 | 10155.2631 | 9455.9671 | 9094.9736 | 9031.0261 | 9508.569 | 10602.895 | 11305.2852 | 12288.219 | 13449.5867 | 14673.8703 | 15828.0182 | 16884.182 | 17894.9638 | 18644.7989 | 19273.959 | 19666.9262 | 19546.2513 | 18985.1642 | 17990.885 | 17421.5466 | 16675.8372 | 15074.0574 | 13343.3514 | 19666.9262
2015-05-23 | 11779.7338 | 10723.57 | 9996.4259 | 9567.3593 | 9394.0825 | 9788.0811 | 10750.3866 | 11642.5563 | 12809.081 | 14198.3903 | 15619.6733 | 17005.8884 | 18170.3503 | 19332.7494 | 20172.3172 | 20719.9959 | 20895.3356 | 20658.1113 | 19921.6845 | 18638.6105 | 18096.0888 | 17323.5627 | 15961.07 | 14472.7454 | 20895.3356
2015-05-24 | 13045.2739 | 11966.419 | 11118.6 | 10534.8219 | 10217.1477 | 10130.5092 | 10213.022 | 10847.3392 | 12523.3805 | 14354.1332 | 15985.8239 | 17473.1171 | 18715.9662 | 19568.9423 | 20085.6787 | 20360.0338 | 20347.6569 | 20114.5582 | 19313.1526 | 18268.3343 | 17821.7337 | 17025.4852 | 15809.4528 | 14469.6512 | 20360.0338
2015-05-25 | 13209.2681 | 12139.6959 | 11327.9762 | 10789.5802 | 10460.5604 | 10335.7598 | 10388.3617 | 10789.5802 | 12139.6959 | 13804.3917 | 15570.1657 | 16953.2865 | 18165.1933 | 18963.5046 | 19434.859 | 19704.057 | 19793.7897 | 19422.4821 | 18638.6105 | 17730.9696 | 17445.2691 | 16727.4077 | 15470.1189 | 14198.3903 | 19793.7897
2015-05-26 | 12870.9656 | 11929.2883 | 11232.0551 | 10774.1091 | 10522.445 | 10526.5707 | 10637.9629 | 11159.8564 | 12785.3586 | 14695.53 | 16392.1994 | 17601.012 | 18611.7938 | 19304.9013 | 19690.6487 | 19890.7422 | 19896.9307 | 19587.5077 | 18823.2329 | 17911.4664 | 17718.5927 | 16893.4647 | 15518.5952 | 13932.2865 | 19896.9307
2015-05-27 | 12601.7676 | 11638.4307 | 11005.1449 | 10617.3347 | 10487.3771 | 10971.1084 | 11971.5761 | 12843.1176 | 14007.5795 | 15431.9567 | 16793.4179 | 18000.1677 | 18883.0546 | 19557.5968 | 19948.5012 | 20132.0922 | 19839.1717 | 19070.7713 | 18343.6272 | 17631.9543 | 17549.4415 | 16788.2609 | 15426.7997 | 13759.0097 | 20132.0922
2015-05-28 | 12405.7997 | 11473.4051 | 10883.4385 | 10513.1623 | 10423.4297 | 10898.9097 | 11940.6338 | 12704.9086 | 13792.0148 | 15087.4658 | 16409.7334 | 17743.3466 | 18680.8983 | 19446.2045 | 19860.8313 | 19978.4121 | 19967.0666 | 19567.9109 | 18939.7822 | 18240.4862 | 18015.6388 | 17199.7935 | 15799.1387 | 14229.3326 | 19978.4121
2015-05-29 | 12804.9554 | 11778.7024 | 11163.982 | 10787.5174 | 10654.4655 | 11086.6263 | 12097.4081 | 12853.4317 | 13773.4494 | 14917.2831 | 16097.2162 | 16927.5012 | 17425.6723 | 17751.5978 | 17524.6876 | 17274.055 | 17114.1865 | 16912.0301 | 16726.3763 | 16163.2264 | 16108.5617 | 15563.9772 | 14433.5518 | 13033.9284 | 17751.5978
2015-05-30 | 11639.4621 | 10633.8373 | 10138.7605 | 9831.4003 | 9774.6728 | 10221.2733 | 11205.2385 | 11982.9216 | 13057.6508 | 14596.5146 | 15946.6303 | 17038.8935 | 17891.8696 | 18547.8464 | 18932.5623 | 19179.0693 | 19109.9648 | 18589.1028 | 17653.6139 | 16881.0878 | 16650.0519 | 15959.0072 | 14880.1523 | 13707.4392 | 19179.0693
2015-05-31 | 12539.883 | 11535.2897 | 10834.9623 | 10377.0162 | 10200.6451 | 10169.7028 | 10377.0162 | 11044.3385 | 12692.5317 | 14511.939 | 16104.436 | 17324.5941 | 18104.3401 | 18600.4483 | 18682.9611 | 18607.6682 | 18332.2817 | 17728.9068 | 17028.5794 | 16286.9956 | 16186.9488 | 15686.715 | 14780.1056 | 13605.3296 | 18682.9611
2015-06-01 | 12532.6631 | 11568.2948 | 10935.009 | 10490.4713 | 10247.0585 | 10234.6816 | 10329.5713 | 10802.9885 | 12206.7376 | 13904.4385 | 15435.0509 | 16571.6648 | 17500.9652 | 18134.251 | 18458.1137 | 18377.6637 | 17986.7593 | 17311.1858 | 16558.2565 | 16040.4886 | 16030.1745 | 15671.2438 | 14685.2159 | 13372.2309 | 18458.1137
2015-06-02 | 12180.9523 | 11353.7615 | 10876.2187 | 10609.0835 | 10642.0886 | 11218.6468 | 12240.7741 | 12922.5361 | 13551.6962 | 14276.7775 | 14967.8222 | 15357.6952 | 15738.2855 | 15992.0123 | 16162.195 | 16153.9437 | 16114.7501 | 15919.8136 | 15719.7201 | 15498.9984 | 15569.1342 | 15133.8792 | 14007.5795 | 12668.8093 | 16162.195
2015-06-03 | 11439.3685 | 10603.9264 | 10086.1586 | 9774.6728 | 9756.1074 | 10284.1893 | 11342.416 | 12011.8011 | 12648.1811 | 13544.4764 | 14438.7089 | 15191.6382 | 15736.2227 | 16129.1899 | 16293.1841 | 16346.8174 | 16146.7239 | 15930.1277 | 15558.8201 | 15234.9574 | 15341.1926 | 14780.1056 | 13681.6539 | 12290.2818 | 16346.8174
2015-06-04 | 11015.459 | 10158.3573 | 9620.9927 | 9340.4491 | 9336.3235 | 9850.9971 | 10877.2501 | 11029.8987 | 12374.8574 | 13586.7642 | 14584.1377 | 15364.9151 | 15897.1226 | 16530.4084 | 16984.2288 | 17289.5262 | 17521.5934 | 17568.0069 | 17267.8665 | 16566.5077 | 16217.8911 | 15627.9246 | 14461.3999 | 12960.6983 | 17568.0069
2015-06-05 | 11599.2371 | 10679.2193 | 10054.1849 | 9667.4061 | 9543.6369 | 9970.6407 | 10865.9046 | 11803.4563 | 13073.122 | 14455.2114 | 15861.0233 | 17098.7153 | 18039.3612 | 18898.5258 | 19487.4609 | 19908.2762 | 20083.6159 | 20006.2601 | 19513.2462 | 18503.4957 | 17931.0632 | 17021.3595 | 15576.3541 | 13861.1192 | 20083.6159
2015-06-06 | 12471.81 | 11383.6724 | 10641.0572 | 10169.7028 | 9950.0125 | 10283.1579 | 10995.8622 | 11942.6966 | 13432.0527 | 15046.2094 | 16687.1827 | 18171.3817 | 19349.252 | 20231.1075 | 20844.7965 | 21185.1618 | 21296.5541 | 21092.3349 | 20431.2011 | 19368.8488 | 18666.4585 | 17873.3042 | 16535.5654 | 15139.0363 | 21296.5541
2015-06-07 | 13759.0097 | 12673.9663 | 11892.1575 | 11397.0807 | 11054.6526 | 10933.9776 | 11035.0558 | 11709.5979 | 13412.4559 | 15207.1093 | 16999.6999 | 18542.6893 | 19540.0628 | 20230.0761 | 20634.3888 | 20742.6869 | 20368.2851 | 19793.7897 | 19023.3264 | 18229.1407 | 17682.4934 | 16936.7839 | 15754.788 | 14449.023 | 20742.6869
2015-06-08 | 13211.3309 | 12189.2036 | 11447.6198 | 10798.8629 | 10592.5809 | 10513.1623 | 10527.6021 | 10970.077 | 12461.4959 | 14429.4262 | 16265.336 | 17799.0427 | 18693.2752 | 18896.463 | 18667.4899 | 18524.1239 | 18251.8317 | 17959.9427 | 17396.7928 | 16711.9365 | 16323.095 | 15716.6259 | 14419.1121 | 13143.2579 | 18896.463
2015-06-09 | 11810.6761 | 10873.1244 | 10216.1162 | 9876.7823 | 9829.3375 | 10259.4355 | 11051.5584 | 11913.8171 | 13155.6348 | 14654.2736 | 16267.3988 | 17877.4299 | 19088.3052 | 20078.4588 | 20602.4151 | 20445.6408 | 20166.1287 | 19452.393 | 18604.5739 | 17844.4247 | 17414.3268 | 16668.6173 | 15283.4337 | 13750.7584 | 20602.4151
2015-06-10 | 12356.292 | 11374.3897 | 10765.8578 | 10380.1104 | 10280.0637 | 10699.8475 | 11496.0961 | 12509.9721 | 13913.7212 | 15381.4176 | 16732.5647 | 17940.3459 | 18862.4264 | 19367.8173 | 19341.0007 | 18675.7412 | 18072.3664 | 17786.6658 | 17711.3729 | 17168.8512 | 16988.3544 | 16174.5719 | 14801.7652 | 13323.7546 | 19367.8173
2015-06-11 | 12068.5286 | 11146.4481 | 10491.5027 | 10135.6663 | 10054.1849 | 10424.4611 | 11258.8718 | 12163.4184 | 13448.5552 | 15064.7747 | 16493.2776 | 17673.2107 | 18402.4176 | 18847.9867 | 18402.4176 | 17615.4517 | 17213.2018 | 17087.3698 | 16907.9044 | 16363.32 | 16101.3418 | 15554.6945 | 14341.7563 | 12960.6983 | 18847.9867
2015-06-12 | 11706.5037 | 10781.3289 | 10186.2054 | 9815.9292 | 9732.3849 | 10087.19 | 10903.0353 | 11608.5198 | 12354.2292 | 13329.9431 | 14552.164 | 15856.8976 | 17232.7986 | 18441.6111 | 19234.7655 | 19408.0423 | 18918.1226 | 18139.408 | 17542.2216 | 16923.3756 | 16592.293 | 15876.4944 | 14463.4627 | 13015.363 | 19408.0423
2015-06-13 | 11718.8806 | 10786.486 | 10173.8284 | 9774.6728 | 9699.3798 | 10049.0278 | 10764.8264 | 11724.0377 | 13105.0957 | 14524.3159 | 15877.5258 | 17164.7255 | 18151.7849 | 18648.9246 | 18637.579 | 18094.026 | 17533.9703 | 16933.6897 | 16395.2937 | 15606.265 | 15125.6279 | 14639.8338 | 13705.3763 | 12522.349 | 18648.9246
2015-06-14 | 11406.3634 | 10542.0418 | 9931.4471 | 9564.2651 | 9400.2709 | 9466.2812 | 9694.2228 | 10339.8854 | 11780.7652 | 13478.4661 | 15068.9004 | 16467.4924 | 17524.6876 | 18377.6637 | 18767.5367 | 18737.6258 | 18236.3606 | 17730.9696 | 16934.7211 | 16061.1168 | 15725.9086 | 15150.3818 | 14169.5108 | 13031.8656 | 18767.5367
2015-06-15 | 11935.4767 | 11120.6628 | 10467.7803 | 10071.7188 | 9957.2323 | 10059.3419 | 10242.9329 | 10844.2449 | 12378.9831 | 14181.8878 | 15760.9765 | 17167.8198 | 18291.0253 | 18999.604 | 19405.9795 | 19253.3308 | 18713.9034 | 18033.1728 | 17304.9973 | 16540.7225 | 16388.0738 | 16023.9861 | 14939.9741 | 13718.7847 | 19405.9795
2015-06-16 | 12408.8939 | 11535.2897 | 10974.2026 | 10621.4604 | 10500.7854 | 10882.4071 | 11621.9281 | 12383.1087 | 13358.8226 | 14560.4152 | 16103.4046 | 17558.7242 | 18542.6893 | 19402.8853 | 19994.9146 | 20342.4998 | 20549.8132 | 20403.353 | 19661.7692 | 18378.6951 | 17768.1004 | 16990.4172 | 15582.5426 | 14063.2756 | 20549.8132
2015-06-17 | 12661.5894 | 11700.3153 | 10977.2968 | 10552.3559 | 10401.77 | 10729.7584 | 11493.0018 | 12323.2869 | 13339.2258 | 14421.1749 | 15453.6163 | 16387.0424 | 17182.2595 | 17873.3042 | 18106.4029 | 18102.2772 | 17923.8433 | 17761.9119 | 17430.8293 | 16881.0878 | 16552.068 | 16116.813 | 14704.8126 | 13229.8963 | 18106.4029
2015-06-18 | 11860.1838 | 10960.7943 | 10380.1104 | 10009.8342 | 9948.981 | 10332.6656 | 11174.2961 | 12027.2722 | 13178.3258 | 14446.9601 | 15806.3585 | 17067.773 | 17745.4094 | 17984.6965 | 17828.9536 | 17405.0441 | 16922.3442 | 16508.7488 | 16101.3418 | 15692.9034 | 15534.0663 | 15125.6279 | 13965.2917 | 12612.0817 | 17984.6965
2015-06-19 | 11350.6673 | 10526.5707 | 10017.0541 | 9714.851 | 9636.4638 | 10027.3682 | 10846.3078 | 11684.8441 | 12926.6618 | 14339.6935 | 15819.7669 | 16974.9461 | 17915.592 | 18592.197 | 18646.8617 | 18061.0208 | 17510.2479 | 16944.0038 | 16370.5398 | 15823.8925 | 15533.0349 | 14912.1261 | 13819.8628 | 12452.2132 | 18646.8617
2015-06-20 | 11204.207 | 10346.0739 | 9784.9869 | 9473.501 | 9394.0825 | 9734.4478 | 10491.5027 | 11385.7352 | 12693.5631 | 14269.5576 | 15734.1598 | 17051.2704 | 18046.5811 | 18607.6682 | 18445.7368 | 17630.9229 | 17112.1236 | 16646.9577 | 16250.8963 | 15729.0028 | 15418.5484 | 15032.801 | 14092.1551 | 12913.2534 | 18607.6682
2015-06-21 | 11698.2524 | 10844.2449 | 10232.6188 | 9872.6567 | 9713.8196 | 9776.7356 | 9932.4785 | 10689.5334 | 12481.0926 | 14407.7666 | 15947.6617 | 17342.1281 | 18430.2656 | 19057.3629 | 18869.6463 | 18195.1042 | 17610.2947 | 17131.7204 | 16548.9738 | 15936.3162 | 15628.956 | 15261.7741 | 14352.0704 | 13147.3835 | 19057.3629
2015-06-22 | 11951.9793 | 11162.9506 | 10524.5078 | 10123.2893 | 9894.3163 | 9880.908 | 9941.7612 | 10691.5963 | 12398.5798 | 14377.8557 | 16007.4835 | 17228.673 | 18352.9099 | 19168.7552 | 19686.523 | 19765.9416 | 19429.7019 | 18668.5214 | 17698.9959 | 16852.2083 | 16506.6859 | 15992.0123 | 14902.8434 | 13475.3719 | 19765.9416
2015-06-23 | 12136.6017 | 11319.725 | 10738.0097 | 10386.2989 | 10309.9746 | 10713.2559 | 11494.0333 | 12437.7734 | 13799.2346 | 15293.7478 | 16868.7109 | 18249.7689 | 19450.3301 | 20402.3216 | 20940.7176 | 21062.424 | 20849.9535 | 20386.8504 | 19708.1826 | 18761.3483 | 18132.1881 | 17289.5262 | 15937.3476 | 14286.0602 | 21062.424
2015-06-24 | 12878.1855 | 11877.7178 | 11214.5211 | 10781.3289 | 10636.9315 | 10981.4225 | 11740.5403 | 12664.6836 | 14094.2179 | 15633.0817 | 17297.7774 | 18699.4637 | 19892.805 | 20935.5606 | 21547.1867 | 21880.3322 | 21940.1539 | 21529.6527 | 20987.1311 | 20048.548 | 19531.8115 | 18633.4534 | 17154.4114 | 15486.6214 | 21940.1539
2015-06-25 | 14018.925 | 12919.4419 | 12108.7536 | 11601.2999 | 11409.4576 | 11711.6608 | 12428.4907 | 13334.0687 | 14760.5088 | 16453.0526 | 18188.9157 | 19490.5551 | 20645.7344 | 21542.0297 | 22093.834 | 22148.4988 | 21689.5213 | 21089.2407 | 20330.1229 | 19330.6866 | 18712.872 | 17907.3408 | 16635.6122 | 15018.3613 | 22148.4988
2015-06-26 | 13601.2039 | 12482.1241 | 11721.9749 | 11232.0551 | 11041.2443 | 11303.2224 | 12044.8062 | 12941.1015 | 14409.8294 | 16193.1373 | 17895.9952 | 19211.043 | 20213.5736 | 20867.4875 | 21506.9617 | 21715.3065 | 21720.4636 | 21392.4752 | 20796.3202 | 19819.5749 | 19117.1847 | 18256.9888 | 16843.957 | 15187.5125 | 21720.4636
2015-06-27 | 13710.5334 | 12682.2176 | 11939.6024 | 11468.248 | 11312.5051 | 11637.3992 | 12250.0568 | 13121.5983 | 14568.6665 | 16237.4879 | 17733.0325 | 19043.9546 | 19857.7371 | 20540.5305 | 21124.3086 | 21187.2246 | 20964.4401 | 20416.7613 | 19422.4821 | 18372.5067 | 17785.6344 | 16958.4435 | 15904.3425 | 14535.6614 | 21187.2246
2015-06-28 | 13096.8444 | 12050.9947 | 11342.416 | 10807.1142 | 10481.1886 | 10216.1162 | 10940.1661 | 11374.3897 | 13124.6925 | 15122.5337 | 16689.2455 | 18261.1144 | 19506.0263 | 20272.3639 | 20738.5613 | 21085.115 | 21043.8586 | 20801.4773 | 20080.5217 | 19074.8969 | 18503.4957 | 17799.0427 | 16624.2667 | 15198.858 | 21085.115
2015-06-29 | 13865.2449 | 12845.1804 | 12083.9998 | 11543.5409 | 11231.0237 | 11109.3173 | 11070.1237 | 11560.0435 | 13350.5713 | 15468.0561 | 17369.9761 | 19035.7033 | 20297.1178 | 20903.5869 | 20930.4035 | 20527.1222 | 20209.4479 | 19697.8685 | 18676.7726 | 17722.7184 | 17149.2544 | 16560.3193 | 15418.5484 | 13999.3282 | 20930.4035
2015-06-30 | 12745.1336 | 11798.2992 | 11155.7308 | 10775.1405 | 10727.6956 | 11141.291 | 11896.2832 | 12666.7464 | 13938.475 | 15583.574 | 17093.5583 | 18384.8836 | 19410.1052 | 20277.521 | 20803.5401 | 21060.3612 | 20832.4196 | 19958.8153 | 19096.5565 | 18295.1509 | 17849.5818 | 17176.0711 | 16034.3002 | 14549.0697 | 21060.3612
2015-07-01 | 13194.8284 | 12238.7113 | 11645.6505 | 11285.6884 | 11200.0814 | 11612.6454 | 12436.742 | 13110.2528 | 13957.0404 | 15132.8478 | 16322.0636 | 17507.1537 | 18242.549 | 18570.5374 | 18889.2431 | 19025.3892 | 19261.5821 | 19115.1219 | 18721.1233 | 18353.9413 | 18159.0048 | 17374.1018 | 16032.2373 | 14554.2268 | 19261.5821
2015-07-02 | 13107.1585 | 12195.3921 | 11588.923 | 11257.8404 | 11151.6051 | 11489.9076 | 12249.0254 | 13021.5515 | 14287.0916 | 15871.3374 | 17546.3472 | 18694.3066 | 19378.1314 | 19461.6757 | 19064.5828 | 18687.0867 | 18586.0085 | 18439.5483 | 18153.8478 | 17629.8915 | 17437.0178 | 17003.8256 | 15931.1592 | 14444.8973 | 19461.6757
2015-07-03 | 13269.0899 | 12326.3811 | 11768.3883 | 11392.9551 | 11332.1019 | 11662.1531 | 12411.9882 | 13201.0168 | 14476.871 | 16193.1373 | 17977.4766 | 19346.1577 | 20301.2434 | 20968.5657 | 21511.0874 | 21809.1649 | 21689.5213 | 20900.4926 | 20036.171 | 19181.1321 | 18650.9874 | 18037.2984 | 16885.2134 | 15445.365 | 21809.1649
2015-07-04 | 14131.3487 | 13051.4624 | 12249.0254 | 11704.4409 | 11414.6147 | 11407.3948 | 11527.0384 | 11907.6287 | 13429.9899 | 15581.5112 | 17516.4364 | 19002.6982 | 19888.6794 | 20316.7146 | 20462.1434 | 20425.0126 | 19384.3199 | 18103.3087 | 17176.0711 | 16339.5975 | 15807.39 | 15129.7536 | 14752.2575 | 13956.009 | 20462.1434
2015-07-05 | 12857.5573 | 11907.6287 | 11270.2173 | 10847.3392 | 10642.0886 | 10650.3399 | 10778.2347 | 11144.3853 | 12426.4279 | 13862.1507 | 15503.124 | 16644.8949 | 17579.3524 | 18462.2393 | 18571.5688 | 17924.8747 | 17325.6255 | 16907.9044 | 16494.309 | 16059.054 | 15783.6675 | 15355.6324 | 14529.4729 | 13422.77 | 18571.5688
2015-07-06 | 12384.1401 | 11535.2897 | 10944.2917 | 10537.9162 | 10407.9585 | 10429.6181 | 10520.3822 | 10922.6321 | 12393.4228 | 13860.0878 | 15163.7901 | 15667.1182 | 16172.5091 | 16627.3609 | 17039.9249 | 17104.9038 | 16986.2916 | 16669.6487 | 16160.1322 | 15370.0721 | 15216.392 | 14892.5293 | 13962.1974 | 12744.1022 | 17104.9038
2015-07-07 | 11719.912 | 10970.077 | 10509.0367 | 10279.0323 | 10267.6867 | 10701.9104 | 11472.3736 | 12297.5017 | 13503.22 | 14732.6607 | 15956.9444 | 16752.1615 | 17119.3435 | 17401.9498 | 17500.9652 | 17785.6344 | 17785.6344 | 17739.2209 | 17532.9389 | 17263.7409 | 17056.4275 | 16563.4135 | 15410.2971 | 14012.7365 | 17785.6344
2015-07-08 | 12709.0343 | 11752.9172 | 11103.1289 | 10725.6328 | 10618.3661 | 10948.4174 | 11709.5979 | 12578.0452 | 13830.1769 | 15508.2811 | 17125.532 | 18547.8464 | 19650.4237 | 20153.7518 | 20055.7678 | 19466.8327 | 18853.1437 | 18312.6849 | 17745.4094 | 16990.4172 | 16361.2571 | 15655.7727 | 14514.0018 | 13213.3938 | 20153.7518
2015-07-09 | 11984.9844 | 11169.1391 | 10636.9315 | 10114.0066 | 10158.3573 | 10652.4027 | 11464.1224 | 12273.7792 | 13595.0155 | 15315.4074 | 16833.6429 | 18294.1195 | 19226.5142 | 19492.618 | 18675.7412 | 18016.6702 | 17697.9645 | 17227.6416 | 16656.2404 | 16321.0321 | 16025.0175 | 16282.87 | 14422.2063 | 13147.3835 | 19492.618
2015-07-10 | 11860.1838 | 11006.1763 | 10488.4085 | 10193.4252 | 10105.7554 | 10481.1886 | 11297.0339 | 12196.4235 | 13514.5655 | 15081.2773 | 16277.7129 | 17082.2127 | 17814.5139 | 18330.2189 | 18309.5907 | 17968.1939 | 17449.3947 | 16882.1192 | 16408.702 | 15911.5624 | 15773.3534 | 15339.1298 | 14336.5993 | 13080.3419 | 18330.2189
2015-07-11 | 11836.4614 | 11001.0193 | 10465.7175 | 10183.1111 | 10116.0695 | 10459.529 | 11166.0449 | 12089.1568 | 13604.2982 | 15242.1773 | 16802.7006 | 18183.7586 | 19212.0744 | 20033.0768 | 20511.6511 | 20627.169 | 20527.1222 | 20171.2857 | 19588.5391 | 18693.2752 | 18162.099 | 17579.3524 | 16456.1469 | 15127.6908 | 20627.169
2015-07-12 | 13853.8994 | 12889.531 | 12152.0728 | 11683.8127 | 11316.6307 | 11319.725 | 11415.6461 | 11877.7178 | 13330.9745 | 15297.8734 | 16862.5224 | 18246.6747 | 19346.1577 | 19944.3755 | 20118.6838 | 20083.6159 | 19924.7788 | 19394.634 | 18654.0816 | 17631.9543 | 17112.1236 | 16388.0738 | 15345.3183 | 14148.8826 | 20118.6838
2015-07-13 | 13166.9803 | 12392.3914 | 11829.2415 | 11386.7666 | 11093.8462 | 10978.3282 | 11002.0507 | 11517.7557 | 13172.1374 | 14996.7017 | 16508.7488 | 17848.5504 | 18812.9188 | 19294.5872 | 19687.5544 | 19960.8781 | 19910.339 | 19536.9686 | 18923.2796 | 18127.0311 | 17688.6818 | 17215.2646 | 16104.436 | 14768.7601 | 19960.8781
2015-07-14 | 13523.8482 | 12588.3593 | 11882.8748 | 11493.0018 | 11388.8294 | 11698.2524 | 12416.1138 | 13196.8912 | 14585.1691 | 16204.4828 | 17782.5401 | 19077.9911 | 20006.2601 | 20254.83 | 20068.1447 | 19968.098 | 19926.8416 | 19907.2448 | 19648.3609 | 18788.1649 | 18010.4818 | 17162.6627 | 15862.0547 | 14391.264 | 20254.83
2015-07-15 | 13071.0592 | 12140.7273 | 11502.2845 | 11090.7519 | 10993.7994 | 11320.7564 | 12102.5652 | 12855.4945 | 13993.1397 | 15563.9772 | 16875.9307 | 17981.6023 | 18645.8303 | 18650.9874 | 18367.3496 | 17851.6446 | 17492.7139 | 17240.0185 | 17130.689 | 16717.0936 | 16576.8218 | 16129.1899 | 15008.0472 | 13668.2456 | 18650.9874
2015-07-16 | 12480.0612 | 11554.8864 | 10917.4751 | 10600.8322 | 10555.4501 | 10995.8622 | 11984.9844 | 12794.6413 | 14174.6679 | 15741.3797 | 17024.4538 | 17979.5395 | 18566.4118 | 18124.9683 | 17612.3575 | 17189.4794 | 16809.9205 | 16453.0526 | 16216.8597 | 15815.6412 | 15871.3374 | 15578.4169 | 14593.4204 | 13341.2886 | 18566.4118
2015-07-17 | 12174.7639 | 11379.5467 | 10755.5437 | 10447.1521 | 10417.2412 | 10824.6482 | 11663.1845 | 12373.826 | 13901.3442 | 15369.0407 | 16785.1667 | 17988.8221 | 18017.7016 | 17824.828 | 17584.5094 | 17975.4138 | 18499.3701 | 18560.2233 | 18443.674 | 17960.9741 | 17565.944 | 16990.4172 | 15657.8355 | 14298.4371 | 18560.2233
2015-07-18 | 12865.8086 | 11913.8171 | 11278.4686 | 10858.6847 | 10698.8161 | 11010.302 | 11693.0954 | 12501.7208 | 13976.6372 | 15760.9765 | 17381.3216 | 18825.2957 | 19995.946 | 20854.0792 | 21377.0041 | 21662.7046 | 21663.736 | 21118.1201 | 20086.7101 | 18995.4783 | 18304.4336 | 17556.6613 | 16345.786 | 15036.9267 | 21663.736
2015-07-19 | 13712.5962 | 12663.6522 | 11918.9742 | 11441.4313 | 11135.1026 | 11115.5058 | 11220.7096 | 11737.446 | 13517.6597 | 15513.4381 | 17229.7044 | 18676.7726 | 19759.7532 | 20535.3735 | 20856.142 | 20965.4715 | 21223.324 | 21025.2932 | 20223.8877 | 19354.409 | 18836.6412 | 18029.0471 | 16806.8263 | 15530.9721 | 21223.324
2015-07-20 | 14235.5211 | 13227.8335 | 12443.9619 | 11891.1261 | 11568.2948 | 11430.0858 | 11445.557 | 11772.514 | 13417.6129 | 15497.967 | 17204.9505 | 18847.9867 | 20072.2704 | 20878.833 | 21264.5804 | 21042.8272 | 20843.7651 | 20526.0908 | 19829.889 | 18961.4418 | 18595.2912 | 17943.4401 | 16799.6064 | 15319.533 | 21264.5804
2015-07-21 | 13960.1346 | 12976.1695 | 12258.3081 | 11813.7704 | 11703.4095 | 12011.8011 | 12768.856 | 13464.0264 | 14670.7761 | 16255.0219 | 17883.6183 | 19226.5142 | 20065.0505 | 20208.4165 | 19729.8423 | 19243.0167 | 18720.0919 | 18247.7061 | 17762.9434 | 17222.4845 | 17116.2493 | 16348.8802 | 15222.5805 | 13901.3442 | 20208.4165
2015-07-22 | 12604.8618 | 11699.2838 | 11178.4218 | 10805.0514 | 10749.3552 | 11216.584 | 11996.3299 | 12774.0131 | 14100.4064 | 15590.7939 | 16925.4384 | 17921.7805 | 18518.9669 | 18852.1123 | 19309.027 | 19575.1308 | 19372.9744 | 18769.5995 | 18235.3291 | 17637.1113 | 17466.9287 | 16821.266 | 15618.6419 | 14298.4371 | 19575.1308
2015-07-23 | 13100.9701 | 12205.7062 | 11580.6717 | 11184.6102 | 11083.5321 | 11415.6461 | 12305.7529 | 13000.9233 | 14308.7512 | 15645.4586 | 16816.109 | 17746.4408 | 18453.9881 | 19122.3418 | 19768.0044 | 20098.0556 | 20221.8248 | 20117.6524 | 20037.2024 | 19310.0584 | 18865.5207 | 18190.9785 | 16799.6064 | 15354.601 | 20221.8248
2015-07-24 | 13977.6686 | 12903.9708 | 12172.701 | 11718.8806 | 11557.9807 | 11849.8697 | 12502.7523 | 13247.4303 | 14614.0486 | 16334.4405 | 17874.3356 | 16540.7225 | 20031.014 | 20537.4363 | 20834.4824 | 21117.0887 | 21504.8989 | 21281.0829 | 20931.4349 | 20077.4274 | 19295.6186 | 18525.1554 | 16993.5115 | 15419.5798 | 21504.8989
2015-07-25 | 14086.998 | 12974.1066 | 12245.9312 | 11745.6973 | 11504.3474 | 11793.1422 | 12443.9619 | 13226.8021 | 14801.7652 | 16542.7853 | 18090.9317 | 19486.4295 | 20321.8716 | 20773.6292 | 21186.1932 | 21571.9406 | 21624.5425 | 21235.7009 | 20427.0754 | 19428.6705 | 18898.5258 | 18079.5862 | 16879.025 | 15560.883 | 21624.5425
2015-07-26 | 14385.0755 | 13394.9219 | 12743.0708 | 12188.1722 | 11847.8069 | 11791.0793 | 11937.5396 | 12329.4754 | 13784.7949 | 15715.5945 | 17458.6774 | 18604.5739 | 19087.2738 | 19352.3462 | 19273.959 | 18982.07 | 18985.1642 | 18767.5367 | 18283.8054 | 17609.2633 | 17431.8607 | 16728.4391 | 15629.9874 | 14594.4518 | 19352.3462
2015-07-27 | 13465.0578 | 12568.7625 | 11945.7908 | 11487.8448 | 11243.4006 | 11173.2647 | 11229.9923 | 11586.8602 | 13394.9219 | 15439.1766 | 17122.4377 | 18606.6367 | 19779.3499 | 20675.6452 | 21250.1406 | 21631.7623 | 21759.6572 | 21614.2284 | 20961.3458 | 19992.8518 | 19546.2513 | 18797.4476 | 17476.2114 | 16042.5514 | 21759.6572
2015-07-28 | 14614.0486 | 13643.4917 | 12910.1592 | 12450.1503 | 12320.1927 | 12650.2439 | 13342.32 | 14022.0192 | 15423.7054 | 17197.7307 | 18742.7829 | 20170.2543 | 21129.4657 | 22010.2898 | 22797.2557 | 23234.5735 | 23392.3792 | 23217.0395 | 22771.4704 | 21889.6148 | 21347.0932 | 20460.0806 | 18824.2643 | 17089.4326 | 23392.3792
2015-07-29 | 15549.5375 | 14458.3057 | 13671.3398 | 13187.6085 | 12973.0752 | 13212.3623 | 13843.5853 | 14444.8973 | 15841.4265 | 17443.2062 | 18954.2219 | 20288.8665 | 21161.4394 | 21751.4059 | 22042.2635 | 21815.3533 | 21592.5688 | 20832.4196 | 19898.9935 | 19067.677 | 18716.9976 | 17987.7907 | 16645.9263 | 15336.0356 | 22042.2635
2015-07-30 | 14018.925 | 13137.0694 | 12460.4644 | 12066.4658 | 11909.6915 | 12229.4286 | 13035.9912 | 13668.2456 | 15021.4555 | 16519.0629 | 17745.4094 | 19157.4097 | 20340.437 | 21368.7528 | 21906.1174 | 21949.4366 | 21312.0252 | 20257.9242 | 19497.775 | 18748.9713 | 18277.617 | 17570.0697 | 16211.7027 | 14834.7703 | 21949.4366
2015-07-31 | 13493.9373 | 12538.8516 | 11885.9691 | 11497.1275 | 11362.0128 | 11656.996 | 12439.8362 | 13038.0541 | 14235.5211 | 15947.6617 | 17726.844 | 19296.6501 | 20314.6517 | 20983.0054 | 21211.9785 | 20954.126 | 20146.5319 | 19385.3513 | 18740.7201 | 18014.6074 | 17794.9171 | 17160.5999 | 15967.2585 | 14595.4832 | 21211.9785
2015-08-01 | 13412.4559 | 12519.2548 | 11796.2364 | 11472.3736 | 11293.9397 | 11620.8967 | 12292.3446 | 13124.6925 | 14541.8499 | 16327.2206 | 17899.0895 | 19258.4879 | 20275.4582 | 20987.1311 | 21577.0976 | 21892.7091 | 21847.327 | 21228.481 | 20309.4947 | 19408.0423 | 19034.6719 | 18265.24 | 16923.3756 | 15598.0137 | 21892.7091
2015-08-02 | 14330.4108 | 13283.5296 | 12548.1343 | 12036.5549 | 11750.8544 | 11725.0691 | 11893.1889 | 12264.4965 | 13851.8366 | 15776.4477 | 17447.3319 | 18711.8406 | 19683.4288 | 20230.0761 | 20717.9331 | 20696.2734 | 20529.185 | 20099.087 | 19328.6238 | 18541.6579 | 18238.4234 | 17628.8601 | 16467.4924 | 15288.5907 | 20717.9331
2015-08-03 | 14089.0609 | 13157.6976 | 12460.4644 | 11995.2985 | 11716.8178 | 11682.7813 | 11806.5505 | 11991.1729 | 13247.4303 | 14825.4876 | 16001.295 | 17247.2383 | 17842.3619 | 18018.733 | 18082.6805 | 18240.4862 | 18371.4753 | 18208.5125 | 17777.3831 | 17354.505 | 16980.1031 | 16275.6501 | 15074.0574 | 13740.4443 | 18371.4753
2015-08-04 | 12477.9984 | 11627.0851 | 11073.218 | 10745.2296 | 10722.5386 | 11162.9506 | 12010.7697 | 12638.8984 | 13842.5539 | 15345.3183 | 16816.109 | 18065.1465 | 18405.5118 | 18250.8003 | 17704.153 | 17147.1916 | 16593.3244 | 15975.5098 | 15581.5112 | 15282.4023 | 15483.5272 | 14994.6389 | 14047.8045 | 12972.0438 | 18405.5118
2015-08-05 | 11914.8485 | 11190.7987 | 10765.8578 | 10531.7277 | 10519.3508 | 10911.2866 | 11823.0531 | 12562.574 | 13886.9045 | 15539.2234 | 16931.6269 | 18225.015 | 19244.0481 | 19851.5486 | 19728.8108 | 19634.9525 | 19727.7794 | 19813.3865 | 19478.1782 | 18730.406 | 18389.0092 | 17512.3107 | 16085.8707 | 14660.462 | 19851.5486
2015-08-06 | 13226.8021 | 12284.0933 | 11604.3941 | 11175.3276 | 11093.8462 | 11405.332 | 12184.0466 | 12930.7874 | 14391.264 | 16156.0065 | 17729.9382 | 19375.0372 | 20497.2113 | 21430.6374 | 22006.1642 | 22052.5776 | 21559.5636 | 21020.1362 | 20285.7723 | 19552.4397 | 19218.2629 | 18408.606 | 16839.8314 | 15385.5433 | 22052.5776
2015-08-07 | 13943.6321 | 12941.1015 | 12270.685 | 11825.1159 | 11661.1217 | 11971.5761 | 12743.0708 | 13414.5187 | 14958.5395 | 16767.6327 | 18372.5067 | 19882.4909 | 21046.9529 | 21843.2014 | 22007.1956 | 21911.2745 | 21753.4687 | 21478.0822 | 20743.7183 | 19898.9935 | 19122.3418 | 18039.3612 | 16383.9482 | 14856.4299 | 22007.1956
2015-08-08 | 13477.4347 | 12430.5536 | 11800.362 | 11418.7403 | 11247.5263 | 11865.3409 | 12352.1664 | 13010.206 | 14069.4641 | 15620.7047 | 17043.0192 | 18554.0348 | 19901.0563 | 21006.7279 | 21572.972 | 21607.0085 | 21421.3547 | 20622.0119 | 19634.9525 | 18710.8092 | 18377.6637 | 17596.8863 | 16397.3565 | 15279.308 | 21607.0085
2015-08-09 | 13871.4334 | 12896.7509 | 12165.4812 | 11694.1268 | 11463.091 | 11463.091 | 11617.8025 | 12086.0626 | 13845.6481 | 15912.5938 | 17646.394 | 19142.97 | 20249.6729 | 20979.9112 | 21482.2079 | 21778.2226 | 21736.9662 | 21105.7432 | 20061.9563 | 19042.9232 | 18654.0816 | 17819.6709 | 16601.5757 | 15468.0561 | 21778.2226
2015-08-10 | 14223.1442 | 13273.2155 | 12495.5324 | 11995.2985 | 11692.064 | 11583.7659 | 11633.2736 | 11913.8171 | 13596.0469 | 15666.0868 | 17444.2377 | 19152.2526 | 20329.0915 | 21207.8528 | 21627.6367 | 21710.1495 | 21636.9194 | 21347.0932 | 20564.253 | 19554.5026 | 19086.2424 | 18091.9631 | 16634.5808 | 15131.8164 | 21710.1495
2015-08-11 | 13729.0988 | 12704.9086 | 11998.3928 | 11567.2634 | 11428.023 | 11803.4563 | 12579.0766 | 13154.6034 | 14488.2165 | 16340.6289 | 18047.6125 | 19737.0621 | 21008.7907 | 21811.2277 | 22015.4469 | 21958.7193 | 21988.6302 | 21794.7251 | 21209.9156 | 20305.3691 | 19940.2499 | 18776.8194 | 17343.1595 | 15677.4323 | 22015.4469
2015-08-12 | 14219.0185 | 13216.488 | 12415.0824 | 11923.0998 | 11761.1685 | 12074.7171 | 12849.306 | 13475.3719 | 14826.519 | 16573.7276 | 18136.3138 | 19544.1885 | 20552.9075 | 21328.5278 | 21611.1341 | 21589.4745 | 21757.5944 | 21645.1707 | 21251.172 | 20387.8819 | 19851.5486 | 18771.6624 | 17260.6467 | 15760.9765 | 21757.5944
2015-08-13 | 14281.9345 | 13350.5713 | 12625.49 | 12025.2094 | 11868.4351 | 12198.4863 | 13005.0489 | 13649.6802 | 15119.4395 | 16891.4019 | 18493.1816 | 20141.3749 | 21321.3079 | 22135.0904 | 22544.5602 | 22755.9993 | 22754.9678 | 22258.8596 | 21492.522 | 20493.0857 | 20075.3646 | 19098.6193 | 17565.944 | 16041.52 | 22755.9993
2015-08-14 | 14670.7761 | 13726.0045 | 13058.6823 | 12623.4272 | 12428.4907 | 12678.092 | 13454.7437 | 14041.616 | 15452.5849 | 17266.8351 | 18907.8085 | 20188.8197 | 21284.1772 | 21861.7668 | 21942.2168 | 21202.6958 | 20102.1813 | 19255.3937 | 18544.7521 | 17939.3145 | 17815.5453 | 16986.2916 | 15853.8034 | 14423.2377 | 21942.2168
2015-08-15 | 13184.5143 | 12340.8209 | 11684.8441 | 11383.6724 | 11304.2538 | 11707.5351 | 12597.642 | 13341.2886 | 14790.4197 | 16353.0059 | 17841.3305 | 18908.8399 | 19714.3711 | 19545.2199 | 18119.8112 | 17205.9819 | 16593.3244 | 16169.4149 | 15638.2387 | 15128.7222 | 15197.8266 | 14662.5248 | 13907.5327 | 12939.0387 | 19714.3711
2015-08-16 | 11935.4767 | 11268.1545 | 10813.3026 | 10509.0367 | 10353.2938 | 10410.0213 | 10695.7219 | 11161.9192 | 12783.2958 | 15040.0209 | 16897.5903 | 18245.6432 | 19495.7122 | 19716.4339 | 20334.2485 | 19867.0198 | 19018.1693 | 18133.2196 | 17290.5576 | 16570.6334 | 16371.5712 | 15789.856 | 14926.5658 | 13750.7584 | 20334.2485
2015-08-17 | 12678.092 | 11880.812 | 11283.6256 | 10864.8731 | 10688.502 | 10696.7533 | 10887.5642 | 11251.6519 | 12785.3586 | 14935.8485 | 16866.648 | 18405.5118 | 19668.9891 | 20718.9645 | 20892.2414 | 20696.2734 | 20796.3202 | 20758.158 | 20299.1806 | 19543.157 | 19303.8699 | 18437.4855 | 16959.4749 | 15227.7375 | 20892.2414
2015-08-18 | 13921.9724 | 12884.374 | 12185.078 | 11764.2627 | 11672.4672 | 12253.151 | 13245.3675 | 13685.7795 | 14740.912 | 16569.602 | 18296.1823 | 19846.3916 | 20998.4766 | 21920.5571 | 22335.184 | 22671.4236 | 22725.057 | 22505.3666 | 22028.8552 | 21173.8163 | 20834.4824 | 19576.1622 | 17770.1632 | 16181.7918 | 22725.057
2015-08-19 | 14639.8338 | 13604.2982 | 12858.5887 | 12382.0773 | 12237.6799 | 12712.1285 | 13729.0988 | 14126.1916 | 15238.0516 | 16998.6685 | 18560.2233 | 20081.5531 | 21283.1457 | 22092.8026 | 22566.2198 | 23132.4639 | 23421.2587 | 23126.2755 | 22570.3455 | 21597.7258 | 21202.6958 | 20022.7627 | 18233.2663 | 16563.4135 | 23421.2587
2015-08-20 | 15049.3036 | 13999.3282 | 13269.0899 | 12719.3484 | 12540.9144 | 12958.6355 | 13921.9724 | 12833.8349 | 15344.2869 | 17116.2493 | 18661.3015 | 20271.3325 | 21295.5227 | 22278.4564 | 22676.5807 | 22754.9678 | 22724.0255 | 22417.6968 | 21753.4687 | 20930.4035 | 20559.0959 | 19520.466 | 17901.1523 | 16228.2052 | 22754.9678
2015-08-21 | 14916.2517 | 13879.6846 | 13145.3207 | 12672.9349 | 12481.0926 | 12925.6304 | 13945.6949 | 14399.5153 | 15530.9721 | 17150.2858 | 18778.8822 | 20327.0287 | 21419.2919 | 22358.9064 | 22883.8941 | 23415.0703 | 23433.6356 | 22656.9839 | 21838.0443 | 20706.5875 | 20447.7036 | 19300.7757 | 17765.0062 | 16099.279 | 23433.6356
2015-08-22 | 14586.2005 | 13601.2039 | 12889.531 | 12438.8048 | 12255.2138 | 12674.9977 | 13700.2193 | 14138.5685 | 15251.46 | 17026.5166 | 18590.1342 | 20070.2076 | 21227.4496 | 22052.5776 | 22357.875 | 23010.7575 | 23178.8774 | 22715.7743 | 21962.845 | 20829.3253 | 20213.5736 | 19015.0751 | 17622.6716 | 16218.9226 | 23178.8774
2015-08-23 | 14808.9851 | 13811.6116 | 13004.0175 | 12447.0561 | 12101.5338 | 12070.5915 | 12230.46 | 12572.8881 | 14160.2282 | 16353.0059 | 18181.6958 | 19780.3814 | 20979.9112 | 21782.3482 | 22141.2789 | 22431.1051 | 22596.1307 | 22365.0949 | 21630.7309 | 20545.6876 | 20025.8569 | 19061.4886 | 17871.2414 | 16455.1154 | 22596.1307
2015-08-24 | 15019.3927 | 13948.7891 | 13112.3156 | 12532.6631 | 12178.8895 | 12042.7434 | 12059.2459 | 12275.8421 | 13975.6058 | 16138.4726 | 17877.4299 | 19638.0468 | 21004.665 | 21970.0648 | 22548.6858 | 22849.8576 | 22880.7999 | 22711.6486 | 22030.918 | 21097.4919 | 20690.085 | 19451.3616 | 17854.7388 | 16273.5873 | 22880.7999
2015-08-25 | 15023.5183 | 13950.8519 | 13327.8803 | 12954.5098 | 12932.8502 | 13503.22 | 14560.4152 | 14974.0107 | 15742.4111 | 17275.0864 | 18750.0027 | 20008.323 | 20788.0689 | 21092.3349 | 21159.3765 | 21140.8112 | 21201.6644 | 20963.4086 | 20252.7671 | 19592.6647 | 19424.5449 | 18273.4913 | 16852.2083 | 15233.926 | 21201.6644
2015-08-26 | 14063.2756 | 13220.6136 | 12627.5529 | 12274.8106 | 12210.8632 | 12746.165 | 13825.0199 | 14216.9557 | 15070.9632 | 16644.8949 | 18014.6074 | 19252.2994 | 20114.5582 | 20875.7388 | 21385.2553 | 21792.6623 | 22001.0071 | 21822.5732 | 21210.947 | 20279.5838 | 19939.2185 | 18784.0393 | 17021.3595 | 15448.4593 | 22001.0071
2015-08-27 | 13924.0353 | 12903.9708 | 12160.3241 | 11710.6294 | 11543.5409 | 12009.7383 | 13065.9021 | 13424.8328 | 14414.9864 | 16138.4726 | 17621.6402 | 19028.4834 | 20144.4691 | 21043.8586 | 21731.8091 | 22220.6975 | 22507.4294 | 22328.9955 | 21728.7149 | 20732.3728 | 20406.4472 | 19241.9853 | 17552.5357 | 16015.7348 | 22507.4294
2015-08-28 | 14591.3575 | 13603.2667 | 12866.84 | 12373.826 | 12169.6068 | 12636.8356 | 13735.2872 | 14136.5057 | 15092.6228 | 16468.5238 | 17541.1902 | 18449.8624 | 19483.3353 | 20522.9966 | 21456.4226 | 22036.0751 | 22288.7705 | 21856.6097 | 20968.5657 | 20240.3902 | 19793.7897 | 18555.0662 | 17041.9877 | 15559.8516 | 22288.7705
2015-08-29 | 14110.7205 | 13180.3886 | 12545.0401 | 12105.6594 | 11988.0787 | 12466.6529 | 13571.293 | 14106.5948 | 15198.858 | 16982.166 | 18613.8566 | 19823.7006 | 20694.2106 | 21514.1816 | 22089.7084 | 22413.5711 | 22305.2731 | 21590.5059 | 20672.551 | 19753.5647 | 19401.8539 | 18324.0304 | 17058.4903 | 15866.1803 | 22413.5711
2015-08-30 | 14672.8389 | 13740.4443 | 13057.6508 | 12559.4798 | 12341.8523 | 12549.1657 | 12623.4272 | 12882.3111 | 14213.8615 | 16259.1475 | 17974.3824 | 19563.7852 | 20613.7606 | 21418.2605 | 22011.3212 | 22266.0795 | 22231.0116 | 21618.354 | 20534.3421 | 19598.8532 | 19250.2366 | 18222.9522 | 17065.7102 | 15943.5361 | 22266.0795
2015-08-31 | 14714.0953 | 13706.4077 | 12942.1329 | 12476.967 | 12146.9158 | 12002.5184 | 12090.1882 | 12330.5068 | 13893.093 | 16106.4989 | 17736.1267 | 19162.5667 | 20325.9973 | 21111.9317 | 21460.5483 | 21572.972 | 21337.8105 | 20876.7702 | 19898.9935 | 18971.7559 | 18695.338 | 17725.8126 | 16540.7225 | 15284.4651 | 21572.972
2015-09-01 | 14092.1551 | 13265.9957 | 12630.6471 | 12155.1671 | 11999.4242 | 12092.2511 | 12374.8574 | 12502.7523 | 13970.4487 | 16156.0065 | 17953.7542 | 19647.3295 | 20574.5671 | 21277.9887 | 21880.3322 | 22085.5827 | 21920.5571 | 21504.8989 | 20793.226 | 19911.3704 | 19638.0468 | 18488.0246 | 16936.7839 | 15487.6529 | 22085.5827
2015-09-02 | 14120.0032 | 13155.6348 | 12472.8414 | 12068.5286 | 11931.3511 | 12408.8939 | 13449.5867 | 13862.1507 | 14762.5716 | 16408.702 | 17855.7703 | 19323.4667 | 20355.9081 | 20986.0997 | 21660.6418 | 22049.4834 | 22130.9648 | 21776.1597 | 20980.9426 | 20094.9614 | 19571.0051 | 18129.0939 | 16432.4244 | 14768.7601 | 22130.9648
2015-09-03 | 13373.2623 | 12423.3337 | 11805.5191 | 11400.1749 | 11291.8769 | 11775.6082 | 12899.8451 | 13311.3777 | 14149.9141 | 15591.8253 | 16593.3244 | 17637.1113 | 18620.0451 | 19646.298 | 20379.6306 | 20624.0747 | 20771.5664 | 20427.0754 | 19812.3551 | 19007.8552 | 18760.3168 | 17659.8024 | 16158.0694 | 14524.3159 | 20771.5664
2015-09-04 | 13184.5143 | 12242.8369 | 11628.1166 | 11248.5577 | 11144.3853 | 11623.9909 | 12789.4842 | 13184.5143 | 13794.0776 | 15070.9632 | 16405.6078 | 17499.9338 | 18406.5432 | 19253.3308 | 19607.1045 | 19755.6275 | 19933.03 | 19664.8634 | 19178.0379 | 18730.406 | 18602.5111 | 17497.871 | 15977.5726 | 14531.5358 | 19933.03
2015-09-05 | 13211.3309 | 12314.0042 | 11742.6031 | 11384.7038 | 11327.9762 | 11827.1787 | 13044.2425 | 13469.1834 | 14363.4159 | 15995.1066 | 17553.5671 | 18934.6251 | 20089.8044 | 20957.2202 | 21446.1085 | 21476.0194 | 21003.6336 | 20050.6108 | 19038.7975 | 18348.7842 | 17943.4401 | 16919.25 | 15789.856 | 14674.9018 | 21476.0194
2015-09-06 | 13500.1257 | 12724.5054 | 12121.1305 | 11704.4409 | 11503.3159 | 11500.2217 | 11750.8544 | 12159.2927 | 13446.4924 | 15126.6593 | 16412.8276 | 17382.3531 | 17945.5029 | 17872.2728 | 17694.8703 | 17461.7716 | 17008.9826 | 16644.8949 | 16218.9226 | 15998.2008 | 16000.2636 | 15378.3234 | 14609.9229 | 13737.35 | 17945.5029
2015-09-07 | 12761.6362 | 11887.0005 | 11288.7827 | 10873.1244 | 10715.3187 | 10743.1668 | 10958.7315 | 11237.2122 | 12465.6215 | 14050.8987 | 15465.9932 | 16862.5224 | 17992.9478 | 18762.3797 | 19119.2475 | 18875.8348 | 18446.7682 | 17851.6446 | 16960.5064 | 16668.6173 | 16655.209 | 15793.9816 | 14575.8864 | 13284.561 | 19119.2475
2015-09-08 | 12221.1773 | 11497.1275 | 10933.9776 | 10594.6437 | 10572.9841 | 11179.4532 | 12339.7895 | 12769.8874 | 13467.1206 | 15100.8741 | 16738.7532 | 18159.0048 | 19273.959 | 20113.5268 | 20725.1529 | 20980.9426 | 20953.0945 | 20723.0901 | 19875.2711 | 19391.5398 | 19054.2687 | 17827.9222 | 16304.5296 | 14778.0428 | 20980.9426
2015-09-09 | 13446.4924 | 12484.1869 | 11876.6864 | 11488.8762 | 11329.0077 | 11794.1736 | 12923.5675 | 13327.8803 | 14030.2705 | 15498.9984 | 17018.2653 | 18365.2868 | 19485.3981 | 20452.8607 | 20891.2099 | 21353.2816 | 21240.8579 | 20750.9382 | 19950.564 | 19299.7443 | 18844.8925 | 17485.4941 | 15903.3111 | 14394.3582 | 21353.2816
2015-09-10 | 13152.5406 | 12332.5696 | 11780.7652 | 11387.798 | 11303.2224 | 11837.4928 | 12988.5464 | 13363.9796 | 14055.0243 | 15356.6638 | 16837.7686 | 18028.0157 | 19067.677 | 19957.7839 | 20471.4261 | 20708.6504 | 20615.8235 | 20189.8511 | 19478.1782 | 18939.7822 | 18615.9194 | 17276.1178 | 15763.0393 | 14228.3012 | 20708.6504
2015-09-11 | 12939.0387 | 12095.3453 | 11490.939 | 11110.3487 | 11023.7103 | 11530.1326 | 12700.783 | 13119.5354 | 13753.8526 | 15160.6959 | 16434.4872 | 17516.4364 | 18305.465 | 18863.4578 | 19054.2687 | 19113.0591 | 18755.1598 | 18046.5811 | 17394.73 | 17025.4852 | 16839.8314 | 15857.929 | 14741.9434 | 13396.9847 | 19113.0591
2015-09-12 | 12031.3979 | 11337.2589 | 10840.1193 | 10586.3924 | 10586.3924 | 11158.825 | 12431.585 | 12796.7041 | 13544.4764 | 14777.0113 | 15898.154 | 16832.6115 | 17745.4094 | 18604.5739 | 18817.0444 | 18735.563 | 18794.3534 | 18864.4893 | 18215.7324 | 17481.3684 | 17184.3223 | 16299.3725 | 15305.0933 | 14088.0295 | 18864.4893
2015-09-13 | 12755.4477 | 11865.3409 | 11234.1179 | 10723.57 | 10515.2251 | 10495.6284 | 10778.2347 | 11161.9192 | 12311.9414 | 13951.8833 | 15657.8355 | 17165.757 | 18308.5593 | 19010.9495 | 19292.5244 | 19260.5507 | 18860.3636 | 18287.9311 | 17316.3428 | 16818.1718 | 16504.6231 | 15515.5009 | 14333.505 | 13105.0957 | 19292.5244
2015-09-14 | 12110.8164 | 11301.1596 | 10717.3815 | 10322.3515 | 10087.19 | 10047.9964 | 10207.865 | 10429.6181 | 11823.0531 | 13670.3084 | 15377.292 | 16940.9096 | 18091.9631 | 18852.1123 | 19234.7655 | 19362.6603 | 19382.2571 | 18885.1175 | 17997.0734 | 17473.1171 | 17191.5422 | 16141.5668 | 14868.8068 | 13404.2046 | 19382.2571
2015-09-15 | 12288.219 | 11464.1224 | 10951.5116 | 10662.7168 | 10651.3713 | 11207.3013 | 12361.4491 | 12817.3323 | 13589.8584 | 15165.8529 | 17034.7679 | 18420.9829 | 19556.5654 | 20534.3421 | 21215.0727 | 21666.8303 | 21747.2803 | 21450.2342 | 20693.1792 | 20114.5582 | 19683.4288 | 18317.8419 | 16786.1981 | 14961.6337 | 21747.2803
2015-09-16 | 13530.0366 | 12624.4586 | 11922.0684 | 11474.4365 | 11348.6044 | 11801.3934 | 12939.0387 | 13346.4457 | 14075.6525 | 15522.7208 | 17087.3698 | 18501.4329 | 19561.7224 | 20342.4998 | 20204.2909 | 19777.2871 | 19426.6077 | 19015.0751 | 18547.8464 | 18363.224 | 17998.1048 | 16789.2923 | 15399.983 | 13934.3494 | 20342.4998
2015-09-17 | 12570.8253 | 11726.1005 | 11127.8827 | 10750.3866 | 10719.4443 | 11289.8141 | 12521.3176 | 12933.8816 | 13551.6962 | 14704.8126 | 16146.7239 | 17232.7986 | 18012.5446 | 18425.1086 | 18876.8662 | 18850.0495 | 18209.5439 | 17468.9915 | 16956.3807 | 17043.0192 | 16896.5589 | 15963.1329 | 14619.2056 | 13147.3835 | 18876.8662
2015-09-18 | 12011.8011 | 11153.6679 | 10700.879 | 10388.3617 | 10361.5451 | 10924.6949 | 12169.6068 | 12588.3593 | 13229.8963 | 14473.7768 | 15658.8669 | 16873.8679 | 18022.8587 | 19063.5514 | 19793.7897 | 20202.228 | 20065.0505 | 20126.9351 | 19243.0167 | 18715.9662 | 18247.7061 | 17038.8935 | 15562.9458 | 14007.5795 | 20202.228
2015-09-19 | 12724.5054 | 11800.362 | 11237.2122 | 10875.1872 | 10809.177 | 11330.0391 | 12548.1343 | 13058.6823 | 13702.2821 | 15052.3978 | 16167.3521 | 16856.3339 | 17060.5531 | 16724.3135 | 16151.8809 | 15883.7143 | 15638.2387 | 15395.8574 | 15107.0626 | 15216.392 | 15091.5914 | 14451.0858 | 13532.0995 | 12504.8151 | 17060.5531
2015-09-20 | 11465.1538 | 10754.5123 | 10283.1579 | 10022.2112 | 9889.1593 | 10021.1797 | 10421.3668 | 10939.1347 | 11906.5973 | 13372.2309 | 14665.6191 | 15680.5265 | 16426.236 | 16913.0615 | 16968.7576 | 16214.7969 | 15584.6054 | 15268.9939 | 14770.8229 | 14880.1523 | 14770.8229 | 14017.8936 | 13100.9701 | 12126.2876 | 16968.7576
2015-09-21 | 11198.0186 | 10427.5553 | 9922.1644 | 9594.176 | 9452.8728 | 9488.9722 | 9750.9503 | 10049.0278 | 11187.7045 | 12927.6932 | 14509.8762 | 15968.2899 | 17132.7518 | 17943.4401 | 18488.0246 | 18693.2752 | 18664.3957 | 18281.7426 | 17420.5152 | 17022.391 | 16584.0417 | 15410.2971 | 14143.7256 | 12702.8458 | 18693.2752
2015-09-22 | 11542.5095 | 10740.0725 | 10207.865 | 9986.1118 | 10040.7765 | 10719.4443 | 11935.4767 | 12486.2497 | 13193.797 | 14461.3999 | 15726.94 | 16835.7057 | 17664.9594 | 17837.2049 | 17619.5774 | 17342.1281 | 17184.3223 | 16874.8993 | 16682.0257 | 16798.575 | 16402.5135 | 15305.0933 | 13953.9462 | 12575.9824 | 17837.2049
2015-09-23 | 11411.5205 | 10612.1777 | 10075.8445 | 9796.3324 | 9826.2433 | 10543.0732 | 11908.6601 | 12494.501 | 12788.4528 | 13629.052 | 14233.4583 | 14951.3196 | 15470.1189 | 15581.5112 | 15638.2387 | 15764.0707 | 15934.2534 | 16209.6399 | 16029.1431 | 16268.4302 | 16059.054 | 15066.8376 | 13827.0827 | 12431.585 | 16268.4302
2015-09-24 | 11251.6519 | 10478.0944 | 10095.4413 | 9795.301 | 9764.3587 | 10464.6861 | 11802.4249 | 12376.9202 | 12838.9919 | 13689.9052 | 14500.5935 | 15303.0305 | 15839.3637 | 16491.2148 | 17226.6101 | 17805.2312 | 17858.8645 | 17624.7344 | 17213.2018 | 17205.9819 | 16971.8519 | 16002.3265 | 14598.5774 | 13273.2155 | 17858.8645
2015-09-25 | 12127.319 | 11287.7513 | 10740.0725 | 10395.5816 | 10374.9534 | 10838.0565 | 11855.0268 | 12487.2811 | 13238.1476 | 14577.9492 | 15887.8399 | 16747.0045 | 17205.9819 | 17611.3261 | 18150.7535 | 18590.1342 | 18274.5227 | 17427.7351 | 16849.1141 | 16757.3186 | 16439.6443 | 15430.9253 | 14155.0711 | 12941.1015 | 18590.1342
2015-09-26 | 11825.1159 | 11075.2808 | 10586.3924 | 10295.5348 | 10289.3464 | 10914.3808 | 12161.3555 | 12765.7618 | 13262.9014 | 14200.4531 | 15399.983 | 16747.0045 | 17757.7863 | 18746.9085 | 19089.3366 | 19121.3103 | 18773.7252 | 18096.0888 | 17390.6043 | 17281.2749 | 16871.8051 | 16004.3893 | 14869.8382 | 14504.7191 | 19121.3103
2015-09-27 | 13154.6034 | 11908.6601 | 11405.332 | 11042.2757 | 10900.9725 | 10962.8571 | 11277.4372 | 11668.3415 | 12925.6304 | 14746.069 | 16274.6187 | 17693.8389 | 18802.6047 | 19553.4711 | 20075.3646 | 20101.1499 | 19446.2045 | 18755.1598 | 17819.6709 | 17584.5094 | 17028.5794 | 16169.4149 | 15054.4606 | 13808.5173 | 20101.1499
2015-09-28 | 12700.783 | 11895.2518 | 11302.191 | 10890.6584 | 10699.8475 | 10725.6328 | 10939.1347 | 11304.2538 | 12444.9933 | 14250.9922 | 15871.3374 | 17335.9396 | 18561.2547 | 19425.5763 | 19963.9723 | 20130.0293 | 19901.0563 | 19232.7026 | 18220.8894 | 18200.2612 | 17804.1998 | 16702.6539 | 15284.4651 | 13786.8577 | 20130.0293
2015-09-29 | 12656.4323 | 11748.7915 | 11223.8038 | 10890.6584 | 10891.6898 | 11450.714 | 12653.3381 | 13164.9175 | 13803.3603 | 15255.5856 | 16795.4808 | 18293.0881 | 19206.9174 | 19969.1294 | 20349.7197 | 20346.6255 | 20087.7415 | 19387.4141 | 18604.5739 | 18282.774 | 17316.3428 | 16143.6296 | 14679.0274 | 13267.0271 | 20349.7197
2015-09-30 | 12040.6806 | 11231.0237 | 10728.727 | 10428.5867 | 10425.4925 | 11028.8673 | 12396.517 | 12855.4945 | 13603.2667 | 15026.6126 | 16421.0789 | 17601.012 | 18539.5951 | 18850.0495 | 19132.6559 | 18689.1496 | 18628.2964 | 18493.1816 | 17984.6965 | 18046.5811 | 17644.3312 | 16586.1045 | 15159.6645 | 13668.2456 | 19132.6559
2015-10-01 | 12464.5901 | 11612.6454 | 11124.7885 | 10826.711 | 10777.2033 | 11403.2692 | 12731.7253 | 13187.6085 | 13954.9776 | 15375.2292 | 16683.0571 | 17956.8484 | 18969.6931 | 19715.4025 | 20035.1396 | 20579.7241 | 20899.4612 | 20576.6299 | 19798.9467 | 19410.1052 | 18882.0232 | 17650.5197 | 16006.4521 | 15155.5388 | 20899.4612
2015-10-02 | 13396.9847 | 12283.0619 | 11685.8755 | 11305.2852 | 11207.3013 | 11721.9749 | 12938.0073 | 13367.0739 | 14158.1653 | 15684.6522 | 17217.3275 | 18476.6791 | 19497.775 | 20537.4363 | 21098.5234 | 21492.522 | 21722.5264 | 21333.6848 | 20443.578 | 19989.7576 | 19395.6654 | 18035.2356 | 16514.9372 | 14841.9902 | 21722.5264
2015-10-03 | 13510.4398 | 12588.3593 | 11876.6864 | 11467.2166 | 11307.348 | 11767.3569 | 12938.0073 | 13444.4296 | 14324.2223 | 15942.5047 | 17516.4364 | 18949.0649 | 19916.5275 | 20960.3144 | 21488.3963 | 21772.0341 | 21758.6258 | 20874.7074 | 19599.8846 | 18894.4001 | 17967.1625 | 16834.6743 | 15552.6317 | 14266.4634 | 21772.0341
2015-10-04 | 13054.5566 | 12097.4081 | 11486.8134 | 11060.841 | 10853.5276 | 10925.7263 | 11246.4949 | 11648.7448 | 12991.6406 | 14750.1947 | 16085.8707 | 17250.3326 | 18232.2349 | 18819.1072 | 19033.6405 | 18905.7457 | 18458.1137 | 17783.5716 | 16906.873 | 16755.2558 | 16259.1475 | 15314.376 | 14157.1339 | 12949.3528 | 19033.6405
2015-10-05 | 11703.4095 | 10666.8424 | 9889.1593 | 9278.5645 | 8941.2935 | 8851.5608 | 9005.2409 | 9152.7325 | 9921.133 | 11061.8725 | 12176.8267 | 12963.7925 | 13810.5802 | 14557.321 | 15178.2298 | 15632.0503 | 16071.4309 | 15899.1854 | 15225.6747 | 15169.9786 | 14788.3569 | 13757.9782 | 12509.9721 | 11182.5474 | 16071.4309
2015-10-06 | 10115.0381 | 9359.0145 | 8897.9742 | 8658.6871 | 8715.4147 | 9435.3389 | 10684.3764 | 11226.8981 | 11756.0114 | 12731.7253 | 13718.7847 | 14594.4518 | 15508.2811 | 16179.729 | 16853.2397 | 17062.6159 | 17293.6518 | 16969.789 | 16640.7693 | 16983.1974 | 16452.0212 | 15326.7529 | 14065.3384 | 12660.558 | 17293.6518
2015-10-07 | 11422.866 | 10680.2508 | 10199.6137 | 9891.2221 | 9822.1176 | 10398.6758 | 11709.5979 | 12304.7215 | 12574.951 | 13542.4136 | 14582.0749 | 15313.3446 | 15909.4995 | 16408.702 | 16658.3032 | 16544.8481 | 16530.4084 | 16332.3777 | 16180.7604 | 16571.6648 | 16127.1271 | 15332.9413 | 13950.8519 | 12390.3286 | 16658.3032
2015-10-08 | 11236.1808 | 10487.3771 | 9951.0439 | 9683.9087 | 9714.851 | 10373.922 | 11699.2838 | 12204.6748 | 12723.474 | 13913.7212 | 15243.2087 | 16349.9116 | 17378.2274 | 18168.2875 | 18810.8559 | 19100.6821 | 19075.9283 | 18766.5053 | 18203.3554 | 18208.5125 | 17683.5248 | 16526.2827 | 15104.9997 | 13670.3084 | 19100.6821
2015-10-09 | 12359.3863 | 11528.0698 | 10949.4488 | 10523.4764 | 10456.4348 | 10336.7912 | 12151.0414 | 12633.7413 | 13247.4303 | 14674.9018 | 16031.2059 | 17228.673 | 18123.9369 | 18982.07 | 19566.8795 | 19953.6582 | 20021.7313 | 19650.4237 | 18816.013 | 18632.422 | 18012.5446 | 16799.6064 | 15438.1452 | 13852.868 | 20021.7313
2015-10-10 | 12507.9093 | 11538.3839 | 10957.7 | 10539.979 | 10464.6861 | 10974.2026 | 12181.9837 | 12723.474 | 13389.7649 | 14832.7075 | 16249.8649 | 17344.1909 | 18307.5278 | 19103.7764 | 19644.2352 | 20009.3544 | 20081.5531 | 19573.0679 | 18535.4695 | 18169.3189 | 17475.18 | 16424.1731 | 15244.2401 | 13983.857 | 20081.5531
2015-10-11 | 12746.165 | 11840.587 | 11261.966 | 10827.7424 | 10584.3296 | 10596.7065 | 10884.4699 | 11184.6102 | 12408.8939 | 14329.3794 | 15915.688 | 17246.2069 | 18269.3657 | 19043.9546 | 19569.9737 | 19904.1506 | 19968.098 | 19530.7801 | 18424.0772 | 17925.9061 | 17226.6101 | 16159.1008 | 15097.7799 | 13830.1769 | 19968.098
2015-10-12 | 12679.1234 | 11746.7287 | 11040.2128 | 10596.7065 | 10383.2047 | 10342.9797 | 10549.2617 | 10705.0046 | 12038.6177 | 14089.0609 | 15744.4739 | 17127.5948 | 18293.0881 | 19044.986 | 19543.157 | 19811.3237 | 19841.2345 | 19454.4558 | 18525.1554 | 18444.7054 | 17775.3203 | 16617.0468 | 15409.2657 | 14009.6423 | 19841.2345
2015-10-13 | 12835.8977 | 11992.2043 | 11459.9967 | 11144.3853 | 11151.6051 | 11727.1319 | 12862.7144 | 13336.1316 | 13963.2288 | 15290.6535 | 16776.9154 | 17955.817 | 18777.8508 | 19438.9846 | 19885.5852 | 20177.4742 | 20138.2806 | 19723.6538 | 18928.4367 | 18892.3373 | 18193.0413 | 17052.3018 | 15669.181 | 14182.9192 | 20177.4742
2015-10-14 | 12929.756 | 12135.5703 | 11647.7133 | 11318.6936 | 11240.3064 | 11834.3986 | 13120.5669 | 13612.5494 | 14239.6467 | 15609.3592 | 16924.407 | 18020.7959 | 18788.1649 | 19608.1359 | 20050.6108 | 20170.2543 | 19931.9986 | 19315.2154 | 18761.3483 | 18899.5572 | 18120.8426 | 16909.9673 | 15463.9304 | 13918.8782 | 20170.2543
2015-10-15 | 12498.6266 | 11580.6717 | 11035.0558 | 10693.6591 | 10700.879 | 11270.2173 | 12516.1606 | 13081.3733 | 13654.8372 | 14853.3357 | 15974.4784 | 17034.7679 | 15936.3162 | 18366.3182 | 18527.2182 | 18643.7675 | 18362.1926 | 17912.4978 | 17364.8191 | 17496.8396 | 16768.6641 | 15661.9611 | 14195.2961 | 12750.2907 | 18643.7675
2015-10-16 | 11472.3736 | 10622.4918 | 10096.4727 | 9737.542 | 9577.6734 | 10019.1169 | 11112.4115 | 11491.9704 | 11871.5293 | 12799.7983 | 13676.4969 | 14357.2275 | 15060.6491 | 15774.3848 | 16412.8276 | 17044.0506 | 17400.9184 | 17220.4217 | 16497.4033 | 16429.3302 | 15743.4425 | 14544.9441 | 13119.5354 | 11607.4884 | 17400.9184
2015-10-17 | 10295.5348 | 9400.2709 | 8895.9114 | 8600.9282 | 8527.698 | 9054.7486 | 10180.0169 | 10679.2193 | 11178.4218 | 12106.6908 | 12965.8554 | 13741.4757 | 14383.0127 | 15120.4709 | 15833.1752 | 16472.6494 | 16781.041 | 16500.4975 | 15613.4849 | 15308.1875 | 14520.1903 | 13429.9899 | 12389.2972 | 11198.0186 | 16781.041
2015-10-18 | 10188.2682 | 9286.8158 | 8723.6659 | 8402.8974 | 8257.4686 | 8388.4577 | 8788.6448 | 9203.2716 | 10243.9643 | 11597.1743 | 12722.4426 | 13646.586 | 14558.3524 | 15351.5067 | 16068.3367 | 16617.0468 | 16817.1404 | 16504.6231 | 15609.3592 | 15365.9465 | 14615.08 | 13571.293 | 12587.3279 | 11412.5519 | 16817.1404
2015-10-19 | 10373.922 | 9560.1395 | 8970.1729 | 8614.3365 | 8465.8134 | 8472.0019 | 8742.2313 | 9003.1781 | 10096.4727 | 11559.0121 | 12829.7092 | 13902.3757 | 15001.8587 | 15839.3637 | 16510.8116 | 16908.9359 | 17045.082 | 16737.7218 | 16051.8341 | 16109.5931 | 15457.742 | 14289.1544 | 13076.2162 | 11758.0742 | 17045.082
2015-10-20 | 10599.8008 | 9759.2016 | 9261.0306 | 9001.1152 | 9016.5864 | 9603.4587 | 10759.6693 | 11353.7615 | 12019.021 | 13310.3463 | 14558.3524 | 15607.2964 | 16490.1834 | 17177.1025 | 17795.9485 | 17976.4452 | 17851.6446 | 17428.7665 | 17011.0454 | 17161.6313 | 16403.5449 | 15219.4862 | 13867.3077 | 12456.3388 | 17976.4452
2015-10-21 | 11214.5211 | 10462.6232 | 10026.3368 | 9751.9817 | 9772.6099 | 10382.1733 | 11672.4672 | 12318.1299 | 12564.6369 | 13367.0739 | 14256.1493 | 14792.4825 | 15156.5702 | 15332.9413 | 15375.2292 | 15412.3599 | 15333.9728 | 15181.3241 | 15176.167 | 15618.6419 | 15057.5549 | 14160.2282 | 12931.8188 | 11503.3159 | 15618.6419
2015-10-22 | 10426.5239 | 9697.317 | 9274.4389 | 9066.0941 | 9115.6018 | 9681.8459 | 11096.9404 | 11778.7024 | 12061.3088 | 12805.9868 | 13744.5699 | 14672.8389 | 15353.5695 | 15935.2848 | 16359.1943 | 16599.5129 | 16459.2411 | 16107.5303 | 15943.5361 | 16215.8283 | 15627.9246 | 14632.6139 | 13309.3149 | 11895.2518 | 16599.5129
2015-10-23 | 10725.6328 | 10045.9336 | 9589.0189 | 9312.6011 | 9281.6588 | 9871.6253 | 11227.9295 | 11899.3774 | 12061.3088 | 12696.6573 | 13423.8014 | 14027.1763 | 14527.4101 | 14846.1158 | 15140.0677 | 15275.1824 | 15196.7952 | 14978.1363 | 14814.1421 | 15110.1568 | 14838.8959 | 13971.4801 | 12792.5785 | 11532.1954 | 15275.1824
2015-10-24 | 10460.5604 | 9735.4792 | 9314.6639 | 9129.0101 | 9187.8005 | 9744.7619 | 10902.0039 | 11614.7082 | 12044.8062 | 12862.7144 | 13538.2879 | 14016.8622 | 14254.0865 | 14508.8447 | 14703.7812 | 14879.1209 | 14860.5556 | 14627.4569 | 14429.4262 | 14538.7556 | 13992.1083 | 13283.5296 | 12465.6215 | 11348.6044 | 14879.1209
2015-10-25 | 10177.9541 | 9334.2607 | 8778.3307 | 8428.6827 | 8303.8821 | 8398.7718 | 8781.4249 | 9257.9363 | 10186.2054 | 11445.557 | 12479.0298 | 13237.1162 | 13886.9045 | 14485.1223 | 14930.6914 | 15252.4914 | 15259.7112 | 14872.9325 | 14168.4794 | 14072.5583 | 13427.927 | 12641.9926 | 11790.0479 | 10705.0046 | 15259.7112
2015-10-26 | 9727.2279 | 9002.1466 | 8558.6403 | 8248.1859 | 8120.2911 | 8146.0763 | 8401.866 | 8794.8332 | 9663.2805 | 10959.7629 | 12075.7485 | 12902.9393 | 13602.2353 | 14282.9659 | 14827.5504 | 15242.1773 | 15426.7997 | 15160.6959 | 14545.9755 | 14734.7235 | 14071.5269 | 12991.6406 | 11733.3204 | 10356.388 | 15426.7997
2015-10-27 | 9221.837 | 8496.7557 | 8074.909 | 7884.0982 | 7951.1398 | 8595.7711 | 9865.4368 | 10580.204 | 10950.4802 | 11887.0005 | 12823.5208 | 13662.0571 | 14353.1018 | 15081.2773 | 15706.3118 | 16275.6501 | 16569.602 | 16348.8802 | 15892.997 | 16085.8707 | 15286.5279 | 14052.9615 | 12658.4952 | 11154.6994 | 16569.602
2015-10-28 | 9972.7035 | 9201.2088 | 8711.289 | 8461.6878 | 8475.0961 | 9122.8216 | 10428.5867 | 11076.3122 | 11479.5935 | 12559.4798 | 13552.7277 | 14497.4992 | 15268.9939 | 16212.7341 | 16890.3705 | 17375.1332 | 17607.2004 | 17334.9082 | 16760.4128 | 16916.1557 | 16087.9335 | 14968.8536 | 13547.5706 | 12076.7799 | 17607.2004
2015-10-29 | 10889.627 | 10059.3419 | 9504.4433 | 9197.0831 | 9196.0517 | 9768.4843 | 11118.6 | 11686.9069 | 12058.2145 | 13336.1316 | 14378.8871 | 15343.2554 | 16246.7706 | 17000.7313 | 17594.8235 | 18104.3401 | 18204.3868 | 17738.1895 | 17001.7628 | 17003.8256 | 16226.1424 | 15084.3715 | 13663.0885 | 12140.7273 | 18204.3868
2015-10-30 | 10767.9206 | 9923.1958 | 9354.8889 | 9034.1204 | 8995.9582 | 9562.2023 | 10842.1821 | 11465.1538 | 11831.3043 | 12980.2951 | 14188.0762 | 15168.9472 | 15995.1066 | 16660.366 | 17044.0506 | 17339.0338 | 17541.1902 | 17153.38 | 16625.2981 | 16733.5962 | 15969.3213 | 14957.5081 | 13631.1148 | 12198.4863 | 17541.1902
2015-10-31 | 10891.6898 | 10025.3054 | 9419.8677 | 9110.4447 | 9044.4345 | 9602.4273 | 10886.5328 | 11537.3525 | 11943.728 | 13057.6508 | 14073.5897 | 14985.3562 | 15653.7099 | 16116.813 | 16459.2411 | 16716.0622 | 16771.7583 | 16237.4879 | 15266.9311 | 14734.7235 | 13726.0045 | 12851.3688 | 11802.4249 | 10627.6488 | 16771.7583
2015-11-01 | 9451.8414 | 8648.373 | 8185.2699 | 7927.4174 | 7832.5277 | 7939.7943 | 8391.5519 | 8851.5608 | 9774.6728 | 10889.627 | 11697.221 | 12066.4658 | 12206.7376 | 12202.6119 | 12244.8997 | 12272.7478 | 12184.0466 | 11853.9954 | 11622.9595 | 11954.0421 | 11432.1487 | 10775.1405 | 9979.9233 | 9148.6069 | 12272.7478
2015-11-02 | 16295.2469 | 7645.8425 | 7556.1098 | 7548.8899 | 7668.5335 | 8023.3385 | 8645.2788 | 9784.9869 | 10776.1719 | 11174.2961 | 11229.9923 | 11121.6942 | 11021.6475 | 10863.8417 | 10792.6744 | 10716.3501 | 10746.261 | 11191.8301 | 12068.5286 | 11820.9902 | 11383.6724 | 10636.9315 | 9682.8773 | 8824.7441 | 16295.2469
2015-11-03 | 8111.0084 | 7885.1296 | 7758.2662 | 7806.7424 | 8083.1603 | 9020.712 | 10553.3873 | 11157.7936 | 11313.5365 | 11511.5672 | 11749.8229 | 11928.2569 | 11948.8851 | 11980.8588 | 11913.8171 | 11810.6761 | 11902.4716 | 12300.5959 | 13136.038 | 12861.6829 | 12325.3497 | 11405.332 | 10315.1316 | 9254.8421 | 13136.038
2015-11-04 | 8508.1012 | 8028.4956 | 7759.2976 | 7706.6957 | 7835.6219 | 8583.3942 | 9796.3324 | 10652.4027 | 11322.8192 | 11838.5242 | 12335.6638 | 12767.8246 | 12973.0752 | 13158.729 | 13257.7444 | 13337.163 | 13210.2995 | 13417.6129 | 14219.0185 | 13970.4487 | 13388.7335 | 12340.8209 | 11279.5 | 10195.488 | 14219.0185
2015-11-05 | 9305.3812 | 8691.6922 | 8372.9865 | 8218.275 | 8321.416 | 9010.3979 | 10237.7759 | 10650.3399 | 11682.7813 | 12669.8407 | 13414.5187 | 13989.0141 | 14367.5416 | 14553.1954 | 14623.3313 | 14485.1223 | 14253.0551 | 14433.5518 | 15127.6908 | 14781.137 | 14187.0448 | 13250.5245 | 12011.8011 | 10746.261 | 15127.6908
2015-11-06 | 9731.3535 | 9049.5915 | 8608.148 | 8374.0179 | 8410.1173 | 9105.2877 | 10284.1893 | 11143.3538 | 12025.2094 | 13001.9547 | 13954.9776 | 14741.9434 | 15343.2554 | 15786.7618 | 15998.2008 | 15982.7297 | 15624.8304 | 15282.4023 | 15647.5214 | 15098.8113 | 14214.8929 | 13058.6823 | 11726.1005 | 10469.8431 | 15998.2008
2015-11-07 | 9399.2395 | 8700.9749 | 8261.5943 | 8090.3802 | 8131.6366 | 8749.4512 | 9994.3631 | 10779.2661 | 11627.0851 | 12567.7311 | 13401.1104 | 14138.5685 | 14726.4723 | 15201.9523 | 15405.14 | 15361.8208 | 14945.1312 | 14606.8287 | 14831.6761 | 14102.4692 | 13340.2572 | 12436.742 | 11502.2845 | 10510.0681 | 15405.14
2015-11-08 | 9551.8882 | 8849.498 | 8363.7038 | 8152.2648 | 8108.9456 | 8291.5051 | 8732.9486 | 9593.1446 | 11091.7833 | 12286.1562 | 13100.9701 | 13743.5385 | 14283.9974 | 14508.8447 | 14475.8396 | 14232.4269 | 13883.8103 | 13997.2654 | 14246.8666 | 13613.5808 | 12960.6983 | 12188.1722 | 11358.9185 | 10390.4245 | 14508.8447
2015-11-09 | 9553.951 | 8846.4037 | 8429.7141 | 8211.0552 | 8121.3225 | 8247.1545 | 8555.5461 | 9201.2088 | 10429.6181 | 11376.4525 | 11904.5344 | 12213.9574 | 12252.1196 | 12098.4395 | 11938.571 | 11685.8755 | 11628.1166 | 12203.6433 | 12706.9714 | 12339.7895 | 11797.2678 | 11007.2077 | 10165.5772 | 9160.9838 | 12706.9714
2015-11-10 | 8353.3897 | 7903.695 | 7663.3764 | 7562.2983 | 7687.0989 | 8235.809 | 9558.0766 | 10596.7065 | 11061.8725 | 11626.0537 | 12057.1831 | 12435.7106 | 12711.0971 | 12952.447 | 13071.0592 | 13165.9489 | 13058.6823 | 13228.8649 | 13859.0564 | 13400.079 | 12681.1862 | 11695.1582 | 10649.3084 | 9540.5427 | 13859.0564
2015-11-11 | 8544.2006 | 7960.4225 | 7643.7797 | 7526.1989 | 7609.7431 | 8079.0347 | 9007.3037 | 9953.1067 | 10780.2975 | 11512.5986 | 12059.2459 | 12451.1818 | 12813.2067 | 13147.3835 | 13303.1264 | 13446.4924 | 13321.6918 | 13388.7335 | 13996.234 | 13570.2616 | 12850.3374 | 11869.4665 | 10764.8264 | 9556.0138 | 13996.234
2015-11-12 | 8528.7294 | 7930.5116 | 7655.1252 | 7538.5758 | 7680.9104 | 8343.0756 | 9685.9715 | 10449.2149 | 10977.2968 | 11649.7762 | 12334.6324 | 12943.1643 | 13476.4033 | 14020.9878 | 14386.1069 | 14517.096 | 14320.0967 | 14186.0134 | 14684.1844 | 14191.1705 | 13443.3982 | 12457.3702 | 11278.4686 | 10043.8708 | 14684.1844
2015-11-13 | 9034.1204 | 8428.6827 | 8058.4065 | 7943.92 | 8035.7155 | 8678.2839 | 9977.8605 | 10776.1719 | 11483.7192 | 12367.6375 | 13151.5092 | 13728.0674 | 14287.0916 | 14778.0428 | 14996.7017 | 15026.6126 | 14754.3203 | 14604.7659 | 15030.7382 | 14529.4729 | 13756.9468 | 12717.2855 | 11455.8711 | 10240.8701 | 15030.7382
2015-11-14 | 9206.3658 | 8518.4153 | 8137.8251 | 7938.7629 | 7986.2078 | 8568.9544 | 9866.4682 | 10698.8161 | 11418.7403 | 12185.078 | 12851.3688 | 13289.7181 | 13700.2193 | 13998.2968 | 14172.6051 | 14170.5423 | 13866.2763 | 13768.2923 | 14092.1551 | 13506.3142 | 12821.458 | 11971.5761 | 11119.6314 | 10151.1374 | 14172.6051
2015-11-15 | 9272.3761 | 8629.8076 | 8265.7199 | 8067.6892 | 8050.1552 | 8257.4686 | 8759.7653 | 9545.6997 | 10758.6379 | 11767.3569 | 12420.2395 | 12917.3791 | 13246.3989 | 13534.1623 | 13640.3975 | 13580.5757 | 13319.629 | 13267.0271 | 13641.4289 | 13062.8079 | 12435.7106 | 11748.7915 | 11019.5846 | 10209.9278 | 13641.4289
2015-11-16 | 9371.3914 | 8810.3044 | 8444.1538 | 8239.9346 | 8179.0815 | 8345.1385 | 8646.3102 | 9303.3184 | 10797.8315 | 12143.8216 | 13108.1899 | 13809.5487 | 14394.3582 | 14760.5088 | 14915.2203 | 14905.9376 | 14615.08 | 14560.4152 | 15008.0472 | 14518.1274 | 13770.3552 | 12882.3111 | 11932.3825 | 10845.2764 | 15008.0472
2015-11-17 | 9935.5727 | 9380.6741 | 9064.0312 | 8925.8223 | 9105.2877 | 9829.3375 | 11154.6994 | 11932.3825 | 12835.8977 | 14042.6474 | 15182.3555 | 16042.5514 | 16655.209 | 16991.4487 | 17035.7993 | 16891.4019 | 16586.1045 | 16595.3872 | 16903.7788 | 16263.2732 | 15308.1875 | 14061.2128 | 12788.4528 | 11395.0179 | 17035.7993
2015-11-18 | 10296.5662 | 9584.8933 | 9092.9107 | 8839.1839 | 8901.0685 | 9467.3126 | 10858.6847 | 11649.7762 | 12288.219 | 13002.9861 | 13480.529 | 13570.2616 | 13341.2886 | 13091.6874 | 12755.4477 | 12419.208 | 12434.6792 | 13105.0957 | 13778.6064 | 13569.2302 | 13057.6508 | 12264.4965 | 11208.3327 | 10204.7707 | 13778.6064
2015-11-19 | 9488.9722 | 9167.1723 | 9036.1832 | 9054.7486 | 9361.0773 | 10274.9066 | 12052.0261 | 12823.5208 | 13133.9752 | 13284.561 | 13203.0797 | 12889.531 | 12508.9407 | 12225.303 | 12002.5184 | 11918.9742 | 12059.2459 | 12861.6829 | 13661.0257 | 13533.1309 | 13138.1008 | 12362.4805 | 11356.8557 | 10320.2887 | 13661.0257
2015-11-20 | 9570.4536 | 9193.9889 | 9101.162 | 9140.3556 | 9461.1241 | 10363.6079 | 11953.0107 | 12590.4221 | 12444.9933 | 12442.9305 | 12389.2972 | 12323.2869 | 12219.1145 | 12112.8793 | 11939.6024 | 11855.0268 | 11893.1889 | 12635.8041 | 13440.304 | 13319.629 | 12877.1541 | 12118.0363 | 11135.1026 | 10096.4727 | 13440.304
2015-11-21 | 9283.7216 | 8778.3307 | 8602.991 | 8497.7871 | 8646.3102 | 9601.3959 | 10922.6321 | 11679.6871 | 11943.728 | 12198.4863 | 12411.9882 | 12460.4644 | 12287.1876 | 12165.4812 | 12016.9581 | 11881.8434 | 11961.262 | 12555.3542 | 12925.6304 | 12594.5477 | 12151.0414 | 11535.2897 | 10814.3341 | 9978.8919 | 12925.6304
2015-11-22 | 9163.0466 | 8635.9961 | 8342.0442 | 8237.8718 | 8276.034 | 8514.2897 | 9062.9998 | 9799.4266 | 11031.9616 | 12099.4709 | 12711.0971 | 13040.1169 | 13057.6508 | 13037.0226 | 12933.8816 | 12757.5105 | 12725.5368 | 13228.8649 | 13615.6437 | 13355.7283 | 12975.138 | 12407.8625 | 11760.137 | 10870.0302 | 13615.6437
2015-11-23 | 10013.9599 | 9455.9671 | 9018.6492 | 8769.048 | 8722.6345 | 8872.189 | 9185.7376 | 9901.5362 | 11535.2897 | 13141.1951 | 14182.9192 | 14854.3671 | 15278.2766 | 15585.6368 | 15641.3329 | 15537.1605 | 15141.0991 | 15299.9362 | 15793.9816 | 15461.8676 | 14874.9953 | 14004.4852 | 13035.9912 | 12066.4658 | 15793.9816
2015-11-24 | 10835.9937 | 10086.1586 | 9661.2177 | 9497.2235 | 9628.2125 | 10287.2835 | 11490.939 | 12330.5068 | 13418.6444 | 14618.1742 | 15700.1233 | 16815.0775 | 17669.085 | 18101.2458 | 18304.4336 | 18228.1093 | 17746.4408 | 17569.0383 | 17924.8747 | 17321.4999 | 16522.1571 | 15320.5644 | 14223.1442 | 12843.1176 | 18304.4336
2015-11-25 | 11638.4307 | 10805.0514 | 10336.7912 | 10153.2002 | 10198.5823 | 10846.3078 | 12041.712 | 12848.2746 | 13918.8782 | 15034.8639 | 16004.3893 | 16645.9263 | 17008.9826 | 17270.9608 | 17238.9871 | 17062.6159 | 16680.9942 | 16805.7949 | 17153.38 | 16691.3083 | 15928.0649 | 15022.4869 | 13924.0353 | 12833.8349 | 17270.9608
2015-11-26 | 11763.2313 | 11034.0244 | 10556.4815 | 10306.8803 | 10308.9431 | 10682.3136 | 11486.8134 | 12250.0568 | 13157.6976 | 13798.2032 | 13841.5225 | 13691.968 | 13458.8693 | 13093.7502 | 12653.3381 | 12222.2087 | 11988.0787 | 12468.7157 | 12996.7977 | 12693.5631 | 12191.2664 | 11666.2787 | 10968.0141 | 10078.9387 | 13841.5225
2015-11-27 | 9262.062 | 8720.5717 | 8445.1852 | 8375.0494 | 8448.2795 | 8780.3935 | 9403.3651 | 10312.0374 | 11352.7301 | 12033.4607 | 12436.742 | 12594.5477 | 12584.2336 | 12368.669 | 12122.162 | 11736.4146 | 11229.9923 | 11020.6161 | 11171.2019 | 10773.0777 | 10499.754 | 10253.247 | 9864.4054 | 9298.1613 | 12594.5477
2015-11-28 | 8756.6711 | 8433.8397 | 8303.8821 | 8348.2327 | 8581.3314 | 9070.2197 | 9849.9657 | 10670.9681 | 11448.6512 | 11887.0005 | 11945.7908 | 11750.8544 | 11509.5044 | 11290.8455 | 11087.6577 | 10955.6372 | 10965.9513 | 11637.3992 | 12401.6741 | 12185.078 | 11850.9011 | 11645.6505 | 10953.5744 | 10167.64 | 12401.6741
2015-11-29 | 9460.0927 | 9076.4082 | 8872.189 | 8846.4037 | 8967.0787 | 9219.7742 | 9771.5785 | 10471.9059 | 11216.584 | 11556.9493 | 11600.2685 | 11572.4204 | 11472.3736 | 11360.9814 | 11224.8352 | 11089.7205 | 10970.077 | 11435.2429 | 12034.4921 | 11765.2941 | 11346.5416 | 10868.9988 | 10224.3675 | 9438.4331 | 12034.4921
2015-11-30 | 8660.7499 | 8155.359 | 7900.6007 | 7803.6482 | 7851.0931 | 8053.2494 | 8442.091 | 9056.8114 | 10096.4727 | 10886.5328 | 11374.3897 | 11693.0954 | 11925.1626 | 12043.7748 | 12067.4972 | 11988.0787 | 11871.5293 | 12336.6952 | 13154.6034 | 12870.9656 | 12397.5484 | 11676.5928 | 10805.0514 | 9701.4426 | 13154.6034
2015-12-01 | 8843.3095 | 8282.2225 | 8002.7103 | 7914.0091 | 8064.5949 | 8799.9903 | 10154.2316 | 10902.0039 | 11540.4467 | 12240.7741 | 12972.0438 | 13539.3193 | 13802.3289 | 13901.3442 | 13777.575 | 13552.7277 | 13342.32 | 13821.9257 | 14602.7031 | 14362.3845 | 13797.1718 | 12883.3426 | 11797.2678 | 10529.6649 | 14602.7031
2015-12-02 | 9451.8414 | 8778.3307 | 8349.2641 | 8180.1129 | 8296.6622 | 8965.0159 | 10359.4822 | 11073.218 | 11584.7973 | 12320.1927 | 13022.5829 | 13450.6181 | 13697.1251 | 13850.8051 | 13798.2032 | 13618.7379 | 13374.2937 | 13898.25 | 14661.4934 | 14385.0755 | 13827.0827 | 12952.447 | 11815.8332 | 10541.0104 | 14661.4934
2015-12-03 | 9437.4017 | 8718.5089 | 8334.8244 | 8152.2648 | 8230.652 | 8907.2569 | 10423.4297 | 11074.2494 | 11706.5037 | 12598.6734 | 13278.3726 | 13827.0827 | 14237.5839 | 14429.4262 | 14577.9492 | 14647.0537 | 14308.7512 | 14467.5883 | 15139.0363 | 14780.1056 | 14136.5057 | 13189.6713 | 12030.3665 | 10679.2193 | 15139.0363
2015-12-04 | 9559.1081 | 8871.1576 | 8475.0961 | 8304.9135 | 8403.9288 | 9100.1306 | 10458.4976 | 11201.1128 | 11813.7704 | 12683.249 | 13374.2937 | 13948.7891 | 14392.2954 | 14588.2633 | 14718.221 | 14766.6972 | 14401.5781 | 14575.8864 | 15283.4337 | 14982.2619 | 14389.2012 | 13517.6597 | 12311.9414 | 10996.8936 | 15283.4337
2015-12-05 | 9859.2484 | 9077.4396 | 8652.4987 | 8478.1904 | 8546.2634 | 9218.7428 | 10581.2354 | 11330.0391 | 12071.6229 | 13099.9387 | 13861.1192 | 14371.6672 | 14651.1793 | 14625.3941 | 14597.546 | 14699.6556 | 14562.4781 | 14742.9748 | 15126.6593 | 14657.3678 | 14047.8045 | 13283.5296 | 12400.6427 | 11299.0968 | 15126.6593
2015-12-06 | 10200.6451 | 9422.9619 | 8935.105 | 8629.8076 | 8506.0384 | 8643.216 | 9074.3454 | 9761.2644 | 11173.2647 | 12547.1029 | 13548.602 | 14206.6416 | 14649.1165 | 14921.4087 | 15043.1151 | 14945.1312 | 14500.5935 | 14309.7826 | 14611.9857 | 13911.6583 | 13227.8335 | 12511.0035 | 11609.5512 | 10545.136 | 15043.1151
2015-12-07 | 9447.7158 | 8757.7025 | 8302.8507 | 8006.836 | 7924.3232 | 8040.8725 | 8344.1071 | 8895.9114 | 10203.7393 | 11497.1275 | 12321.2241 | 12854.4631 | 13132.9438 | 13285.5925 | 13330.9745 | 13132.9438 | 12861.6829 | 13180.3886 | 13995.2026 | 13460.9322 | 12885.4054 | 12048.9318 | 10958.7315 | 9754.0446 | 13995.2026
2015-12-08 | 8726.7602 | 8101.7257 | 7788.1771 | 7678.8476 | 7804.6796 | 8498.8186 | 9837.5888 | 10576.0783 | 11061.8725 | 11630.1794 | 12121.1305 | 12440.8677 | 12648.1811 | 12815.2695 | 12892.6252 | 12985.4521 | 12949.3528 | 13401.1104 | 14272.6518 | 14026.1449 | 13338.1944 | 12372.7946 | 11226.8981 | 9878.8452 | 14272.6518
2015-12-09 | 8796.8961 | 8220.3379 | 7929.4802 | 7847.9988 | 7981.0507 | 8746.357 | 10319.2572 | 11048.4641 | 11420.8031 | 11721.9749 | 11900.4088 | 11938.571 | 11923.0998 | 11855.0268 | 11746.7287 | 11587.8916 | 11666.2787 | 12485.2183 | 13529.0052 | 13415.5501 | 12974.1066 | 12230.46 | 11157.7936 | 10031.4938 | 13529.0052
2015-12-10 | 9162.0152 | 8781.4249 | 8602.991 | 8708.1948 | 9008.3351 | 10140.8233 | 12049.9633 | 13103.0329 | 13008.1432 | 12684.2804 | 12428.4907 | 12115.9735 | 11848.8383 | 11665.2473 | 11439.3685 | 11352.7301 | 11475.4679 | 12434.6792 | 13723.9417 | 13722.9103 | 13538.2879 | 12897.7823 | 11908.6601 | 10810.2084 | 13723.9417
2015-12-11 | 10084.0958 | 9739.6048 | 9659.1548 | 9685.9715 | 10043.8708 | 11157.7936 | 13141.1951 | 14058.1186 | 13670.3084 | 13274.2469 | 12782.2644 | 12453.2446 | 12126.2876 | 11878.7492 | 11645.6505 | 11547.6666 | 11677.6242 | 12584.2336 | 13657.9315 | 13574.3873 | 13315.5033 | 12667.7779 | 11586.8602 | 10502.8482 | 14058.1186
2015-12-12 | 9710.7253 | 9300.2241 | 9155.8267 | 9138.2928 | 9497.2235 | 10568.8585 | 12337.7267 | 13189.6713 | 13249.4931 | 13238.1476 | 13031.8656 | 12766.7932 | 12446.0247 | 12173.7325 | 11893.1889 | 11794.1736 | 11949.9165 | 12927.6932 | 13840.491 | 13673.4026 | 13470.2149 | 12971.0124 | 12234.5856 | 11343.4474 | 13840.491
2015-12-13 | 10530.6963 | 10175.8913 | 10007.7714 | 10028.3996 | 10221.2733 | 10742.1354 | 11542.5095 | 12491.4067 | 13050.431 | 13017.4259 | 12623.4272 | 12259.3395 | 11988.0787 | 11718.8806 | 11479.5935 | 11353.7615 | 11318.6936 | 11950.9479 | 12716.2541 | 12471.81 | 12209.8318 | 11822.0216 | 11234.1179 | 10583.2982 | 13050.431
2015-12-14 | 9914.9445 | 9496.192 | 9351.7946 | 9364.1716 | 9509.6004 | 9926.29 | 10684.3764 | 11622.9595 | 12474.9042 | 12570.8253 | 12229.4286 | 11969.5133 | 11767.3569 | 11600.2685 | 11487.8448 | 11387.798 | 11391.9237 | 12055.1203 | 13145.3207 | 13011.2374 | 12701.8144 | 12129.3818 | 11155.7308 | 10200.6451 | 13145.3207
2015-12-15 | 9480.7209 | 9115.6018 | 9087.7537 | 9166.1408 | 9589.0189 | 10666.8424 | 12585.2651 | 13569.2302 | 13486.7174 | 13005.0489 | 12650.2439 | 12366.6061 | 12299.5645 | 12192.2978 | 12063.3716 | 12043.7748 | 12074.7171 | 12793.6099 | 13905.4699 | 13794.0776 | 13361.9168 | 12572.8881 | 11487.8448 | 10340.9169 | 13905.4699
2015-12-16 | 9468.344 | 9053.7171 | 8902.0999 | 8956.7646 | 9258.9677 | 10270.781 | 12123.1934 | 12973.0752 | 12884.374 | 12550.1971 | 12328.444 | 12214.9889 | 12176.8267 | 12194.3607 | 12173.7325 | 12200.5491 | 12216.0203 | 12763.699 | 13759.0097 | 13576.4501 | 13041.1483 | 12134.5389 | 11054.6526 | 9866.4682 | 13759.0097
2015-12-17 | 8876.3146 | 8355.4526 | 8149.1706 | 8125.4481 | 8392.5833 | 9287.8472 | 10888.5956 | 11746.7287 | 11832.3357 | 11932.3825 | 12022.1152 | 12074.7171 | 12179.9209 | 12308.8472 | 12443.9619 | 12580.108 | 12513.0664 | 13004.0175 | 13870.4019 | 13597.0783 | 13016.3944 | 12242.8369 | 11142.3224 | 9898.442 | 13870.4019
2015-12-18 | 8923.7595 | 8388.4577 | 8168.7674 | 8157.4218 | 8407.0231 | 9248.6536 | 10870.0302 | 11761.1685 | 12070.5915 | 12253.151 | 12329.4754 | 12266.5594 | 12256.2453 | 12450.1503 | 12568.7625 | 12598.6734 | 12537.8202 | 12989.5778 | 13860.0878 | 13589.8584 | 13150.4777 | 12354.2292 | 11313.5365 | 10135.6663 | 13860.0878
2015-12-19 | 9191.9261 | 8678.2839 | 8428.6827 | 8389.4891 | 8613.3051 | 9426.0562 | 10891.6898 | 11839.5556 | 12166.5126 | 12352.1664 | 12515.1292 | 12579.0766 | 12571.8567 | 12630.6471 | 12629.6157 | 12605.8933 | 12487.2811 | 12840.0233 | 13580.5757 | 13192.7656 | 12665.715 | 12004.5812 | 11243.4006 | 10237.7759 | 13580.5757
2015-12-20 | 9332.1979 | 8728.823 | 8418.3686 | 8276.034 | 8261.5943 | 8566.8916 | 9151.7011 | 9928.3528 | 10940.1661 | 11713.7236 | 12139.6959 | 12216.0203 | 12522.349 | 12558.4484 | 12594.5477 | 12604.8618 | 12489.3439 | 12801.8612 | 13460.9322 | 12972.0438 | 12428.4907 | 11808.6133 | 11032.993 | 10074.8131 | 13460.9322
2015-12-21 | 9104.2562 | 8421.4628 | 8002.7103 | 7808.8053 | 7781.9886 | 7923.2918 | 8294.5994 | 8914.4768 | 10128.4464 | 11330.0391 | 12062.3402 | 12441.8991 | 12833.8349 | 12950.3842 | 12862.7144 | 12699.7516 | 12566.6997 | 13074.1534 | 13854.9308 | 13540.3507 | 13096.8444 | 12443.9619 | 11532.1954 | 10359.4822 | 13854.9308
2015-12-22 | 9287.8472 | 8577.2057 | 8150.202 | 7938.7629 | 8002.7103 | 8513.2583 | 9405.428 | 10294.5034 | 11475.4679 | 12602.799 | 13534.1623 | 14123.0974 | 14518.1274 | 14810.0165 | 15013.2042 | 14912.1261 | 14561.4467 | 14766.6972 | 15542.3176 | 15122.5337 | 14494.405 | 13738.3815 | 12711.0971 | 11313.5365 | 15542.3176
2015-12-23 | 10100.5983 | 9249.6851 | 8707.1634 | 8434.8711 | 8472.0019 | 8978.4242 | 9841.7144 | 10714.2873 | 11965.3876 | 13227.8335 | 14158.1653 | 14816.2049 | 15290.6535 | 15478.3702 | 15056.5235 | 14602.7031 | 14199.4217 | 14357.2275 | 15078.1831 | 14669.7447 | 14081.841 | 13629.052 | 12964.8239 | 12101.5338 | 15478.3702
2015-12-24 | 11048.4641 | 10232.6188 | 9701.4426 | 9467.3126 | 9413.6792 | 9731.3535 | 10323.3829 | 11073.218 | 12495.5324 | 14079.7782 | 15300.9676 | 16114.7501 | 16536.5968 | 16609.827 | 16664.4917 | 16466.461 | 16251.9277 | 16446.8642 | 16628.3923 | 15687.7464 | 14802.7966 | 14055.0243 | 13326.8489 | 12285.1247 | 16664.4917
2015-12-25 | 11224.8352 | 10404.8643 | 9671.5318 | 9107.3505 | 8719.5403 | 8650.4358 | 8811.3358 | 9258.9677 | 10319.2572 | 11399.1435 | 12076.7799 | 12417.1452 | 12535.7574 | 12450.1503 | 12267.5908 | 11882.8748 | 11472.3736 | 11648.7448 | 12135.5703 | 11882.8748 | 11677.6242 | 11355.8243 | 10769.9834 | 9936.6041 | 12535.7574
2015-12-26 | 9071.2511 | 8468.9077 | 8193.5212 | 8048.0924 | 8116.1654 | 8484.3788 | 9113.5389 | 9843.7772 | 10760.7007 | 11613.6768 | 12267.5908 | 12536.7888 | 12529.5689 | 12371.7632 | 12274.8106 | 12205.7062 | 12266.5594 | 12961.7297 | 13701.2507 | 13435.1469 | 12938.0073 | 12322.2555 | 11578.6089 | 10581.2354 | 13701.2507
2015-12-27 | 9574.5792 | 8843.3095 | 8361.641 | 8140.9193 | 8141.9507 | 8304.9135 | 8732.9486 | 9209.4601 | 10325.4457 | 11661.1217 | 12693.5631 | 13357.7912 | 13770.3552 | 13904.4385 | 13909.5955 | 13691.968 | 13426.8956 | 13733.2244 | 14417.0493 | 13986.9513 | 13367.0739 | 12700.783 | 11824.0845 | 10715.3187 | 14417.0493
2015-12-28 | 9667.4061 | 8887.6601 | 8393.6147 | 8111.0084 | 7971.768 | 8035.7155 | 8353.3897 | 8766.9852 | 10148.0432 | 11641.5249 | 12734.8195 | 13549.6334 | 14114.8461 | 14509.8762 | 14718.221 | 14711.0011 | 14485.1223 | 14419.1121 | 15060.6491 | 14560.4152 | 13873.4962 | 13083.4361 | 12069.56 | 10799.8943 | 15060.6491
2015-12-29 | 9711.7567 | 8965.0159 | 8514.2897 | 8316.259 | 8337.9186 | 8732.9486 | 9553.951 | 10326.4771 | 11577.5775 | 12989.5778 | 14107.6262 | 14830.6447 | 15207.1093 | 15375.2292 | 15498.9984 | 15561.9144 | 15314.376 | 15244.2401 | 15954.8816 | 15415.4541 | 14683.153 | 13689.9052 | 12603.8304 | 11247.5263 | 15954.8816
2015-12-30 | 10019.1169 | 9214.6171 | 8725.7288 | 8459.625 | 8433.8397 | 8829.9012 | 9595.2074 | 10344.0111 | 11433.1801 | 12644.0554 | 13727.0359 | 14606.8287 | 15154.5074 | 15538.1919 | 15642.3644 | 15514.4695 | 15214.3292 | 15211.235 | 15912.5938 | 15380.3862 | 14720.2838 | 13775.5122 | 12757.5105 | 11507.4416 | 15912.5938
2015-12-31 | 10345.0425 | 9508.569 | 8998.021 | 8722.6345 | 8698.9121 | 9045.4659 | 9754.0446 | 10551.3245 | 11600.2685 | 12673.9663 | 13527.9738 | 14023.0506 | 14140.6314 | 14216.9557 | 14193.2333 | 14044.7102 | 14086.998 | 14819.2992 | 15447.4279 | 14707.9069 | 13821.9257 | 12852.4003 | 11864.3095 | 11051.5584 | 15447.4279
Max | 16295.2469 | 14458.3057 | 13671.3398 | 13187.6085 | 13318.5976 | 14662.5248 | 16939.8782 | 18040.3926 | 17415.3582 | 17443.2062 | 18954.2219 | 20327.0287 | 21419.2919 | 22358.9064 | 22883.8941 | 23415.0703 | 23433.6356 | 23217.0395 | 22771.4704 | 21889.6148 | 21347.0932 | 20460.0806 | 18824.2643 | 17089.4326 | 6320171.1755
Note on C79: Jessica Shrader: Blank due to DST beginning. No HR-2 occurred.
Note on R243: Del Portal, Carlos: Shouldn't this be the summer peak?
Note on B317: Hour 1 and Hour 2 of Nov 3 added together to account for DST. Hour 1: 10,320 & Hour 2: 9,399

## Hourly Loads p.u of Peak
OPC 012913
FPL RC-16
Hourly Loads p.u. of Peak
(hourly load/peak)
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | Max
2015-01-01 | 0.44147 | 0.4254 | 0.40339 | 0.38836 | 0.38182 | 0.38502 | 0.39504 | 0.4033 | 0.43989 | 0.49768 | 0.55178 | 0.58882 | 0.61074 | 0.61936 | 0.61679 | 0.60889 | 0.60073 | 0.60772 | 0.63723 | 0.61968 | 0.5931 | 0.56351 | 0.52416 | 0.47463 | 0.63723
2015-01-02 | 0.42825 | 0.39851 | 0.37853 | 0.36896 | 0.36626 | 0.37736 | 0.41981 | 0.45428 | 0.50549 | 0.56572 | 0.61417 | 0.64738 | 0.67111 | 0.68762 | 0.69502 | 0.69128 | 0.67734 | 0.67142 | 0.69637 | 0.66985 | 0.63416 | 0.59437 | 0.54979 | 0.49759 | 0.69637
2015-01-03 | 0.44756 | 0.41178 | 0.38958 | 0.3788 | 0.3779 | 0.39039 | 0.42707 | 0.46154 | 0.50174 | 0.53585 | 0.55534 | 0.56166 | 0.5617 | 0.55651 | 0.55128 | 0.54803 | 0.54636 | 0.57248 | 0.61183 | 0.60113 | 0.57921 | 0.55268 | 0.51672 | 0.47517 | 0.61183
2015-01-04 | 0.43804 | 0.41318 | 0.39829 | 0.39184 | 0.39265 | 0.40239 | 0.42319 | 0.45062 | 0.4929 | 0.53026 | 0.55209 | 0.55687 | 0.55236 | 0.54514 | 0.53589 | 0.52728 | 0.52908 | 0.55575 | 0.57907 | 0.56333 | 0.54325 | 0.51862 | 0.48771 | 0.45121 | 0.57907
2015-01-05 | 0.4139 | 0.38715 | 0.37027 | 0.36057 | 0.35859 | 0.36698 | 0.38683 | 0.40975 | 0.45432 | 0.49773 | 0.54478 | 0.57384 | 0.58891 | 0.59364 | 0.59324 | 0.58769 | 0.58002 | 0.58647 | 0.62238 | 0.60411 | 0.57853 | 0.53982 | 0.49452 | 0.44589 | 0.62238
2015-01-06 | 0.39707 | 0.37018 | 0.35417 | 0.34844 | 0.35299 | 0.37939 | 0.43398 | 0.46845 | 0.49971 | 0.54171 | 0.58498 | 0.61241 | 0.63398 | 0.64548 | 0.64192 | 0.62825 | 0.6153 | 0.6347 | 0.66718 | 0.64851 | 0.60686 | 0.55561 | 0.51252 | 0.46493 | 0.66718
2015-01-07 | 0.42852 | 0.40835 | 0.40321 | 0.40731 | 0.42653 | 0.46998 | 0.55114 | 0.60871 | 0.63416 | 0.64923 | 0.64327 | 0.62653 | 0.61047 | 0.59455 | 0.582 | 0.58119 | 0.59834 | 0.65315 | 0.71519 | 0.71943 | 0.70382 | 0.66353 | 0.61318 | 0.56342 | 0.71943
2015-01-08 | 0.52516 | 0.50513 | 0.49795 | 0.49475 | 0.50242 | 0.5368 | 0.60113 | 0.63222 | 0.62911 | 0.62911 | 0.62523 | 0.60943 | 0.58782 | 0.56734 | 0.5497 | 0.54275 | 0.54785 | 0.57821 | 0.61359 | 0.6024 | 0.57636 | 0.53418 | 0.48523 | 0.43357 | 0.63222
2015-01-09 | 0.39157 | 0.36987 | 0.35962 | 0.35588 | 0.36328 | 0.39396 | 0.45644 | 0.49741 | 0.51027 | 0.53337 | 0.5492 | 0.55778 | 0.55854 | 0.55444 | 0.5492 | 0.54735 | 0.55065 | 0.57668 | 0.61584 | 0.60844 | 0.58453 | 0.54654 | 0.50102 | 0.44855 | 0.61584
2015-01-10 | 0.40208 | 0.37271 | 0.35583 | 0.34947 | 0.35326 | 0.37957 | 0.43885 | 0.47846 | 0.50842 | 0.54465 | 0.57334 | 0.59161 | 0.60176 | 0.60939 | 0.60966 | 0.60799 | 0.60564 | 0.60925 | 0.64133 | 0.62342 | 0.59495 | 0.5594 | 0.52245 | 0.48018 | 0.64133
2015-01-11 | 0.43077 | 0.39982 | 0.37889 | 0.36874 | 0.36662 | 0.37654 | 0.39879 | 0.42694 | 0.48992 | 0.55692 | 0.60339 | 0.63226 | 0.65369 | 0.66669 | 0.67197 | 0.66908 | 0.65469 | 0.64296 | 0.66213 | 0.63736 | 0.60515 | 0.56703 | 0.5275 | 0.4832 | 0.67197
2015-01-12 | 0.43551 | 0.40172 | 0.3806 | 0.36833 | 0.3622 | 0.36594 | 0.38078 | 0.40045 | 0.4485 | 0.49786 | 0.53287 | 0.5529 | 0.57054 | 0.58169 | 0.5848 | 0.58115 | 0.57262 | 0.56666 | 0.59987 | 0.58823 | 0.56157 | 0.52421 | 0.48175 | 0.4324 | 0.59987
2015-01-13 | 0.39157 | 0.36892 | 0.35836 | 0.35728 | 0.36707 | 0.40397 | 0.47336 | 0.51487 | 0.53129 | 0.55322 | 0.57257 | 0.58701 | 0.60019 | 0.61034 | 0.61683 | 0.62148 | 0.61877 | 0.62423 | 0.66294 | 0.65437 | 0.62044 | 0.57339 | 0.52186 | 0.46366 | 0.66294
2015-01-14 | 0.41322 | 0.3825 | 0.36612 | 0.35773 | 0.36107 | 0.38994 | 0.45247 | 0.4897 | 0.51952 | 0.56021 | 0.59405 | 0.61372 | 0.62378 | 0.62428 | 0.61999 | 0.60844 | 0.60528 | 0.61936 | 0.65654 | 0.64679 | 0.61652 | 0.57312 | 0.51916 | 0.46091 | 0.65654
2015-01-15 | 0.41092 | 0.38299 | 0.36729 | 0.36197 | 0.36562 | 0.39766 | 0.46429 | 0.50305 | 0.51677 | 0.53495 | 0.54438 | 0.54505 | 0.53756 | 0.53016 | 0.52191 | 0.51798 | 0.52209 | 0.55105 | 0.58891 | 0.58038 | 0.55751 | 0.52177 | 0.47616 | 0.42586 | 0.58891
2015-01-16 | 0.38845 | 0.36851 | 0.3626 | 0.36481 | 0.37776 | 0.42116 | 0.50197 | 0.55421 | 0.5631 | 0.5663 | 0.56621 | 0.55773 | 0.54474 | 0.53098 | 0.51898 | 0.51307 | 0.51911 | 0.55575 | 0.63362 | 0.6486 | 0.64517 | 0.62428 | 0.59058 | 0.55304 | 0.6486
2015-01-17 | 0.52651 | 0.51604 | 0.51758 | 0.52651 | 0.54641 | 0.59685 | 0.68604 | 0.73996 | 0.73229 | 0.69407 | 0.65198 | 0.6088 | 0.57294 | 0.54393 | 0.52362 | 0.51243 | 0.51446 | 0.54614 | 0.59707 | 0.59337 | 0.58137 | 0.55764 | 0.53026 | 0.49709 | 0.73996
2015-01-18 | 0.46524 | 0.45108 | 0.44688 | 0.44868 | 0.45852 | 0.48099 | 0.51898 | 0.56748 | 0.6001 | 0.6037 | 0.59238 | 0.56915 | 0.54469 | 0.52272 | 0.50323 | 0.49263 | 0.49276 | 0.52078 | 0.5825 | 0.59333 | 0.59328 | 0.58841 | 0.57551 | 0.55705 | 0.6037
2015-01-19 | 0.54384 | 0.53932 | 0.5428 | 0.55313 | 0.56973 | 0.59658 | 0.63817 | 0.68834 | 0.71699 | 0.69466 | 0.64589 | 0.59834 | 0.56035 | 0.53238 | 0.50986 | 0.49173 | 0.48631 | 0.50197 | 0.5562 | 0.55277 | 0.53964 | 0.51302 | 0.48591 | 0.44774 | 0.71699
2015-01-20 | 0.41981 | 0.40659 | 0.40357 | 0.4074 | 0.42342 | 0.45523 | 0.50743 | 0.5566 | 0.57447 | 0.56644 | 0.55552 | 0.54501 | 0.5326 | 0.52304 | 0.51573 | 0.51167 | 0.51239 | 0.52967 | 0.5783 | 0.57442 | 0.54893 | 0.51158 | 0.46556 | 0.4162 | 0.5783
2015-01-21 | 0.37902 | 0.35953 | 0.3515 | 0.35146 | 0.36057 | 0.39734 | 0.46845 | 0.51004 | 0.51902 | 0.52177 | 0.52457 | 0.52448 | 0.5234 | 0.51857 | 0.51433 | 0.51 | 0.51167 | 0.53427 | 0.57876 | 0.57713 | 0.55313 | 0.51474 | 0.46926 | 0.42274 | 0.57876
2015-01-22 | 0.38602 | 0.37221 | 0.36996 | 0.37699 | 0.39793 | 0.44954 | 0.54131 | 0.5987 | 0.59017 | 0.60073 | 0.59328 | 0.57835 | 0.5613 | 0.54144 | 0.52746 | 0.51988 | 0.52507 | 0.56008 | 0.63732 | 0.65848 | 0.65784 | 0.63759 | 0.60592 | 0.56806 | 0.65848
2015-01-23 | 0.54532 | 0.53982 | 0.54564 | 0.55859 | 0.58259 | 0.64138 | 0.74099 | 0.78913 | 0.76179 | 0.71618 | 0.67278 | 0.62468 | 0.58449 | 0.55096 | 0.52845 | 0.5169 | 0.51785 | 0.54501 | 0.60993 | 0.62175 | 0.61192 | 0.5843 | 0.54099 | 0.49782 | 0.78913
2015-01-24 | 0.46623 | 0.45509 | 0.45437 | 0.4605 | 0.47864 | 0.5285 | 0.61602 | 0.66186 | 0.66141 | 0.64661 | 0.62762 | 0.60005 | 0.57555 | 0.55448 | 0.53716 | 0.52714 | 0.52976 | 0.55354 | 0.60655 | 0.60781 | 0.5941 | 0.57095 | 0.54185 | 0.50558 | 0.66186
2015-01-25 | 0.47535 | 0.4601 | 0.45396 | 0.45572 | 0.46398 | 0.48315 | 0.51677 | 0.5589 | 0.59825 | 0.59599 | 0.5733 | 0.54848 | 0.52863 | 0.51293 | 0.50084 | 0.49168 | 0.48767 | 0.49958 | 0.54014 | 0.53594 | 0.51771 | 0.49538 | 0.46488 | 0.43005 | 0.59825
2015-01-26 | 0.40005 | 0.38024 | 0.37176 | 0.36815 | 0.3709 | 0.38372 | 0.40803 | 0.44147 | 0.4883 | 0.51234 | 0.52313 | 0.522 | 0.52137 | 0.52078 | 0.51731 | 0.51361 | 0.51289 | 0.52583 | 0.5668 | 0.56545 | 0.54027 | 0.50454 | 0.46294 | 0.41435 | 0.5668
2015-01-27 | 0.37429 | 0.35051 | 0.34009 | 0.33729 | 0.34672 | 0.38006 | 0.44941 | 0.48798 | 0.504 | 0.52272 | 0.54397 | 0.55791 | 0.56928 | 0.57862 | 0.58291 | 0.58832 | 0.59076 | 0.59522 | 0.63087 | 0.62676 | 0.59391 | 0.54492 | 0.49046 | 0.431 | 0.63087
2015-01-28 | 0.38105 | 0.35362 | 0.34022 | 0.3349 | 0.34149 | 0.37352 | 0.43898 | 0.48013 | 0.4984 | 0.52299 | 0.5483 | 0.56612 | 0.58264 | 0.59635 | 0.60641 | 0.61404 | 0.61665 | 0.61787 | 0.64846 | 0.64305 | 0.61318 | 0.56346 | 0.51162 | 0.45405 | 0.64846
2015-01-29 | 0.40366 | 0.37523 | 0.36138 | 0.35642 | 0.36319 | 0.39698 | 0.46285 | 0.50684 | 0.52579 | 0.5516 | 0.57068 | 0.58647 | 0.51392 | 0.58381 | 0.57763 | 0.58011 | 0.58922 | 0.61309 | 0.64309 | 0.63569 | 0.61516 | 0.57663 | 0.5294 | 0.47539 | 0.64309
2015-01-30 | 0.43565 | 0.41178 | 0.39982 | 0.39721 | 0.40646 | 0.44232 | 0.51586 | 0.56039 | 0.58255 | 0.60352 | 0.61503 | 0.61354 | 0.60695 | 0.59919 | 0.59053 | 0.58552 | 0.58891 | 0.60907 | 0.64467 | 0.63912 | 0.61377 | 0.57668 | 0.52498 | 0.47138 | 0.64467
2015-01-31 | 0.43131 | 0.40808 | 0.39856 | 0.3945 | 0.40077 | 0.4347 | 0.50364 | 0.54487 | 0.56134 | 0.58241 | 0.59775 | 0.60623 | 0.60799 | 0.60574 | 0.60154 | 0.60398 | 0.6005 | 0.60605 | 0.63208 | 0.62202 | 0.5945 | 0.55949 | 0.51875 | 0.47151 | 0.63208
2015-02-01 | 0.42752 | 0.39766 | 0.37889 | 0.36901 | 0.3672 | 0.37591 | 0.39892 | 0.43222 | 0.49191 | 0.5479 | 0.58516 | 0.60555 | 0.62058 | 0.6296 | 0.63524 | 0.63723 | 0.63235 | 0.62035 | 0.63434 | 0.62184 | 0.58922 | 0.55241 | 0.51257 | 0.46687 | 0.63723
2015-02-02 | 0.42184 | 0.39143 | 0.37199 | 0.36107 | 0.35723 | 0.3608 | 0.37587 | 0.40208 | 0.46836 | 0.52922 | 0.56675 | 0.59044 | 0.61986 | 0.64061 | 0.65523 | 0.66195 | 0.66114 | 0.64814 | 0.64792 | 0.6176 | 0.58909 | 0.57167 | 0.54808 | 0.49051 | 0.66195
2015-02-03 | 0.4384 | 0.39509 | 0.37821 | 0.37104 | 0.37564 | 0.4056 | 0.46596 | 0.50282 | 0.53635 | 0.57894 | 0.62148 | 0.65094 | 0.67382 | 0.69155 | 0.70445 | 0.70968 | 0.7008 | 0.68875 | 0.70747 | 0.69827 | 0.65888 | 0.61345 | 0.55687 | 0.49565 | 0.70968
2015-02-04 | 0.44341 | 0.41259 | 0.39405 | 0.38502 | 0.38701 | 0.41345 | 0.47386 | 0.50955 | 0.54081 | 0.58584 | 0.62622 | 0.65586 | 0.679 | 0.69353 | 0.70328 | 0.70887 | 0.70368 | 0.68911 | 0.70815 | 0.70459 | 0.67016 | 0.6222 | 0.56892 | 0.5081 | 0.70887
2015-02-05 | 0.45667 | 0.42274 | 0.40447 | 0.39482 | 0.39648 | 0.42586 | 0.48924 | 0.52516 | 0.55674 | 0.60393 | 0.64508 | 0.67576 | 0.69498 | 0.70842 | 0.71668 | 0.71289 | 0.69782 | 0.68519 | 0.70247 | 0.69304 | 0.65852 | 0.61169 | 0.55493 | 0.49403 | 0.71668
2015-02-06 | 0.44228 | 0.40718 | 0.38881 | 0.37939 | 0.38209 | 0.40916 | 0.47192 | 0.50806 | 0.54086 | 0.57857 | 0.61137 | 0.63529 | 0.65469 | 0.67273 | 0.68027 | 0.68482 | 0.68049 | 0.67499 | 0.69425 | 0.68943 | 0.65554 | 0.60952 | 0.55394 | 0.49109 | 0.69425
2015-02-07 | 0.43804 | 0.4056 | 0.38336 | 0.37311 | 0.37469 | 0.40244 | 0.46452 | 0.5026 | 0.52678 | 0.55796 | 0.58746 | 0.61485 | 0.63105 | 0.63371 | 0.65455 | 0.66042 | 0.65875 | 0.65446 | 0.65658 | 0.6393 | 0.61404 | 0.57172 | 0.53229 | 0.48333 | 0.66042
2015-02-08 | 0.43849 | 0.40461 | 0.38439 | 0.3742 | 0.37343 | 0.38182 | 0.40506 | 0.43754 | 0.49782 | 0.55949 | 0.60551 | 0.63366 | 0.65243 | 0.66154 | 0.66732 | 0.66371 | 0.65563 | 0.64372 | 0.65121 | 0.63592 | 0.60411 | 0.56806 | 0.5285 | 0.48559 | 0.66732
2015-02-09 | 0.44038 | 0.40713 | 0.38696 | 0.37645 | 0.37411 | 0.38124 | 0.39802 | 0.42383 | 0.47102 | 0.5141 | 0.54257 | 0.55728 | 0.57086 | 0.57907 | 0.58268 | 0.57966 | 0.57244 | 0.57023 | 0.59644 | 0.60041 | 0.57095 | 0.53147 | 0.48906 | 0.4356 | 0.60041
2015-02-10 | 0.3913 | 0.36626 | 0.35588 | 0.35421 | 0.36265 | 0.39779 | 0.46691 | 0.50702 | 0.52421 | 0.54559 | 0.56924 | 0.58462 | 0.59888 | 0.60998 | 0.61458 | 0.61936 | 0.62022 | 0.61679 | 0.6412 | 0.64724 | 0.61521 | 0.56955 | 0.51555 | 0.45681 | 0.64724
2015-02-11 | 0.4097 | 0.38029 | 0.36603 | 0.36134 | 0.36743 | 0.40054 | 0.46962 | 0.50946 | 0.52967 | 0.55669 | 0.58097 | 0.60325 | 0.62198 | 0.63849 | 0.64846 | 0.65875 | 0.66172 | 0.6559 | 0.67355 | 0.67576 | 0.64724 | 0.59211 | 0.53364 | 0.4707 | 0.67576
2015-02-12 | 0.41616 | 0.38588 | 0.36734 | 0.35958 | 0.36368 | 0.39297 | 0.45802 | 0.49371 | 0.52128 | 0.55651 | 0.58719 | 0.61192 | 0.63028 | 0.64526 | 0.64909 | 0.64314 | 0.63511 | 0.63659 | 0.66601 | 0.6587 | 0.62771 | 0.58164 | 0.51717 | 0.45171 | 0.66601
2015-02-13 | 0.40411 | 0.37402 | 0.35999 | 0.35453 | 0.36084 | 0.39292 | 0.46091 | 0.50282 | 0.52484 | 0.53887 | 0.55141 | 0.55584 | 0.55827 | 0.55755 | 0.55507 | 0.55119 | 0.54731 | 0.5474 | 0.57921 | 0.59152 | 0.57271 | 0.54023 | 0.49664 | 0.44679 | 0.59152
2015-02-14 | 0.40749 | 0.38805 | 0.38151 | 0.38372 | 0.39788 | 0.44336 | 0.53039 | 0.5857 | 0.58462 | 0.57091 | 0.55981 | 0.54113 | 0.52624 | 0.51604 | 0.50959 | 0.50937 | 0.50919 | 0.51397 | 0.54609 | 0.55236 | 0.53265 | 0.50589 | 0.47575 | 0.43975 | 0.5857
2015-02-15 | 0.40849 | 0.38859 | 0.37803 | 0.37415 | 0.37582 | 0.3889 | 0.41449 | 0.45053 | 0.48961 | 0.51455 | 0.52868 | 0.53012 | 0.52362 | 0.51704 | 0.51122 | 0.50905 | 0.50783 | 0.51108 | 0.53612 | 0.54199 | 0.52313 | 0.49813 | 0.46894 | 0.43113 | 0.54199
2015-02-16 | 0.39924 | 0.38114 | 0.37875 | 0.38092 | 0.3853 | 0.40438 | 0.43799 | 0.48351 | 0.52024 | 0.53093 | 0.52583 | 0.51397 | 0.50725 | 0.50233 | 0.50007 | 0.50088 | 0.50364 | 0.50878 | 0.53729 | 0.54722 | 0.5252 | 0.49556 | 0.46411 | 0.42207 | 0.54722
2015-02-17 | 0.38863 | 0.37054 | 0.36459 | 0.36648 | 0.37826 | 0.41052 | 0.46375 | 0.51212 | 0.53892 | 0.54916 | 0.55376 | 0.55484 | 0.55651 | 0.55958 | 0.56278 | 0.56743 | 0.56987 | 0.57122 | 0.59373 | 0.60118 | 0.57127 | 0.52926 | 0.47724 | 0.42581 | 0.60118
2015-02-18 | 0.38128 | 0.35552 | 0.3465 | 0.34415 | 0.35349 | 0.38859 | 0.4596 | 0.50368 | 0.52046 | 0.53684 | 0.55209 | 0.56459 | 0.57546 | 0.58701 | 0.59779 | 0.60804 | 0.61169 | 0.60614 | 0.62094 | 0.62811 | 0.59649 | 0.54785 | 0.49633 | 0.43614 | 0.62811
2015-02-19 | 0.38872 | 0.36026 | 0.3474 | 0.34216 | 0.34844 | 0.38042 | 0.4476 | 0.486 | 0.50869 | 0.53454 | 0.56062 | 0.58286 | 0.60028 | 0.61701 | 0.63299 | 0.64819 | 0.65189 | 0.64282 | 0.65117 | 0.65491 | 0.62396 | 0.57654 | 0.52159 | 0.461 | 0.65491
2015-02-20 | 0.4088 | 0.37857 | 0.36174 | 0.35277 | 0.35529 | 0.38579 | 0.45053 | 0.49001 | 0.52281 | 0.56111 | 0.59712 | 0.62157 | 0.64399 | 0.66145 | 0.67373 | 0.68433 | 0.68577 | 0.67571 | 0.68731 | 0.69322 | 0.66434 | 0.62184 | 0.5668 | 0.50973 | 0.69322
2015-02-21 | 0.45703 | 0.41967 | 0.40005 | 0.39026 | 0.39084 | 0.4167 | 0.47918 | 0.5188 | 0.56653 | 0.61652 | 0.65879 | 0.68965 | 0.71081 | 0.72448 | 0.72615 | 0.72232 | 0.6998 | 0.68122 | 0.68934 | 0.679 | 0.64602 | 0.60321 | 0.56121 | 0.50914 | 0.72615
2015-02-22 | 0.45924 | 0.42004 | 0.39879 | 0.38516 | 0.3816 | 0.38615 | 0.40655 | 0.44142 | 0.51451 | 0.58065 | 0.62798 | 0.66249 | 0.68938 | 0.704 | 0.70968 | 0.71221 | 0.70301 | 0.67923 | 0.67521 | 0.66574 | 0.62893 | 0.58949 | 0.54659 | 0.49651 | 0.71221
2015-02-23 | 0.44846 | 0.41349 | 0.39103 | 0.3779 | 0.37194 | 0.37411 | 0.38728 | 0.41751 | 0.48789 | 0.55687 | 0.6102 | 0.65022 | 0.69633 | 0.70373 | 0.71004 | 0.71573 | 0.71036 | 0.69547 | 0.69529 | 0.69642 | 0.66335 | 0.60916 | 0.5585 | 0.49651 | 0.71573
2015-02-24 | 0.44038 | 0.41015 | 0.3903 | 0.37889 | 0.38029 | 0.40745 | 0.46204 | 0.50242 | 0.54158 | 0.58886 | 0.63222 | 0.66276 | 0.69258 | 0.71293 | 0.72543 | 0.73504 | 0.72647 | 0.71293 | 0.72593 | 0.72854 | 0.68577 | 0.63136 | 0.56815 | 0.50246 | 0.73504
2015-02-25 | 0.44517 | 0.4097 | 0.38836 | 0.37659 | 0.37749 | 0.40497 | 0.46637 | 0.50097 | 0.53671 | 0.57736 | 0.61368 | 0.64386 | 0.67251 | 0.69746 | 0.7169 | 0.72823 | 0.72489 | 0.70517 | 0.70914 | 0.70928 | 0.67102 | 0.61638 | 0.55778 | 0.49105 | 0.72823
2015-02-26 | 0.43438 | 0.3986 | 0.37654 | 0.36626 | 0.36702 | 0.39107 | 0.45031 | 0.48794 | 0.51907 | 0.55367 | 0.59933 | 0.62965 | 0.65667 | 0.67508 | 0.68681 | 0.6892 | 0.67878 | 0.67156 | 0.69037 | 0.68979 | 0.65753 | 0.61214 | 0.55593 | 0.49619 | 0.69037
2015-02-27 | 0.44422 | 0.41408 | 0.39793 | 0.39035 | 0.39274 | 0.41909 | 0.48063 | 0.51428 | 0.53427 | 0.55904 | 0.58602 | 0.58033 | 0.60709 | 0.61074 | 0.60939 | 0.60605 | 0.59879 | 0.61065 | 0.63253 | 0.63641 | 0.60966 | 0.56342 | 0.50901 | 0.45437 | 0.63641
2015-02-28 | 0.4079 | 0.38124 | 0.36887 | 0.36499 | 0.37072 | 0.40312 | 0.47169 | 0.51081 | 0.52304 | 0.53053 | 0.53644 | 0.53824 | 0.5386 | 0.54153 | 0.54474 | 0.5492 | 0.552 | 0.54835 | 0.56111 | 0.56869 | 0.54429 | 0.51216 | 0.47395 | 0.43041 | 0.56869
2015-03-01 | 0.39143 | 0.36684 | 0.3534 | 0.34753 | 0.34983 | 0.36396 | 0.39116 | 0.42784 | 0.47386 | 0.50409 | 0.52313 | 0.53296 | 0.54235 | 0.5516 | 0.55845 | 0.56725 | 0.56833 | 0.56093 | 0.56157 | 0.5719 | 0.54388 | 0.51243 | 0.4763 | 0.43249 | 0.5719
2015-03-02 | 0.39378 | 0.36928 | 0.35538 | 0.34293 | 0.34108 | 0.34807 | 0.36517 | 0.39486 | 0.45252 | 0.50039 | 0.53044 | 0.55214 | 0.56874 | 0.58498 | 0.59631 | 0.60623 | 0.60943 | 0.60186 | 0.60492 | 0.61593 | 0.58453 | 0.54203 | 0.4933 | 0.43953 | 0.61593
2015-03-03 | 0.39946 | 0.3663 | 0.34821 | 0.34144 | 0.34532 | 0.37478 | 0.43452 | 0.4721 | 0.5058 | 0.5432 | 0.57785 | 0.60316 | 0.62793 | 0.65189 | 0.66709 | 0.68072 | 0.68478 | 0.67463 | 0.67449 | 0.68085 | 0.64151 | 0.58764 | 0.52841 | 0.4624 | 0.68478
2015-03-04 | 0.40885 | 0.3746 | 0.35588 | 0.34641 | 0.34848 | 0.3756 | 0.43551 | 0.47445 | 0.5063 | 0.54325 | 0.57641 | 0.60343 | 0.6278 | 0.65031 | 0.66944 | 0.68361 | 0.68704 | 0.67639 | 0.67747 | 0.68158 | 0.64724 | 0.59992 | 0.54144 | 0.47873 | 0.68704
2015-03-05 | 0.42432 | 0.39301 | 0.37483 | 0.36729 | 0.37036 | 0.39766 | 0.46145 | 0.50007 | 0.52998 | 0.57172 | 0.60763 | 0.63835 | 0.66389 | 0.68031 | 0.68685 | 0.68898 | 0.68058 | 0.66962 | 0.6772 | 0.68099 | 0.65126 | 0.60533 | 0.54943 | 0.48685 | 0.68898
2015-03-06 | 0.43443 | 0.4037 | 0.38444 | 0.37632 | 0.37763 | 0.40384 | 0.46384 | 0.50215 | 0.54365 | 0.58588 | 0.61697 | 0.6426 | 0.6596 | 0.65613 | 0.64823 | 0.60077 | 0.57758 | 0.58142 | 0.60768 | 0.613 | 0.58832 | 0.5488 | 0.50264 | 0.45004 | 0.6596
2015-03-07 | 0.40433 | 0.376 | 0.36418 | 0.35872 | 0.36377 | 0.39315 | 0.45581 | 0.49412 | 0.52859 | 0.55692 | 0.58006 | 0.59049 | 0.5959 | 0.5964 | 0.59594 | 0.59635 | 0.59243 | 0.58187 | 0.58724 | 0.59107 | 0.56883 | 0.53035 | 0.48938 | 0.43664 | 0.5964
2015-03-08 | 0.40091 | 0.37433 | 0.36206 | 0.35755 | 0.36098 | 0.37257 | 0.40185 | 0.44264 | 0.48496 | 0.5091 | 0.516 | 0.51546 | 0.51433 | 0.51388 | 0.51735 | 0.5225 | 0.52525 | 0.52272 | 0.53044 | 0.54406 | 0.5206 | 0.49227 | 0.45739 | 0.42216 | 0.54406
2015-03-09 | 0.38223 | 0 | 0.35967 | 0.34744 | 0.34311 | 0.34875 | 0.36463 | 0.3876 | 0.42103 | 0.46208 | 0.49543 | 0.51004 | 0.5298 | 0.54072 | 0.54871 | 0.5603 | 0.57226 | 0.57799 | 0.56942 | 0.5719 | 0.58543 | 0.55178 | 0.50783 | 0.44503 | 0.58543
2015-03-10 | 0.39292 | 0.35832 | 0.34153 | 0.3363 | 0.34243 | 0.37005 | 0.43001 | 0.47418 | 0.48735 | 0.51316 | 0.54415 | 0.56274 | 0.58367 | 0.59757 | 0.61828 | 0.63831 | 0.65482 | 0.65595 | 0.64228 | 0.63863 | 0.64413 | 0.59703 | 0.54456 | 0.47855 | 0.65595
2015-03-11 | 0.41728 | 0.37925 | 0.35818 | 0.34771 | 0.34767 | 0.37424 | 0.43362 | 0.47602 | 0.48744 | 0.51771 | 0.5446 | 0.56955 | 0.59121 | 0.61106 | 0.62969 | 0.65054 | 0.66809 | 0.67323 | 0.66127 | 0.65532 | 0.66136 | 0.62071 | 0.56554 | 0.49385 | 0.67323
2015-03-12 | 0.43768 | 0.39915 | 0.37916 | 0.37032 | 0.3723 | 0.3991 | 0.461 | 0.45847 | 0.51266 | 0.54898 | 0.59319 | 0.62852 | 0.65586 | 0.6744 | 0.68437 | 0.70359 | 0.71514 | 0.70977 | 0.6906 | 0.68261 | 0.68604 | 0.64408 | 0.59107 | 0.52601 | 0.71514
2015-03-13 | 0.46574 | 0.4254 | 0.40136 | 0.38854 | 0.38521 | 0.40533 | 0.45829 | 0.49155 | 0.50125 | 0.52985 | 0.55114 | 0.5636 | 0.5705 | 0.57483 | 0.57781 | 0.58092 | 0.58697 | 0.58552 | 0.56892 | 0.56689 | 0.57812 | 0.54307 | 0.49601 | 0.43921 | 0.58697
2015-03-14 | 0.39148 | 0.3645 | 0.34947 | 0.34573 | 0.35326 | 0.38557 | 0.45775 | 0.50946 | 0.52101 | 0.53125 | 0.53905 | 0.54095 | 0.54014 | 0.54217 | 0.54478 | 0.54956 | 0.55642 | 0.55602 | 0.54541 | 0.54451 | 0.55435 | 0.52678 | 0.48843 | 0.44426 | 0.55642
2015-03-15 | 0.39545 | 0.36626 | 0.34844 | 0.3404 | 0.34194 | 0.3529 | 0.37582 | 0.41422 | 0.45735 | 0.49678 | 0.52678 | 0.54393 | 0.55624 | 0.56653 | 0.57857 | 0.59094 | 0.60429 | 0.60659 | 0.59175 | 0.57736 | 0.58065 | 0.54911 | 0.51302 | 0.46213 | 0.60659
2015-03-16 | 0.41697 | 0.38557 | 0.36544 | 0.35417 | 0.34961 | 0.35254 | 0.36743 | 0.39066 | 0.43727 | 0.4975 | 0.53982 | 0.57072 | 0.59518 | 0.61386 | 0.63195 | 0.64431 | 0.65004 | 0.64805 | 0.63204 | 0.62595 | 0.63678 | 0.60289 | 0.56012 | 0.4998 | 0.65004
2015-03-17 | 0.44679 | 0.41173 | 0.39206 | 0.38493 | 0.38881 | 0.41679 | 0.47436 | 0.51735 | 0.54045 | 0.58593 | 0.6352 | 0.66881 | 0.69299 | 0.70526 | 0.71167 | 0.71618 | 0.71753 | 0.70756 | 0.69619 | 0.70296 | 0.70247 | 0.66461 | 0.61972 | 0.55796 | 0.71753
2015-03-18 | 0.50309 | 0.46714 | 0.44882 | 0.43998 | 0.43858 | 0.45843 | 0.50887 | 0.5386 | 0.53355 | 0.54988 | 0.56581 | 0.57447 | 0.58187 | 0.59211 | 0.60546 | 0.61963 | 0.63452 | 0.63912 | 0.6264 | 0.62008 | 0.62771 | 0.58882 | 0.53544 | 0.46935 | 0.63912
2015-03-19 | 0.41119 | 0.37641 | 0.35777 | 0.34947 | 0.35168 | 0.37875 | 0.43826 | 0.47842 | 0.49493 | 0.52714 | 0.55886 | 0.58218 | 0.59757 | 0.61629 | 0.6347 | 0.65239 | 0.66344 | 0.66412 | 0.64625 | 0.63411 | 0.64255 | 0.60474 | 0.5539 | 0.48933 | 0.66412
2015-03-20 | 0.43416 | 0.39761 | 0.37826 | 0.36729 | 0.36797 | 0.39265 | 0.45008 | 0.49087 | 0.50851 | 0.53946 | 0.57176 | 0.59585 | 0.61467 | 0.63425 | 0.65198 | 0.66606 | 0.67526 | 0.67201 | 0.65609 | 0.643 | 0.6499 | 0.60619 | 0.55218 | 0.48956 | 0.67526
2015-03-21 | 0.42928 | 0.39035 | 0.3663 | 0.35304 | 0.35272 | 0.37307 | 0.42112 | 0.46321 | 0.48956 | 0.5289 | 0.56851 | 0.59955 | 0.62419 | 0.64869 | 0.67192 | 0.69078 | 0.69813 | 0.69092 | 0.66515 | 0.64607 | 0.64765 | 0.60984 | 0.56865 | 0.51731 | 0.69813
2015-03-22 | 0.46506 | 0.42996 | 0.40587 | 0.39143 | 0.38561 | 0.39179 | 0.41079 | 0.43547 | 0.47706 | 0.54122 | 0.58891 | 0.61404 | 0.63596 | 0.65257 | 0.66394 | 0.67625 | 0.69204 | 0.69173 | 0.67161 | 0.6472 | 0.64435 | 0.60564 | 0.55904 | 0.50278 | 0.69204
2015-03-23 | 0.4499 | 0.40979 | 0.38561 | 0.37144 | 0.36468 | 0.36756 | 0.38065 | 0.40077 | 0.44508 | 0.51049 | 0.56703 | 0.60948 | 0.64972 | 0.68451 | 0.70806 | 0.72769 | 0.73617 | 0.73522 | 0.71835 | 0.69777 | 0.70111 | 0.65613 | 0.60375 | 0.53806 | 0.73617
2015-03-24 | 0.47963 | 0.43772 | 0.40966 | 0.39793 | 0.39639 | 0.4162 | 0.45879 | 0.49574 | 0.52168 | 0.55823 | 0.58688 | 0.60664 | 0.61422 | 0.61336 | 0.60533 | 0.60005 | 0.60059 | 0.60384 | 0.6033 | 0.60655 | 0.60176 | 0.56409 | 0.52056 | 0.46375 | 0.61422
2015-03-25 | 0.41566 | 0.38006 | 0.35755 | 0.34929 | 0.35168 | 0.37338 | 0.4236 | 0.46335 | 0.48721 | 0.52231 | 0.54686 | 0.57131 | 0.5904 | 0.60361 | 0.61584 | 0.62554 | 0.63389 | 0.63456 | 0.62184 | 0.60655 | 0.61219 | 0.57091 | 0.51505 | 0.45031 | 0.63456
2015-03-26 | 0.39297 | 0.35967 | 0.3409 | 0.3344 | 0.3395 | 0.36626 | 0.42477 | 0.47431 | 0.50278 | 0.51726 | 0.52872 | 0.52881 | 0.52335 | 0.51668 | 0.51234 | 0.50991 | 0.51428 | 0.51731 | 0.51577 | 0.53035 | 0.55182 | 0.52457 | 0.48157 | 0.43438 | 0.55182
2015-03-27 | 0.39152 | 0.36612 | 0.35299 | 0.34992 | 0.35592 | 0.38223 | 0.43772 | 0.47684 | 0.49619 | 0.52335 | 0.53666 | 0.5432 | 0.54623 | 0.54871 | 0.54839 | 0.54781 | 0.5488 | 0.54812 | 0.54469 | 0.55696 | 0.56829 | 0.54009 | 0.49894 | 0.44886 | 0.56829
2015-03-28 | 0.40334 | 0.37248 | 0.35633 | 0.34771 | 0.35114 | 0.37388 | 0.42234 | 0.46235 | 0.49091 | 0.52958 | 0.56811 | 0.5908 | 0.60641 | 0.61553 | 0.62292 | 0.62753 | 0.62671 | 0.61697 | 0.60262 | 0.60276 | 0.60871 | 0.58187 | 0.54731 | 0.50111 | 0.62753
2015-03-29 | 0.45635 | 0.42527 | 0.40501 | 0.3945 | 0.39229 | 0.39969 | 0.41922 | 0.4476 | 0.48983 | 0.54722 | 0.59622 | 0.62978 | 0.64445 | 0.65225 | 0.65063 | 0.64273 | 0.63235 | 0.62148 | 0.60443 | 0.59955 | 0.58742 | 0.55015 | 0.5151 | 0.46975 | 0.65225
2015-03-30 | 0.42401 | 0.39152 | 0.36869 | 0.35737 | 0.35322 | 0.35755 | 0.37483 | 0.3963 | 0.4356 | 0.48649 | 0.52159 | 0.53919 | 0.54717 | 0.55317 | 0.55886 | 0.56364 | 0.56847 | 0.56739 | 0.55588 | 0.54776 | 0.56292 | 0.52804 | 0.48126 | 0.42355 | 0.56847
2015-03-31 | 0.37474 | 0.34857 | 0.3317 | 0.32624 | 0.33255 | 0.36811 | 0.43177 | 0.47205 | 0.48563 | 0.50445 | 0.52385 | 0.53932 | 0.55038 | 0.56351 | 0.57506 | 0.58467 | 0.58918 | 0.5843 | 0.57867 | 0.58561 | 0.59829 | 0.5594 | 0.50837 | 0.44584 | 0.59829
2015-04-01 | 0.39265 | 0.36107 | 0.34496 | 0.33837 | 0.34289 | 0.37239 | 0.44165 | 0.48369 | 0.49872 | 0.51911 | 0.53887 | 0.55588 | 0.56951 | 0.5871 | 0.60826 | 0.63199 | 0.65356 | 0.66127 | 0.64954 | 0.62865 | 0.63357 | 0.59197 | 0.53035 | 0.4629 | 0.66127
2015-04-02 | 0.40587 | 0.37063 | 0.35146 | 0.34158 | 0.34415 | 0.37375 | 0.43727 | 0.47273 | 0.48911 | 0.51965 | 0.54528 | 0.56842 | 0.58417 | 0.60352 | 0.63285 | 0.65906 | 0.67873 | 0.68694 | 0.67147 | 0.65036 | 0.65469 | 0.61291 | 0.55056 | 0.48252 | 0.68694
2015-04-03 | 0.42297 | 0.38525 | 0.36387 | 0.35502 | 0.35696 | 0.38678 | 0.44494 | 0.4795 | 0.5026 | 0.53729 | 0.56991 | 0.59685 | 0.62094 | 0.6439 | 0.6753 | 0.69592 | 0.71041 | 0.70463 | 0.68848 | 0.66484 | 0.6772 | 0.63393 | 0.57045 | 0.50115 | 0.71041
2015-04-04 | 0.4402 | 0.40226 | 0.37875 | 0.3672 | 0.3659 | 0.3917 | 0.45414 | 0.48703 | 0.51234 | 0.55227 | 0.59044 | 0.62166 | 0.64557 | 0.67003 | 0.69349 | 0.71388 | 0.7303 | 0.72877 | 0.70869 | 0.67373 | 0.66628 | 0.62865 | 0.57907 | 0.52083 | 0.7303
2015-04-05 | 0.46438 | 0.42392 | 0.39757 | 0.38119 | 0.37456 | 0.3769 | 0.39617 | 0.4204 | 0.47787 | 0.54325 | 0.59319 | 0.63299 | 0.66529 | 0.698 | 0.72042 | 0.73693 | 0.74316 | 0.7391 | 0.71171 | 0.67544 | 0.67142 | 0.63208 | 0.58471 | 0.52985 | 0.74316
2015-04-06 | 0.47287 | 0.43086 | 0.40054 | 0.38236 | 0.37478 | 0.37591 | 0.3889 | 0.40713 | 0.46741 | 0.53743 | 0.59292 | 0.63267 | 0.66863 | 0.69998 | 0.72872 | 0.74704 | 0.75593 | 0.7553 | 0.73373 | 0.7045 | 0.70553 | 0.65978 | 0.60262 | 0.53107 | 0.75593
2015-04-07 | 0.47553 | 0.43691 | 0.41566 | 0.40533 | 0.40817 | 0.43673 | 0.49597 | 0.52953 | 0.55931 | 0.61417 | 0.66822 | 0.71496 | 0.7534 | 0.78742 | 0.81413 | 0.83425 | 0.84657 | 0.84165 | 0.81733 | 0.79599 | 0.78959 | 0.73725 | 0.67228 | 0.60461 | 0.84657
2015-04-08 | 0.54713 | 0.50382 | 0.47192 | 0.45518 | 0.45545 | 0.4795 | 0.54045 | 0.57271 | 0.5991 | 0.63623 | 0.67923 | 0.71478 | 0.73558 | 0.74641 | 0.74424 | 0.73278 | 0.73896 | 0.7142 | 0.6666 | 0.6435 | 0.64661 | 0.60307 | 0.54212 | 0.47684 | 0.74641
2015-04-09 | 0.42626 | 0.39238 | 0.37271 | 0.36278 | 0.36211 | 0.38701 | 0.44629 | 0.47418 | 0.48839 | 0.51695 | 0.5391 | 0.55087 | 0.55787 | 0.56369 | 0.57312 | 0.58462 | 0.59558 | 0.60258 | 0.59504 | 0.58439 | 0.60064 | 0.56463 | 0.50652 | 0.44498 | 0.60258
2015-04-10 | 0.3936 | 0.36328 | 0.34564 | 0.3391 | 0.34225 | 0.37045 | 0.43362 | 0.46691 | 0.48266 | 0.50864 | 0.53256 | 0.54984 | 0.56152 | 0.57492 | 0.5894 | 0.6051 | 0.61593 | 0.61566 | 0.60501 | 0.59752 | 0.61322 | 0.57474 | 0.52074 | 0.45789 | 0.61593
2015-04-11 | 0.40627 | 0.37135 | 0.35313 | 0.34537 | 0.34794 | 0.37348 | 0.43456 | 0.46881 | 0.4924 | 0.53057 | 0.56481 | 0.58809 | 0.60416 | 0.62013 | 0.63465 | 0.63998 | 0.64165 | 0.63348 | 0.61837 | 0.60673 | 0.6148 | 0.58643 | 0.5469 | 0.49651 | 0.64165
2015-04-12 | 0.44683 | 0.41169 | 0.38669 | 0.37235 | 0.3663 | 0.37095 | 0.39202 | 0.41819 | 0.47593 | 0.53887 | 0.5867 | 0.62338 | 0.64801 | 0.66989 | 0.68297 | 0.69489 | 0.69931 | 0.69439 | 0.66818 | 0.63777 | 0.63754 | 0.60731 | 0.55999 | 0.51117 | 0.69931
2015-04-13 | 0.4629 | 0.42513 | 0.4014 | 0.38539 | 0.37866 | 0.38114 | 0.39513 | 0.41494 | 0.46673 | 0.52917 | 0.57605 | 0.60939 | 0.6384 | 0.65753 | 0.66551 | 0.67192 | 0.67359 | 0.67043 | 0.65527 | 0.65072 | 0.66452 | 0.63023 | 0.5811 | 0.51925 | 0.67359
2015-04-14 | 0.46488 | 0.42937 | 0.40961 | 0.39829 | 0.39933 | 0.42432 | 0.48374 | 0.5174 | 0.55358 | 0.60835 | 0.65861 | 0.70192 | 0.73662 | 0.7705 | 0.7973 | 0.81995 | 0.83177 | 0.82789 | 0.80298 | 0.77154 | 0.76716 | 0.71947 | 0.65324 | 0.57808 | 0.83177
2015-04-15 | 0.51365 | 0.47214 | 0.44629 | 0.42843 | 0.425 | 0.44715 | 0.50571 | 0.53657 | 0.58006 | 0.64079 | 0.69119 | 0.73689 | 0.76991 | 0.79342 | 0.80267 | 0.8098 | 0.80461 | 0.77312 | 0.75697 | 0.7345 | 0.73617 | 0.6929 | 0.62703 | 0.55507 | 0.8098
2015-04-16 | 0.49529 | 0.45441 | 0.4287 | 0.41539 | 0.41259 | 0.43371 | 0.48785 | 0.51446 | 0.5335 | 0.56278 | 0.58724 | 0.60398 | 0.62135 | 0.64133 | 0.65577 | 0.66655 | 0.67309 | 0.6707 | 0.65947 | 0.65681 | 0.66917 | 0.64097 | 0.58724 | 0.52195 | 0.67309
2015-04-17 | 0.46939 | 0.43492 | 0.41476 | 0.4042 | 0.40569 | 0.43118 | 0.48915 | 0.52213 | 0.55105 | 0.59414 | 0.6319 | 0.65618 | 0.66425 | 0.67048 | 0.67282 | 0.66926 | 0.66385 | 0.65252 | 0.64196 | 0.63556 | 0.64359 | 0.61945 | 0.57609 | 0.52019 | 0.67282
2015-04-18 | 0.46966 | 0.43416 | 0.4111 | 0.39842 | 0.39644 | 0.41652 | 0.45762 | 0.49209 | 0.53761 | 0.59423 | 0.64016 | 0.67061 | 0.68938 | 0.70973 | 0.71961 | 0.71785 | 0.71392 | 0.70928 | 0.68965 | 0.66642 | 0.66768 | 0.63989 | 0.6001 | 0.55317 | 0.71961
2015-04-19 | 0.50201 | 0.46799 | 0.44422 | 0.4287 | 0.42342 | 0.42834 | 0.43777 | 0.45202 | 0.49294 | 0.56057 | 0.61557 | 0.65324 | 0.68356 | 0.70571 | 0.7178 | 0.72597 | 0.72466 | 0.70819 | 0.67612 | 0.63678 | 0.62978 | 0.59405 | 0.55178 | 0.49263 | 0.72597
2015-04-20 | 0.43898 | 0.39888 | 0.37153 | 0.35728 | 0.35128 | 0.35444 | 0.36887 | 0.38593 | 0.43407 | 0.48397 | 0.51158 | 0.53414 | 0.54925 | 0.56012 | 0.56743 | 0.57316 | 0.57686 | 0.57298 | 0.56319 | 0.5576 | 0.57718 | 0.55529 | 0.51135 | 0.45333 | 0.57718
2015-04-21 | 0.40226 | 0.36878 | 0.35092 | 0.34221 | 0.34492 | 0.37172 | 0.4282 | 0.45847 | 0.48333 | 0.5151 | 0.54474 | 0.56725 | 0.58999 | 0.60831 | 0.62902 | 0.64539 | 0.65857 | 0.65739 | 0.64729 | 0.63326 | 0.64404 | 0.60583 | 0.54835 | 0.48568 | 0.65857
2015-04-22 | 0.42698 | 0.38773 | 0.36869 | 0.35701 | 0.35723 | 0.38629 | 0.44539 | 0.47111 | 0.49732 | 0.52944 | 0.56278 | 0.59572 | 0.62044 | 0.64052 | 0.66123 | 0.68627 | 0.70355 | 0.7068 | 0.69358 | 0.67346 | 0.68252 | 0.64223 | 0.57767 | 0.50607 | 0.7068
2015-04-23 | 0.44692 | 0.40934 | 0.38566 | 0.37131 | 0.36901 | 0.39288 | 0.44738 | 0.41679 | 0.50716 | 0.54388 | 0.57889 | 0.60483 | 0.63569 | 0.67273 | 0.71198 | 0.74136 | 0.76252 | 0.76784 | 0.75142 | 0.71997 | 0.71668 | 0.68216 | 0.61877 | 0.53332 | 0.76784
2015-04-24 | 0.47454 | 0.43506 | 0.39833 | 0.38259 | 0.38308 | 0.39766 | 0.45071 | 0.48198 | 0.51631 | 0.56504 | 0.61363 | 0.65428 | 0.69132 | 0.72417 | 0.75169 | 0.77853 | 0.79405 | 0.79202 | 0.76919 | 0.73342 | 0.73044 | 0.68879 | 0.62229 | 0.55096 | 0.79405
2015-04-25 | 0.48717 | 0.44101 | 0.412 | 0.39518 | 0.39125 | 0.41286 | 0.46542 | 0.49506 | 0.53192 | 0.58223 | 0.63538 | 0.68162 | 0.72177 | 0.75864 | 0.79035 | 0.81711 | 0.83172 | 0.82775 | 0.79707 | 0.752 | 0.73946 | 0.69863 | 0.64034 | 0.57609 | 0.83172
2015-04-26 | 0.51122 | 0.46235 | 0.43032 | 0.40952 | 0.39757 | 0.39838 | 0.41173 | 0.43786 | 0.50278 | 0.57442 | 0.63894 | 0.69407 | 0.73707 | 0.76951 | 0.78895 | 0.80623 | 0.81512 | 0.80984 | 0.78016 | 0.73463 | 0.72187 | 0.68424 | 0.63317 | 0.57673 | 0.81512
2015-04-27 | 0.52159 | 0.47815 | 0.44544 | 0.42581 | 0.41318 | 0.41097 | 0.41819 | 0.43853 | 0.51 | 0.59071 | 0.65766 | 0.71149 | 0.75309 | 0.7867 | 0.80899 | 0.82798 | 0.83551 | 0.83046 | 0.80393 | 0.76603 | 0.76053 | 0.71938 | 0.65451 | 0.589 | 0.83551
2015-04-28 | 0.53156 | 0.49209 | 0.46687 | 0.45108 | 0.44972 | 0.47463 | 0.52732 | 0.55818 | 0.5991 | 0.65545 | 0.71848 | 0.77091 | 0.8102 | 0.84363 | 0.87125 | 0.89241 | 0.898 | 0.89579 | 0.87084 | 0.83299 | 0.82211 | 0.77185 | 0.69922 | 0.62586 | 0.898
2015-04-29 | 0.56572 | 0.52317 | 0.49538 | 0.47927 | 0.47657 | 0.49867 | 0.54826 | 0.57848 | 0.62703 | 0.68753 | 0.74709 | 0.79703 | 0.83357 | 0.86285 | 0.88316 | 0.89755 | 0.89457 | 0.88415 | 0.86344 | 0.82942 | 0.81643 | 0.76901 | 0.69881 | 0.62554 | 0.89755
2015-04-30 | 0.56373 | 0.52484 | 0.49944 | 0.48523 | 0.48433 | 0.50612 | 0.55683 | 0.58679 | 0.63362 | 0.69403 | 0.75272 | 0.79879 | 0.83272 | 0.86204 | 0.87991 | 0.89218 | 0.88582 | 0.8509 | 0.82482 | 0.79671 | 0.79477 | 0.75223 | 0.68514 | 0.61512 | 0.89218
2015-05-01 | 0.55381 | 0.51352 | 0.48654 | 0.47205 | 0.46795 | 0.49191 | 0.54564 | 0.57709 | 0.61972 | 0.68072 | 0.74262 | 0.78895 | 0.8255 | 0.85654 | 0.87621 | 0.88604 | 0.88113 | 0.855 | 0.81494 | 0.78386 | 0.78097 | 0.73468 | 0.67183 | 0.60497 | 0.88604
2015-05-02 | 0.54785 | 0.50774 | 0.48189 | 0.46605 | 0.4619 | 0.4846 | 0.53653 | 0.56883 | 0.60695 | 0.66195 | 0.70865 | 0.74352 | 0.76369 | 0.78692 | 0.80357 | 0.81228 | 0.80686 | 0.79049 | 0.76527 | 0.73093 | 0.73026 | 0.68122 | 0.63168 | 0.57812 | 0.81228
2015-05-03 | 0.52511 | 0.48469 | 0.45753 | 0.44101 | 0.43258 | 0.43722 | 0.45306 | 0.47778 | 0.52615 | 0.58516 | 0.63276 | 0.66506 | 0.67986 | 0.68694 | 0.68297 | 0.66479 | 0.62274 | 0.60641 | 0.59134 | 0.58719 | 0.59748 | 0.57853 | 0.54645 | 0.50576 | 0.68694
2015-05-04 | 0.46384 | 0.43082 | 0.41025 | 0.3963 | 0.39193 | 0.39202 | 0.3973 | 0.4037 | 0.45053 | 0.50337 | 0.54451 | 0.57379 | 0.60343 | 0.62879 | 0.65067 | 0.67503 | 0.69394 | 0.7035 | 0.69525 | 0.6656 | 0.65554 | 0.61683 | 0.56648 | 0.49606 | 0.7035
2015-05-05 | 0.44011 | 0.39621 | 0.37916 | 0.36689 | 0.36725 | 0.39269 | 0.44268 | 0.47345 | 0.5095 | 0.55656 | 0.60456 | 0.64454 | 0.68221 | 0.71663 | 0.74821 | 0.77465 | 0.79775 | 0.801 | 0.78246 | 0.72191 | 0.72362 | 0.67797 | 0.59098 | 0.53301 | 0.801
2015-05-06 | 0.46912 | 0.42892 | 0.4019 | 0.38584 | 0.38205 | 0.40397 | 0.45464 | 0.4855 | 0.5225 | 0.57393 | 0.62495 | 0.67422 | 0.72029 | 0.75498 | 0.78774 | 0.81593 | 0.83384 | 0.83267 | 0.81047 | 0.7511 | 0.75841 | 0.71401 | 0.64634 | 0.56951 | 0.83384
2015-05-07 | 0.50837 | 0.46646 | 0.4421 | 0.4259 | 0.42238 | 0.44323 | 0.49321 | 0.52362 | 0.56689 | 0.61868 | 0.67481 | 0.72087 | 0.76157 | 0.79861 | 0.83195 | 0.84837 | 0.86046 | 0.85708 | 0.83046 | 0.79162 | 0.78219 | 0.74397 | 0.67472 | 0.60276 | 0.86046
2015-05-08 | 0.53851 | 0.498 | 0.47219 | 0.45338 | 0.44896 | 0.4684 | 0.51686 | 0.54496 | 0.59062 | 0.64445 | 0.69822 | 0.74208 | 0.77903 | 0.81368 | 0.84034 | 0.86385 | 0.87806 | 0.87413 | 0.85135 | 0.80984 | 0.79392 | 0.75173 | 0.68722 | 0.61877 | 0.87806
2015-05-09 | 0.54776 | 0.50296 | 0.4776 | 0.4582 | 0.45342 | 0.47359 | 0.52182 | 0.55051 | 0.59378 | 0.6481 | 0.70012 | 0.74226 | 0.77835 | 0.81038 | 0.83903 | 0.86015 | 0.8707 | 0.86024 | 0.82762 | 0.7816 | 0.76229 | 0.72317 | 0.67215 | 0.61544 | 0.8707
2015-05-10 | 0.55868 | 0.51825 | 0.49105 | 0.47156 | 0.46217 | 0.46457 | 0.47436 | 0.49989 | 0.56806 | 0.63745 | 0.68785 | 0.72611 | 0.76473 | 0.78981 | 0.80601 | 0.81792 | 0.81724 | 0.80849 | 0.78349 | 0.73914 | 0.74343 | 0.71023 | 0.66642 | 0.61327 | 0.81792
2015-05-11 | 0.56021 | 0.52119 | 0.4924 | 0.47386 | 0.46479 | 0.46244 | 0.4661 | 0.48198 | 0.53711 | 0.60361 | 0.65599 | 0.69615 | 0.73125 | 0.76085 | 0.78255 | 0.79328 | 0.7973 | 0.78625 | 0.76315 | 0.72972 | 0.73035 | 0.70747 | 0.65572 | 0.58994 | 0.7973
2015-05-12 | 0.52868 | 0.48866 | 0.46375 | 0.45067 | 0.44954 | 0.47237 | 0.52155 | 0.55042 | 0.59044 | 0.64724 | 0.70409 | 0.7493 | 0.78607 | 0.81472 | 0.83556 | 0.8537 | 0.86042 | 0.85482 | 0.83597 | 0.80745 | 0.79951 | 0.75399 | 0.68681 | 0.6185 | 0.86042
2015-05-13 | 0.55832 | 0.51979 | 0.49245 | 0.47566 | 0.47201 | 0.49367 | 0.54185 | 0.56933 | 0.60736 | 0.66326 | 0.71537 | 0.75457 | 0.78999 | 0.81327 | 0.83042 | 0.84463 | 0.85194 | 0.84382 | 0.81999 | 0.78751 | 0.78246 | 0.74695 | 0.68347 | 0.6125 | 0.85194
2015-05-14 | 0.55778 | 0.51947 | 0.49073 | 0.47399 | 0.47079 | 0.47963 | 0.54578 | 0.56788 | 0.60998 | 0.67129 | 0.7234 | 0.77145 | 0.80547 | 0.8269 | 0.84197 | 0.84151 | 0.83714 | 0.82766 | 0.8019 | 0.77131 | 0.77352 | 0.73653 | 0.67729 | 0.60763 | 0.84197
2015-05-15 | 0.54726 | 0.50747 | 0.48063 | 0.46587 | 0.46533 | 0.48672 | 0.53567 | 0.56265 | 0.59807 | 0.65631 | 0.7072 | 0.73364 | 0.74343 | 0.74149 | 0.72579 | 0.70747 | 0.70247 | 0.70174 | 0.69213 | 0.67634 | 0.67634 | 0.65112 | 0.59852 | 0.53991 | 0.74343
2015-05-16 | 0.48622 | 0.45202 | 0.42996 | 0.41597 | 0.41385 | 0.43835 | 0.48893 | 0.51108 | 0.52755 | 0.55723 | 0.5825 | 0.60032 | 0.60826 | 0.61368 | 0.62486 | 0.63127 | 0.63844 | 0.63096 | 0.61133 | 0.58579 | 0.57515 | 0.55205 | 0.51279 | 0.46263 | 0.63844
2015-05-17 | 0.41453 | 0.38272 | 0.36075 | 0.34835 | 0.3446 | 0.34884 | 0.36224 | 0.38764 | 0.44119 | 0.49669 | 0.54162 | 0.57582 | 0.60068 | 0.62338 | 0.64512 | 0.66222 | 0.67296 | 0.67093 | 0.65108 | 0.61697 | 0.60673 | 0.58679 | 0.54424 | 0.49669 | 0.67296
2015-05-18 | 0.45031 | 0.41521 | 0.3908 | 0.3742 | 0.36671 | 0.36824 | 0.3728 | 0.39337 | 0.45053 | 0.51595 | 0.56788 | 0.60695 | 0.63921 | 0.66524 | 0.6887 | 0.70567 | 0.71785 | 0.7151 | 0.69218 | 0.65956 | 0.65581 | 0.63154 | 0.57925 | 0.51672 | 0.71785
2015-05-19 | 0.46168 | 0.42364 | 0.39978 | 0.388 | 0.38854 | 0.41155 | 0.4605 | 0.48911 | 0.53147 | 0.58137 | 0.62748 | 0.66642 | 0.69935 | 0.73188 | 0.75358 | 0.77447 | 0.78575 | 0.78395 | 0.76522 | 0.72877 | 0.71591 | 0.68221 | 0.62193 | 0.54997 | 0.78575
2015-05-20 | 0.48961 | 0.44819 | 0.42423 | 0.40961 | 0.40542 | 0.42486 | 0.47075 | 0.50454 | 0.54636 | 0.59725 | 0.64688 | 0.68726 | 0.71929 | 0.74582 | 0.76459 | 0.77961 | 0.78837 | 0.78449 | 0.76856 | 0.73111 | 0.71961 | 0.6823 | 0.62031 | 0.55105 | 0.78837
2015-05-21 | 0.49064 | 0.44868 | 0.42198 | 0.40483 | 0.40014 | 0.41963 | 0.467 | 0.4998 | 0.53675 | 0.58322 | 0.62874 | 0.66845 | 0.70138 | 0.73644 | 0.76951 | 0.79189 | 0.80538 | 0.79983 | 0.77659 | 0.73761 | 0.71956 | 0.68667 | 0.62559 | 0.55412 | 0.80538
2015-05-22 | 0.48762 | 0.44422 | 0.41363 | 0.39784 | 0.39504 | 0.41593 | 0.4638 | 0.49452 | 0.53752 | 0.58832 | 0.64187 | 0.69236 | 0.73856 | 0.78277 | 0.81557 | 0.84309 | 0.86028 | 0.855 | 0.83046 | 0.78697 | 0.76206 | 0.72944 | 0.65938 | 0.58367 | 0.86028
2015-05-23 | 0.51528 | 0.46908 | 0.43727 | 0.4185 | 0.41092 | 0.42816 | 0.47025 | 0.50928 | 0.5603 | 0.62107 | 0.68325 | 0.74388 | 0.79482 | 0.84567 | 0.88239 | 0.90635 | 0.91402 | 0.90364 | 0.87143 | 0.8153 | 0.79157 | 0.75778 | 0.69818 | 0.63308 | 0.91402
2015-05-24 | 0.57063 | 0.52344 | 0.48636 | 0.46082 | 0.44692 | 0.44313 | 0.44674 | 0.47449 | 0.54781 | 0.62789 | 0.69926 | 0.76432 | 0.81869 | 0.856 | 0.8786 | 0.8906 | 0.89006 | 0.87986 | 0.84481 | 0.7991 | 0.77957 | 0.74474 | 0.69155 | 0.63294 | 0.8906
2015-05-25 | 0.57781 | 0.53102 | 0.49552 | 0.47196 | 0.45757 | 0.45211 | 0.45441 | 0.47196 | 0.53102 | 0.60384 | 0.68108 | 0.74158 | 0.79459 | 0.82951 | 0.85013 | 0.86191 | 0.86583 | 0.84959 | 0.8153 | 0.7756 | 0.7631 | 0.7317 | 0.6767 | 0.62107 | 0.86583
2015-05-26 | 0.56301 | 0.52182 | 0.49132 | 0.47129 | 0.46028 | 0.46046 | 0.46533 | 0.48816 | 0.55927 | 0.64282 | 0.71704 | 0.76991 | 0.81413 | 0.84445 | 0.86132 | 0.87007 | 0.87034 | 0.85681 | 0.82338 | 0.78349 | 0.77506 | 0.73896 | 0.67882 | 0.60943 | 0.87034
2015-05-27 | 0.55123 | 0.5091 | 0.48139 | 0.46443 | 0.45875 | 0.47991 | 0.52367 | 0.56179 | 0.61273 | 0.67503 | 0.73459 | 0.78737 | 0.82599 | 0.8555 | 0.8726 | 0.88063 | 0.86782 | 0.83421 | 0.8024 | 0.77127 | 0.76766 | 0.73436 | 0.67481 | 0.60186 | 0.88063
2015-05-28 | 0.54266 | 0.50188 | 0.47607 | 0.45987 | 0.45595 | 0.47675 | 0.52231 | 0.55575 | 0.6033 | 0.65997 | 0.7178 | 0.77614 | 0.81715 | 0.85063 | 0.86876 | 0.87391 | 0.87341 | 0.85595 | 0.82848 | 0.79789 | 0.78805 | 0.75236 | 0.6911 | 0.62243 | 0.87391
2015-05-29 | 0.56012 | 0.51523 | 0.48834 | 0.47187 | 0.46605 | 0.48496 | 0.52917 | 0.56224 | 0.60249 | 0.65252 | 0.70413 | 0.74045 | 0.76224 | 0.7765 | 0.76658 | 0.75561 | 0.74862 | 0.73978 | 0.73166 | 0.70702 | 0.70463 | 0.68081 | 0.63136 | 0.57014 | 0.7765
2015-05-30 | 0.50914 | 0.46515 | 0.4435 | 0.43005 | 0.42757 | 0.44711 | 0.49015 | 0.52416 | 0.57118 | 0.63849 | 0.69755 | 0.74533 | 0.78264 | 0.81133 | 0.82816 | 0.83894 | 0.83592 | 0.81314 | 0.77222 | 0.73842 | 0.72832 | 0.69809 | 0.6509 | 0.5996 | 0.83894
2015-05-31 | 0.54853 | 0.50458 | 0.47395 | 0.45392 | 0.4462 | 0.44485 | 0.45392 | 0.48311 | 0.5552 | 0.63479 | 0.70445 | 0.75782 | 0.79193 | 0.81363 | 0.81724 | 0.81395 | 0.8019 | 0.77551 | 0.74487 | 0.71244 | 0.70806 | 0.68618 | 0.64652 | 0.59513 | 0.81724
2015-06-01 | 0.54821 | 0.50603 | 0.47833 | 0.45888 | 0.44823 | 0.44769 | 0.45184 | 0.47255 | 0.53395 | 0.60822 | 0.67517 | 0.72489 | 0.76554 | 0.79324 | 0.80741 | 0.80389 | 0.78679 | 0.75724 | 0.7243 | 0.70165 | 0.7012 | 0.6855 | 0.64237 | 0.58494 | 0.80741
2015-06-02 | 0.53283 | 0.49664 | 0.47575 | 0.46407 | 0.46551 | 0.49073 | 0.53544 | 0.56527 | 0.59279 | 0.6245 | 0.65473 | 0.67179 | 0.68843 | 0.69953 | 0.70698 | 0.70662 | 0.7049 | 0.69637 | 0.68762 | 0.67797 | 0.68103 | 0.662 | 0.61273 | 0.55417 | 0.70698
2015-06-03 | 0.50039 | 0.46384 | 0.44119 | 0.42757 | 0.42676 | 0.44986 | 0.49615 | 0.52543 | 0.55326 | 0.59247 | 0.63159 | 0.66452 | 0.68834 | 0.70553 | 0.71271 | 0.71505 | 0.7063 | 0.69683 | 0.68058 | 0.66642 | 0.67106 | 0.64652 | 0.59847 | 0.53761 | 0.71505
2015-06-04 | 0.48185 | 0.44435 | 0.42085 | 0.40858 | 0.4084 | 0.43091 | 0.4758 | 0.48248 | 0.54131 | 0.59432 | 0.63795 | 0.6721 | 0.69538 | 0.72308 | 0.74293 | 0.75629 | 0.76644 | 0.76847 | 0.75534 | 0.72466 | 0.70941 | 0.68361 | 0.63258 | 0.56693 | 0.76847
2015-06-05 | 0.50738 | 0.46714 | 0.4398 | 0.42288 | 0.41746 | 0.43614 | 0.4753 | 0.51631 | 0.57185 | 0.63231 | 0.6938 | 0.74794 | 0.78909 | 0.82667 | 0.85243 | 0.87084 | 0.87851 | 0.87513 | 0.85356 | 0.80939 | 0.78435 | 0.74456 | 0.68135 | 0.60632 | 0.87851
2015-06-06 | 0.54555 | 0.49795 | 0.46547 | 0.44485 | 0.43524 | 0.44981 | 0.48099 | 0.5224 | 0.58755 | 0.65816 | 0.72994 | 0.79486 | 0.84639 | 0.88496 | 0.91181 | 0.92669 | 0.93157 | 0.92263 | 0.89371 | 0.84724 | 0.81652 | 0.78183 | 0.72331 | 0.66222 | 0.93157
2015-06-07 | 0.60186 | 0.55439 | 0.52019 | 0.49854 | 0.48356 | 0.47828 | 0.4827 | 0.51221 | 0.5867 | 0.6652 | 0.74361 | 0.81111 | 0.85473 | 0.88492 | 0.9026 | 0.90734 | 0.89096 | 0.86583 | 0.83213 | 0.79739 | 0.77348 | 0.74086 | 0.68916 | 0.63204 | 0.90734
2015-06-08 | 0.5779 | 0.53319 | 0.50075 | 0.47237 | 0.46335 | 0.45987 | 0.4605 | 0.47986 | 0.5451 | 0.63118 | 0.71149 | 0.77858 | 0.81769 | 0.82658 | 0.81656 | 0.81029 | 0.79838 | 0.78561 | 0.76098 | 0.73102 | 0.71401 | 0.68749 | 0.63073 | 0.57492 | 0.82658
2015-06-09 | 0.51663 | 0.47562 | 0.44688 | 0.43204 | 0.42996 | 0.44877 | 0.48342 | 0.52114 | 0.57546 | 0.64102 | 0.71158 | 0.78201 | 0.83497 | 0.87828 | 0.9012 | 0.89435 | 0.88212 | 0.8509 | 0.81381 | 0.78056 | 0.76175 | 0.72913 | 0.66854 | 0.60149 | 0.9012
2015-06-10 | 0.5405 | 0.49755 | 0.47093 | 0.45405 | 0.44968 | 0.46804 | 0.50287 | 0.54722 | 0.60862 | 0.67282 | 0.73193 | 0.78476 | 0.82509 | 0.8472 | 0.84603 | 0.81693 | 0.79053 | 0.77804 | 0.77474 | 0.75101 | 0.74312 | 0.70752 | 0.64747 | 0.58282 | 0.8472
2015-06-11 | 0.52791 | 0.48757 | 0.45893 | 0.44336 | 0.4398 | 0.45599 | 0.49249 | 0.53206 | 0.58828 | 0.65897 | 0.72146 | 0.77307 | 0.80497 | 0.82446 | 0.80497 | 0.77055 | 0.75295 | 0.74745 | 0.7396 | 0.71577 | 0.70431 | 0.6804 | 0.62735 | 0.56693 | 0.82446
2015-06-12 | 0.51207 | 0.4716 | 0.44557 | 0.42937 | 0.42572 | 0.44124 | 0.47693 | 0.50779 | 0.54041 | 0.58309 | 0.63655 | 0.69362 | 0.75381 | 0.80668 | 0.84138 | 0.84896 | 0.82753 | 0.79347 | 0.76734 | 0.74027 | 0.72579 | 0.69448 | 0.63267 | 0.56933 | 0.84896
2015-06-13 | 0.51261 | 0.47183 | 0.44503 | 0.42757 | 0.42428 | 0.43957 | 0.47088 | 0.51284 | 0.57325 | 0.63533 | 0.69452 | 0.75083 | 0.79401 | 0.81575 | 0.81526 | 0.79148 | 0.76698 | 0.74072 | 0.71717 | 0.68266 | 0.66163 | 0.64038 | 0.59951 | 0.54776 | 0.81575
2015-06-14 | 0.49894 | 0.46114 | 0.43443 | 0.41837 | 0.41119 | 0.41408 | 0.42405 | 0.45229 | 0.51532 | 0.58958 | 0.65915 | 0.72033 | 0.76658 | 0.80389 | 0.82094 | 0.81963 | 0.79771 | 0.7756 | 0.74077 | 0.70256 | 0.68789 | 0.66272 | 0.61981 | 0.57005 | 0.82094
2015-06-15 | 0.52209 | 0.48645 | 0.45789 | 0.44056 | 0.43556 | 0.44002 | 0.44805 | 0.47436 | 0.54149 | 0.62035 | 0.68943 | 0.75097 | 0.8001 | 0.83109 | 0.84887 | 0.84219 | 0.8186 | 0.78882 | 0.75697 | 0.72353 | 0.71686 | 0.70093 | 0.65351 | 0.6001 | 0.84887
2015-06-16 | 0.5428 | 0.50458 | 0.48004 | 0.46461 | 0.45933 | 0.47602 | 0.50837 | 0.54167 | 0.58435 | 0.63691 | 0.70441 | 0.76806 | 0.81111 | 0.84873 | 0.87463 | 0.88983 | 0.8989 | 0.8925 | 0.86006 | 0.80393 | 0.77722 | 0.74321 | 0.68162 | 0.61516 | 0.8989
2015-06-17 | 0.55385 | 0.5118 | 0.48018 | 0.46159 | 0.455 | 0.46935 | 0.50273 | 0.53905 | 0.58349 | 0.63082 | 0.67598 | 0.71681 | 0.7516 | 0.78183 | 0.79202 | 0.79184 | 0.78404 | 0.77695 | 0.76247 | 0.73842 | 0.72403 | 0.70499 | 0.64323 | 0.57871 | 0.79202
2015-06-18 | 0.5188 | 0.47945 | 0.45405 | 0.43786 | 0.43519 | 0.45198 | 0.48879 | 0.5261 | 0.57645 | 0.63195 | 0.69141 | 0.74659 | 0.77623 | 0.7867 | 0.77989 | 0.76134 | 0.74023 | 0.72214 | 0.70431 | 0.68645 | 0.6795 | 0.66163 | 0.61088 | 0.55169 | 0.7867
2015-06-19 | 0.49651 | 0.46046 | 0.43817 | 0.42495 | 0.42152 | 0.43862 | 0.47445 | 0.51113 | 0.56545 | 0.62726 | 0.692 | 0.74253 | 0.78367 | 0.81327 | 0.81566 | 0.79004 | 0.76594 | 0.74118 | 0.71609 | 0.69218 | 0.67946 | 0.6523 | 0.60452 | 0.54469 | 0.81566
2015-06-20 | 0.4901 | 0.45256 | 0.42802 | 0.4144 | 0.41092 | 0.42581 | 0.45893 | 0.49804 | 0.55525 | 0.62419 | 0.68825 | 0.74587 | 0.7894 | 0.81395 | 0.80686 | 0.77122 | 0.74853 | 0.72818 | 0.71086 | 0.68803 | 0.67445 | 0.65757 | 0.61643 | 0.56486 | 0.81395
2015-06-21 | 0.51171 | 0.47436 | 0.4476 | 0.43186 | 0.42491 | 0.42766 | 0.43447 | 0.46759 | 0.54596 | 0.63023 | 0.69759 | 0.75859 | 0.80619 | 0.83362 | 0.82541 | 0.7959 | 0.77032 | 0.74939 | 0.7239 | 0.6971 | 0.68365 | 0.66759 | 0.6278 | 0.5751 | 0.83362
2015-06-22 | 0.52281 | 0.4883 | 0.46037 | 0.44282 | 0.4328 | 0.43222 | 0.43488 | 0.46768 | 0.54235 | 0.62893 | 0.70021 | 0.75363 | 0.8028 | 0.83849 | 0.86114 | 0.86461 | 0.84991 | 0.81661 | 0.7742 | 0.73716 | 0.72205 | 0.69953 | 0.65189 | 0.58945 | 0.86461
2015-06-23 | 0.53089 | 0.49515 | 0.46971 | 0.45432 | 0.45099 | 0.46863 | 0.50278 | 0.54406 | 0.60361 | 0.66899 | 0.73788 | 0.79829 | 0.85081 | 0.89245 | 0.916 | 0.92133 | 0.91203 | 0.89177 | 0.86209 | 0.82067 | 0.79315 | 0.75629 | 0.69714 | 0.62491 | 0.92133
2015-06-24 | 0.56333 | 0.51956 | 0.49055 | 0.4716 | 0.46529 | 0.48036 | 0.51356 | 0.55399 | 0.61652 | 0.68383 | 0.75665 | 0.81796 | 0.87016 | 0.91578 | 0.94253 | 0.9571 | 0.95972 | 0.94176 | 0.91803 | 0.87698 | 0.85437 | 0.81508 | 0.75038 | 0.67743 | 0.95972
2015-06-25 | 0.61322 | 0.56513 | 0.52967 | 0.50747 | 0.49908 | 0.5123 | 0.54365 | 0.58327 | 0.64566 | 0.7197 | 0.79563 | 0.85257 | 0.9031 | 0.9423 | 0.96644 | 0.96883 | 0.94876 | 0.9225 | 0.88929 | 0.84557 | 0.81855 | 0.78331 | 0.72769 | 0.65694 | 0.96883
2015-06-26 | 0.59495 | 0.546 | 0.51275 | 0.49132 | 0.48297 | 0.49443 | 0.52687 | 0.56608 | 0.63032 | 0.70833 | 0.78282 | 0.84034 | 0.88419 | 0.9128 | 0.94077 | 0.94988 | 0.95011 | 0.93576 | 0.90969 | 0.86696 | 0.83624 | 0.79861 | 0.7368 | 0.66434 | 0.95011
2015-06-27 | 0.59973 | 0.55475 | 0.52227 | 0.50165 | 0.49484 | 0.50905 | 0.53585 | 0.57397 | 0.63727 | 0.71027 | 0.77569 | 0.83303 | 0.86863 | 0.8985 | 0.92403 | 0.92678 | 0.91704 | 0.89308 | 0.84959 | 0.80366 | 0.77799 | 0.74181 | 0.6957 | 0.63583 | 0.92678
2015-06-28 | 0.57289 | 0.52714 | 0.49615 | 0.47273 | 0.45847 | 0.44688 | 0.47855 | 0.49755 | 0.57411 | 0.6615 | 0.73003 | 0.79879 | 0.85324 | 0.88677 | 0.90716 | 0.92232 | 0.92051 | 0.90991 | 0.87837 | 0.83439 | 0.80939 | 0.77858 | 0.72719 | 0.66484 | 0.92232
2015-06-29 | 0.6065 | 0.56188 | 0.52859 | 0.50494 | 0.49127 | 0.48595 | 0.48424 | 0.50567 | 0.58399 | 0.67661 | 0.75981 | 0.83267 | 0.88785 | 0.91438 | 0.91555 | 0.89791 | 0.88401 | 0.86164 | 0.81697 | 0.77524 | 0.75015 | 0.72439 | 0.67445 | 0.61237 | 0.91555
2015-06-30 | 0.55751 | 0.51609 | 0.48798 | 0.47133 | 0.46926 | 0.48735 | 0.52037 | 0.55408 | 0.60971 | 0.68167 | 0.74772 | 0.8042 | 0.84905 | 0.88699 | 0.91 | 0.92124 | 0.91126 | 0.87305 | 0.83533 | 0.80028 | 0.78079 | 0.75133 | 0.70138 | 0.63641 | 0.92124
2015-07-01 | 0.57718 | 0.53535 | 0.50941 | 0.49367 | 0.48992 | 0.50797 | 0.54402 | 0.57348 | 0.61052 | 0.66195 | 0.71397 | 0.76581 | 0.79798 | 0.81232 | 0.82626 | 0.83222 | 0.84255 | 0.83615 | 0.81891 | 0.80285 | 0.79432 | 0.75999 | 0.70129 | 0.63664 | 0.84255
2015-07-02 | 0.57334 | 0.53346 | 0.50693 | 0.49245 | 0.4878 | 0.5026 | 0.5358 | 0.5696 | 0.62495 | 0.69425 | 0.76752 | 0.81774 | 0.84765 | 0.8513 | 0.83393 | 0.81742 | 0.813 | 0.80659 | 0.7941 | 0.77118 | 0.76274 | 0.74379 | 0.69687 | 0.63186 | 0.8513
2015-07-03 | 0.58042 | 0.53919 | 0.51478 | 0.49836 | 0.4957 | 0.51013 | 0.54293 | 0.57745 | 0.63326 | 0.70833 | 0.78638 | 0.84625 | 0.88803 | 0.91722 | 0.94095 | 0.95399 | 0.94876 | 0.91424 | 0.87643 | 0.83903 | 0.81584 | 0.789 | 0.7386 | 0.67562 | 0.95399
2015-07-04 | 0.61814 | 0.57091 | 0.5358 | 0.51198 | 0.49931 | 0.49899 | 0.50422 | 0.52087 | 0.58746 | 0.68158 | 0.76621 | 0.83123 | 0.86998 | 0.88871 | 0.89507 | 0.89344 | 0.84792 | 0.79189 | 0.75133 | 0.71474 | 0.69146 | 0.66182 | 0.6453 | 0.61047 | 0.89507
2015-07-05 | 0.56242 | 0.52087 | 0.49299 | 0.47449 | 0.46551 | 0.46587 | 0.47147 | 0.48748 | 0.54356 | 0.60637 | 0.67815 | 0.72809 | 0.76897 | 0.80759 | 0.81237 | 0.78408 | 0.75787 | 0.7396 | 0.7215 | 0.70247 | 0.69042 | 0.6717 | 0.63556 | 0.58715 | 0.81237
2015-07-06 | 0.54171 | 0.50458 | 0.47873 | 0.46096 | 0.45527 | 0.45622 | 0.46019 | 0.47778 | 0.54212 | 0.60628 | 0.6633 | 0.68532 | 0.70743 | 0.72732 | 0.74537 | 0.74821 | 0.74302 | 0.72917 | 0.70689 | 0.67233 | 0.6656 | 0.65144 | 0.61074 | 0.55746 | 0.74821
2015-07-07 | 0.51266 | 0.47986 | 0.45969 | 0.44963 | 0.44914 | 0.46813 | 0.50183 | 0.53792 | 0.59067 | 0.64445 | 0.698 | 0.73278 | 0.74884 | 0.76121 | 0.76554 | 0.77799 | 0.77799 | 0.77596 | 0.76694 | 0.75516 | 0.74609 | 0.72453 | 0.67409 | 0.61295 | 0.77799
2015-07-08 | 0.55593 | 0.5141 | 0.48568 | 0.46917 | 0.46448 | 0.47891 | 0.51221 | 0.5502 | 0.60497 | 0.67837 | 0.74912 | 0.81133 | 0.85956 | 0.88158 | 0.87729 | 0.85153 | 0.82469 | 0.80104 | 0.77623 | 0.74321 | 0.71568 | 0.68482 | 0.63488 | 0.57799 | 0.88158
2015-07-09 | 0.52425 | 0.48857 | 0.46529 | 0.44241 | 0.44435 | 0.46596 | 0.50147 | 0.53689 | 0.59468 | 0.66994 | 0.73635 | 0.80023 | 0.84102 | 0.85266 | 0.81693 | 0.7881 | 0.77416 | 0.75358 | 0.72859 | 0.71392 | 0.70098 | 0.71226 | 0.63087 | 0.5751 | 0.85266
2015-07-10 | 0.5188 | 0.48144 | 0.45879 | 0.44589 | 0.44205 | 0.45847 | 0.49416 | 0.5335 | 0.59116 | 0.65969 | 0.71203 | 0.74722 | 0.77925 | 0.80181 | 0.80091 | 0.78598 | 0.76328 | 0.73847 | 0.71776 | 0.69601 | 0.68997 | 0.67097 | 0.62712 | 0.57217 | 0.80181
2015-07-11 | 0.51776 | 0.48121 | 0.4578 | 0.44544 | 0.4425 | 0.45753 | 0.48843 | 0.52881 | 0.59509 | 0.66673 | 0.73499 | 0.79541 | 0.84039 | 0.8763 | 0.89723 | 0.90229 | 0.89791 | 0.88234 | 0.85685 | 0.81769 | 0.79446 | 0.76897 | 0.71983 | 0.66172 | 0.90229
2015-07-12 | 0.60601 | 0.56382 | 0.53156 | 0.51108 | 0.49502 | 0.49515 | 0.49935 | 0.51956 | 0.58313 | 0.66917 | 0.73761 | 0.79816 | 0.84625 | 0.87242 | 0.88004 | 0.87851 | 0.87156 | 0.84837 | 0.81598 | 0.77127 | 0.74853 | 0.71686 | 0.67124 | 0.61891 | 0.88004
2015-07-13 | 0.57596 | 0.54208 | 0.51744 | 0.49809 | 0.48527 | 0.48022 | 0.48126 | 0.50382 | 0.57618 | 0.65599 | 0.72214 | 0.78074 | 0.82293 | 0.844 | 0.86119 | 0.87314 | 0.87093 | 0.8546 | 0.82775 | 0.79292 | 0.77375 | 0.75304 | 0.70445 | 0.64602 | 0.87314
2015-07-14 | 0.59157 | 0.55065 | 0.51979 | 0.50273 | 0.49818 | 0.51171 | 0.54311 | 0.57727 | 0.63799 | 0.70883 | 0.77785 | 0.83452 | 0.87513 | 0.886 | 0.87783 | 0.87346 | 0.87165 | 0.8708 | 0.85947 | 0.82184 | 0.78783 | 0.75074 | 0.69385 | 0.62951 | 0.886
2015-07-15 | 0.57176 | 0.53107 | 0.50314 | 0.48514 | 0.4809 | 0.4952 | 0.5294 | 0.56233 | 0.6121 | 0.68081 | 0.7382 | 0.78656 | 0.81562 | 0.81584 | 0.80344 | 0.78088 | 0.76518 | 0.75412 | 0.74934 | 0.73125 | 0.72511 | 0.70553 | 0.65649 | 0.59788 | 0.81584
2015-07-16 | 0.54591 | 0.50544 | 0.47756 | 0.46371 | 0.46172 | 0.48099 | 0.52425 | 0.55967 | 0.62004 | 0.68857 | 0.74469 | 0.78647 | 0.81214 | 0.79283 | 0.77041 | 0.75191 | 0.73531 | 0.7197 | 0.70937 | 0.69182 | 0.69425 | 0.68144 | 0.63835 | 0.58358 | 0.81214
2015-07-17 | 0.53256 | 0.49777 | 0.47048 | 0.45699 | 0.45568 | 0.4735 | 0.51018 | 0.54126 | 0.60808 | 0.67228 | 0.73423 | 0.78688 | 0.78814 | 0.7797 | 0.76919 | 0.78629 | 0.80921 | 0.81187 | 0.80677 | 0.78566 | 0.76838 | 0.74321 | 0.68491 | 0.62545 | 0.81187
2015-07-18 | 0.56278 | 0.52114 | 0.49335 | 0.47499 | 0.46799 | 0.48162 | 0.51149 | 0.54686 | 0.61137 | 0.68943 | 0.7603 | 0.82347 | 0.87468 | 0.91221 | 0.93509 | 0.94758 | 0.94763 | 0.92376 | 0.87865 | 0.83091 | 0.80068 | 0.76797 | 0.71501 | 0.65775 | 0.94763
2015-07-19 | 0.59982 | 0.55394 | 0.52137 | 0.50048 | 0.48708 | 0.48622 | 0.49082 | 0.51343 | 0.5913 | 0.6786 | 0.75367 | 0.81697 | 0.86434 | 0.89827 | 0.9123 | 0.91708 | 0.92836 | 0.9197 | 0.88465 | 0.84661 | 0.82396 | 0.78864 | 0.73517 | 0.67937 | 0.92836
2015-07-20 | 0.6227 | 0.57862 | 0.54433 | 0.52015 | 0.50603 | 0.49998 | 0.50066 | 0.51496 | 0.58692 | 0.67792 | 0.75259 | 0.82446 | 0.87801 | 0.91329 | 0.93017 | 0.92047 | 0.91176 | 0.89786 | 0.86741 | 0.82942 | 0.81341 | 0.78489 | 0.73486 | 0.67012 | 0.93017
2015-07-21 | 0.61065 | 0.56761 | 0.53621 | 0.51677 | 0.51194 | 0.52543 | 0.55854 | 0.58895 | 0.64174 | 0.71104 | 0.78228 | 0.84102 | 0.8777 | 0.88397 | 0.86303 | 0.84174 | 0.81887 | 0.7982 | 0.777 | 0.75336 | 0.74871 | 0.71514 | 0.66588 | 0.60808 | 0.88397
2015-07-22 | 0.55137 | 0.51176 | 0.48897 | 0.47264 | 0.4702 | 0.49064 | 0.52475 | 0.55877 | 0.61679 | 0.68198 | 0.74036 | 0.78395 | 0.81007 | 0.82464 | 0.84463 | 0.85627 | 0.84742 | 0.82103 | 0.79766 | 0.77149 | 0.76405 | 0.73581 | 0.6832 | 0.62545 | 0.85627
2015-07-23 | 0.57307 | 0.53391 | 0.50657 | 0.48924 | 0.48482 | 0.49935 | 0.53829 | 0.56869 | 0.6259 | 0.68437 | 0.73558 | 0.77628 | 0.80723 | 0.83646 | 0.8647 | 0.87914 | 0.88456 | 0.88 | 0.87648 | 0.84467 | 0.82523 | 0.79572 | 0.73486 | 0.67165 | 0.88456
2015-07-24 | 0.61142 | 0.56445 | 0.53247 | 0.51261 | 0.50558 | 0.51834 | 0.5469 | 0.57948 | 0.63926 | 0.71451 | 0.78187 | 0.72353 | 0.87621 | 0.89836 | 0.91135 | 0.92372 | 0.94068 | 0.93089 | 0.9156 | 0.87824 | 0.84404 | 0.81034 | 0.74334 | 0.67449 | 0.94068
2015-07-25 | 0.6162 | 0.56752 | 0.53567 | 0.51379 | 0.50323 | 0.51586 | 0.54433 | 0.57857 | 0.64747 | 0.72362 | 0.79134 | 0.85239 | 0.88893 | 0.90869 | 0.92674 | 0.94361 | 0.94591 | 0.92891 | 0.89353 | 0.84986 | 0.82667 | 0.79085 | 0.73833 | 0.68067 | 0.94591
2015-07-26 | 0.62924 | 0.58593 | 0.55742 | 0.53314 | 0.51825 | 0.51577 | 0.52218 | 0.53932 | 0.60298 | 0.68744 | 0.76369 | 0.81381 | 0.83493 | 0.84652 | 0.84309 | 0.83033 | 0.83046 | 0.82094 | 0.79978 | 0.77028 | 0.76252 | 0.73175 | 0.6837 | 0.6384 | 0.84652
2015-07-27 | 0.589 | 0.54979 | 0.52254 | 0.50251 | 0.49182 | 0.48875 | 0.49123 | 0.50684 | 0.58593 | 0.67535 | 0.74898 | 0.8139 | 0.8652 | 0.90441 | 0.92954 | 0.94623 | 0.95182 | 0.94546 | 0.9169 | 0.87454 | 0.855 | 0.82225 | 0.76446 | 0.70174 | 0.95182
2015-07-28 | 0.63926 | 0.5968 | 0.56472 | 0.5446 | 0.53892 | 0.55335 | 0.58363 | 0.61336 | 0.67467 | 0.75227 | 0.81986 | 0.8823 | 0.92426 | 0.96279 | 0.99721 | 1.0163 | 1.0232 | 1.0156 | 0.99608 | 0.95751 | 0.93378 | 0.89498 | 0.82342 | 0.74754 | 1.0232
2015-07-29 | 0.68018 | 0.63244 | 0.59802 | 0.57686 | 0.56748 | 0.57794 | 0.60555 | 0.63186 | 0.69295 | 0.76301 | 0.82911 | 0.88749 | 0.92566 | 0.95146 | 0.96419 | 0.95426 | 0.94452 | 0.91126 | 0.87043 | 0.83407 | 0.81873 | 0.78683 | 0.72814 | 0.67084 | 0.96419
2015-07-30 | 0.61322 | 0.57465 | 0.54505 | 0.52782 | 0.52096 | 0.53495 | 0.57023 | 0.59788 | 0.65708 | 0.72259 | 0.77623 | 0.838 | 0.88974 | 0.93473 | 0.95823 | 0.96013 | 0.93224 | 0.88613 | 0.85288 | 0.82013 | 0.79951 | 0.76856 | 0.70914 | 0.64891 | 0.96013
2015-07-31 | 0.59026 | 0.54848 | 0.51992 | 0.50291 | 0.497 | 0.50991 | 0.54415 | 0.57032 | 0.6227 | 0.69759 | 0.77542 | 0.84409 | 0.88862 | 0.91785 | 0.92787 | 0.91659 | 0.88126 | 0.84797 | 0.81977 | 0.78801 | 0.7784 | 0.75065 | 0.69845 | 0.63844 | 0.92787
2015-08-01 | 0.5867 | 0.54762 | 0.516 | 0.50183 | 0.49403 | 0.50833 | 0.5377 | 0.57411 | 0.6361 | 0.7142 | 0.78295 | 0.84242 | 0.8869 | 0.91803 | 0.94384 | 0.95764 | 0.95566 | 0.92859 | 0.88839 | 0.84896 | 0.83263 | 0.79897 | 0.74027 | 0.6823 | 0.95764
2015-08-02 | 0.62685 | 0.58106 | 0.54889 | 0.52651 | 0.51401 | 0.51289 | 0.52024 | 0.53648 | 0.60592 | 0.6901 | 0.76319 | 0.8185 | 0.861 | 0.88492 | 0.90626 | 0.90531 | 0.898 | 0.87919 | 0.84548 | 0.81106 | 0.7978 | 0.77113 | 0.72033 | 0.66876 | 0.90626
2015-08-03 | 0.61629 | 0.57555 | 0.54505 | 0.52471 | 0.51252 | 0.51104 | 0.51645 | 0.52453 | 0.57948 | 0.64851 | 0.69994 | 0.75444 | 0.78047 | 0.78819 | 0.79098 | 0.79789 | 0.80362 | 0.79649 | 0.77763 | 0.75913 | 0.74275 | 0.71194 | 0.65938 | 0.60104 | 0.80362
2015-08-04 | 0.54582 | 0.5086 | 0.48437 | 0.47002 | 0.46903 | 0.4883 | 0.52538 | 0.55286 | 0.60551 | 0.67124 | 0.73558 | 0.79022 | 0.80511 | 0.79834 | 0.77443 | 0.75006 | 0.72584 | 0.69881 | 0.68158 | 0.66849 | 0.67729 | 0.6559 | 0.61449 | 0.56743 | 0.80511
2015-08-05 | 0.52119 | 0.48951 | 0.47093 | 0.46069 | 0.46014 | 0.47729 | 0.51717 | 0.54952 | 0.60745 | 0.67973 | 0.74063 | 0.79721 | 0.84179 | 0.86836 | 0.86299 | 0.85888 | 0.86294 | 0.86669 | 0.85203 | 0.81932 | 0.80438 | 0.76603 | 0.70364 | 0.64129 | 0.86836
2015-08-06 | 0.57857 | 0.53734 | 0.50761 | 0.48884 | 0.48527 | 0.4989 | 0.53296 | 0.56563 | 0.62951 | 0.70671 | 0.77555 | 0.84751 | 0.8966 | 0.93743 | 0.96261 | 0.96464 | 0.94307 | 0.91948 | 0.88735 | 0.85527 | 0.84066 | 0.80524 | 0.73662 | 0.673 | 0.96464
2015-08-07 | 0.60993 | 0.56608 | 0.53675 | 0.51726 | 0.51009 | 0.52367 | 0.55742 | 0.58679 | 0.65433 | 0.73346 | 0.80366 | 0.86971 | 0.92065 | 0.95548 | 0.96265 | 0.95846 | 0.95155 | 0.93951 | 0.90738 | 0.87043 | 0.83646 | 0.78909 | 0.71668 | 0.64986 | 0.96265
2015-08-08 | 0.58954 | 0.54374 | 0.51618 | 0.49949 | 0.492 | 0.51902 | 0.54032 | 0.5691 | 0.61544 | 0.68329 | 0.74551 | 0.8116 | 0.87052 | 0.91889 | 0.94366 | 0.94515 | 0.93703 | 0.90206 | 0.85888 | 0.81846 | 0.80389 | 0.76973 | 0.71726 | 0.66836 | 0.94515
2015-08-09 | 0.60677 | 0.56414 | 0.53215 | 0.51153 | 0.50143 | 0.50143 | 0.50819 | 0.52868 | 0.60564 | 0.69606 | 0.7719 | 0.83736 | 0.88577 | 0.91772 | 0.93969 | 0.95264 | 0.95083 | 0.92322 | 0.87756 | 0.83299 | 0.81598 | 0.77948 | 0.7262 | 0.67661 | 0.95264
2015-08-10 | 0.62216 | 0.58061 | 0.54659 | 0.52471 | 0.51144 | 0.5067 | 0.50887 | 0.52114 | 0.59473 | 0.68528 | 0.76306 | 0.83777 | 0.88925 | 0.92769 | 0.94605 | 0.94966 | 0.94646 | 0.93378 | 0.89953 | 0.85537 | 0.83488 | 0.79139 | 0.72764 | 0.66191 | 0.94966
2015-08-11 | 0.60055 | 0.55575 | 0.52484 | 0.50598 | 0.49989 | 0.51631 | 0.55024 | 0.57542 | 0.63375 | 0.71478 | 0.78945 | 0.86335 | 0.91898 | 0.95408 | 0.96301 | 0.96053 | 0.96184 | 0.95336 | 0.92778 | 0.88821 | 0.87224 | 0.82135 | 0.75864 | 0.68577 | 0.96301
2015-08-12 | 0.62198 | 0.57812 | 0.54307 | 0.52155 | 0.51446 | 0.52818 | 0.56206 | 0.58945 | 0.64855 | 0.72498 | 0.79333 | 0.85491 | 0.89904 | 0.93297 | 0.94533 | 0.94438 | 0.95173 | 0.94682 | 0.92958 | 0.89182 | 0.86836 | 0.82112 | 0.75503 | 0.68943 | 0.95173
2015-08-13 | 0.62473 | 0.58399 | 0.55227 | 0.52601 | 0.51916 | 0.53359 | 0.56887 | 0.59707 | 0.66136 | 0.73887 | 0.80894 | 0.88104 | 0.93265 | 0.96825 | 0.98616 | 0.99541 | 0.99536 | 0.97366 | 0.94014 | 0.89642 | 0.87815 | 0.83542 | 0.76838 | 0.7017 | 0.99541
2015-08-14 | 0.64174 | 0.60041 | 0.57122 | 0.55218 | 0.54365 | 0.55457 | 0.58855 | 0.61422 | 0.67594 | 0.7553 | 0.82708 | 0.88311 | 0.93103 | 0.95629 | 0.95981 | 0.92746 | 0.87932 | 0.84228 | 0.8112 | 0.78471 | 0.7793 | 0.74302 | 0.69349 | 0.63091 | 0.95981
2015-08-15 | 0.57673 | 0.53982 | 0.51113 | 0.49795 | 0.49448 | 0.51212 | 0.55105 | 0.58358 | 0.64697 | 0.71532 | 0.78043 | 0.82712 | 0.86236 | 0.85496 | 0.79261 | 0.75263 | 0.72584 | 0.70729 | 0.68406 | 0.66177 | 0.66479 | 0.64138 | 0.60835 | 0.56599 | 0.86236
2015-08-16 | 0.52209 | 0.4929 | 0.473 | 0.45969 | 0.45288 | 0.45536 | 0.46786 | 0.48825 | 0.55917 | 0.65789 | 0.73914 | 0.79811 | 0.85279 | 0.86245 | 0.88947 | 0.86904 | 0.8319 | 0.79319 | 0.75633 | 0.72484 | 0.71614 | 0.69069 | 0.65293 | 0.60149 | 0.88947
2015-08-17 | 0.55457 | 0.5197 | 0.49358 | 0.47526 | 0.46754 | 0.4679 | 0.47625 | 0.49218 | 0.55927 | 0.65333 | 0.73779 | 0.80511 | 0.86037 | 0.9063 | 0.91388 | 0.90531 | 0.90969 | 0.90802 | 0.88794 | 0.85487 | 0.8444 | 0.8065 | 0.74185 | 0.6661 | 0.91388
2015-08-18 | 0.60898 | 0.5636 | 0.53301 | 0.5146 | 0.51058 | 0.53598 | 0.57939 | 0.59865 | 0.64481 | 0.7248 | 0.80032 | 0.86813 | 0.91853 | 0.95886 | 0.977 | 0.99171 | 0.99405 | 0.98444 | 0.9636 | 0.9262 | 0.91135 | 0.85631 | 0.77731 | 0.70783 | 0.99405
2015-08-19 | 0.64038 | 0.59509 | 0.56247 | 0.54162 | 0.53531 | 0.55606 | 0.60055 | 0.61792 | 0.66655 | 0.74357 | 0.81187 | 0.87842 | 0.93098 | 0.9664 | 0.98711 | 1.0119 | 1.0245 | 1.0116 | 0.98729 | 0.94474 | 0.92746 | 0.87585 | 0.79757 | 0.72453 | 1.0245
2015-08-20 | 0.6583 | 0.61237 | 0.58042 | 0.55638 | 0.54857 | 0.56684 | 0.60898 | 0.56139 | 0.6712 | 0.74871 | 0.81629 | 0.88672 | 0.93152 | 0.97452 | 0.99193 | 0.99536 | 0.99401 | 0.98061 | 0.95155 | 0.91555 | 0.89931 | 0.85388 | 0.78304 | 0.70986 | 0.99536
2015-08-21 | 0.65248 | 0.60713 | 0.57501 | 0.55435 | 0.54596 | 0.5654 | 0.61002 | 0.62987 | 0.67937 | 0.7502 | 0.82144 | 0.88916 | 0.93694 | 0.97804 | 1.001 | 1.0242 | 1.025 | 0.99108 | 0.95525 | 0.90576 | 0.89444 | 0.84427 | 0.77709 | 0.70422 | 1.025
2015-08-22 | 0.63804 | 0.59495 | 0.56382 | 0.54411 | 0.53608 | 0.55444 | 0.59928 | 0.61846 | 0.66714 | 0.74478 | 0.81318 | 0.87792 | 0.92854 | 0.96464 | 0.97799 | 1.0066 | 1.0139 | 0.99365 | 0.96071 | 0.91113 | 0.88419 | 0.83177 | 0.77086 | 0.70946 | 1.0139
2015-08-23 | 0.64778 | 0.60416 | 0.56883 | 0.54447 | 0.52935 | 0.528 | 0.53499 | 0.54997 | 0.61941 | 0.71532 | 0.79531 | 0.86525 | 0.91772 | 0.95282 | 0.96852 | 0.9812 | 0.98841 | 0.97831 | 0.94618 | 0.89872 | 0.87598 | 0.8338 | 0.78173 | 0.71979 | 0.98841
2015-08-24 | 0.65699 | 0.61016 | 0.57357 | 0.54821 | 0.53274 | 0.52678 | 0.5275 | 0.53698 | 0.61133 | 0.70594 | 0.78201 | 0.85902 | 0.9188 | 0.96103 | 0.98634 | 0.99951 | 1.0009 | 0.99347 | 0.96369 | 0.92286 | 0.90504 | 0.85085 | 0.78101 | 0.71185 | 1.0009
2015-08-25 | 0.65717 | 0.61025 | 0.583 | 0.56666 | 0.56572 | 0.59067 | 0.63691 | 0.655 | 0.68861 | 0.75566 | 0.82017 | 0.87522 | 0.90932 | 0.92263 | 0.92557 | 0.92475 | 0.92742 | 0.91699 | 0.88591 | 0.85703 | 0.84968 | 0.79933 | 0.73716 | 0.66637 | 0.92742
2015-08-26 | 0.61516 | 0.5783 | 0.55236 | 0.53693 | 0.53414 | 0.55755 | 0.60474 | 0.62189 | 0.65924 | 0.72809 | 0.78801 | 0.84215 | 0.87986 | 0.91316 | 0.93545 | 0.95327 | 0.96238 | 0.95458 | 0.92782 | 0.88708 | 0.87219 | 0.82166 | 0.74456 | 0.67576 | 0.96238
2015-08-27 | 0.60907 | 0.56445 | 0.53192 | 0.51225 | 0.50494 | 0.52534 | 0.57154 | 0.58724 | 0.63055 | 0.70594 | 0.77082 | 0.83236 | 0.88117 | 0.92051 | 0.95061 | 0.97199 | 0.98453 | 0.97673 | 0.95047 | 0.90689 | 0.89263 | 0.84169 | 0.76779 | 0.70057 | 0.98453
2015-08-28 | 0.63826 | 0.59504 | 0.56283 | 0.54126 | 0.53233 | 0.55277 | 0.60082 | 0.61837 | 0.66019 | 0.72038 | 0.7673 | 0.80705 | 0.85225 | 0.89773 | 0.93856 | 0.96392 | 0.97497 | 0.95607 | 0.91722 | 0.88537 | 0.86583 | 0.81165 | 0.74546 | 0.68063 | 0.97497
2015-08-29 | 0.61724 | 0.57654 | 0.54875 | 0.52953 | 0.52439 | 0.54532 | 0.59364 | 0.61706 | 0.66484 | 0.74284 | 0.81422 | 0.86714 | 0.90522 | 0.94109 | 0.96626 | 0.98043 | 0.97569 | 0.94443 | 0.90427 | 0.86407 | 0.84869 | 0.80154 | 0.74618 | 0.69403 | 0.98043
2015-08-30 | 0.64183 | 0.60104 | 0.57118 | 0.54938 | 0.53986 | 0.54893 | 0.55218 | 0.56351 | 0.62175 | 0.71122 | 0.78625 | 0.85577 | 0.9017 | 0.93689 | 0.96283 | 0.97398 | 0.97244 | 0.94564 | 0.89823 | 0.85731 | 0.84206 | 0.79712 | 0.7465 | 0.69741 | 0.97398
2015-08-31 | 0.64363 | 0.59955 | 0.56612 | 0.54578 | 0.53134 | 0.52502 | 0.52886 | 0.53937 | 0.60772 | 0.70454 | 0.77582 | 0.83822 | 0.88911 | 0.92349 | 0.93874 | 0.94366 | 0.93337 | 0.9132 | 0.87043 | 0.82987 | 0.81778 | 0.77537 | 0.72353 | 0.66858 | 0.94366
2015-09-01 | 0.61643 | 0.58029 | 0.5525 | 0.5317 | 0.52489 | 0.52895 | 0.54131 | 0.5469 | 0.6111 | 0.70671 | 0.78534 | 0.85943 | 0.89999 | 0.93075 | 0.9571 | 0.96608 | 0.95886 | 0.94068 | 0.90955 | 0.87098 | 0.85902 | 0.80871 | 0.74086 | 0.67747 | 0.96608
2015-09-02 | 0.61765 | 0.57546 | 0.54559 | 0.52791 | 0.52191 | 0.5428 | 0.58832 | 0.60637 | 0.64575 | 0.71776 | 0.78106 | 0.84526 | 0.89042 | 0.91799 | 0.94749 | 0.9645 | 0.96807 | 0.95255 | 0.91776 | 0.87901 | 0.85609 | 0.79301 | 0.7188 | 0.64602 | 0.96807
2015-09-03 | 0.58498 | 0.54343 | 0.5164 | 0.49867 | 0.49394 | 0.5151 | 0.56427 | 0.58227 | 0.61895 | 0.68203 | 0.72584 | 0.77149 | 0.81449 | 0.85938 | 0.89146 | 0.90215 | 0.9086 | 0.89353 | 0.86664 | 0.83145 | 0.82063 | 0.77249 | 0.7068 | 0.63533 | 0.9086
2015-09-04 | 0.57673 | 0.53553 | 0.50864 | 0.49204 | 0.48748 | 0.50846 | 0.55945 | 0.57673 | 0.60339 | 0.65924 | 0.71762 | 0.76549 | 0.80515 | 0.84219 | 0.85767 | 0.86416 | 0.87192 | 0.86019 | 0.8389 | 0.81932 | 0.81372 | 0.7654 | 0.6989 | 0.63565 | 0.87192
2015-09-05 | 0.5779 | 0.53865 | 0.51365 | 0.498 | 0.49552 | 0.51735 | 0.57059 | 0.58918 | 0.62829 | 0.69967 | 0.76784 | 0.82825 | 0.87878 | 0.91672 | 0.93811 | 0.93942 | 0.91875 | 0.87707 | 0.83281 | 0.80262 | 0.78489 | 0.74009 | 0.69069 | 0.64192 | 0.93942
2015-09-06 | 0.59053 | 0.5566 | 0.53021 | 0.51198 | 0.50319 | 0.50305 | 0.51401 | 0.53188 | 0.58818 | 0.66168 | 0.71794 | 0.76035 | 0.78498 | 0.78178 | 0.77402 | 0.76382 | 0.74402 | 0.72809 | 0.70946 | 0.6998 | 0.69989 | 0.67269 | 0.63908 | 0.60091 | 0.78498
2015-09-07 | 0.55823 | 0.51997 | 0.4938 | 0.47562 | 0.46872 | 0.46993 | 0.47936 | 0.49155 | 0.54528 | 0.61462 | 0.67652 | 0.73761 | 0.78706 | 0.82072 | 0.83633 | 0.82568 | 0.80691 | 0.78088 | 0.7419 | 0.72913 | 0.72854 | 0.69087 | 0.63759 | 0.5811 | 0.83633
2015-09-08 | 0.53459 | 0.50291 | 0.47828 | 0.46344 | 0.46249 | 0.48902 | 0.53977 | 0.55859 | 0.58909 | 0.66055 | 0.7322 | 0.79432 | 0.84309 | 0.87982 | 0.90657 | 0.91776 | 0.91654 | 0.90648 | 0.8694 | 0.84824 | 0.83348 | 0.77984 | 0.7132 | 0.64643 | 0.91776
2015-09-09 | 0.58818 | 0.54609 | 0.51952 | 0.50255 | 0.49556 | 0.51591 | 0.56531 | 0.583 | 0.61372 | 0.67797 | 0.74442 | 0.80335 | 0.85234 | 0.89466 | 0.91384 | 0.93405 | 0.92913 | 0.9077 | 0.87269 | 0.84422 | 0.82432 | 0.76486 | 0.69565 | 0.62965 | 0.93405
2015-09-10 | 0.57533 | 0.53946 | 0.51532 | 0.49813 | 0.49443 | 0.5178 | 0.56815 | 0.58458 | 0.6148 | 0.67174 | 0.73653 | 0.78859 | 0.83407 | 0.87301 | 0.89547 | 0.90585 | 0.90179 | 0.88316 | 0.85203 | 0.82848 | 0.81431 | 0.7557 | 0.68952 | 0.62238 | 0.90585
2015-09-11 | 0.56599 | 0.52908 | 0.50264 | 0.486 | 0.48221 | 0.50436 | 0.55557 | 0.57388 | 0.60163 | 0.66317 | 0.71889 | 0.76621 | 0.80073 | 0.82514 | 0.83348 | 0.83606 | 0.8204 | 0.7894 | 0.76089 | 0.74474 | 0.73662 | 0.69367 | 0.64485 | 0.58602 | 0.83606
2015-09-12 | 0.52628 | 0.49592 | 0.47418 | 0.46308 | 0.46308 | 0.48812 | 0.54379 | 0.55976 | 0.59247 | 0.64639 | 0.69543 | 0.7363 | 0.77623 | 0.81381 | 0.82311 | 0.81954 | 0.82211 | 0.82518 | 0.7968 | 0.76468 | 0.75169 | 0.71298 | 0.66948 | 0.61625 | 0.82518
2015-09-13 | 0.55796 | 0.51902 | 0.49141 | 0.46908 | 0.45996 | 0.45911 | 0.47147 | 0.48825 | 0.53856 | 0.61029 | 0.68491 | 0.75088 | 0.80086 | 0.83159 | 0.84391 | 0.84251 | 0.825 | 0.79996 | 0.75746 | 0.73567 | 0.72196 | 0.67869 | 0.62699 | 0.57325 | 0.84391
2015-09-14 | 0.52976 | 0.49434 | 0.46881 | 0.45153 | 0.44124 | 0.43953 | 0.44652 | 0.45622 | 0.51717 | 0.59798 | 0.67264 | 0.74104 | 0.79139 | 0.82464 | 0.84138 | 0.84697 | 0.84783 | 0.82608 | 0.78724 | 0.76432 | 0.752 | 0.70607 | 0.6504 | 0.58634 | 0.84783
2015-09-15 | 0.53752 | 0.50147 | 0.47905 | 0.46642 | 0.46592 | 0.49024 | 0.54072 | 0.56066 | 0.59446 | 0.66339 | 0.74515 | 0.80578 | 0.85546 | 0.89823 | 0.928 | 0.94776 | 0.95128 | 0.93829 | 0.90517 | 0.87986 | 0.861 | 0.80127 | 0.73427 | 0.65446 | 0.95128
2015-09-16 | 0.59184 | 0.55223 | 0.5215 | 0.50192 | 0.49642 | 0.51622 | 0.56599 | 0.58381 | 0.61571 | 0.679 | 0.74745 | 0.8093 | 0.85568 | 0.88983 | 0.88379 | 0.86511 | 0.84977 | 0.83177 | 0.81133 | 0.80326 | 0.78728 | 0.73441 | 0.67364 | 0.60952 | 0.88983
2015-09-17 | 0.54988 | 0.51293 | 0.48676 | 0.47025 | 0.4689 | 0.49385 | 0.54772 | 0.56576 | 0.59279 | 0.64323 | 0.7063 | 0.75381 | 0.78792 | 0.80596 | 0.82572 | 0.82455 | 0.79653 | 0.76414 | 0.74172 | 0.74551 | 0.7391 | 0.69827 | 0.63948 | 0.5751 | 0.82572
2015-09-18 | 0.52543 | 0.48789 | 0.46808 | 0.45441 | 0.45324 | 0.47787 | 0.53233 | 0.55065 | 0.57871 | 0.63312 | 0.68496 | 0.73811 | 0.78837 | 0.83389 | 0.86583 | 0.8837 | 0.8777 | 0.8804 | 0.84174 | 0.81869 | 0.7982 | 0.74533 | 0.68076 | 0.61273 | 0.8837
2015-09-19 | 0.5566 | 0.51618 | 0.49155 | 0.47571 | 0.47282 | 0.49561 | 0.54889 | 0.57122 | 0.59937 | 0.65843 | 0.7072 | 0.73734 | 0.74627 | 0.73157 | 0.70653 | 0.6948 | 0.68406 | 0.67346 | 0.66082 | 0.6656 | 0.66015 | 0.63213 | 0.59193 | 0.54699 | 0.74627
2015-09-20 | 0.50152 | 0.47043 | 0.44981 | 0.4384 | 0.43258 | 0.43835 | 0.45586 | 0.47851 | 0.52083 | 0.58494 | 0.64151 | 0.68591 | 0.71853 | 0.73982 | 0.74226 | 0.70928 | 0.68171 | 0.66791 | 0.64611 | 0.6509 | 0.64611 | 0.61318 | 0.57307 | 0.53044 | 0.74226
2015-09-21 | 0.48983 | 0.45613 | 0.43402 | 0.41967 | 0.41349 | 0.41507 | 0.42653 | 0.43957 | 0.48938 | 0.56549 | 0.6347 | 0.69849 | 0.74943 | 0.78489 | 0.80871 | 0.81769 | 0.81643 | 0.79969 | 0.76202 | 0.7446 | 0.72543 | 0.67409 | 0.61868 | 0.55566 | 0.81769
2015-09-22 | 0.5049 | 0.4698 | 0.44652 | 0.43682 | 0.43921 | 0.4689 | 0.52209 | 0.54618 | 0.57713 | 0.63258 | 0.68794 | 0.73644 | 0.77271 | 0.78025 | 0.77073 | 0.75859 | 0.75169 | 0.73815 | 0.72972 | 0.73481 | 0.71749 | 0.66948 | 0.61038 | 0.55011 | 0.78025
2015-09-23 | 0.49917 | 0.4642 | 0.44074 | 0.42852 | 0.42983 | 0.46118 | 0.52092 | 0.54654 | 0.5594 | 0.59617 | 0.62261 | 0.65401 | 0.6767 | 0.68158 | 0.68406 | 0.68956 | 0.69701 | 0.70905 | 0.70116 | 0.71162 | 0.70247 | 0.65906 | 0.60483 | 0.54379 | 0.71162
2015-09-24 | 0.49218 | 0.45834 | 0.4416 | 0.42847 | 0.42712 | 0.45775 | 0.51627 | 0.5414 | 0.56161 | 0.59883 | 0.63429 | 0.66939 | 0.69286 | 0.72137 | 0.75354 | 0.77885 | 0.78119 | 0.77095 | 0.75295 | 0.75263 | 0.74239 | 0.69998 | 0.63858 | 0.58061 | 0.78119
2015-09-25 | 0.53048 | 0.49376 | 0.4698 | 0.45473 | 0.45383 | 0.47408 | 0.51857 | 0.54623 | 0.57907 | 0.63768 | 0.69498 | 0.73256 | 0.75263 | 0.77037 | 0.79396 | 0.81318 | 0.79938 | 0.76233 | 0.73702 | 0.73301 | 0.71911 | 0.67499 | 0.61918 | 0.56608 | 0.81318
2015-09-26 | 0.51726 | 0.48446 | 0.46308 | 0.45035 | 0.45008 | 0.47742 | 0.53197 | 0.55841 | 0.58015 | 0.62117 | 0.67364 | 0.73256 | 0.77677 | 0.82004 | 0.83502 | 0.83642 | 0.82121 | 0.79157 | 0.76071 | 0.75593 | 0.73802 | 0.70007 | 0.65045 | 0.63447 | 0.83642
2015-09-27 | 0.57542 | 0.52092 | 0.4989 | 0.48302 | 0.47684 | 0.47954 | 0.4933 | 0.5104 | 0.5654 | 0.64503 | 0.71189 | 0.77397 | 0.82248 | 0.85532 | 0.87815 | 0.87928 | 0.85063 | 0.8204 | 0.77948 | 0.76919 | 0.74487 | 0.70729 | 0.65852 | 0.60402 | 0.87928
2015-09-28 | 0.55557 | 0.52033 | 0.49439 | 0.47639 | 0.46804 | 0.46917 | 0.47851 | 0.49448 | 0.54438 | 0.62338 | 0.69425 | 0.75832 | 0.81192 | 0.84973 | 0.87328 | 0.88054 | 0.87052 | 0.84129 | 0.79703 | 0.79613 | 0.7788 | 0.73062 | 0.66858 | 0.60307 | 0.88054
2015-09-29 | 0.55363 | 0.51392 | 0.49096 | 0.47639 | 0.47643 | 0.50088 | 0.55349 | 0.57587 | 0.6038 | 0.66732 | 0.73468 | 0.80019 | 0.84016 | 0.8735 | 0.89015 | 0.89001 | 0.87869 | 0.84806 | 0.81381 | 0.79974 | 0.75746 | 0.70616 | 0.6421 | 0.58033 | 0.89015
2015-09-30 | 0.52669 | 0.49127 | 0.4693 | 0.45617 | 0.45604 | 0.48243 | 0.54226 | 0.56233 | 0.59504 | 0.6573 | 0.7183 | 0.76991 | 0.81097 | 0.82455 | 0.83691 | 0.81751 | 0.81485 | 0.80894 | 0.7867 | 0.7894 | 0.77181 | 0.72552 | 0.66312 | 0.59788 | 0.83691
2015-10-01 | 0.54523 | 0.50797 | 0.48663 | 0.47359 | 0.47142 | 0.49881 | 0.55692 | 0.57686 | 0.61043 | 0.67255 | 0.72976 | 0.78548 | 0.82978 | 0.8624 | 0.87639 | 0.90021 | 0.9142 | 0.90008 | 0.86606 | 0.84905 | 0.82595 | 0.77208 | 0.70016 | 0.66294 | 0.9142
2015-10-02 | 0.58602 | 0.53729 | 0.51117 | 0.49452 | 0.49024 | 0.51275 | 0.56594 | 0.58471 | 0.61932 | 0.68609 | 0.75313 | 0.80822 | 0.85288 | 0.89836 | 0.9229 | 0.94014 | 0.9502 | 0.93319 | 0.89426 | 0.8744 | 0.84842 | 0.78891 | 0.72241 | 0.64923 | 0.9502
2015-10-03 | 0.59098 | 0.55065 | 0.51952 | 0.50161 | 0.49461 | 0.51474 | 0.56594 | 0.58809 | 0.62658 | 0.69737 | 0.76621 | 0.82888 | 0.8712 | 0.91686 | 0.93996 | 0.95237 | 0.95178 | 0.91311 | 0.85735 | 0.82649 | 0.78593 | 0.73639 | 0.68031 | 0.62405 | 0.95237
2015-10-04 | 0.57104 | 0.52917 | 0.50246 | 0.48383 | 0.47476 | 0.47792 | 0.49195 | 0.50955 | 0.56829 | 0.64521 | 0.70364 | 0.75457 | 0.79753 | 0.8232 | 0.83258 | 0.82699 | 0.80741 | 0.7779 | 0.73955 | 0.73292 | 0.71122 | 0.66989 | 0.61927 | 0.56644 | 0.83258
2015-10-05 | 0.51194 | 0.4666 | 0.43258 | 0.40587 | 0.39112 | 0.38719 | 0.39391 | 0.40036 | 0.43398 | 0.48388 | 0.53265 | 0.56707 | 0.60411 | 0.63678 | 0.66394 | 0.68379 | 0.70301 | 0.69547 | 0.66601 | 0.66357 | 0.64688 | 0.60181 | 0.54722 | 0.48915 | 0.70301
2015-10-06 | 0.44246 | 0.40939 | 0.38922 | 0.37875 | 0.38124 | 0.41273 | 0.46736 | 0.49109 | 0.51424 | 0.55692 | 0.6001 | 0.6384 | 0.67837 | 0.70774 | 0.7372 | 0.74636 | 0.75647 | 0.7423 | 0.72791 | 0.74289 | 0.71965 | 0.67043 | 0.61525 | 0.55381 | 0.75647
2015-10-07 | 0.49967 | 0.46718 | 0.44616 | 0.43267 | 0.42965 | 0.45487 | 0.51221 | 0.53824 | 0.55006 | 0.59238 | 0.63786 | 0.66985 | 0.69592 | 0.71776 | 0.72868 | 0.72371 | 0.72308 | 0.71442 | 0.70779 | 0.72489 | 0.70544 | 0.6707 | 0.61025 | 0.54199 | 0.72868
2015-10-08 | 0.4915 | 0.45875 | 0.43528 | 0.4236 | 0.42495 | 0.45378 | 0.51176 | 0.53386 | 0.55656 | 0.60862 | 0.66678 | 0.71519 | 0.76017 | 0.79473 | 0.82284 | 0.83551 | 0.83443 | 0.8209 | 0.79626 | 0.79649 | 0.77352 | 0.7229 | 0.66073 | 0.59798 | 0.83551
2015-10-09 | 0.54063 | 0.50427 | 0.47896 | 0.46032 | 0.45739 | 0.45216 | 0.53152 | 0.55263 | 0.57948 | 0.64192 | 0.70125 | 0.75363 | 0.79279 | 0.83033 | 0.85591 | 0.87283 | 0.8758 | 0.85956 | 0.82306 | 0.81503 | 0.78792 | 0.73486 | 0.6753 | 0.60596 | 0.8758
2015-10-10 | 0.54713 | 0.50472 | 0.47932 | 0.46105 | 0.45775 | 0.48004 | 0.53287 | 0.55656 | 0.5857 | 0.64882 | 0.71081 | 0.75868 | 0.80082 | 0.83565 | 0.85929 | 0.87526 | 0.87842 | 0.85618 | 0.81079 | 0.79477 | 0.76441 | 0.71844 | 0.66682 | 0.61169 | 0.87842
2015-10-11 | 0.55755 | 0.51794 | 0.49263 | 0.47363 | 0.46299 | 0.46353 | 0.47612 | 0.48924 | 0.5428 | 0.6268 | 0.69619 | 0.75439 | 0.79915 | 0.83303 | 0.85604 | 0.87066 | 0.87346 | 0.85433 | 0.80592 | 0.78413 | 0.75354 | 0.70684 | 0.66042 | 0.60497 | 0.87346
2015-10-12 | 0.55462 | 0.51383 | 0.48293 | 0.46353 | 0.45419 | 0.45243 | 0.46145 | 0.46826 | 0.5266 | 0.61629 | 0.6887 | 0.74921 | 0.80019 | 0.83308 | 0.85487 | 0.8666 | 0.86791 | 0.85099 | 0.81034 | 0.80682 | 0.77754 | 0.72687 | 0.67404 | 0.61282 | 0.86791
2015-10-13 | 0.56148 | 0.52457 | 0.50129 | 0.48748 | 0.4878 | 0.51298 | 0.56265 | 0.58336 | 0.61079 | 0.66885 | 0.73387 | 0.78543 | 0.82139 | 0.85031 | 0.86985 | 0.88262 | 0.8809 | 0.86276 | 0.82798 | 0.8264 | 0.79581 | 0.74591 | 0.68541 | 0.6204 | 0.88262
2015-10-14 | 0.56558 | 0.53084 | 0.5095 | 0.49511 | 0.49168 | 0.51767 | 0.57393 | 0.59545 | 0.62288 | 0.68279 | 0.74032 | 0.78828 | 0.82184 | 0.85771 | 0.87707 | 0.8823 | 0.87188 | 0.8449 | 0.82067 | 0.82672 | 0.79265 | 0.73969 | 0.67643 | 0.60885 | 0.8823
2015-10-15 | 0.54672 | 0.50657 | 0.4827 | 0.46777 | 0.46808 | 0.49299 | 0.54749 | 0.57221 | 0.5973 | 0.64972 | 0.69877 | 0.74515 | 0.6971 | 0.80339 | 0.81043 | 0.81553 | 0.80321 | 0.78354 | 0.75958 | 0.76536 | 0.73351 | 0.6851 | 0.62094 | 0.55773 | 0.81553
2015-10-16 | 0.50183 | 0.46466 | 0.44165 | 0.42595 | 0.41895 | 0.43826 | 0.48609 | 0.50269 | 0.51929 | 0.5599 | 0.59825 | 0.62802 | 0.65879 | 0.69001 | 0.71794 | 0.74555 | 0.76116 | 0.75327 | 0.72164 | 0.71866 | 0.68866 | 0.63623 | 0.57388 | 0.50774 | 0.76116
2015-10-17 | 0.45035 | 0.41119 | 0.38913 | 0.37623 | 0.37302 | 0.39608 | 0.4453 | 0.46714 | 0.48897 | 0.52958 | 0.56716 | 0.60109 | 0.62915 | 0.66141 | 0.69258 | 0.72056 | 0.73405 | 0.72177 | 0.68297 | 0.66962 | 0.63515 | 0.58746 | 0.54194 | 0.48983 | 0.73405
2015-10-18 | 0.44566 | 0.40623 | 0.3816 | 0.36756 | 0.3612 | 0.36693 | 0.38444 | 0.40258 | 0.4481 | 0.50729 | 0.55651 | 0.59694 | 0.63682 | 0.67152 | 0.70287 | 0.72687 | 0.73563 | 0.72196 | 0.68279 | 0.67215 | 0.6393 | 0.59364 | 0.5506 | 0.49921 | 0.73563
2015-10-19 | 0.45378 | 0.41819 | 0.39238 | 0.37681 | 0.37032 | 0.37059 | 0.38241 | 0.39382 | 0.44165 | 0.50562 | 0.56121 | 0.60813 | 0.65622 | 0.69286 | 0.72223 | 0.73964 | 0.7456 | 0.73215 | 0.70215 | 0.70468 | 0.67616 | 0.62505 | 0.57199 | 0.51433 | 0.7456
2015-10-20 | 0.46366 | 0.42689 | 0.4051 | 0.39373 | 0.39441 | 0.42008 | 0.47066 | 0.49664 | 0.52574 | 0.58223 | 0.63682 | 0.6827 | 0.72132 | 0.75137 | 0.77844 | 0.78634 | 0.78088 | 0.76238 | 0.74411 | 0.75069 | 0.71753 | 0.66574 | 0.60659 | 0.54487 | 0.78634
2015-10-21 | 0.49055 | 0.45766 | 0.43858 | 0.42658 | 0.42748 | 0.45414 | 0.51058 | 0.53883 | 0.54961 | 0.58471 | 0.6236 | 0.64706 | 0.66299 | 0.6707 | 0.67255 | 0.67418 | 0.67075 | 0.66407 | 0.66385 | 0.6832 | 0.65866 | 0.61941 | 0.56567 | 0.50319 | 0.6832
2015-10-22 | 0.45608 | 0.42419 | 0.40569 | 0.39657 | 0.39874 | 0.42351 | 0.48541 | 0.51523 | 0.52759 | 0.56017 | 0.60122 | 0.64183 | 0.67161 | 0.69705 | 0.71559 | 0.72611 | 0.71997 | 0.70459 | 0.69741 | 0.70932 | 0.68361 | 0.64007 | 0.58218 | 0.52033 | 0.72611
2015-10-23 | 0.46917 | 0.43944 | 0.41945 | 0.40736 | 0.406 | 0.43181 | 0.49114 | 0.52051 | 0.52759 | 0.55539 | 0.58719 | 0.61359 | 0.63547 | 0.64941 | 0.66227 | 0.66818 | 0.66475 | 0.65518 | 0.64801 | 0.66096 | 0.64909 | 0.61115 | 0.55958 | 0.50445 | 0.66818
2015-10-24 | 0.45757 | 0.42586 | 0.40745 | 0.39933 | 0.4019 | 0.42626 | 0.47688 | 0.50806 | 0.52687 | 0.56265 | 0.5922 | 0.61313 | 0.62351 | 0.63465 | 0.64318 | 0.65085 | 0.65004 | 0.63984 | 0.63118 | 0.63596 | 0.61205 | 0.58106 | 0.54528 | 0.49642 | 0.65085
2015-10-25 | 0.44521 | 0.40831 | 0.38399 | 0.36869 | 0.36323 | 0.36738 | 0.38412 | 0.40497 | 0.44557 | 0.50066 | 0.54587 | 0.57903 | 0.60745 | 0.63362 | 0.65311 | 0.66718 | 0.6675 | 0.65058 | 0.61977 | 0.61557 | 0.58737 | 0.55299 | 0.51573 | 0.46826 | 0.6675
2015-10-26 | 0.42549 | 0.39378 | 0.37438 | 0.3608 | 0.3552 | 0.35633 | 0.36752 | 0.38471 | 0.4227 | 0.47941 | 0.52822 | 0.56441 | 0.595 | 0.62477 | 0.6486 | 0.66673 | 0.67481 | 0.66317 | 0.63628 | 0.64454 | 0.61553 | 0.56829 | 0.51325 | 0.45302 | 0.67481
2015-10-27 | 0.40339 | 0.37167 | 0.35322 | 0.34487 | 0.3478 | 0.376 | 0.43154 | 0.46281 | 0.479 | 0.51997 | 0.56093 | 0.59761 | 0.62784 | 0.65969 | 0.68704 | 0.71194 | 0.7248 | 0.71514 | 0.6952 | 0.70364 | 0.66867 | 0.61471 | 0.55372 | 0.48794 | 0.7248
2015-10-28 | 0.43623 | 0.40248 | 0.38105 | 0.37014 | 0.37072 | 0.39906 | 0.45617 | 0.48451 | 0.50215 | 0.54938 | 0.59283 | 0.63416 | 0.66791 | 0.70919 | 0.73883 | 0.76003 | 0.77019 | 0.75827 | 0.73314 | 0.73996 | 0.70373 | 0.65478 | 0.59261 | 0.52827 | 0.77019
2015-10-29 | 0.47634 | 0.44002 | 0.41575 | 0.4023 | 0.40226 | 0.4273 | 0.48636 | 0.51122 | 0.52746 | 0.58336 | 0.62897 | 0.67115 | 0.71068 | 0.74366 | 0.76964 | 0.79193 | 0.79631 | 0.77591 | 0.7437 | 0.74379 | 0.70977 | 0.65983 | 0.59766 | 0.53107 | 0.79631
2015-10-30 | 0.47102 | 0.43407 | 0.40921 | 0.39518 | 0.39351 | 0.41828 | 0.47427 | 0.50152 | 0.51753 | 0.56779 | 0.62062 | 0.66353 | 0.69967 | 0.72877 | 0.74555 | 0.75845 | 0.7673 | 0.75033 | 0.72723 | 0.73197 | 0.69854 | 0.65428 | 0.59626 | 0.53359 | 0.7673
2015-10-31 | 0.47643 | 0.43853 | 0.41205 | 0.39851 | 0.39563 | 0.42004 | 0.47621 | 0.50467 | 0.52245 | 0.57118 | 0.61562 | 0.6555 | 0.68473 | 0.70499 | 0.71997 | 0.7312 | 0.73364 | 0.71027 | 0.66782 | 0.64454 | 0.60041 | 0.56215 | 0.51627 | 0.46488 | 0.73364
2015-11-01 | 0.41345 | 0.3783 | 0.35805 | 0.34677 | 0.34262 | 0.34731 | 0.36707 | 0.38719 | 0.42757 | 0.47634 | 0.51167 | 0.52782 | 0.53395 | 0.53377 | 0.53562 | 0.53684 | 0.53296 | 0.51852 | 0.50842 | 0.5229 | 0.50007 | 0.47133 | 0.43655 | 0.40018 | 0.53684
2015-11-02 | 0.7128 | 0.33445 | 0.33052 | 0.33021 | 0.33544 | 0.35096 | 0.37817 | 0.42802 | 0.47138 | 0.48879 | 0.49123 | 0.48649 | 0.48212 | 0.47521 | 0.4721 | 0.46876 | 0.47007 | 0.48956 | 0.52791 | 0.51708 | 0.49795 | 0.46529 | 0.42355 | 0.38602 | 0.7128
2015-11-03 | 0.3548 | 0.34492 | 0.33937 | 0.34149 | 0.35358 | 0.39459 | 0.46163 | 0.48807 | 0.49488 | 0.50355 | 0.51397 | 0.52177 | 0.52268 | 0.52407 | 0.52114 | 0.51663 | 0.52065 | 0.53806 | 0.5746 | 0.5626 | 0.53914 | 0.4989 | 0.45121 | 0.40483 | 0.5746
2015-11-04 | 0.37217 | 0.35119 | 0.33941 | 0.33711 | 0.34275 | 0.37546 | 0.42852 | 0.46596 | 0.49529 | 0.51785 | 0.53959 | 0.5585 | 0.56748 | 0.5756 | 0.57993 | 0.5834 | 0.57785 | 0.58692 | 0.62198 | 0.6111 | 0.58566 | 0.53982 | 0.49339 | 0.44598 | 0.62198
2015-11-05 | 0.40704 | 0.3802 | 0.36626 | 0.35949 | 0.364 | 0.39414 | 0.44783 | 0.46587 | 0.51104 | 0.55421 | 0.58679 | 0.61192 | 0.62847 | 0.63659 | 0.63966 | 0.63362 | 0.62347 | 0.63136 | 0.66172 | 0.64657 | 0.62058 | 0.57961 | 0.52543 | 0.47007 | 0.66172
2015-11-06 | 0.42567 | 0.39585 | 0.37654 | 0.3663 | 0.36788 | 0.39829 | 0.44986 | 0.48744 | 0.52601 | 0.56874 | 0.61043 | 0.64485 | 0.67115 | 0.69055 | 0.6998 | 0.69913 | 0.68347 | 0.66849 | 0.68446 | 0.66046 | 0.6218 | 0.57122 | 0.51293 | 0.45798 | 0.6998
2015-11-07 | 0.41115 | 0.3806 | 0.36138 | 0.35389 | 0.3557 | 0.38272 | 0.43718 | 0.47151 | 0.5086 | 0.54975 | 0.5862 | 0.61846 | 0.64417 | 0.66497 | 0.67386 | 0.67197 | 0.65374 | 0.63894 | 0.64878 | 0.61688 | 0.58354 | 0.54402 | 0.50314 | 0.45974 | 0.67386
2015-11-08 | 0.41782 | 0.3871 | 0.36585 | 0.3566 | 0.35471 | 0.36269 | 0.382 | 0.41963 | 0.48518 | 0.53743 | 0.57307 | 0.60118 | 0.62482 | 0.63465 | 0.63321 | 0.62256 | 0.60731 | 0.61228 | 0.6232 | 0.59549 | 0.56693 | 0.53314 | 0.49687 | 0.4545 | 0.63465
2015-11-09 | 0.41791 | 0.38696 | 0.36874 | 0.35917 | 0.35525 | 0.36075 | 0.37424 | 0.40248 | 0.45622 | 0.49764 | 0.52074 | 0.53427 | 0.53594 | 0.52922 | 0.52222 | 0.51117 | 0.50864 | 0.53382 | 0.55584 | 0.53977 | 0.51604 | 0.48148 | 0.44467 | 0.40073 | 0.55584
2015-11-10 | 0.3654 | 0.34573 | 0.33522 | 0.33079 | 0.33625 | 0.36026 | 0.4181 | 0.46353 | 0.48388 | 0.50855 | 0.52741 | 0.54397 | 0.55602 | 0.56657 | 0.57176 | 0.57591 | 0.57122 | 0.57867 | 0.60623 | 0.58615 | 0.55471 | 0.51158 | 0.46583 | 0.41733 | 0.60623
2015-11-11 | 0.37375 | 0.34821 | 0.33436 | 0.32922 | 0.33287 | 0.3534 | 0.394 | 0.43537 | 0.47156 | 0.50359 | 0.5275 | 0.54465 | 0.56048 | 0.5751 | 0.58191 | 0.58818 | 0.58273 | 0.58566 | 0.61223 | 0.5936 | 0.56211 | 0.5192 | 0.47088 | 0.41801 | 0.61223
2015-11-12 | 0.37307 | 0.3469 | 0.33486 | 0.32976 | 0.33598 | 0.36495 | 0.42369 | 0.45708 | 0.48018 | 0.50959 | 0.53955 | 0.56617 | 0.58949 | 0.61331 | 0.62929 | 0.63502 | 0.6264 | 0.62053 | 0.64232 | 0.62076 | 0.58805 | 0.54492 | 0.49335 | 0.43935 | 0.64232
2015-11-13 | 0.39518 | 0.36869 | 0.3525 | 0.34749 | 0.3515 | 0.37961 | 0.43646 | 0.47138 | 0.50233 | 0.54099 | 0.57528 | 0.6005 | 0.62495 | 0.64643 | 0.65599 | 0.6573 | 0.64539 | 0.63885 | 0.65748 | 0.63556 | 0.60176 | 0.55629 | 0.50111 | 0.44796 | 0.65748
2015-11-14 | 0.40271 | 0.37262 | 0.35597 | 0.34726 | 0.34934 | 0.37483 | 0.43159 | 0.46799 | 0.49949 | 0.53301 | 0.56215 | 0.58133 | 0.59928 | 0.61232 | 0.61995 | 0.61986 | 0.60655 | 0.60226 | 0.61643 | 0.5908 | 0.56084 | 0.52367 | 0.4864 | 0.44404 | 0.61995
2015-11-15 | 0.4056 | 0.37749 | 0.36156 | 0.3529 | 0.35213 | 0.3612 | 0.38318 | 0.41755 | 0.47061 | 0.51474 | 0.54329 | 0.56504 | 0.57943 | 0.59202 | 0.59667 | 0.59405 | 0.58264 | 0.58033 | 0.59671 | 0.5714 | 0.54397 | 0.51392 | 0.48203 | 0.44661 | 0.59671
2015-11-16 | 0.40993 | 0.38539 | 0.36937 | 0.36044 | 0.35777 | 0.36504 | 0.37821 | 0.40695 | 0.47233 | 0.5312 | 0.57339 | 0.60407 | 0.62965 | 0.64566 | 0.65243 | 0.65202 | 0.6393 | 0.63691 | 0.65649 | 0.63506 | 0.60235 | 0.56351 | 0.52195 | 0.4744 | 0.65649
2015-11-17 | 0.43461 | 0.41034 | 0.39648 | 0.39044 | 0.39829 | 0.42996 | 0.48794 | 0.52195 | 0.56148 | 0.61426 | 0.66412 | 0.70174 | 0.72854 | 0.74325 | 0.74519 | 0.73887 | 0.72552 | 0.72593 | 0.73942 | 0.7114 | 0.66962 | 0.61507 | 0.5594 | 0.49845 | 0.74519
2015-11-18 | 0.4504 | 0.41927 | 0.39775 | 0.38665 | 0.38936 | 0.41413 | 0.47499 | 0.50959 | 0.53752 | 0.56878 | 0.58967 | 0.5936 | 0.58358 | 0.57266 | 0.55796 | 0.54325 | 0.54393 | 0.57325 | 0.60271 | 0.59355 | 0.57118 | 0.53648 | 0.49028 | 0.44638 | 0.60271
2015-11-19 | 0.41507 | 0.401 | 0.39527 | 0.39608 | 0.40948 | 0.44945 | 0.52719 | 0.56093 | 0.57451 | 0.5811 | 0.57754 | 0.56382 | 0.54717 | 0.53477 | 0.52502 | 0.52137 | 0.5275 | 0.5626 | 0.59757 | 0.59197 | 0.57469 | 0.54077 | 0.49678 | 0.45144 | 0.59757
2015-11-20 | 0.41864 | 0.40217 | 0.39811 | 0.39982 | 0.41385 | 0.45333 | 0.52286 | 0.55074 | 0.54438 | 0.54429 | 0.54194 | 0.53905 | 0.5345 | 0.52985 | 0.52227 | 0.51857 | 0.52024 | 0.55272 | 0.58791 | 0.58264 | 0.56328 | 0.53007 | 0.48708 | 0.44165 | 0.58791
2015-11-21 | 0.40609 | 0.38399 | 0.37632 | 0.37172 | 0.37821 | 0.41999 | 0.47778 | 0.5109 | 0.52245 | 0.53359 | 0.54293 | 0.54505 | 0.53747 | 0.53215 | 0.52565 | 0.51974 | 0.52322 | 0.5492 | 0.5654 | 0.55092 | 0.53152 | 0.50458 | 0.47305 | 0.4365 | 0.5654
2015-11-22 | 0.40082 | 0.37776 | 0.3649 | 0.36035 | 0.36202 | 0.37244 | 0.39644 | 0.42865 | 0.48257 | 0.52926 | 0.55602 | 0.57041 | 0.57118 | 0.57027 | 0.56576 | 0.55805 | 0.55665 | 0.57867 | 0.59558 | 0.58421 | 0.56757 | 0.54275 | 0.51442 | 0.47548 | 0.59558
2015-11-23 | 0.43804 | 0.41363 | 0.3945 | 0.38358 | 0.38155 | 0.38809 | 0.40181 | 0.43312 | 0.50458 | 0.57483 | 0.6204 | 0.64977 | 0.66831 | 0.68176 | 0.68419 | 0.67964 | 0.66231 | 0.66926 | 0.69087 | 0.67634 | 0.65067 | 0.61259 | 0.57023 | 0.52782 | 0.69087
2015-11-24 | 0.47399 | 0.44119 | 0.42261 | 0.41543 | 0.42116 | 0.44999 | 0.50264 | 0.53937 | 0.58697 | 0.63944 | 0.68676 | 0.73554 | 0.77289 | 0.7918 | 0.80068 | 0.79735 | 0.77628 | 0.76852 | 0.78408 | 0.75769 | 0.72272 | 0.67016 | 0.62216 | 0.56179 | 0.80068
2015-11-25 | 0.5091 | 0.47264 | 0.45216 | 0.44413 | 0.44611 | 0.47445 | 0.52674 | 0.56202 | 0.60885 | 0.65766 | 0.70007 | 0.72814 | 0.74402 | 0.75548 | 0.75408 | 0.74636 | 0.72967 | 0.73513 | 0.75033 | 0.73012 | 0.69674 | 0.65712 | 0.60907 | 0.56139 | 0.75548
2015-11-26 | 0.51455 | 0.48266 | 0.46177 | 0.45085 | 0.45094 | 0.46727 | 0.50246 | 0.53585 | 0.57555 | 0.60357 | 0.60546 | 0.59892 | 0.58873 | 0.57275 | 0.55349 | 0.53463 | 0.52439 | 0.54541 | 0.56851 | 0.55525 | 0.53328 | 0.51031 | 0.47977 | 0.44088 | 0.60546
2015-11-27 | 0.40515 | 0.38146 | 0.36941 | 0.36635 | 0.36955 | 0.38408 | 0.41133 | 0.45108 | 0.4966 | 0.52638 | 0.54402 | 0.55092 | 0.55047 | 0.54104 | 0.53026 | 0.51338 | 0.49123 | 0.48207 | 0.48866 | 0.47124 | 0.45929 | 0.4485 | 0.43149 | 0.40673 | 0.55092
2015-11-28 | 0.38304 | 0.36892 | 0.36323 | 0.36517 | 0.37537 | 0.39676 | 0.43086 | 0.46678 | 0.50079 | 0.51997 | 0.52254 | 0.51401 | 0.50346 | 0.49389 | 0.485 | 0.47923 | 0.47968 | 0.50905 | 0.54248 | 0.53301 | 0.51839 | 0.50941 | 0.47914 | 0.44476 | 0.54248
2015-11-29 | 0.41381 | 0.39703 | 0.38809 | 0.38696 | 0.39224 | 0.4033 | 0.42743 | 0.45807 | 0.49064 | 0.50553 | 0.50743 | 0.50621 | 0.50183 | 0.49696 | 0.491 | 0.48509 | 0.47986 | 0.50021 | 0.52642 | 0.51464 | 0.49633 | 0.47544 | 0.44724 | 0.41286 | 0.52642
2015-11-30 | 0.37884 | 0.35674 | 0.34559 | 0.34135 | 0.34343 | 0.35227 | 0.36928 | 0.39617 | 0.44165 | 0.47621 | 0.49755 | 0.51149 | 0.52164 | 0.52683 | 0.52786 | 0.52439 | 0.51929 | 0.53964 | 0.57542 | 0.56301 | 0.5423 | 0.51076 | 0.47264 | 0.42437 | 0.57542
2015-12-01 | 0.38683 | 0.36229 | 0.35006 | 0.34618 | 0.35277 | 0.38493 | 0.44417 | 0.47688 | 0.50481 | 0.53544 | 0.56743 | 0.59225 | 0.60375 | 0.60808 | 0.60267 | 0.59283 | 0.58363 | 0.60461 | 0.63876 | 0.62825 | 0.60352 | 0.56355 | 0.51604 | 0.4606 | 0.63876
2015-12-02 | 0.41345 | 0.38399 | 0.36522 | 0.35782 | 0.36292 | 0.39215 | 0.45315 | 0.48437 | 0.50675 | 0.53892 | 0.56964 | 0.58837 | 0.59915 | 0.60587 | 0.60357 | 0.59572 | 0.58503 | 0.60795 | 0.64133 | 0.62924 | 0.60483 | 0.56657 | 0.51686 | 0.46109 | 0.64133
2015-12-03 | 0.41282 | 0.38137 | 0.36459 | 0.3566 | 0.36003 | 0.38963 | 0.45595 | 0.48442 | 0.51207 | 0.5511 | 0.58083 | 0.60483 | 0.62279 | 0.63118 | 0.63768 | 0.6407 | 0.6259 | 0.63285 | 0.66222 | 0.64652 | 0.61837 | 0.57695 | 0.52624 | 0.46714 | 0.66222
2015-12-04 | 0.41814 | 0.38805 | 0.37072 | 0.36328 | 0.36761 | 0.39806 | 0.45748 | 0.48997 | 0.51677 | 0.5548 | 0.58503 | 0.61016 | 0.62956 | 0.63813 | 0.64381 | 0.64593 | 0.62996 | 0.63759 | 0.66854 | 0.65536 | 0.62942 | 0.5913 | 0.53856 | 0.48103 | 0.66854
2015-12-05 | 0.43127 | 0.39707 | 0.37848 | 0.37086 | 0.37384 | 0.40325 | 0.46285 | 0.49561 | 0.52804 | 0.57303 | 0.60632 | 0.62865 | 0.64088 | 0.63975 | 0.63853 | 0.643 | 0.637 | 0.6449 | 0.66168 | 0.64115 | 0.61449 | 0.58106 | 0.54244 | 0.49425 | 0.66168
2015-12-06 | 0.4462 | 0.41219 | 0.39084 | 0.37749 | 0.37208 | 0.37808 | 0.39694 | 0.42698 | 0.48875 | 0.54884 | 0.59265 | 0.62144 | 0.64079 | 0.6527 | 0.65803 | 0.65374 | 0.63429 | 0.62595 | 0.63917 | 0.60853 | 0.57862 | 0.54726 | 0.50783 | 0.46127 | 0.65803
2015-12-07 | 0.41327 | 0.38308 | 0.36319 | 0.35024 | 0.34663 | 0.35173 | 0.36499 | 0.38913 | 0.44634 | 0.50291 | 0.53896 | 0.56229 | 0.57447 | 0.58115 | 0.58313 | 0.57447 | 0.5626 | 0.57654 | 0.61219 | 0.58882 | 0.56364 | 0.52705 | 0.47936 | 0.42667 | 0.61219
2015-12-08 | 0.38173 | 0.35439 | 0.34068 | 0.33589 | 0.3414 | 0.37176 | 0.43032 | 0.46263 | 0.48388 | 0.50873 | 0.53021 | 0.5442 | 0.55326 | 0.56057 | 0.56396 | 0.56802 | 0.56644 | 0.5862 | 0.62432 | 0.61354 | 0.58345 | 0.54122 | 0.49109 | 0.43213 | 0.62432
2015-12-09 | 0.3848 | 0.35958 | 0.34686 | 0.34329 | 0.34911 | 0.38259 | 0.45139 | 0.48329 | 0.49958 | 0.51275 | 0.52056 | 0.52222 | 0.52155 | 0.51857 | 0.51383 | 0.50688 | 0.51031 | 0.54614 | 0.59179 | 0.58683 | 0.56752 | 0.53499 | 0.48807 | 0.4388 | 0.59179
2015-12-10 | 0.40077 | 0.38412 | 0.37632 | 0.38092 | 0.39405 | 0.44359 | 0.5271 | 0.57316 | 0.56901 | 0.55484 | 0.54365 | 0.52998 | 0.5183 | 0.51027 | 0.50039 | 0.4966 | 0.50197 | 0.54393 | 0.60032 | 0.60028 | 0.5922 | 0.56418 | 0.52092 | 0.47287 | 0.60032
2015-12-11 | 0.4411 | 0.42604 | 0.42252 | 0.42369 | 0.43935 | 0.48807 | 0.57483 | 0.61494 | 0.59798 | 0.58065 | 0.55913 | 0.54474 | 0.53044 | 0.51961 | 0.50941 | 0.50513 | 0.51081 | 0.55047 | 0.59743 | 0.59378 | 0.58245 | 0.55412 | 0.50684 | 0.45942 | 0.61494
2015-12-12 | 0.42477 | 0.40682 | 0.4005 | 0.39973 | 0.41543 | 0.46231 | 0.53968 | 0.57695 | 0.57957 | 0.57907 | 0.57005 | 0.55845 | 0.54442 | 0.53251 | 0.52024 | 0.51591 | 0.52272 | 0.56549 | 0.60542 | 0.59811 | 0.58922 | 0.56739 | 0.53517 | 0.49619 | 0.60542
2015-12-13 | 0.46064 | 0.44512 | 0.43777 | 0.43867 | 0.44711 | 0.46989 | 0.5049 | 0.54641 | 0.57086 | 0.56942 | 0.55218 | 0.53626 | 0.52439 | 0.51261 | 0.50215 | 0.49664 | 0.49511 | 0.52277 | 0.55624 | 0.54555 | 0.53409 | 0.51713 | 0.49141 | 0.46294 | 0.57086
2015-12-14 | 0.43371 | 0.41539 | 0.40907 | 0.40961 | 0.41597 | 0.4342 | 0.46736 | 0.50842 | 0.54568 | 0.54988 | 0.53495 | 0.52358 | 0.51474 | 0.50743 | 0.50251 | 0.49813 | 0.49831 | 0.52732 | 0.57501 | 0.56915 | 0.55561 | 0.53057 | 0.48798 | 0.4462 | 0.57501
2015-12-15 | 0.41471 | 0.39874 | 0.39752 | 0.40095 | 0.41945 | 0.4666 | 0.55051 | 0.59355 | 0.58994 | 0.56887 | 0.55335 | 0.54095 | 0.53802 | 0.53332 | 0.52768 | 0.52683 | 0.52818 | 0.55963 | 0.60826 | 0.60339 | 0.58449 | 0.54997 | 0.50251 | 0.45234 | 0.60826
2015-12-16 | 0.41417 | 0.39603 | 0.3894 | 0.39179 | 0.40501 | 0.44927 | 0.5303 | 0.56748 | 0.5636 | 0.54898 | 0.53928 | 0.53432 | 0.53265 | 0.53341 | 0.53251 | 0.53368 | 0.53436 | 0.55832 | 0.60186 | 0.59387 | 0.57045 | 0.5308 | 0.48356 | 0.43159 | 0.60186
2015-12-17 | 0.38827 | 0.36549 | 0.35647 | 0.35543 | 0.36711 | 0.40627 | 0.4763 | 0.51383 | 0.51758 | 0.52195 | 0.52588 | 0.52818 | 0.53278 | 0.53842 | 0.54433 | 0.55029 | 0.54735 | 0.56883 | 0.60673 | 0.59477 | 0.56937 | 0.53553 | 0.48739 | 0.43298 | 0.60673
2015-12-18 | 0.39035 | 0.36693 | 0.35732 | 0.35683 | 0.36775 | 0.40456 | 0.47548 | 0.51446 | 0.528 | 0.53598 | 0.53932 | 0.53657 | 0.53612 | 0.5446 | 0.54979 | 0.5511 | 0.54844 | 0.5682 | 0.60628 | 0.59446 | 0.57524 | 0.54041 | 0.49488 | 0.44336 | 0.60628
2015-12-19 | 0.40208 | 0.37961 | 0.36869 | 0.36698 | 0.37677 | 0.41232 | 0.47643 | 0.51789 | 0.5322 | 0.54032 | 0.54744 | 0.55024 | 0.54993 | 0.5525 | 0.55245 | 0.55141 | 0.54623 | 0.56166 | 0.59405 | 0.57709 | 0.55403 | 0.52511 | 0.49182 | 0.44783 | 0.59405
2015-12-20 | 0.40821 | 0.38182 | 0.36824 | 0.36202 | 0.36138 | 0.37474 | 0.40032 | 0.43429 | 0.47855 | 0.51239 | 0.53102 | 0.53436 | 0.54776 | 0.54934 | 0.55092 | 0.55137 | 0.54632 | 0.55999 | 0.58882 | 0.56743 | 0.54365 | 0.51654 | 0.48261 | 0.4407 | 0.58882
2015-12-21 | 0.39824 | 0.36838 | 0.35006 | 0.34158 | 0.3404 | 0.34659 | 0.36283 | 0.38994 | 0.44304 | 0.49561 | 0.52764 | 0.54424 | 0.56139 | 0.56648 | 0.56265 | 0.55552 | 0.5497 | 0.5719 | 0.60605 | 0.59229 | 0.57289 | 0.54433 | 0.50445 | 0.45315 | 0.60605
2015-12-22 | 0.40627 | 0.37519 | 0.35651 | 0.34726 | 0.35006 | 0.37239 | 0.41142 | 0.45031 | 0.50197 | 0.55128 | 0.59202 | 0.61778 | 0.63506 | 0.64783 | 0.65672 | 0.6523 | 0.63696 | 0.64593 | 0.67986 | 0.6615 | 0.63402 | 0.60095 | 0.55602 | 0.49488 | 0.67986
2015-12-23 | 0.44183 | 0.40461 | 0.38087 | 0.36896 | 0.37059 | 0.39274 | 0.4305 | 0.46867 | 0.5234 | 0.57862 | 0.61932 | 0.6481 | 0.66885 | 0.67706 | 0.65861 | 0.63876 | 0.62112 | 0.62802 | 0.65956 | 0.64169 | 0.61598 | 0.59617 | 0.56712 | 0.52935 | 0.67706
2015-12-24 | 0.48329 | 0.4476 | 0.42437 | 0.41413 | 0.41178 | 0.42567 | 0.45157 | 0.48437 | 0.54659 | 0.61589 | 0.6693 | 0.7049 | 0.72335 | 0.72656 | 0.72895 | 0.72029 | 0.7109 | 0.71943 | 0.72737 | 0.68622 | 0.64751 | 0.6148 | 0.58295 | 0.53738 | 0.72895
2015-12-25 | 0.491 | 0.45514 | 0.42306 | 0.39838 | 0.38142 | 0.37839 | 0.38543 | 0.40501 | 0.45139 | 0.49863 | 0.52827 | 0.54316 | 0.54835 | 0.5446 | 0.53662 | 0.51979 | 0.50183 | 0.50955 | 0.53084 | 0.51979 | 0.51081 | 0.49673 | 0.47111 | 0.43465 | 0.54835
2015-12-26 | 0.3968 | 0.37045 | 0.35841 | 0.35204 | 0.35502 | 0.37113 | 0.39865 | 0.43059 | 0.4707 | 0.50801 | 0.53662 | 0.54839 | 0.54808 | 0.54117 | 0.53693 | 0.53391 | 0.53657 | 0.56698 | 0.59933 | 0.58769 | 0.56594 | 0.53901 | 0.50648 | 0.46285 | 0.59933
2015-12-27 | 0.41882 | 0.38683 | 0.36576 | 0.35611 | 0.35615 | 0.36328 | 0.382 | 0.40285 | 0.45166 | 0.51009 | 0.55525 | 0.5843 | 0.60235 | 0.60822 | 0.60844 | 0.59892 | 0.58733 | 0.60073 | 0.63064 | 0.61183 | 0.58471 | 0.55557 | 0.51722 | 0.46872 | 0.63064
2015-12-28 | 0.42288 | 0.38877 | 0.36716 | 0.3548 | 0.34871 | 0.3515 | 0.3654 | 0.38349 | 0.4439 | 0.50923 | 0.55705 | 0.5927 | 0.61742 | 0.6347 | 0.64381 | 0.6435 | 0.63362 | 0.63073 | 0.65879 | 0.63691 | 0.60686 | 0.5723 | 0.52795 | 0.47242 | 0.65879
2015-12-29 | 0.42482 | 0.39215 | 0.37244 | 0.36377 | 0.36472 | 0.382 | 0.41791 | 0.45171 | 0.50643 | 0.5682 | 0.6171 | 0.64873 | 0.6652 | 0.67255 | 0.67797 | 0.68072 | 0.66989 | 0.66682 | 0.69791 | 0.67431 | 0.64228 | 0.59883 | 0.55132 | 0.492 | 0.69791
2015-12-30 | 0.43826 | 0.40307 | 0.38169 | 0.37005 | 0.36892 | 0.38624 | 0.41972 | 0.45247 | 0.50012 | 0.55308 | 0.60046 | 0.63894 | 0.6629 | 0.67968 | 0.68424 | 0.67864 | 0.66551 | 0.66538 | 0.69606 | 0.67278 | 0.6439 | 0.60258 | 0.55805 | 0.50337 | 0.69606
2015-12-31 | 0.45252 | 0.41593 | 0.3936 | 0.38155 | 0.38051 | 0.39567 | 0.42667 | 0.46154 | 0.50743 | 0.55439 | 0.59175 | 0.6134 | 0.61855 | 0.62189 | 0.62085 | 0.61435 | 0.6162 | 0.64823 | 0.67571 | 0.64336 | 0.60461 | 0.5622 | 0.51898 | 0.48342 | 0.67571
Max | 0.7128 | 0.63244 | 0.59802 | 0.57686 | 0.58259 | 0.64138 | 0.74099 | 0.78913 | 0.76179 | 0.76301 | 0.82911 | 0.88916 | 0.93694 | 0.97804 | 1.001 | 1.0242 | 1.025 | 1.0156 | 0.99608 | 0.95751 | 0.93378 | 0.89498 | 0.82342 | 0.74754

## CLEF
OPC 012914
FPL RC-16
CLEF = (Hourly Loads p.u of Peak) **2
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24
2015-01-01 | 0.19489 | 0.18097 | 0.16272 | 0.15083 | 0.14579 | 0.14824 | 0.15606 | 0.16265 | 0.1935 | 0.24769 | 0.30446 | 0.3467 | 0.37301 | 0.38361 | 0.38043 | 0.37075 | 0.36087 | 0.36932 | 0.40606 | 0.384 | 0.35177 | 0.31754 | 0.27475 | 0.22527
2015-01-02 | 0.1834 | 0.15881 | 0.14328 | 0.13613 | 0.13414 | 0.1424 | 0.17624 | 0.20637 | 0.25552 | 0.32004 | 0.37721 | 0.4191 | 0.45039 | 0.47282 | 0.48305 | 0.47786 | 0.45878 | 0.45081 | 0.48494 | 0.44869 | 0.40216 | 0.35327 | 0.30227 | 0.2476
2015-01-03 | 0.20031 | 0.16956 | 0.15177 | 0.14349 | 0.14281 | 0.15241 | 0.18239 | 0.21302 | 0.25174 | 0.28713 | 0.3084 | 0.31546 | 0.31551 | 0.30971 | 0.30391 | 0.30034 | 0.29851 | 0.32774 | 0.37433 | 0.36136 | 0.33548 | 0.30545 | 0.267 | 0.22578
2015-01-04 | 0.19188 | 0.17072 | 0.15863 | 0.15354 | 0.15417 | 0.16192 | 0.17909 | 0.20306 | 0.24295 | 0.28117 | 0.30481 | 0.31011 | 0.3051 | 0.29718 | 0.28718 | 0.27802 | 0.27993 | 0.30885 | 0.33532 | 0.31734 | 0.29512 | 0.26896 | 0.23786 | 0.20359
2015-01-05 | 0.17131 | 0.14988 | 0.1371 | 0.13001 | 0.12858 | 0.13467 | 0.14964 | 0.16789 | 0.20641 | 0.24773 | 0.29679 | 0.32929 | 0.34681 | 0.35241 | 0.35193 | 0.34538 | 0.33642 | 0.34395 | 0.38736 | 0.36495 | 0.3347 | 0.29141 | 0.24455 | 0.19882
2015-01-06 | 0.15767 | 0.13703 | 0.12543 | 0.12141 | 0.1246 | 0.14393 | 0.18834 | 0.21944 | 0.24971 | 0.29345 | 0.3422 | 0.37505 | 0.40193 | 0.41665 | 0.41206 | 0.3947 | 0.37859 | 0.40284 | 0.44513 | 0.42056 | 0.36828 | 0.3087 | 0.26268 | 0.21616
2015-01-07 | 0.18363 | 0.16675 | 0.16258 | 0.1659 | 0.18193 | 0.22088 | 0.30376 | 0.37053 | 0.40216 | 0.4215 | 0.4138 | 0.39254 | 0.37268 | 0.35349 | 0.33873 | 0.33778 | 0.35801 | 0.42661 | 0.51149 | 0.51758 | 0.49536 | 0.44027 | 0.37599 | 0.31744
2015-01-08 | 0.27579 | 0.25515 | 0.24796 | 0.24478 | 0.25242 | 0.28815 | 0.36136 | 0.3997 | 0.39577 | 0.39577 | 0.39091 | 0.37141 | 0.34554 | 0.32188 | 0.30217 | 0.29458 | 0.30014 | 0.33433 | 0.37649 | 0.36288 | 0.3322 | 0.28535 | 0.23545 | 0.18798
2015-01-09 | 0.15332 | 0.1368 | 0.12933 | 0.12665 | 0.13197 | 0.1552 | 0.20834 | 0.24742 | 0.26037 | 0.28448 | 0.30163 | 0.31111 | 0.31197 | 0.3074 | 0.30163 | 0.2996 | 0.30321 | 0.33256 | 0.37926 | 0.3702 | 0.34168 | 0.29871 | 0.25102 | 0.2012
2015-01-10 | 0.16167 | 0.13891 | 0.12662 | 0.12213 | 0.12479 | 0.14407 | 0.19259 | 0.22893 | 0.25849 | 0.29664 | 0.32872 | 0.35001 | 0.36212 | 0.37136 | 0.37169 | 0.36965 | 0.36681 | 0.37119 | 0.41131 | 0.38865 | 0.35397 | 0.31293 | 0.27295 | 0.23057
2015-01-11 | 0.18557 | 0.15986 | 0.14356 | 0.13597 | 0.13441 | 0.14178 | 0.15903 | 0.18228 | 0.24002 | 0.31016 | 0.36408 | 0.39976 | 0.42732 | 0.44447 | 0.45154 | 0.44767 | 0.42861 | 0.41339 | 0.43842 | 0.40623 | 0.3662 | 0.32152 | 0.27826 | 0.23348
2015-01-12 | 0.18967 | 0.16138 | 0.14486 | 0.13567 | 0.13119 | 0.13391 | 0.145 | 0.16036 | 0.20116 | 0.24787 | 0.28395 | 0.3057 | 0.32552 | 0.33836 | 0.34199 | 0.33773 | 0.32789 | 0.32111 | 0.35984 | 0.34601 | 0.31536 | 0.2748 | 0.23209 | 0.18697
2015-01-13 | 0.15332 | 0.1361 | 0.12842 | 0.12765 | 0.13474 | 0.16319 | 0.22407 | 0.26509 | 0.28227 | 0.30605 | 0.32784 | 0.34458 | 0.36022 | 0.37251 | 0.38048 | 0.38624 | 0.38288 | 0.38967 | 0.43949 | 0.4282 | 0.38495 | 0.32877 | 0.27234 | 0.21498
2015-01-14 | 0.17075 | 0.1463 | 0.13404 | 0.12797 | 0.13037 | 0.15206 | 0.20473 | 0.2398 | 0.2699 | 0.31384 | 0.3529 | 0.37665 | 0.3891 | 0.38972 | 0.38439 | 0.3702 | 0.36637 | 0.38361 | 0.43104 | 0.41834 | 0.38009 | 0.32846 | 0.26952 | 0.21244
2015-01-15 | 0.16886 | 0.14668 | 0.1349 | 0.13102 | 0.13368 | 0.15813 | 0.21557 | 0.25306 | 0.26705 | 0.28617 | 0.29635 | 0.29708 | 0.28898 | 0.28107 | 0.27239 | 0.26831 | 0.27258 | 0.30366 | 0.34681 | 0.33684 | 0.31081 | 0.27225 | 0.22673 | 0.18135
2015-01-16 | 0.1509 | 0.1358 | 0.13148 | 0.13309 | 0.1427 | 0.17738 | 0.25197 | 0.30715 | 0.31708 | 0.3207 | 0.3206 | 0.31106 | 0.29674 | 0.28194 | 0.26934 | 0.26324 | 0.26948 | 0.30885 | 0.40147 | 0.42068 | 0.41624 | 0.38972 | 0.34878 | 0.30585
2015-01-17 | 0.27721 | 0.2663 | 0.26789 | 0.27721 | 0.29856 | 0.35623 | 0.47065 | 0.54754 | 0.53624 | 0.48174 | 0.42508 | 0.37064 | 0.32825 | 0.29585 | 0.27418 | 0.26259 | 0.26467 | 0.29826 | 0.3565 | 0.35209 | 0.33799 | 0.31096 | 0.28117 | 0.2471
2015-01-18 | 0.21645 | 0.20347 | 0.1997 | 0.20132 | 0.21024 | 0.23135 | 0.26934 | 0.32203 | 0.36011 | 0.36446 | 0.35091 | 0.32393 | 0.29669 | 0.27324 | 0.25324 | 0.24268 | 0.24282 | 0.27121 | 0.33931 | 0.35204 | 0.35198 | 0.34623 | 0.33121 | 0.31031
2015-01-19 | 0.29576 | 0.29087 | 0.29463 | 0.30595 | 0.32459 | 0.3559 | 0.40727 | 0.47382 | 0.51408 | 0.48255 | 0.41717 | 0.35801 | 0.31399 | 0.28342 | 0.25996 | 0.24179 | 0.2365 | 0.25197 | 0.30936 | 0.30555 | 0.29121 | 0.26319 | 0.2361 | 0.20047
2015-01-20 | 0.17624 | 0.16532 | 0.16287 | 0.16598 | 0.17928 | 0.20723 | 0.25748 | 0.30981 | 0.33002 | 0.32085 | 0.3086 | 0.29703 | 0.28366 | 0.27357 | 0.26597 | 0.2618 | 0.26254 | 0.28055 | 0.33444 | 0.32996 | 0.30133 | 0.26171 | 0.21674 | 0.17322
2015-01-21 | 0.14366 | 0.12926 | 0.12355 | 0.12352 | 0.13001 | 0.15788 | 0.21944 | 0.26014 | 0.26938 | 0.27225 | 0.27517 | 0.27508 | 0.27394 | 0.26891 | 0.26453 | 0.2601 | 0.2618 | 0.28544 | 0.33496 | 0.33308 | 0.30595 | 0.26495 | 0.2202 | 0.17871
2015-01-22 | 0.14901 | 0.13854 | 0.13687 | 0.14212 | 0.15835 | 0.20209 | 0.29302 | 0.35844 | 0.3483 | 0.36087 | 0.35198 | 0.33449 | 0.31505 | 0.29316 | 0.27821 | 0.27027 | 0.2757 | 0.31369 | 0.40617 | 0.43359 | 0.43276 | 0.40652 | 0.36713 | 0.3227
2015-01-23 | 0.29738 | 0.29141 | 0.29772 | 0.31202 | 0.33941 | 0.41136 | 0.54907 | 0.62273 | 0.58033 | 0.51291 | 0.45263 | 0.39023 | 0.34162 | 0.30356 | 0.27926 | 0.26719 | 0.26817 | 0.29703 | 0.37202 | 0.38657 | 0.37444 | 0.34141 | 0.29267 | 0.24782
2015-01-24 | 0.21737 | 0.20711 | 0.20645 | 0.21206 | 0.2291 | 0.27931 | 0.37948 | 0.43806 | 0.43746 | 0.41811 | 0.3939 | 0.36006 | 0.33126 | 0.30745 | 0.28854 | 0.27788 | 0.28064 | 0.3064 | 0.3679 | 0.36943 | 0.35295 | 0.32598 | 0.2936 | 0.25561
2015-01-25 | 0.22596 | 0.21169 | 0.20608 | 0.20768 | 0.21528 | 0.23344 | 0.26705 | 0.31237 | 0.3579 | 0.3552 | 0.32867 | 0.30083 | 0.27945 | 0.2631 | 0.25084 | 0.24175 | 0.23782 | 0.24958 | 0.29175 | 0.28723 | 0.26803 | 0.2454 | 0.21611 | 0.18494
2015-01-26 | 0.16004 | 0.14458 | 0.13821 | 0.13554 | 0.13757 | 0.14724 | 0.16649 | 0.19489 | 0.23843 | 0.2625 | 0.27366 | 0.27248 | 0.27182 | 0.27121 | 0.26761 | 0.26379 | 0.26305 | 0.2765 | 0.32126 | 0.31973 | 0.29189 | 0.25456 | 0.21431 | 0.17169
2015-01-27 | 0.14009 | 0.12286 | 0.11566 | 0.11377 | 0.12022 | 0.14445 | 0.20197 | 0.23813 | 0.25401 | 0.27324 | 0.2959 | 0.31127 | 0.32408 | 0.3348 | 0.33978 | 0.34612 | 0.34899 | 0.35429 | 0.39799 | 0.39283 | 0.35273 | 0.29694 | 0.24055 | 0.18576
2015-01-28 | 0.1452 | 0.12505 | 0.11575 | 0.11216 | 0.11661 | 0.13952 | 0.19271 | 0.23053 | 0.24841 | 0.27352 | 0.30063 | 0.3205 | 0.33946 | 0.35563 | 0.36774 | 0.37704 | 0.38026 | 0.38177 | 0.4205 | 0.41351 | 0.37599 | 0.31749 | 0.26176 | 0.20616
2015-01-29 | 0.16294 | 0.1408 | 0.1306 | 0.12704 | 0.13191 | 0.15759 | 0.21423 | 0.25689 | 0.27645 | 0.30426 | 0.32568 | 0.34395 | 0.26412 | 0.34083 | 0.33365 | 0.33653 | 0.34718 | 0.37588 | 0.41357 | 0.40411 | 0.37843 | 0.33251 | 0.28026 | 0.226
2015-01-30 | 0.18979 | 0.16956 | 0.15986 | 0.15777 | 0.16521 | 0.19565 | 0.26611 | 0.31404 | 0.33936 | 0.36424 | 0.37826 | 0.37643 | 0.36839 | 0.35903 | 0.34873 | 0.34284 | 0.34681 | 0.37097 | 0.4156 | 0.40848 | 0.37671 | 0.33256 | 0.2756 | 0.2222
2015-01-31 | 0.18603 | 0.16653 | 0.15885 | 0.15563 | 0.16062 | 0.18896 | 0.25365 | 0.29689 | 0.3151 | 0.3392 | 0.3573 | 0.36752 | 0.36965 | 0.36692 | 0.36185 | 0.36479 | 0.3606 | 0.3673 | 0.39953 | 0.38691 | 0.35343 | 0.31303 | 0.2691 | 0.22232
2015-02-01 | 0.18278 | 0.15813 | 0.14356 | 0.13617 | 0.13484 | 0.14131 | 0.15914 | 0.18681 | 0.24197 | 0.30019 | 0.34241 | 0.3667 | 0.38512 | 0.3964 | 0.40353 | 0.40606 | 0.39987 | 0.38484 | 0.40239 | 0.38669 | 0.34718 | 0.30515 | 0.26273 | 0.21796
2015-02-02 | 0.17795 | 0.15322 | 0.13837 | 0.13037 | 0.12762 | 0.13017 | 0.14128 | 0.16167 | 0.21936 | 0.28007 | 0.32121 | 0.34862 | 0.38422 | 0.41038 | 0.42932 | 0.43818 | 0.4371 | 0.42009 | 0.4198 | 0.38143 | 0.34702 | 0.32681 | 0.30039 | 0.2406
2015-02-03 | 0.19219 | 0.15609 | 0.14304 | 0.13767 | 0.14111 | 0.16451 | 0.21712 | 0.25283 | 0.28767 | 0.33517 | 0.38624 | 0.42373 | 0.45403 | 0.47824 | 0.49625 | 0.50365 | 0.49111 | 0.47438 | 0.50052 | 0.48758 | 0.43413 | 0.37632 | 0.31011 | 0.24567
2015-02-04 | 0.19661 | 0.17023 | 0.15527 | 0.14824 | 0.14978 | 0.17094 | 0.22454 | 0.25964 | 0.29248 | 0.34321 | 0.39215 | 0.43015 | 0.46105 | 0.48099 | 0.4946 | 0.5025 | 0.49517 | 0.47487 | 0.50148 | 0.49644 | 0.44912 | 0.38714 | 0.32367 | 0.25817
2015-02-05 | 0.20855 | 0.17871 | 0.1636 | 0.15588 | 0.1572 | 0.18135 | 0.23936 | 0.27579 | 0.30996 | 0.36473 | 0.41612 | 0.45665 | 0.48299 | 0.50186 | 0.51363 | 0.50821 | 0.48695 | 0.46948 | 0.49346 | 0.4803 | 0.43365 | 0.37417 | 0.30795 | 0.24406
2015-02-06 | 0.19561 | 0.16579 | 0.15118 | 0.14393 | 0.14599 | 0.16741 | 0.22271 | 0.25812 | 0.29253 | 0.33475 | 0.37378 | 0.40359 | 0.42861 | 0.45257 | 0.46276 | 0.46898 | 0.46307 | 0.45561 | 0.48199 | 0.47531 | 0.42974 | 0.37152 | 0.30685 | 0.24117
2015-02-07 | 0.19188 | 0.16451 | 0.14696 | 0.13921 | 0.14039 | 0.16196 | 0.21578 | 0.25261 | 0.2775 | 0.31132 | 0.34511 | 0.37804 | 0.39822 | 0.40159 | 0.42844 | 0.43615 | 0.43395 | 0.42832 | 0.4311 | 0.40871 | 0.37704 | 0.32686 | 0.28333 | 0.23361
2015-02-08 | 0.19227 | 0.16371 | 0.14776 | 0.14002 | 0.13945 | 0.14579 | 0.16407 | 0.19144 | 0.24782 | 0.31303 | 0.36664 | 0.40153 | 0.42567 | 0.43764 | 0.44531 | 0.44051 | 0.42986 | 0.41438 | 0.42408 | 0.40439 | 0.36495 | 0.3227 | 0.27931 | 0.2358
2015-02-09 | 0.19394 | 0.16576 | 0.14974 | 0.14172 | 0.13996 | 0.14534 | 0.15842 | 0.17963 | 0.22186 | 0.2643 | 0.29438 | 0.31056 | 0.32588 | 0.33532 | 0.33952 | 0.336 | 0.32769 | 0.32516 | 0.35574 | 0.36049 | 0.32598 | 0.28246 | 0.23918 | 0.18975
2015-02-10 | 0.15311 | 0.13414 | 0.12665 | 0.12546 | 0.13151 | 0.15824 | 0.21801 | 0.25707 | 0.2748 | 0.29767 | 0.32403 | 0.34178 | 0.35865 | 0.37207 | 0.37771 | 0.38361 | 0.38467 | 0.38043 | 0.41113 | 0.41892 | 0.37848 | 0.32439 | 0.26579 | 0.20867
2015-02-11 | 0.16786 | 0.14462 | 0.13398 | 0.13057 | 0.135 | 0.16044 | 0.22054 | 0.25955 | 0.28055 | 0.30991 | 0.33752 | 0.36392 | 0.38686 | 0.40767 | 0.4205 | 0.43395 | 0.43788 | 0.43021 | 0.45366 | 0.45665 | 0.41892 | 0.35059 | 0.28477 | 0.22156
2015-02-12 | 0.17319 | 0.1489 | 0.13494 | 0.1293 | 0.13227 | 0.15442 | 0.20979 | 0.24375 | 0.27173 | 0.30971 | 0.34479 | 0.37444 | 0.39725 | 0.41636 | 0.42132 | 0.41362 | 0.40336 | 0.40525 | 0.44357 | 0.43389 | 0.39402 | 0.33831 | 0.26747 | 0.20404
2015-02-13 | 0.1633 | 0.13989 | 0.12959 | 0.12569 | 0.13021 | 0.15439 | 0.21244 | 0.25283 | 0.27546 | 0.29038 | 0.30406 | 0.30895 | 0.31167 | 0.31086 | 0.3081 | 0.30381 | 0.29955 | 0.29965 | 0.33548 | 0.3499 | 0.328 | 0.29184 | 0.24665 | 0.19962
2015-02-14 | 0.16605 | 0.15058 | 0.14555 | 0.14724 | 0.15831 | 0.19657 | 0.28131 | 0.34305 | 0.34178 | 0.32593 | 0.31338 | 0.29282 | 0.27693 | 0.2663 | 0.25968 | 0.25945 | 0.25927 | 0.26416 | 0.29822 | 0.3051 | 0.28371 | 0.25593 | 0.22634 | 0.19338
2015-02-15 | 0.16686 | 0.151 | 0.14291 | 0.13999 | 0.14124 | 0.15125 | 0.1718 | 0.20298 | 0.23971 | 0.26477 | 0.2795 | 0.28103 | 0.27418 | 0.26733 | 0.26134 | 0.25913 | 0.25789 | 0.2612 | 0.28742 | 0.29375 | 0.27366 | 0.24814 | 0.21991 | 0.18588
2015-02-16 | 0.15939 | 0.14527 | 0.14345 | 0.1451 | 0.14845 | 0.16352 | 0.19184 | 0.23379 | 0.27065 | 0.28189 | 0.2765 | 0.26416 | 0.2573 | 0.25233 | 0.25007 | 0.25088 | 0.25365 | 0.25886 | 0.28868 | 0.29945 | 0.27584 | 0.24558 | 0.2154 | 0.17814
2015-02-17 | 0.15104 | 0.1373 | 0.13292 | 0.13431 | 0.14308 | 0.16852 | 0.21507 | 0.26227 | 0.29043 | 0.30158 | 0.30665 | 0.30785 | 0.30971 | 0.31313 | 0.31673 | 0.32198 | 0.32475 | 0.32629 | 0.35252 | 0.36142 | 0.32634 | 0.28012 | 0.22776 | 0.18131
2015-02-18 | 0.14537 | 0.12639 | 0.12006 | 0.11844 | 0.12495 | 0.151 | 0.21123 | 0.25369 | 0.27088 | 0.2882 | 0.30481 | 0.31876 | 0.33116 | 0.34458 | 0.35736 | 0.36971 | 0.37417 | 0.36741 | 0.38557 | 0.39453 | 0.3558 | 0.30014 | 0.24634 | 0.19022
2015-02-19 | 0.15111 | 0.12978 | 0.12069 | 0.11708 | 0.12141 | 0.14472 | 0.20035 | 0.23619 | 0.25876 | 0.28573 | 0.31429 | 0.33973 | 0.36033 | 0.38071 | 0.40067 | 0.42015 | 0.42496 | 0.41322 | 0.42402 | 0.42891 | 0.38933 | 0.3324 | 0.27206 | 0.21252
2015-02-20 | 0.16712 | 0.14332 | 0.13086 | 0.12444 | 0.12623 | 0.14884 | 0.20298 | 0.24011 | 0.27333 | 0.31485 | 0.35655 | 0.38635 | 0.41473 | 0.43752 | 0.45391 | 0.46831 | 0.47028 | 0.45659 | 0.47239 | 0.48055 | 0.44135 | 0.38669 | 0.32126 | 0.25982
2015-02-21 | 0.20888 | 0.17613 | 0.16004 | 0.1523 | 0.15276 | 0.17364 | 0.22962 | 0.26915 | 0.32095 | 0.38009 | 0.43401 | 0.47562 | 0.50525 | 0.52487 | 0.5273 | 0.52174 | 0.48972 | 0.46405 | 0.47518 | 0.46105 | 0.41735 | 0.36386 | 0.31495 | 0.25922
2015-02-22 | 0.2109 | 0.17643 | 0.15903 | 0.14835 | 0.14562 | 0.14911 | 0.16528 | 0.19485 | 0.26472 | 0.33715 | 0.39436 | 0.4389 | 0.47525 | 0.49561 | 0.50365 | 0.50724 | 0.49422 | 0.46135 | 0.45591 | 0.44321 | 0.39555 | 0.3475 | 0.29876 | 0.24652
2015-02-23 | 0.20112 | 0.17098 | 0.1529 | 0.14281 | 0.13834 | 0.13996 | 0.14999 | 0.17431 | 0.23804 | 0.31011 | 0.37235 | 0.42279 | 0.48487 | 0.49523 | 0.50416 | 0.51227 | 0.50461 | 0.48368 | 0.48343 | 0.485 | 0.44003 | 0.37108 | 0.31192 | 0.24652
2015-02-24 | 0.19394 | 0.16823 | 0.15234 | 0.14356 | 0.14462 | 0.16601 | 0.21348 | 0.25242 | 0.29331 | 0.34676 | 0.3997 | 0.43925 | 0.47967 | 0.50827 | 0.52625 | 0.54028 | 0.52775 | 0.50827 | 0.52697 | 0.53077 | 0.47028 | 0.39862 | 0.3228 | 0.25247
2015-02-25 | 0.19817 | 0.16786 | 0.15083 | 0.14182 | 0.1425 | 0.164 | 0.2175 | 0.25098 | 0.28805 | 0.33334 | 0.3766 | 0.41455 | 0.45227 | 0.48645 | 0.51395 | 0.53031 | 0.52546 | 0.49727 | 0.50288 | 0.50307 | 0.45027 | 0.37993 | 0.31111 | 0.24113
2015-02-26 | 0.18869 | 0.15889 | 0.14178 | 0.13414 | 0.13471 | 0.15294 | 0.20278 | 0.23808 | 0.26943 | 0.30655 | 0.35919 | 0.39646 | 0.43122 | 0.45573 | 0.47171 | 0.475 | 0.46074 | 0.45099 | 0.47662 | 0.47581 | 0.43234 | 0.37472 | 0.30905 | 0.24621
2015-02-27 | 0.19733 | 0.17146 | 0.15835 | 0.15237 | 0.15424 | 0.17563 | 0.231 | 0.26449 | 0.28544 | 0.31253 | 0.34342 | 0.33679 | 0.36856 | 0.37301 | 0.37136 | 0.3673 | 0.35855 | 0.3729 | 0.4001 | 0.40502 | 0.37169 | 0.31744 | 0.25909 | 0.20645
2015-02-28 | 0.16638 | 0.14534 | 0.13607 | 0.13322 | 0.13744 | 0.1625 | 0.2225 | 0.26093 | 0.27357 | 0.28146 | 0.28776 | 0.2897 | 0.29009 | 0.29326 | 0.29674 | 0.30163 | 0.30471 | 0.30068 | 0.31485 | 0.32341 | 0.29625 | 0.26231 | 0.22463 | 0.18525
2015-03-01 | 0.15322 | 0.13457 | 0.12489 | 0.12078 | 0.12238 | 0.13246 | 0.15301 | 0.18305 | 0.22454 | 0.2541 | 0.27366 | 0.28405 | 0.29414 | 0.30426 | 0.31187 | 0.32177 | 0.323 | 0.31465 | 0.31536 | 0.32707 | 0.29581 | 0.26259 | 0.22686 | 0.18705
2015-03-02 | 0.15506 | 0.13637 | 0.1263 | 0.1176 | 0.11634 | 0.12116 | 0.13335 | 0.15591 | 0.20477 | 0.25039 | 0.28136 | 0.30485 | 0.32346 | 0.3422 | 0.35558 | 0.36752 | 0.37141 | 0.36223 | 0.36593 | 0.37937 | 0.34168 | 0.2938 | 0.24335 | 0.19318
2015-03-03 | 0.15957 | 0.13418 | 0.12125 | 0.11658 | 0.11925 | 0.14046 | 0.18881 | 0.22288 | 0.25584 | 0.29507 | 0.33391 | 0.36381 | 0.3943 | 0.42496 | 0.44501 | 0.46338 | 0.46892 | 0.45512 | 0.45494 | 0.46356 | 0.41154 | 0.34532 | 0.27921 | 0.21381
2015-03-04 | 0.16716 | 0.14033 | 0.12665 | 0.12 | 0.12144 | 0.14107 | 0.18967 | 0.2251 | 0.25634 | 0.29512 | 0.33225 | 0.36413 | 0.39413 | 0.4229 | 0.44815 | 0.46732 | 0.47202 | 0.4575 | 0.45897 | 0.46455 | 0.41892 | 0.3599 | 0.29316 | 0.22918
2015-03-05 | 0.18005 | 0.15446 | 0.1405 | 0.1349 | 0.13717 | 0.15813 | 0.21294 | 0.25007 | 0.28088 | 0.32686 | 0.36921 | 0.4075 | 0.44075 | 0.46283 | 0.47177 | 0.47469 | 0.46319 | 0.44839 | 0.4586 | 0.46375 | 0.42414 | 0.36642 | 0.30187 | 0.23703
2015-03-06 | 0.18873 | 0.16298 | 0.14779 | 0.14161 | 0.1426 | 0.16309 | 0.21515 | 0.25215 | 0.29556 | 0.34326 | 0.38065 | 0.41293 | 0.43508 | 0.43051 | 0.42021 | 0.36093 | 0.3336 | 0.33805 | 0.36927 | 0.37577 | 0.34612 | 0.30118 | 0.25265 | 0.20253
2015-03-07 | 0.16349 | 0.14138 | 0.13263 | 0.12868 | 0.13233 | 0.15456 | 0.20777 | 0.24415 | 0.2794 | 0.31016 | 0.33647 | 0.34867 | 0.3551 | 0.35569 | 0.35515 | 0.35563 | 0.35097 | 0.33857 | 0.34485 | 0.34937 | 0.32357 | 0.28127 | 0.23949 | 0.19065
2015-03-08 | 0.16073 | 0.14012 | 0.13109 | 0.12784 | 0.1303 | 0.13881 | 0.16149 | 0.19593 | 0.23518 | 0.25918 | 0.26625 | 0.2657 | 0.26453 | 0.26407 | 0.26765 | 0.273 | 0.27588 | 0.27324 | 0.28136 | 0.296 | 0.27102 | 0.24233 | 0.20921 | 0.17822
2015-03-09 | 0.1461 | 0 | 0.12936 | 0.12072 | 0.11773 | 0.12163 | 0.13296 | 0.15023 | 0.17726 | 0.21352 | 0.24545 | 0.26014 | 0.28069 | 0.29238 | 0.30108 | 0.31394 | 0.32748 | 0.33407 | 0.32423 | 0.32707 | 0.34273 | 0.30446 | 0.25789 | 0.19805
2015-03-10 | 0.15439 | 0.12839 | 0.11664 | 0.1131 | 0.11726 | 0.13693 | 0.18491 | 0.22484 | 0.23751 | 0.26333 | 0.2961 | 0.31668 | 0.34067 | 0.35709 | 0.38227 | 0.40744 | 0.42879 | 0.43027 | 0.41252 | 0.40784 | 0.4149 | 0.35644 | 0.29654 | 0.22901
2015-03-11 | 0.17413 | 0.14383 | 0.12829 | 0.1209 | 0.12087 | 0.14006 | 0.18802 | 0.2266 | 0.2376 | 0.26803 | 0.29659 | 0.32439 | 0.34953 | 0.37339 | 0.39651 | 0.4232 | 0.44634 | 0.45324 | 0.43728 | 0.42944 | 0.4374 | 0.38529 | 0.31983 | 0.24388
2015-03-12 | 0.19156 | 0.15932 | 0.14376 | 0.13713 | 0.13861 | 0.15928 | 0.21252 | 0.2102 | 0.26282 | 0.30138 | 0.35188 | 0.39504 | 0.43015 | 0.45482 | 0.46837 | 0.49504 | 0.51143 | 0.50378 | 0.47693 | 0.46596 | 0.47065 | 0.41484 | 0.34937 | 0.27669
2015-03-13 | 0.21691 | 0.18097 | 0.16109 | 0.15097 | 0.14838 | 0.16429 | 0.21003 | 0.24162 | 0.25125 | 0.28074 | 0.30376 | 0.31764 | 0.32547 | 0.33043 | 0.33386 | 0.33747 | 0.34453 | 0.34284 | 0.32367 | 0.32136 | 0.33423 | 0.29492 | 0.24603 | 0.19291
2015-03-14 | 0.15325 | 0.13286 | 0.12213 | 0.11953 | 0.12479 | 0.14866 | 0.20954 | 0.25955 | 0.27145 | 0.28222 | 0.29058 | 0.29262 | 0.29175 | 0.29394 | 0.29679 | 0.30202 | 0.30961 | 0.30915 | 0.29748 | 0.29649 | 0.3073 | 0.2775 | 0.23857 | 0.19737
2015-03-15 | 0.15638 | 0.13414 | 0.12141 | 0.11588 | 0.11692 | 0.12454 | 0.14124 | 0.17157 | 0.20917 | 0.24679 | 0.2775 | 0.29585 | 0.30941 | 0.32095 | 0.33475 | 0.34921 | 0.36517 | 0.36795 | 0.35017 | 0.33334 | 0.33715 | 0.30153 | 0.26319 | 0.21356
2015-03-16 | 0.17386 | 0.14866 | 0.13355 | 0.12543 | 0.12223 | 0.12429 | 0.135 | 0.15262 | 0.1912 | 0.24751 | 0.29141 | 0.32573 | 0.35424 | 0.37682 | 0.39936 | 0.41514 | 0.42255 | 0.41997 | 0.39947 | 0.39181 | 0.40548 | 0.36348 | 0.31374 | 0.2498
2015-03-17 | 0.19962 | 0.16952 | 0.15371 | 0.14817 | 0.15118 | 0.17371 | 0.22501 | 0.26765 | 0.29209 | 0.34331 | 0.40347 | 0.4473 | 0.48024 | 0.49739 | 0.50647 | 0.51291 | 0.51486 | 0.50065 | 0.48469 | 0.49415 | 0.49346 | 0.44171 | 0.38405 | 0.31132
2015-03-18 | 0.2531 | 0.21822 | 0.20144 | 0.19358 | 0.19235 | 0.21016 | 0.25895 | 0.29009 | 0.28467 | 0.30237 | 0.32014 | 0.33002 | 0.33857 | 0.35059 | 0.36659 | 0.38394 | 0.40262 | 0.40848 | 0.39238 | 0.3845 | 0.39402 | 0.3467 | 0.2867 | 0.22029
2015-03-19 | 0.16908 | 0.14168 | 0.128 | 0.12213 | 0.12368 | 0.14345 | 0.19207 | 0.22888 | 0.24495 | 0.27788 | 0.31232 | 0.33894 | 0.35709 | 0.37982 | 0.40284 | 0.42561 | 0.44015 | 0.44105 | 0.41764 | 0.4021 | 0.41287 | 0.36571 | 0.3068 | 0.23945
2015-03-20 | 0.18849 | 0.1581 | 0.14308 | 0.1349 | 0.1354 | 0.15417 | 0.20257 | 0.24095 | 0.25858 | 0.29102 | 0.32691 | 0.35504 | 0.37782 | 0.40227 | 0.42508 | 0.44363 | 0.45598 | 0.4516 | 0.43045 | 0.41345 | 0.42238 | 0.36746 | 0.3049 | 0.23967
2015-03-21 | 0.18428 | 0.15237 | 0.13418 | 0.12464 | 0.12441 | 0.13918 | 0.17734 | 0.21457 | 0.23967 | 0.27974 | 0.32321 | 0.35947 | 0.38961 | 0.42079 | 0.45148 | 0.47718 | 0.48739 | 0.47736 | 0.44243 | 0.41741 | 0.41945 | 0.37191 | 0.32336 | 0.26761
2015-03-22 | 0.21628 | 0.18487 | 0.16473 | 0.15322 | 0.1487 | 0.1535 | 0.16875 | 0.18963 | 0.22759 | 0.29292 | 0.34681 | 0.37704 | 0.40445 | 0.42584 | 0.44081 | 0.45732 | 0.47892 | 0.47849 | 0.45105 | 0.41886 | 0.41519 | 0.36681 | 0.31253 | 0.25279
2015-03-23 | 0.20241 | 0.16793 | 0.1487 | 0.13797 | 0.13299 | 0.1351 | 0.14489 | 0.16062 | 0.19809 | 0.2606 | 0.32152 | 0.37147 | 0.42214 | 0.46855 | 0.50135 | 0.52953 | 0.54194 | 0.54055 | 0.51602 | 0.48689 | 0.49156 | 0.43051 | 0.36451 | 0.28951
2015-03-24 | 0.23005 | 0.1916 | 0.16782 | 0.15835 | 0.15713 | 0.17322 | 0.21049 | 0.24576 | 0.27215 | 0.31162 | 0.34442 | 0.36801 | 0.37726 | 0.37621 | 0.36642 | 0.36006 | 0.36071 | 0.36462 | 0.36397 | 0.3679 | 0.36212 | 0.3182 | 0.27098 | 0.21507
2015-03-25 | 0.17277 | 0.14445 | 0.12784 | 0.12201 | 0.12368 | 0.13942 | 0.17944 | 0.21469 | 0.23738 | 0.27281 | 0.29905 | 0.3264 | 0.34857 | 0.36435 | 0.37926 | 0.3913 | 0.40181 | 0.40267 | 0.38669 | 0.3679 | 0.37477 | 0.32593 | 0.26528 | 0.20278
2015-03-26 | 0.15442 | 0.12936 | 0.11621 | 0.11183 | 0.11526 | 0.13414 | 0.18043 | 0.22497 | 0.25279 | 0.26756 | 0.27955 | 0.27964 | 0.2739 | 0.26695 | 0.2625 | 0.26001 | 0.26449 | 0.26761 | 0.26602 | 0.28127 | 0.30451 | 0.27517 | 0.23191 | 0.18869
2015-03-27 | 0.15329 | 0.13404 | 0.1246 | 0.12245 | 0.12668 | 0.1461 | 0.1916 | 0.22737 | 0.24621 | 0.2739 | 0.28801 | 0.29507 | 0.29836 | 0.30108 | 0.30073 | 0.30009 | 0.30118 | 0.30044 | 0.29669 | 0.31021 | 0.32295 | 0.2917 | 0.24895 | 0.20148
2015-03-28 | 0.16268 | 0.13874 | 0.12697 | 0.1209 | 0.1233 | 0.13979 | 0.17837 | 0.21377 | 0.241 | 0.28045 | 0.32275 | 0.34905 | 0.36774 | 0.37887 | 0.38803 | 0.39379 | 0.39277 | 0.38065 | 0.36315 | 0.36332 | 0.37053 | 0.33857 | 0.29955 | 0.25111
2015-03-29 | 0.20826 | 0.18085 | 0.16403 | 0.15563 | 0.15389 | 0.15975 | 0.17575 | 0.20035 | 0.23993 | 0.29945 | 0.35547 | 0.39663 | 0.41531 | 0.42543 | 0.42331 | 0.4131 | 0.39987 | 0.38624 | 0.36533 | 0.35947 | 0.34506 | 0.30267 | 0.26532 | 0.22067
2015-03-30 | 0.17978 | 0.15329 | 0.13593 | 0.12771 | 0.12476 | 0.12784 | 0.1405 | 0.15706 | 0.18975 | 0.23667 | 0.27206 | 0.29072 | 0.2994 | 0.306 | 0.31232 | 0.31769 | 0.32316 | 0.32193 | 0.309 | 0.30004 | 0.31688 | 0.27883 | 0.23161 | 0.1794
2015-03-31 | 0.14043 | 0.1215 | 0.11002 | 0.10643 | 0.11059 | 0.1355 | 0.18642 | 0.22284 | 0.23584 | 0.25447 | 0.27442 | 0.29087 | 0.30291 | 0.31754 | 0.33069 | 0.34183 | 0.34713 | 0.34141 | 0.33485 | 0.34294 | 0.35795 | 0.31293 | 0.25844 | 0.19878
2015-04-01 | 0.15417 | 0.13037 | 0.119 | 0.1145 | 0.11757 | 0.13868 | 0.19505 | 0.23396 | 0.24872 | 0.26948 | 0.29038 | 0.309 | 0.32434 | 0.34469 | 0.36998 | 0.39942 | 0.42714 | 0.43728 | 0.42191 | 0.39521 | 0.40141 | 0.35043 | 0.28127 | 0.21427
2015-04-02 | 0.16473 | 0.13737 | 0.12352 | 0.11668 | 0.11844 | 0.13969 | 0.1912 | 0.22348 | 0.23923 | 0.27004 | 0.29733 | 0.32311 | 0.34125 | 0.36424 | 0.4005 | 0.43436 | 0.46068 | 0.47189 | 0.45087 | 0.42296 | 0.42861 | 0.37566 | 0.30311 | 0.23283
2015-04-03 | 0.1789 | 0.14842 | 0.1324 | 0.12604 | 0.12742 | 0.1496 | 0.19797 | 0.22992 | 0.25261 | 0.28868 | 0.3248 | 0.35623 | 0.38557 | 0.41461 | 0.45604 | 0.48431 | 0.50468 | 0.4965 | 0.474 | 0.44201 | 0.4586 | 0.40187 | 0.32542 | 0.25116
2015-04-04 | 0.19378 | 0.16181 | 0.14345 | 0.13484 | 0.13388 | 0.15343 | 0.20625 | 0.2372 | 0.2625 | 0.305 | 0.34862 | 0.38646 | 0.41676 | 0.44894 | 0.48092 | 0.50962 | 0.53334 | 0.5311 | 0.50224 | 0.45391 | 0.44393 | 0.39521 | 0.33532 | 0.27126
2015-04-05 | 0.21565 | 0.1797 | 0.15806 | 0.14531 | 0.14029 | 0.14206 | 0.15695 | 0.17673 | 0.22836 | 0.29512 | 0.35188 | 0.40067 | 0.44261 | 0.4872 | 0.51901 | 0.54307 | 0.55229 | 0.54627 | 0.50654 | 0.45622 | 0.45081 | 0.39953 | 0.34189 | 0.28074
2015-04-06 | 0.2236 | 0.18564 | 0.16044 | 0.1462 | 0.14046 | 0.14131 | 0.15125 | 0.16576 | 0.21847 | 0.28883 | 0.35156 | 0.40027 | 0.44706 | 0.48998 | 0.53104 | 0.55807 | 0.57143 | 0.57047 | 0.53836 | 0.49631 | 0.49778 | 0.43532 | 0.36315 | 0.28203
2015-04-07 | 0.22613 | 0.19089 | 0.17277 | 0.16429 | 0.1666 | 0.19073 | 0.24598 | 0.28041 | 0.31283 | 0.37721 | 0.44652 | 0.51117 | 0.56761 | 0.62003 | 0.66281 | 0.69597 | 0.71668 | 0.70837 | 0.66803 | 0.6336 | 0.62344 | 0.54354 | 0.45196 | 0.36555
2015-04-08 | 0.29935 | 0.25383 | 0.22271 | 0.20719 | 0.20744 | 0.22992 | 0.29209 | 0.328 | 0.35892 | 0.40479 | 0.46135 | 0.51091 | 0.54108 | 0.55713 | 0.5539 | 0.53697 | 0.54607 | 0.51008 | 0.44435 | 0.41409 | 0.41811 | 0.3637 | 0.29389 | 0.22737
2015-04-09 | 0.1817 | 0.15396 | 0.13891 | 0.13161 | 0.13112 | 0.14978 | 0.19918 | 0.22484 | 0.23852 | 0.26723 | 0.29063 | 0.30346 | 0.31121 | 0.31774 | 0.32846 | 0.34178 | 0.35472 | 0.3631 | 0.35408 | 0.34152 | 0.36076 | 0.31881 | 0.25657 | 0.19801
2015-04-10 | 0.15492 | 0.13197 | 0.11947 | 0.11499 | 0.11714 | 0.13723 | 0.18802 | 0.21801 | 0.23296 | 0.25872 | 0.28362 | 0.30232 | 0.31531 | 0.33053 | 0.3474 | 0.36615 | 0.37937 | 0.37904 | 0.36604 | 0.35703 | 0.37604 | 0.33033 | 0.27117 | 0.20966
2015-04-11 | 0.16506 | 0.1379 | 0.1247 | 0.11928 | 0.12106 | 0.13948 | 0.18884 | 0.21978 | 0.24246 | 0.28151 | 0.31902 | 0.34586 | 0.365 | 0.38456 | 0.40279 | 0.40957 | 0.41171 | 0.4013 | 0.38238 | 0.36812 | 0.37798 | 0.34389 | 0.2991 | 0.24652
2015-04-12 | 0.19966 | 0.16949 | 0.14953 | 0.13864 | 0.13418 | 0.1376 | 0.15368 | 0.17488 | 0.22651 | 0.29038 | 0.34421 | 0.3886 | 0.41992 | 0.44875 | 0.46645 | 0.48287 | 0.48903 | 0.48218 | 0.44646 | 0.40675 | 0.40646 | 0.36883 | 0.31359 | 0.2613
2015-04-13 | 0.21427 | 0.18074 | 0.16112 | 0.14852 | 0.14339 | 0.14527 | 0.15613 | 0.17217 | 0.21784 | 0.28002 | 0.33183 | 0.37136 | 0.40755 | 0.43234 | 0.44291 | 0.45148 | 0.45372 | 0.44948 | 0.42938 | 0.42343 | 0.44159 | 0.39719 | 0.33768 | 0.26962
2015-04-14 | 0.21611 | 0.18436 | 0.16778 | 0.15863 | 0.15946 | 0.18005 | 0.234 | 0.2677 | 0.30645 | 0.37009 | 0.43377 | 0.4927 | 0.54261 | 0.59367 | 0.63569 | 0.67232 | 0.69184 | 0.6854 | 0.64478 | 0.59527 | 0.58854 | 0.51764 | 0.42673 | 0.33417
2015-04-15 | 0.26384 | 0.22292 | 0.19918 | 0.18355 | 0.18062 | 0.19994 | 0.25574 | 0.28791 | 0.33647 | 0.41061 | 0.47774 | 0.54301 | 0.59277 | 0.62952 | 0.64428 | 0.65577 | 0.6474 | 0.59771 | 0.573 | 0.53949 | 0.54194 | 0.48011 | 0.39317 | 0.3081
2015-04-16 | 0.24531 | 0.20649 | 0.18378 | 0.17255 | 0.17023 | 0.1881 | 0.23799 | 0.26467 | 0.28463 | 0.31673 | 0.34485 | 0.36479 | 0.38607 | 0.41131 | 0.43003 | 0.44429 | 0.45306 | 0.44984 | 0.4349 | 0.4314 | 0.44779 | 0.41084 | 0.34485 | 0.27244
2015-04-17 | 0.22033 | 0.18916 | 0.17202 | 0.16338 | 0.16458 | 0.18592 | 0.23927 | 0.27262 | 0.30366 | 0.353 | 0.3993 | 0.43057 | 0.44123 | 0.44954 | 0.45269 | 0.44791 | 0.44069 | 0.42578 | 0.41212 | 0.40393 | 0.41421 | 0.38372 | 0.33188 | 0.2706
2015-04-18 | 0.22058 | 0.18849 | 0.16901 | 0.15874 | 0.15716 | 0.17349 | 0.20941 | 0.24215 | 0.28902 | 0.35311 | 0.4098 | 0.44972 | 0.47525 | 0.50372 | 0.51784 | 0.51531 | 0.50969 | 0.50307 | 0.47562 | 0.44411 | 0.4458 | 0.40946 | 0.36011 | 0.306
2015-04-19 | 0.25202 | 0.21902 | 0.19733 | 0.18378 | 0.17928 | 0.18347 | 0.19164 | 0.20432 | 0.24299 | 0.31424 | 0.37893 | 0.42673 | 0.46726 | 0.49803 | 0.51524 | 0.52703 | 0.52514 | 0.50154 | 0.45713 | 0.40548 | 0.39663 | 0.3529 | 0.30446 | 0.24268
2015-04-20 | 0.19271 | 0.1591 | 0.13804 | 0.12765 | 0.1234 | 0.12562 | 0.13607 | 0.14894 | 0.18841 | 0.23422 | 0.26171 | 0.2853 | 0.30167 | 0.31374 | 0.32198 | 0.32851 | 0.33277 | 0.32831 | 0.31718 | 0.31091 | 0.33313 | 0.30835 | 0.26148 | 0.20551
2015-04-21 | 0.16181 | 0.136 | 0.12314 | 0.11711 | 0.11897 | 0.13817 | 0.18336 | 0.2102 | 0.23361 | 0.26532 | 0.29674 | 0.32177 | 0.34809 | 0.37004 | 0.39566 | 0.41653 | 0.43371 | 0.43217 | 0.41898 | 0.40101 | 0.41479 | 0.36702 | 0.30068 | 0.23588
2015-04-22 | 0.18231 | 0.15034 | 0.13593 | 0.12745 | 0.12762 | 0.14922 | 0.19837 | 0.22194 | 0.24733 | 0.28031 | 0.31673 | 0.35488 | 0.38495 | 0.41027 | 0.43722 | 0.47096 | 0.49498 | 0.49956 | 0.48105 | 0.45354 | 0.46584 | 0.41247 | 0.33371 | 0.25611
2015-04-23 | 0.19974 | 0.16756 | 0.14873 | 0.13787 | 0.13617 | 0.15435 | 0.20015 | 0.17371 | 0.25721 | 0.29581 | 0.33511 | 0.36582 | 0.40411 | 0.45257 | 0.50692 | 0.54961 | 0.58143 | 0.58958 | 0.56463 | 0.51836 | 0.51363 | 0.46535 | 0.38288 | 0.28443
2015-04-24 | 0.22518 | 0.18928 | 0.15867 | 0.14637 | 0.14675 | 0.15813 | 0.20314 | 0.23231 | 0.26658 | 0.31927 | 0.37654 | 0.42808 | 0.47793 | 0.52442 | 0.56503 | 0.60611 | 0.63052 | 0.6273 | 0.59166 | 0.5379 | 0.53354 | 0.47444 | 0.38725 | 0.30356
2015-04-25 | 0.23733 | 0.19449 | 0.16975 | 0.15616 | 0.15308 | 0.17045 | 0.21662 | 0.24509 | 0.28294 | 0.33899 | 0.4037 | 0.46461 | 0.52096 | 0.57553 | 0.62466 | 0.66766 | 0.69176 | 0.68518 | 0.63533 | 0.56551 | 0.5468 | 0.48808 | 0.41003 | 0.33188
2015-04-26 | 0.26134 | 0.21377 | 0.18518 | 0.16771 | 0.15806 | 0.15871 | 0.16952 | 0.19172 | 0.25279 | 0.32996 | 0.40825 | 0.48174 | 0.54327 | 0.59214 | 0.62245 | 0.65001 | 0.66442 | 0.65584 | 0.60864 | 0.53969 | 0.52109 | 0.46818 | 0.4009 | 0.33261
2015-04-27 | 0.27206 | 0.22862 | 0.19841 | 0.18131 | 0.17072 | 0.16889 | 0.17488 | 0.19231 | 0.2601 | 0.34894 | 0.43252 | 0.50622 | 0.56714 | 0.61889 | 0.65446 | 0.68555 | 0.69808 | 0.68967 | 0.64631 | 0.58681 | 0.57841 | 0.51751 | 0.42838 | 0.34692
2015-04-28 | 0.28256 | 0.24215 | 0.21796 | 0.20347 | 0.20225 | 0.22527 | 0.27807 | 0.31157 | 0.35892 | 0.42962 | 0.51622 | 0.5943 | 0.65643 | 0.71172 | 0.75907 | 0.79639 | 0.8064 | 0.80244 | 0.75836 | 0.69387 | 0.67587 | 0.59576 | 0.4889 | 0.3917
2015-04-29 | 0.32004 | 0.27371 | 0.2454 | 0.2297 | 0.22712 | 0.24868 | 0.30059 | 0.33464 | 0.39317 | 0.4727 | 0.55814 | 0.63526 | 0.69485 | 0.74452 | 0.77997 | 0.80559 | 0.80026 | 0.78172 | 0.74553 | 0.68794 | 0.66656 | 0.59138 | 0.48834 | 0.3913
2015-04-30 | 0.31779 | 0.27546 | 0.24944 | 0.23545 | 0.23457 | 0.25616 | 0.31006 | 0.34432 | 0.40147 | 0.48168 | 0.56659 | 0.63806 | 0.69342 | 0.74312 | 0.77424 | 0.79599 | 0.78468 | 0.72403 | 0.68033 | 0.63475 | 0.63167 | 0.56585 | 0.46942 | 0.37837
2015-05-01 | 0.3067 | 0.2637 | 0.23672 | 0.22284 | 0.21898 | 0.24197 | 0.29772 | 0.33303 | 0.38405 | 0.46338 | 0.55148 | 0.62245 | 0.68145 | 0.73366 | 0.76774 | 0.78507 | 0.77638 | 0.73103 | 0.66413 | 0.61443 | 0.60991 | 0.53975 | 0.45136 | 0.36599
2015-05-02 | 0.30014 | 0.2578 | 0.23222 | 0.21721 | 0.21335 | 0.23483 | 0.28786 | 0.32357 | 0.36839 | 0.43818 | 0.50218 | 0.55282 | 0.58322 | 0.61925 | 0.64573 | 0.6598 | 0.65103 | 0.62487 | 0.58563 | 0.53426 | 0.53328 | 0.46405 | 0.39902 | 0.33423
2015-05-03 | 0.27574 | 0.23492 | 0.20933 | 0.19449 | 0.18712 | 0.19117 | 0.20526 | 0.22828 | 0.27683 | 0.34241 | 0.40039 | 0.44231 | 0.46221 | 0.47189 | 0.46645 | 0.44195 | 0.38781 | 0.36774 | 0.34969 | 0.34479 | 0.35698 | 0.3347 | 0.29861 | 0.25579
2015-05-04 | 0.21515 | 0.1856 | 0.1683 | 0.15706 | 0.15361 | 0.15368 | 0.15784 | 0.16298 | 0.20298 | 0.25338 | 0.29649 | 0.32924 | 0.36413 | 0.39538 | 0.42337 | 0.45567 | 0.48155 | 0.49492 | 0.48337 | 0.44303 | 0.42974 | 0.38048 | 0.3209 | 0.24607
2015-05-05 | 0.1937 | 0.15699 | 0.14376 | 0.13461 | 0.13487 | 0.15421 | 0.19597 | 0.22416 | 0.25959 | 0.30976 | 0.3655 | 0.41543 | 0.46541 | 0.51356 | 0.55982 | 0.60009 | 0.63641 | 0.6416 | 0.61224 | 0.52115 | 0.52363 | 0.45964 | 0.34926 | 0.2841
2015-05-06 | 0.22008 | 0.18398 | 0.16152 | 0.14887 | 0.14596 | 0.16319 | 0.2067 | 0.23571 | 0.273 | 0.32939 | 0.39057 | 0.45458 | 0.51881 | 0.57 | 0.62053 | 0.66575 | 0.6953 | 0.69334 | 0.65687 | 0.56415 | 0.57519 | 0.50982 | 0.41776 | 0.32434
2015-05-07 | 0.25844 | 0.21759 | 0.19545 | 0.18139 | 0.17841 | 0.19645 | 0.24326 | 0.27418 | 0.32136 | 0.38277 | 0.45537 | 0.51966 | 0.57999 | 0.63778 | 0.69214 | 0.71974 | 0.7404 | 0.73459 | 0.68967 | 0.62665 | 0.61182 | 0.55349 | 0.45524 | 0.36332
2015-05-08 | 0.28999 | 0.248 | 0.22296 | 0.20555 | 0.20156 | 0.2194 | 0.26714 | 0.29698 | 0.34883 | 0.41531 | 0.48752 | 0.55068 | 0.60688 | 0.66207 | 0.70617 | 0.74623 | 0.77099 | 0.76411 | 0.7248 | 0.65584 | 0.6303 | 0.5651 | 0.47227 | 0.38288
2015-05-09 | 0.30004 | 0.25297 | 0.22811 | 0.20995 | 0.20559 | 0.22429 | 0.27229 | 0.30306 | 0.35257 | 0.42003 | 0.49017 | 0.55095 | 0.60583 | 0.65672 | 0.70398 | 0.73985 | 0.75813 | 0.74001 | 0.68495 | 0.6109 | 0.58109 | 0.52298 | 0.45178 | 0.37876
2015-05-10 | 0.31212 | 0.26859 | 0.24113 | 0.22237 | 0.2136 | 0.21582 | 0.22501 | 0.24989 | 0.3227 | 0.40635 | 0.47313 | 0.52723 | 0.58481 | 0.6238 | 0.64965 | 0.66899 | 0.66788 | 0.65365 | 0.61386 | 0.54634 | 0.55269 | 0.50442 | 0.44411 | 0.3761
2015-05-11 | 0.31384 | 0.27164 | 0.24246 | 0.22454 | 0.21603 | 0.21386 | 0.21725 | 0.23231 | 0.28849 | 0.36435 | 0.43033 | 0.48462 | 0.53473 | 0.57889 | 0.61238 | 0.6293 | 0.63569 | 0.61818 | 0.58239 | 0.53248 | 0.53341 | 0.50052 | 0.42997 | 0.34803
2015-05-12 | 0.2795 | 0.23879 | 0.21507 | 0.2031 | 0.20209 | 0.22313 | 0.27201 | 0.30296 | 0.34862 | 0.41892 | 0.49574 | 0.56144 | 0.6179 | 0.66376 | 0.69816 | 0.7288 | 0.74032 | 0.73072 | 0.69884 | 0.65198 | 0.63922 | 0.5685 | 0.47171 | 0.38255
2015-05-13 | 0.31172 | 0.27018 | 0.2425 | 0.22626 | 0.22279 | 0.24371 | 0.2936 | 0.32413 | 0.36889 | 0.43991 | 0.51175 | 0.56938 | 0.62409 | 0.66141 | 0.68959 | 0.7134 | 0.7258 | 0.71202 | 0.67239 | 0.62017 | 0.61224 | 0.55793 | 0.46713 | 0.37516
2015-05-14 | 0.31111 | 0.26985 | 0.24082 | 0.22467 | 0.22164 | 0.23005 | 0.29787 | 0.32249 | 0.37207 | 0.45063 | 0.52331 | 0.59513 | 0.64878 | 0.68376 | 0.70891 | 0.70815 | 0.7008 | 0.68503 | 0.64305 | 0.59492 | 0.59834 | 0.54247 | 0.45872 | 0.36921
2015-05-15 | 0.2995 | 0.25753 | 0.231 | 0.21704 | 0.21653 | 0.23689 | 0.28694 | 0.31657 | 0.35768 | 0.43074 | 0.50014 | 0.53823 | 0.55269 | 0.54981 | 0.52677 | 0.50052 | 0.49346 | 0.49244 | 0.47905 | 0.45744 | 0.45744 | 0.42396 | 0.35822 | 0.2915
2015-05-16 | 0.23641 | 0.20432 | 0.18487 | 0.17304 | 0.17128 | 0.19215 | 0.23905 | 0.2612 | 0.27831 | 0.31051 | 0.33931 | 0.36039 | 0.36998 | 0.3766 | 0.39046 | 0.3985 | 0.40761 | 0.3981 | 0.37372 | 0.34315 | 0.33079 | 0.30476 | 0.26296 | 0.21402
2015-05-17 | 0.17184 | 0.14648 | 0.13014 | 0.12134 | 0.11875 | 0.12169 | 0.13122 | 0.15027 | 0.19465 | 0.2467 | 0.29336 | 0.33157 | 0.36082 | 0.3886 | 0.41618 | 0.43854 | 0.45287 | 0.45015 | 0.4239 | 0.38065 | 0.36812 | 0.34432 | 0.2962 | 0.2467
2015-05-18 | 0.20278 | 0.1724 | 0.15272 | 0.14002 | 0.13447 | 0.1356 | 0.13898 | 0.15474 | 0.20298 | 0.26621 | 0.32249 | 0.36839 | 0.40859 | 0.44255 | 0.47431 | 0.49797 | 0.51531 | 0.51136 | 0.47911 | 0.43502 | 0.43009 | 0.39885 | 0.33553 | 0.267
2015-05-19 | 0.21315 | 0.17947 | 0.15982 | 0.15055 | 0.15097 | 0.16938 | 0.21206 | 0.23923 | 0.28246 | 0.33799 | 0.39373 | 0.44411 | 0.48909 | 0.53565 | 0.56789 | 0.59981 | 0.6174 | 0.61457 | 0.58557 | 0.5311 | 0.51253 | 0.46541 | 0.3868 | 0.30247
2015-05-20 | 0.23971 | 0.20087 | 0.17997 | 0.16778 | 0.16436 | 0.18051 | 0.2216 | 0.25456 | 0.29851 | 0.35671 | 0.41846 | 0.47233 | 0.51738 | 0.55625 | 0.5846 | 0.6078 | 0.62152 | 0.61542 | 0.59069 | 0.53453 | 0.51784 | 0.46553 | 0.38478 | 0.30366
2015-05-21 | 0.24073 | 0.20132 | 0.17806 | 0.16389 | 0.16011 | 0.17609 | 0.21809 | 0.2498 | 0.2881 | 0.34015 | 0.39532 | 0.44682 | 0.49194 | 0.54234 | 0.59214 | 0.62708 | 0.64863 | 0.63972 | 0.60309 | 0.54407 | 0.51777 | 0.47152 | 0.39136 | 0.30705
2015-05-22 | 0.23777 | 0.19733 | 0.17109 | 0.15828 | 0.15606 | 0.173 | 0.21511 | 0.24455 | 0.28893 | 0.34612 | 0.412 | 0.47936 | 0.54547 | 0.61273 | 0.66516 | 0.71081 | 0.74009 | 0.73103 | 0.68967 | 0.61932 | 0.58074 | 0.53209 | 0.43478 | 0.34067
2015-05-23 | 0.26551 | 0.22003 | 0.1912 | 0.17514 | 0.16886 | 0.18332 | 0.22114 | 0.25936 | 0.31394 | 0.38573 | 0.46682 | 0.55336 | 0.63174 | 0.71515 | 0.77861 | 0.82146 | 0.83543 | 0.81657 | 0.75938 | 0.66472 | 0.62658 | 0.57423 | 0.48745 | 0.40078
2015-05-24 | 0.32562 | 0.27399 | 0.23654 | 0.21236 | 0.19974 | 0.19637 | 0.19958 | 0.22514 | 0.30009 | 0.39424 | 0.48897 | 0.58418 | 0.67025 | 0.73273 | 0.77194 | 0.79317 | 0.79221 | 0.77416 | 0.7137 | 0.63857 | 0.60773 | 0.55464 | 0.47824 | 0.40061
2015-05-25 | 0.33386 | 0.28198 | 0.24554 | 0.22275 | 0.20937 | 0.20441 | 0.20649 | 0.22275 | 0.28198 | 0.36462 | 0.46387 | 0.54994 | 0.63138 | 0.68809 | 0.72272 | 0.74288 | 0.74967 | 0.7218 | 0.66472 | 0.60155 | 0.58232 | 0.53539 | 0.45793 | 0.38573
2015-05-26 | 0.31698 | 0.27229 | 0.24139 | 0.22211 | 0.21186 | 0.21202 | 0.21653 | 0.2383 | 0.31278 | 0.41322 | 0.51414 | 0.59277 | 0.66281 | 0.71309 | 0.74187 | 0.75703 | 0.7575 | 0.73412 | 0.67795 | 0.61386 | 0.60071 | 0.54607 | 0.4608 | 0.37141
2015-05-27 | 0.30386 | 0.25918 | 0.23174 | 0.2157 | 0.21045 | 0.23031 | 0.27423 | 0.31561 | 0.37544 | 0.45567 | 0.53962 | 0.61996 | 0.68227 | 0.73188 | 0.76143 | 0.77551 | 0.75311 | 0.6959 | 0.64384 | 0.59485 | 0.5893 | 0.53929 | 0.45537 | 0.36223
2015-05-28 | 0.29448 | 0.25188 | 0.22664 | 0.21148 | 0.20789 | 0.22729 | 0.27281 | 0.30885 | 0.36397 | 0.43555 | 0.51524 | 0.60239 | 0.66774 | 0.72357 | 0.75475 | 0.76372 | 0.76285 | 0.73265 | 0.68637 | 0.63662 | 0.62102 | 0.56605 | 0.47761 | 0.38742
2015-05-29 | 0.31374 | 0.26546 | 0.23848 | 0.22267 | 0.21721 | 0.23518 | 0.28002 | 0.31612 | 0.36299 | 0.42578 | 0.49581 | 0.54827 | 0.58102 | 0.60295 | 0.58764 | 0.57095 | 0.56043 | 0.54727 | 0.53532 | 0.49988 | 0.4965 | 0.4635 | 0.39862 | 0.32506
2015-05-30 | 0.25922 | 0.21637 | 0.19669 | 0.18494 | 0.18282 | 0.1999 | 0.24024 | 0.27475 | 0.32624 | 0.40767 | 0.48657 | 0.55551 | 0.61252 | 0.65826 | 0.68585 | 0.70382 | 0.69876 | 0.66119 | 0.59632 | 0.54527 | 0.53045 | 0.48733 | 0.42367 | 0.35952
2015-05-31 | 0.30088 | 0.2546 | 0.22463 | 0.20604 | 0.1991 | 0.19789 | 0.20604 | 0.23339 | 0.30825 | 0.40296 | 0.49625 | 0.5743 | 0.62716 | 0.662 | 0.66788 | 0.66251 | 0.64305 | 0.60141 | 0.55484 | 0.50756 | 0.50135 | 0.47084 | 0.41799 | 0.35418
2015-06-01 | 0.30054 | 0.25606 | 0.2288 | 0.21057 | 0.20091 | 0.20043 | 0.20416 | 0.2233 | 0.28511 | 0.36993 | 0.45585 | 0.52546 | 0.58605 | 0.62923 | 0.6519 | 0.64623 | 0.61904 | 0.57341 | 0.52461 | 0.49232 | 0.49168 | 0.46991 | 0.41264 | 0.34215
2015-06-02 | 0.2839 | 0.24665 | 0.22634 | 0.21536 | 0.2167 | 0.24082 | 0.2867 | 0.31953 | 0.3514 | 0.39 | 0.42867 | 0.4513 | 0.47394 | 0.48935 | 0.49982 | 0.49931 | 0.49689 | 0.48494 | 0.47282 | 0.45964 | 0.46381 | 0.43824 | 0.37544 | 0.3071
2015-06-03 | 0.25039 | 0.21515 | 0.19465 | 0.18282 | 0.18212 | 0.20237 | 0.24616 | 0.27607 | 0.3061 | 0.35102 | 0.3989 | 0.44159 | 0.47382 | 0.49778 | 0.50795 | 0.5113 | 0.49886 | 0.48557 | 0.46319 | 0.44411 | 0.45033 | 0.41799 | 0.35817 | 0.28902
2015-06-04 | 0.23217 | 0.19745 | 0.17711 | 0.16693 | 0.16679 | 0.18568 | 0.22639 | 0.23278 | 0.29302 | 0.35322 | 0.40698 | 0.45172 | 0.48356 | 0.52285 | 0.55195 | 0.57197 | 0.58743 | 0.59055 | 0.57054 | 0.52514 | 0.50327 | 0.46732 | 0.40016 | 0.32142
2015-06-05 | 0.25744 | 0.21822 | 0.19342 | 0.17883 | 0.17428 | 0.19022 | 0.22591 | 0.26658 | 0.32702 | 0.39981 | 0.48136 | 0.55942 | 0.62266 | 0.68338 | 0.72664 | 0.75836 | 0.77178 | 0.76585 | 0.72857 | 0.65511 | 0.61521 | 0.55437 | 0.46424 | 0.36763
2015-06-06 | 0.29762 | 0.24796 | 0.21666 | 0.19789 | 0.18943 | 0.20233 | 0.23135 | 0.27291 | 0.34522 | 0.43318 | 0.53281 | 0.63181 | 0.71637 | 0.78316 | 0.83139 | 0.85876 | 0.86782 | 0.85125 | 0.79873 | 0.71782 | 0.6667 | 0.61125 | 0.52318 | 0.43854
2015-06-07 | 0.36223 | 0.30735 | 0.2706 | 0.24854 | 0.23383 | 0.22875 | 0.233 | 0.26236 | 0.34421 | 0.44249 | 0.55296 | 0.65789 | 0.73057 | 0.78308 | 0.81469 | 0.82326 | 0.79381 | 0.74967 | 0.69244 | 0.63583 | 0.59827 | 0.54887 | 0.47494 | 0.39947
2015-06-08 | 0.33397 | 0.28429 | 0.25075 | 0.22313 | 0.21469 | 0.21148 | 0.21206 | 0.23027 | 0.29713 | 0.39839 | 0.50622 | 0.60618 | 0.66862 | 0.68324 | 0.66678 | 0.65658 | 0.63742 | 0.61719 | 0.57909 | 0.5344 | 0.50982 | 0.47264 | 0.39782 | 0.33053
2015-06-09 | 0.26691 | 0.22621 | 0.1997 | 0.18666 | 0.18487 | 0.2014 | 0.2337 | 0.27159 | 0.33116 | 0.4109 | 0.50634 | 0.61153 | 0.69718 | 0.77138 | 0.81217 | 0.79985 | 0.77813 | 0.72403 | 0.66229 | 0.60928 | 0.58026 | 0.53163 | 0.44694 | 0.3618
2015-06-10 | 0.29214 | 0.24755 | 0.22177 | 0.20616 | 0.20221 | 0.21906 | 0.25288 | 0.29945 | 0.37042 | 0.45269 | 0.53572 | 0.61584 | 0.68078 | 0.71775 | 0.71576 | 0.66737 | 0.62494 | 0.60534 | 0.60022 | 0.56402 | 0.55222 | 0.50058 | 0.41921 | 0.33967
2015-06-11 | 0.27869 | 0.23773 | 0.21061 | 0.19657 | 0.19342 | 0.20793 | 0.24255 | 0.28309 | 0.34607 | 0.43425 | 0.5205 | 0.59764 | 0.64798 | 0.67973 | 0.64798 | 0.59374 | 0.56693 | 0.55868 | 0.547 | 0.51233 | 0.49606 | 0.46295 | 0.39356 | 0.32142
2015-06-12 | 0.26222 | 0.22241 | 0.19853 | 0.18436 | 0.18124 | 0.19469 | 0.22746 | 0.25785 | 0.29204 | 0.33999 | 0.4052 | 0.48111 | 0.56823 | 0.65074 | 0.70792 | 0.72073 | 0.6848 | 0.62959 | 0.58881 | 0.548 | 0.52677 | 0.4823 | 0.40027 | 0.32413
2015-06-13 | 0.26277 | 0.22262 | 0.19805 | 0.18282 | 0.18001 | 0.19322 | 0.22173 | 0.263 | 0.32862 | 0.40365 | 0.48236 | 0.56375 | 0.63045 | 0.66545 | 0.66464 | 0.62644 | 0.58826 | 0.54867 | 0.51434 | 0.46602 | 0.43776 | 0.41009 | 0.35941 | 0.30004
2015-06-14 | 0.24895 | 0.21265 | 0.18873 | 0.17503 | 0.16908 | 0.17146 | 0.17982 | 0.20457 | 0.26556 | 0.34761 | 0.43448 | 0.51888 | 0.58764 | 0.64623 | 0.67394 | 0.6718 | 0.63634 | 0.60155 | 0.54874 | 0.49358 | 0.4732 | 0.43919 | 0.38417 | 0.32495
2015-06-15 | 0.27258 | 0.23663 | 0.20966 | 0.1941 | 0.18971 | 0.19362 | 0.20075 | 0.22501 | 0.29321 | 0.38484 | 0.47531 | 0.56395 | 0.64016 | 0.69071 | 0.72058 | 0.70929 | 0.6701 | 0.62223 | 0.573 | 0.5235 | 0.51388 | 0.4913 | 0.42708 | 0.36011
2015-06-16 | 0.29463 | 0.2546 | 0.23044 | 0.21586 | 0.21099 | 0.2266 | 0.25844 | 0.29341 | 0.34146 | 0.40566 | 0.49619 | 0.58992 | 0.65789 | 0.72035 | 0.76498 | 0.7918 | 0.80803 | 0.79655 | 0.7397 | 0.64631 | 0.60408 | 0.55235 | 0.46461 | 0.37843
2015-06-17 | 0.30675 | 0.26194 | 0.23057 | 0.21306 | 0.20703 | 0.22029 | 0.25274 | 0.29058 | 0.34046 | 0.39793 | 0.45695 | 0.51382 | 0.5649 | 0.61125 | 0.6273 | 0.62701 | 0.61471 | 0.60366 | 0.58136 | 0.54527 | 0.52422 | 0.49701 | 0.41374 | 0.33491
2015-06-18 | 0.26915 | 0.22988 | 0.20616 | 0.19172 | 0.18939 | 0.20428 | 0.23892 | 0.27679 | 0.3323 | 0.39936 | 0.47805 | 0.5574 | 0.60253 | 0.61889 | 0.60822 | 0.57964 | 0.54794 | 0.52148 | 0.49606 | 0.47121 | 0.46172 | 0.43776 | 0.37317 | 0.30436
2015-06-19 | 0.24652 | 0.21202 | 0.19199 | 0.18059 | 0.17768 | 0.19239 | 0.2251 | 0.26125 | 0.31973 | 0.39345 | 0.47886 | 0.55135 | 0.61415 | 0.66141 | 0.66531 | 0.62416 | 0.58667 | 0.54934 | 0.51279 | 0.47911 | 0.46166 | 0.42549 | 0.36544 | 0.29669
2015-06-20 | 0.2402 | 0.20481 | 0.1832 | 0.17172 | 0.16886 | 0.18131 | 0.21061 | 0.24805 | 0.3083 | 0.38961 | 0.47369 | 0.55632 | 0.62316 | 0.66251 | 0.65103 | 0.59478 | 0.5603 | 0.53025 | 0.50532 | 0.47338 | 0.45488 | 0.4324 | 0.37998 | 0.31907
2015-06-21 | 0.26185 | 0.22501 | 0.20035 | 0.1865 | 0.18055 | 0.18289 | 0.18877 | 0.21864 | 0.29807 | 0.39719 | 0.48664 | 0.57546 | 0.64994 | 0.69492 | 0.6813 | 0.63346 | 0.59339 | 0.56158 | 0.52402 | 0.48594 | 0.46738 | 0.44568 | 0.39413 | 0.33074
2015-06-22 | 0.27333 | 0.23843 | 0.21194 | 0.19609 | 0.18732 | 0.18681 | 0.18912 | 0.21872 | 0.29414 | 0.39555 | 0.49029 | 0.56795 | 0.64449 | 0.70307 | 0.74156 | 0.74756 | 0.72234 | 0.66685 | 0.59939 | 0.5434 | 0.52135 | 0.48935 | 0.42496 | 0.34745
2015-06-23 | 0.28184 | 0.24518 | 0.22063 | 0.20641 | 0.20339 | 0.21961 | 0.25279 | 0.296 | 0.36435 | 0.44755 | 0.54447 | 0.63727 | 0.72387 | 0.79647 | 0.83906 | 0.84884 | 0.8318 | 0.79526 | 0.74319 | 0.6735 | 0.62909 | 0.57197 | 0.48601 | 0.39051
2015-06-24 | 0.31734 | 0.26995 | 0.24064 | 0.22241 | 0.21649 | 0.23074 | 0.26375 | 0.3069 | 0.38009 | 0.46763 | 0.57252 | 0.66906 | 0.75718 | 0.83865 | 0.88836 | 0.91605 | 0.92106 | 0.88692 | 0.84278 | 0.76909 | 0.72995 | 0.66435 | 0.56307 | 0.45891
2015-06-25 | 0.37604 | 0.31937 | 0.28055 | 0.25753 | 0.24908 | 0.26245 | 0.29556 | 0.3402 | 0.41688 | 0.51797 | 0.63303 | 0.72687 | 0.81559 | 0.88794 | 0.93401 | 0.93864 | 0.90014 | 0.851 | 0.79084 | 0.715 | 0.67002 | 0.61358 | 0.52953 | 0.43157
2015-06-26 | 0.35397 | 0.29812 | 0.26291 | 0.24139 | 0.23326 | 0.24446 | 0.27759 | 0.32044 | 0.39731 | 0.50173 | 0.6128 | 0.70617 | 0.7818 | 0.8332 | 0.88505 | 0.90228 | 0.90271 | 0.87565 | 0.82753 | 0.75162 | 0.69929 | 0.63778 | 0.54287 | 0.44135
2015-06-27 | 0.35968 | 0.30775 | 0.27277 | 0.25165 | 0.24487 | 0.25913 | 0.28713 | 0.32945 | 0.40612 | 0.50448 | 0.60169 | 0.69394 | 0.75452 | 0.8073 | 0.85384 | 0.85893 | 0.84096 | 0.7976 | 0.7218 | 0.64587 | 0.60527 | 0.55028 | 0.484 | 0.40428
2015-06-28 | 0.3282 | 0.27788 | 0.24616 | 0.22348 | 0.2102 | 0.1997 | 0.22901 | 0.24755 | 0.3296 | 0.43758 | 0.53295 | 0.63806 | 0.72803 | 0.78635 | 0.82294 | 0.85067 | 0.84735 | 0.82794 | 0.77154 | 0.6962 | 0.65511 | 0.60618 | 0.5288 | 0.44201
2015-06-29 | 0.36784 | 0.31571 | 0.2794 | 0.25497 | 0.24135 | 0.23615 | 0.23448 | 0.2557 | 0.34104 | 0.45781 | 0.57731 | 0.69334 | 0.78828 | 0.83609 | 0.83823 | 0.80624 | 0.78148 | 0.74242 | 0.66744 | 0.60099 | 0.56273 | 0.52474 | 0.45488 | 0.37499
2015-06-30 | 0.31081 | 0.26635 | 0.23813 | 0.22215 | 0.2202 | 0.23751 | 0.27079 | 0.307 | 0.37174 | 0.46467 | 0.55908 | 0.64674 | 0.72088 | 0.78675 | 0.8281 | 0.84867 | 0.8304 | 0.76222 | 0.69778 | 0.64044 | 0.60963 | 0.56449 | 0.49194 | 0.40502
2015-07-01 | 0.33313 | 0.2866 | 0.2595 | 0.24371 | 0.24002 | 0.25803 | 0.29595 | 0.32888 | 0.37273 | 0.43818 | 0.50975 | 0.58646 | 0.63677 | 0.65987 | 0.68271 | 0.69259 | 0.70989 | 0.69914 | 0.67062 | 0.64457 | 0.63095 | 0.57758 | 0.49181 | 0.40531
2015-07-02 | 0.32872 | 0.28458 | 0.25698 | 0.2425 | 0.23795 | 0.25261 | 0.28709 | 0.32444 | 0.39057 | 0.48199 | 0.58909 | 0.6687 | 0.71851 | 0.72472 | 0.69545 | 0.66818 | 0.66097 | 0.65059 | 0.63059 | 0.59471 | 0.58177 | 0.55323 | 0.48563 | 0.39924
2015-07-03 | 0.33689 | 0.29072 | 0.265 | 0.24836 | 0.24571 | 0.26024 | 0.29478 | 0.33345 | 0.40101 | 0.50173 | 0.6184 | 0.71614 | 0.7886 | 0.84129 | 0.88539 | 0.9101 | 0.90014 | 0.83584 | 0.76814 | 0.70398 | 0.6656 | 0.62252 | 0.54554 | 0.45646
2015-07-04 | 0.3821 | 0.32593 | 0.28709 | 0.26213 | 0.24931 | 0.24899 | 0.25424 | 0.27131 | 0.34511 | 0.46455 | 0.58709 | 0.69094 | 0.75687 | 0.7898 | 0.80115 | 0.79824 | 0.71897 | 0.62708 | 0.56449 | 0.51085 | 0.47811 | 0.438 | 0.41642 | 0.37268
2015-07-05 | 0.31632 | 0.27131 | 0.24304 | 0.22514 | 0.2167 | 0.21704 | 0.22228 | 0.23764 | 0.29546 | 0.36768 | 0.45988 | 0.53012 | 0.59131 | 0.6522 | 0.65994 | 0.61478 | 0.57436 | 0.547 | 0.52057 | 0.49346 | 0.47668 | 0.45117 | 0.40393 | 0.34474
2015-07-06 | 0.29345 | 0.2546 | 0.22918 | 0.21248 | 0.20727 | 0.20814 | 0.21177 | 0.22828 | 0.29389 | 0.36757 | 0.43997 | 0.46966 | 0.50045 | 0.529 | 0.55558 | 0.55982 | 0.55209 | 0.53169 | 0.49969 | 0.45202 | 0.44303 | 0.42437 | 0.37301 | 0.31076
2015-07-07 | 0.26282 | 0.23027 | 0.21132 | 0.20217 | 0.20172 | 0.21915 | 0.25184 | 0.28936 | 0.34889 | 0.41531 | 0.4872 | 0.53697 | 0.56077 | 0.57944 | 0.58605 | 0.60527 | 0.60527 | 0.60211 | 0.58819 | 0.57027 | 0.55665 | 0.52494 | 0.45439 | 0.37571
2015-07-08 | 0.30905 | 0.2643 | 0.23588 | 0.22012 | 0.21574 | 0.22936 | 0.26236 | 0.30272 | 0.36599 | 0.46019 | 0.56117 | 0.65826 | 0.73885 | 0.77718 | 0.76964 | 0.7251 | 0.68011 | 0.64167 | 0.60253 | 0.55235 | 0.5122 | 0.46898 | 0.40307 | 0.33407
2015-07-09 | 0.27484 | 0.2387 | 0.21649 | 0.19573 | 0.19745 | 0.21712 | 0.25147 | 0.28825 | 0.35365 | 0.44881 | 0.54221 | 0.64037 | 0.70731 | 0.72703 | 0.66737 | 0.6211 | 0.59932 | 0.56789 | 0.53084 | 0.50969 | 0.49137 | 0.50731 | 0.39799 | 0.33074
2015-07-10 | 0.26915 | 0.23178 | 0.21049 | 0.19882 | 0.19541 | 0.2102 | 0.2442 | 0.28463 | 0.34947 | 0.4352 | 0.50699 | 0.55834 | 0.60724 | 0.6429 | 0.64146 | 0.61776 | 0.5826 | 0.54534 | 0.51518 | 0.48443 | 0.47606 | 0.45021 | 0.39328 | 0.32738
2015-07-11 | 0.26807 | 0.23157 | 0.20958 | 0.19841 | 0.19581 | 0.20933 | 0.23857 | 0.27964 | 0.35413 | 0.44453 | 0.54022 | 0.63267 | 0.70625 | 0.7679 | 0.80503 | 0.81412 | 0.80624 | 0.77853 | 0.7342 | 0.66862 | 0.63116 | 0.59131 | 0.51816 | 0.43788
2015-07-12 | 0.36724 | 0.3179 | 0.28256 | 0.2612 | 0.24504 | 0.24518 | 0.24935 | 0.26995 | 0.34004 | 0.44779 | 0.54407 | 0.63706 | 0.71614 | 0.76112 | 0.77448 | 0.77178 | 0.75962 | 0.71974 | 0.66582 | 0.59485 | 0.5603 | 0.51388 | 0.45057 | 0.38305
2015-07-13 | 0.33173 | 0.29385 | 0.26775 | 0.24809 | 0.23549 | 0.23061 | 0.23161 | 0.25383 | 0.33199 | 0.43033 | 0.52148 | 0.60956 | 0.67721 | 0.71233 | 0.74164 | 0.76238 | 0.75852 | 0.73034 | 0.68518 | 0.62873 | 0.59869 | 0.56707 | 0.49625 | 0.41735
2015-07-14 | 0.34995 | 0.30321 | 0.27018 | 0.25274 | 0.24818 | 0.26185 | 0.29497 | 0.33324 | 0.40704 | 0.50244 | 0.60506 | 0.69643 | 0.76585 | 0.78499 | 0.77059 | 0.76293 | 0.75978 | 0.75828 | 0.73869 | 0.67543 | 0.62067 | 0.56361 | 0.48142 | 0.39628
2015-07-15 | 0.32691 | 0.28203 | 0.25315 | 0.23536 | 0.23126 | 0.24522 | 0.28026 | 0.31622 | 0.37466 | 0.4635 | 0.54494 | 0.61868 | 0.66523 | 0.6656 | 0.64551 | 0.60977 | 0.5855 | 0.5687 | 0.56151 | 0.53473 | 0.52579 | 0.49778 | 0.43098 | 0.35747
2015-07-16 | 0.29802 | 0.25547 | 0.22806 | 0.21503 | 0.21319 | 0.23135 | 0.27484 | 0.31323 | 0.38445 | 0.47413 | 0.55457 | 0.61854 | 0.65958 | 0.62859 | 0.59353 | 0.56537 | 0.54068 | 0.51797 | 0.5032 | 0.47861 | 0.48199 | 0.46436 | 0.4075 | 0.34057
2015-07-17 | 0.28362 | 0.24778 | 0.22135 | 0.20884 | 0.20764 | 0.2242 | 0.26028 | 0.29297 | 0.36976 | 0.45196 | 0.53909 | 0.61918 | 0.62117 | 0.60794 | 0.59166 | 0.61825 | 0.65482 | 0.65914 | 0.65089 | 0.61726 | 0.59041 | 0.55235 | 0.46911 | 0.39119
2015-07-18 | 0.31673 | 0.27159 | 0.24339 | 0.22561 | 0.21902 | 0.23196 | 0.26162 | 0.29905 | 0.37378 | 0.47531 | 0.57806 | 0.6781 | 0.76506 | 0.83213 | 0.87439 | 0.89791 | 0.898 | 0.85334 | 0.77202 | 0.69041 | 0.64109 | 0.58978 | 0.51124 | 0.43264
2015-07-19 | 0.35979 | 0.30685 | 0.27182 | 0.25048 | 0.23725 | 0.23641 | 0.24091 | 0.26361 | 0.34963 | 0.4605 | 0.56802 | 0.66744 | 0.74709 | 0.80689 | 0.8323 | 0.84104 | 0.86186 | 0.84585 | 0.7826 | 0.71675 | 0.67892 | 0.62195 | 0.54048 | 0.46154
2015-07-20 | 0.38775 | 0.3348 | 0.2963 | 0.27055 | 0.25606 | 0.24998 | 0.25066 | 0.26518 | 0.34448 | 0.45958 | 0.56639 | 0.67973 | 0.77091 | 0.83411 | 0.86521 | 0.84726 | 0.83131 | 0.80616 | 0.7524 | 0.68794 | 0.66163 | 0.61606 | 0.54002 | 0.44906
2015-07-21 | 0.3729 | 0.32218 | 0.28752 | 0.26705 | 0.26208 | 0.27607 | 0.31197 | 0.34686 | 0.41183 | 0.50557 | 0.61196 | 0.70731 | 0.77035 | 0.7814 | 0.74483 | 0.70853 | 0.67054 | 0.63713 | 0.60373 | 0.56755 | 0.56057 | 0.51143 | 0.44339 | 0.36976
2015-07-22 | 0.30401 | 0.2619 | 0.2391 | 0.22339 | 0.22109 | 0.24073 | 0.27536 | 0.31222 | 0.38043 | 0.4651 | 0.54814 | 0.61457 | 0.65621 | 0.68003 | 0.7134 | 0.73319 | 0.71813 | 0.67409 | 0.63626 | 0.5952 | 0.58377 | 0.54141 | 0.46676 | 0.39119
2015-07-23 | 0.32841 | 0.28506 | 0.25661 | 0.23936 | 0.23505 | 0.24935 | 0.28975 | 0.32341 | 0.39175 | 0.46837 | 0.54108 | 0.6026 | 0.65161 | 0.69967 | 0.74771 | 0.77289 | 0.78244 | 0.7744 | 0.76822 | 0.71347 | 0.681 | 0.63317 | 0.54002 | 0.45111
2015-07-24 | 0.37383 | 0.31861 | 0.28352 | 0.26277 | 0.25561 | 0.26868 | 0.2991 | 0.33579 | 0.40865 | 0.51053 | 0.61132 | 0.5235 | 0.76774 | 0.80705 | 0.83057 | 0.85325 | 0.88488 | 0.86656 | 0.83832 | 0.7713 | 0.71241 | 0.65665 | 0.55256 | 0.45494
2015-07-25 | 0.37971 | 0.32208 | 0.28694 | 0.26398 | 0.25324 | 0.26611 | 0.2963 | 0.33475 | 0.41921 | 0.52363 | 0.62623 | 0.72656 | 0.7902 | 0.82572 | 0.85885 | 0.89041 | 0.89475 | 0.86286 | 0.7984 | 0.72226 | 0.68338 | 0.62544 | 0.54514 | 0.46332
2015-07-26 | 0.39594 | 0.34331 | 0.31071 | 0.28424 | 0.26859 | 0.26602 | 0.27267 | 0.29087 | 0.36359 | 0.47258 | 0.58322 | 0.66229 | 0.6971 | 0.7166 | 0.71081 | 0.68944 | 0.68967 | 0.67394 | 0.63965 | 0.59332 | 0.58143 | 0.53545 | 0.46744 | 0.40755
2015-07-27 | 0.34692 | 0.30227 | 0.27305 | 0.25251 | 0.24188 | 0.23887 | 0.24131 | 0.25689 | 0.34331 | 0.4561 | 0.56097 | 0.66244 | 0.74857 | 0.81795 | 0.86404 | 0.89535 | 0.90597 | 0.8939 | 0.84071 | 0.76482 | 0.73103 | 0.67609 | 0.58439 | 0.49244
2015-07-28 | 0.40865 | 0.35617 | 0.31891 | 0.29659 | 0.29043 | 0.3062 | 0.34062 | 0.37621 | 0.45518 | 0.56592 | 0.67217 | 0.77845 | 0.85425 | 0.92696 | 0.99443 | 1.0329 | 1.047 | 1.0314 | 0.99218 | 0.91682 | 0.87194 | 0.80098 | 0.67802 | 0.55881
2015-07-29 | 0.46264 | 0.39999 | 0.35763 | 0.33277 | 0.32203 | 0.33402 | 0.3667 | 0.39924 | 0.48017 | 0.58219 | 0.68742 | 0.78764 | 0.85684 | 0.90528 | 0.92966 | 0.91061 | 0.89211 | 0.8304 | 0.75766 | 0.69567 | 0.67032 | 0.61911 | 0.53018 | 0.45002
2015-07-30 | 0.37604 | 0.33022 | 0.29708 | 0.27859 | 0.2714 | 0.28617 | 0.32516 | 0.35747 | 0.43175 | 0.52213 | 0.60253 | 0.70224 | 0.79164 | 0.87371 | 0.91821 | 0.92184 | 0.86908 | 0.78523 | 0.72741 | 0.67261 | 0.63922 | 0.59069 | 0.50288 | 0.42109
2015-07-31 | 0.34841 | 0.30083 | 0.27032 | 0.25292 | 0.24701 | 0.26001 | 0.2961 | 0.32526 | 0.38775 | 0.48664 | 0.60127 | 0.71248 | 0.78964 | 0.84245 | 0.86094 | 0.84013 | 0.77662 | 0.71905 | 0.67202 | 0.62095 | 0.6059 | 0.56347 | 0.48783 | 0.40761
2015-08-01 | 0.34421 | 0.29989 | 0.26625 | 0.25184 | 0.24406 | 0.2584 | 0.28912 | 0.3296 | 0.40462 | 0.51008 | 0.61302 | 0.70967 | 0.78659 | 0.84278 | 0.89083 | 0.91708 | 0.91328 | 0.86228 | 0.78924 | 0.72073 | 0.69327 | 0.63835 | 0.548 | 0.46553
2015-08-02 | 0.39294 | 0.33763 | 0.30128 | 0.27721 | 0.26421 | 0.26305 | 0.27065 | 0.28781 | 0.36713 | 0.47624 | 0.58246 | 0.66995 | 0.74133 | 0.78308 | 0.8213 | 0.81958 | 0.8064 | 0.77297 | 0.71484 | 0.65782 | 0.63648 | 0.59465 | 0.51888 | 0.44724
2015-08-03 | 0.37982 | 0.33126 | 0.29708 | 0.27532 | 0.26268 | 0.26116 | 0.26672 | 0.27513 | 0.33579 | 0.42056 | 0.48991 | 0.56918 | 0.60914 | 0.62124 | 0.62566 | 0.63662 | 0.6458 | 0.63439 | 0.60471 | 0.57628 | 0.55168 | 0.50686 | 0.43478 | 0.36125
2015-08-04 | 0.29792 | 0.25867 | 0.23462 | 0.22092 | 0.21999 | 0.23843 | 0.27603 | 0.30565 | 0.36664 | 0.45057 | 0.54108 | 0.62444 | 0.64819 | 0.63734 | 0.59974 | 0.56259 | 0.52684 | 0.48834 | 0.46455 | 0.44688 | 0.45872 | 0.43021 | 0.3776 | 0.32198
2015-08-05 | 0.27164 | 0.23962 | 0.22177 | 0.21223 | 0.21173 | 0.2278 | 0.26747 | 0.30197 | 0.36899 | 0.46203 | 0.54854 | 0.63554 | 0.7086 | 0.75405 | 0.74475 | 0.73768 | 0.74467 | 0.75115 | 0.72595 | 0.67128 | 0.64703 | 0.58681 | 0.49511 | 0.41125
2015-08-06 | 0.33475 | 0.28873 | 0.25766 | 0.23896 | 0.23549 | 0.2489 | 0.28405 | 0.31993 | 0.39628 | 0.49943 | 0.60148 | 0.71828 | 0.80389 | 0.87878 | 0.92661 | 0.93053 | 0.88938 | 0.84544 | 0.78739 | 0.7315 | 0.7067 | 0.64841 | 0.54261 | 0.45293
2015-08-07 | 0.37202 | 0.32044 | 0.2881 | 0.26756 | 0.26019 | 0.27423 | 0.31071 | 0.34432 | 0.42814 | 0.53796 | 0.64587 | 0.7564 | 0.84759 | 0.91294 | 0.9267 | 0.91864 | 0.90545 | 0.88267 | 0.82335 | 0.75766 | 0.69967 | 0.62266 | 0.51363 | 0.42232
2015-08-08 | 0.34756 | 0.29566 | 0.26644 | 0.24949 | 0.24206 | 0.26938 | 0.29194 | 0.32388 | 0.37876 | 0.46689 | 0.55578 | 0.6587 | 0.75781 | 0.84436 | 0.89049 | 0.8933 | 0.87802 | 0.81371 | 0.73768 | 0.66988 | 0.64623 | 0.59249 | 0.51447 | 0.4467
2015-08-09 | 0.36817 | 0.31825 | 0.28318 | 0.26166 | 0.25143 | 0.25143 | 0.25826 | 0.2795 | 0.36681 | 0.4845 | 0.59583 | 0.70118 | 0.7846 | 0.8422 | 0.88301 | 0.90752 | 0.90408 | 0.85234 | 0.77012 | 0.69387 | 0.66582 | 0.60759 | 0.52736 | 0.45781
2015-08-10 | 0.38708 | 0.3371 | 0.29876 | 0.27532 | 0.26157 | 0.25675 | 0.25895 | 0.27159 | 0.3537 | 0.4696 | 0.58226 | 0.70186 | 0.79076 | 0.8606 | 0.89501 | 0.90185 | 0.89578 | 0.87194 | 0.80916 | 0.73165 | 0.69703 | 0.6263 | 0.52946 | 0.43812
2015-08-11 | 0.36066 | 0.30885 | 0.27546 | 0.25602 | 0.24989 | 0.26658 | 0.30277 | 0.3311 | 0.40164 | 0.51091 | 0.62323 | 0.74537 | 0.84452 | 0.91027 | 0.92739 | 0.92262 | 0.92514 | 0.90889 | 0.86077 | 0.78892 | 0.7608 | 0.67461 | 0.57553 | 0.47028
2015-08-12 | 0.38686 | 0.33423 | 0.29492 | 0.27201 | 0.26467 | 0.27897 | 0.31591 | 0.34745 | 0.42062 | 0.52559 | 0.62937 | 0.73088 | 0.80827 | 0.87042 | 0.89364 | 0.89185 | 0.9058 | 0.89646 | 0.86412 | 0.79534 | 0.75405 | 0.67424 | 0.57006 | 0.47531
2015-08-13 | 0.39029 | 0.34104 | 0.305 | 0.27669 | 0.26952 | 0.28472 | 0.32362 | 0.3565 | 0.4374 | 0.54594 | 0.65438 | 0.77623 | 0.86984 | 0.9375 | 0.97251 | 0.99084 | 0.99075 | 0.94802 | 0.88386 | 0.80357 | 0.77115 | 0.69793 | 0.59041 | 0.49238
2015-08-14 | 0.41183 | 0.36049 | 0.32629 | 0.3049 | 0.29556 | 0.30755 | 0.34639 | 0.37726 | 0.45689 | 0.57047 | 0.68406 | 0.77989 | 0.86681 | 0.91449 | 0.92124 | 0.86018 | 0.77321 | 0.70944 | 0.65804 | 0.61577 | 0.60731 | 0.55209 | 0.48092 | 0.39805
2015-08-15 | 0.33261 | 0.29141 | 0.26125 | 0.24796 | 0.24451 | 0.26227 | 0.30366 | 0.34057 | 0.41857 | 0.51169 | 0.60907 | 0.68413 | 0.74366 | 0.73096 | 0.62823 | 0.56646 | 0.52684 | 0.50026 | 0.46793 | 0.43794 | 0.44195 | 0.41136 | 0.37009 | 0.32034
2015-08-16 | 0.27258 | 0.24295 | 0.22373 | 0.21132 | 0.2051 | 0.20735 | 0.21889 | 0.23839 | 0.31268 | 0.43282 | 0.54634 | 0.63698 | 0.72726 | 0.74382 | 0.79116 | 0.75522 | 0.69207 | 0.62916 | 0.57204 | 0.5254 | 0.51285 | 0.47705 | 0.42631 | 0.3618
2015-08-17 | 0.30755 | 0.27009 | 0.24362 | 0.22587 | 0.2186 | 0.21893 | 0.22681 | 0.24224 | 0.31278 | 0.42684 | 0.54434 | 0.64819 | 0.74024 | 0.82138 | 0.83518 | 0.81958 | 0.82753 | 0.82449 | 0.78844 | 0.7308 | 0.71301 | 0.65045 | 0.55034 | 0.44369
2015-08-18 | 0.37086 | 0.31764 | 0.2841 | 0.26481 | 0.2607 | 0.28728 | 0.33569 | 0.35838 | 0.41577 | 0.52533 | 0.64052 | 0.75366 | 0.84369 | 0.91942 | 0.95453 | 0.98348 | 0.98814 | 0.96913 | 0.92852 | 0.85784 | 0.83057 | 0.73327 | 0.60422 | 0.50103
2015-08-19 | 0.41009 | 0.35413 | 0.31637 | 0.29336 | 0.28655 | 0.3092 | 0.36066 | 0.38182 | 0.44429 | 0.55289 | 0.65914 | 0.77162 | 0.86672 | 0.93392 | 0.97438 | 1.0239 | 1.0496 | 1.0233 | 0.97473 | 0.89254 | 0.86018 | 0.76711 | 0.63612 | 0.52494
2015-08-20 | 0.43335 | 0.37499 | 0.33689 | 0.30956 | 0.30093 | 0.32131 | 0.37086 | 0.31515 | 0.45051 | 0.56057 | 0.66634 | 0.78627 | 0.86773 | 0.94969 | 0.98393 | 0.99075 | 0.98805 | 0.96159 | 0.90545 | 0.83823 | 0.80876 | 0.7291 | 0.61316 | 0.50391
2015-08-21 | 0.42572 | 0.36861 | 0.33064 | 0.3073 | 0.29807 | 0.31968 | 0.37213 | 0.39674 | 0.46154 | 0.5628 | 0.67476 | 0.7906 | 0.87785 | 0.95656 | 1.002 | 1.0491 | 1.0507 | 0.98223 | 0.91251 | 0.8204 | 0.80002 | 0.71279 | 0.60387 | 0.49593
2015-08-22 | 0.40709 | 0.35397 | 0.3179 | 0.29605 | 0.28738 | 0.3074 | 0.35914 | 0.38249 | 0.44507 | 0.5547 | 0.66126 | 0.77075 | 0.86219 | 0.93053 | 0.95647 | 1.0131 | 1.028 | 0.98734 | 0.92297 | 0.83016 | 0.7818 | 0.69184 | 0.59423 | 0.50333
2015-08-23 | 0.41962 | 0.365 | 0.32357 | 0.29644 | 0.28021 | 0.27878 | 0.28622 | 0.30247 | 0.38366 | 0.51169 | 0.63253 | 0.74865 | 0.8422 | 0.90786 | 0.93803 | 0.96274 | 0.97696 | 0.95709 | 0.89527 | 0.8077 | 0.76735 | 0.69522 | 0.61111 | 0.5181
2015-08-24 | 0.43163 | 0.37229 | 0.32898 | 0.30054 | 0.28381 | 0.2775 | 0.27826 | 0.28834 | 0.37372 | 0.49835 | 0.61153 | 0.73791 | 0.84419 | 0.92358 | 0.97286 | 0.99903 | 1.0017 | 0.98698 | 0.9287 | 0.85167 | 0.81909 | 0.72395 | 0.60998 | 0.50673
2015-08-25 | 0.43187 | 0.3724 | 0.33988 | 0.32111 | 0.32004 | 0.34889 | 0.40566 | 0.42903 | 0.47419 | 0.57102 | 0.67269 | 0.766 | 0.82687 | 0.85125 | 0.85667 | 0.85517 | 0.8601 | 0.84088 | 0.78483 | 0.73451 | 0.72196 | 0.63893 | 0.5434 | 0.44405
2015-08-26 | 0.37843 | 0.33444 | 0.3051 | 0.2883 | 0.2853 | 0.31086 | 0.36571 | 0.38674 | 0.4346 | 0.53012 | 0.62095 | 0.70921 | 0.77416 | 0.83386 | 0.87506 | 0.90872 | 0.92618 | 0.91122 | 0.86085 | 0.78691 | 0.76072 | 0.67513 | 0.55437 | 0.45665
2015-08-27 | 0.37097 | 0.31861 | 0.28294 | 0.2624 | 0.25497 | 0.27598 | 0.32665 | 0.34485 | 0.39759 | 0.49835 | 0.59416 | 0.69282 | 0.77646 | 0.84735 | 0.90365 | 0.94477 | 0.96931 | 0.954 | 0.90339 | 0.82245 | 0.79679 | 0.70845 | 0.58951 | 0.4908
2015-08-28 | 0.40738 | 0.35408 | 0.31678 | 0.29297 | 0.28338 | 0.30555 | 0.36098 | 0.38238 | 0.43585 | 0.51894 | 0.58875 | 0.65132 | 0.72633 | 0.80592 | 0.8809 | 0.92913 | 0.95056 | 0.91406 | 0.84129 | 0.78388 | 0.74967 | 0.65877 | 0.55571 | 0.46326
2015-08-29 | 0.38099 | 0.3324 | 0.30113 | 0.28041 | 0.27498 | 0.29738 | 0.35241 | 0.38076 | 0.44201 | 0.55182 | 0.66295 | 0.75193 | 0.81942 | 0.88564 | 0.93366 | 0.96124 | 0.95197 | 0.89194 | 0.81771 | 0.74662 | 0.72027 | 0.64247 | 0.55679 | 0.48168
2015-08-30 | 0.41194 | 0.36125 | 0.32624 | 0.30182 | 0.29145 | 0.30133 | 0.3049 | 0.31754 | 0.38657 | 0.50583 | 0.61818 | 0.73234 | 0.81306 | 0.87776 | 0.92705 | 0.94863 | 0.94564 | 0.89424 | 0.80681 | 0.73497 | 0.70906 | 0.6354 | 0.55726 | 0.48638
2015-08-31 | 0.41426 | 0.35947 | 0.3205 | 0.29787 | 0.28232 | 0.27565 | 0.27969 | 0.29092 | 0.36932 | 0.49638 | 0.6019 | 0.70261 | 0.79052 | 0.85284 | 0.88123 | 0.89049 | 0.87118 | 0.83394 | 0.75766 | 0.68869 | 0.66877 | 0.6012 | 0.5235 | 0.447
2015-09-01 | 0.37998 | 0.33674 | 0.30525 | 0.2827 | 0.27551 | 0.27978 | 0.29302 | 0.2991 | 0.37345 | 0.49943 | 0.61677 | 0.73861 | 0.80997 | 0.8663 | 0.91605 | 0.93331 | 0.91942 | 0.88488 | 0.82728 | 0.7586 | 0.73791 | 0.65402 | 0.54887 | 0.45897
2015-09-02 | 0.38149 | 0.33116 | 0.29767 | 0.27869 | 0.27239 | 0.29463 | 0.34612 | 0.36768 | 0.417 | 0.51518 | 0.61005 | 0.71446 | 0.79285 | 0.8427 | 0.89774 | 0.93026 | 0.93715 | 0.90734 | 0.84229 | 0.77265 | 0.73288 | 0.62887 | 0.51667 | 0.41735
2015-09-03 | 0.3422 | 0.29532 | 0.26667 | 0.24868 | 0.24397 | 0.26532 | 0.3184 | 0.33904 | 0.3831 | 0.46516 | 0.52684 | 0.5952 | 0.66339 | 0.73853 | 0.7947 | 0.81388 | 0.82556 | 0.7984 | 0.75107 | 0.69131 | 0.67343 | 0.59673 | 0.49956 | 0.40365
2015-09-04 | 0.33261 | 0.2868 | 0.25872 | 0.2421 | 0.23764 | 0.25854 | 0.31298 | 0.33261 | 0.36408 | 0.4346 | 0.51498 | 0.58598 | 0.64827 | 0.70929 | 0.73559 | 0.74678 | 0.76025 | 0.73993 | 0.70375 | 0.67128 | 0.66214 | 0.58584 | 0.48846 | 0.40405
2015-09-05 | 0.33397 | 0.29014 | 0.26384 | 0.248 | 0.24554 | 0.26765 | 0.32557 | 0.34713 | 0.39475 | 0.48954 | 0.58958 | 0.686 | 0.77226 | 0.84038 | 0.88005 | 0.8825 | 0.84411 | 0.76925 | 0.69357 | 0.64421 | 0.61606 | 0.54774 | 0.47705 | 0.41206
2015-09-06 | 0.34873 | 0.30981 | 0.28112 | 0.26213 | 0.2532 | 0.25306 | 0.26421 | 0.2829 | 0.34596 | 0.43782 | 0.51544 | 0.57813 | 0.6162 | 0.61118 | 0.59911 | 0.58343 | 0.55356 | 0.53012 | 0.50333 | 0.48972 | 0.48985 | 0.45251 | 0.40842 | 0.36109
2015-09-07 | 0.31162 | 0.27037 | 0.24384 | 0.22621 | 0.21969 | 0.22084 | 0.22979 | 0.24162 | 0.29733 | 0.37776 | 0.45768 | 0.54407 | 0.61946 | 0.67357 | 0.69944 | 0.68174 | 0.6511 | 0.60977 | 0.55041 | 0.53163 | 0.53077 | 0.4773 | 0.40652 | 0.33768
2015-09-08 | 0.28578 | 0.25292 | 0.22875 | 0.21477 | 0.2139 | 0.23914 | 0.29136 | 0.31202 | 0.34702 | 0.43633 | 0.53611 | 0.63095 | 0.71081 | 0.77408 | 0.82187 | 0.84229 | 0.84005 | 0.82171 | 0.75585 | 0.71951 | 0.69469 | 0.60815 | 0.50866 | 0.41787
2015-09-09 | 0.34596 | 0.29822 | 0.2699 | 0.25256 | 0.24558 | 0.26616 | 0.31958 | 0.33988 | 0.37665 | 0.45964 | 0.55417 | 0.64536 | 0.72649 | 0.80042 | 0.8351 | 0.87245 | 0.86328 | 0.82392 | 0.76159 | 0.71271 | 0.67951 | 0.58501 | 0.48393 | 0.39646
2015-09-10 | 0.331 | 0.29102 | 0.26556 | 0.24814 | 0.24446 | 0.26812 | 0.3228 | 0.34173 | 0.37798 | 0.45124 | 0.54247 | 0.62188 | 0.69567 | 0.76214 | 0.80187 | 0.82057 | 0.81323 | 0.77997 | 0.72595 | 0.68637 | 0.6631 | 0.57109 | 0.47543 | 0.38736
2015-09-11 | 0.32034 | 0.27993 | 0.25265 | 0.23619 | 0.23252 | 0.25438 | 0.30865 | 0.32934 | 0.36196 | 0.43979 | 0.5168 | 0.58709 | 0.64117 | 0.68085 | 0.69469 | 0.69899 | 0.67306 | 0.62316 | 0.57896 | 0.55464 | 0.54261 | 0.48117 | 0.41583 | 0.34342
2015-09-12 | 0.27698 | 0.24594 | 0.22484 | 0.21444 | 0.21444 | 0.23826 | 0.29571 | 0.31333 | 0.35102 | 0.41781 | 0.48362 | 0.54214 | 0.60253 | 0.66229 | 0.6775 | 0.67165 | 0.67587 | 0.68093 | 0.6349 | 0.58474 | 0.56503 | 0.50834 | 0.44821 | 0.37976
2015-09-13 | 0.31132 | 0.26938 | 0.24148 | 0.22003 | 0.21157 | 0.21078 | 0.22228 | 0.23839 | 0.29004 | 0.37246 | 0.46911 | 0.56381 | 0.64138 | 0.69154 | 0.71218 | 0.70982 | 0.68063 | 0.63994 | 0.57375 | 0.54121 | 0.52122 | 0.46062 | 0.39311 | 0.32862
2015-09-14 | 0.28064 | 0.24437 | 0.21978 | 0.20388 | 0.19469 | 0.19318 | 0.19938 | 0.20814 | 0.26747 | 0.35757 | 0.45245 | 0.54914 | 0.6263 | 0.68003 | 0.70792 | 0.71736 | 0.71882 | 0.68242 | 0.61975 | 0.58418 | 0.56551 | 0.49854 | 0.42302 | 0.34379
2015-09-15 | 0.28893 | 0.25147 | 0.22949 | 0.21754 | 0.21708 | 0.24033 | 0.29238 | 0.31434 | 0.35338 | 0.44009 | 0.55524 | 0.64928 | 0.7318 | 0.80681 | 0.86119 | 0.89826 | 0.90494 | 0.88039 | 0.81934 | 0.77416 | 0.74133 | 0.64203 | 0.53916 | 0.42832
2015-09-16 | 0.35027 | 0.30495 | 0.27196 | 0.25193 | 0.24643 | 0.26649 | 0.32034 | 0.34083 | 0.37909 | 0.46105 | 0.55868 | 0.65497 | 0.73219 | 0.7918 | 0.78108 | 0.74842 | 0.72211 | 0.69184 | 0.65826 | 0.64522 | 0.61982 | 0.53935 | 0.45378 | 0.37152
2015-09-17 | 0.30237 | 0.2631 | 0.23694 | 0.22114 | 0.21986 | 0.24388 | 0.29999 | 0.32009 | 0.3514 | 0.41374 | 0.49886 | 0.56823 | 0.62081 | 0.64958 | 0.68182 | 0.67988 | 0.63447 | 0.58391 | 0.55014 | 0.55578 | 0.54627 | 0.48758 | 0.40894 | 0.33074
2015-09-18 | 0.27607 | 0.23804 | 0.2191 | 0.20649 | 0.20543 | 0.22836 | 0.28338 | 0.30321 | 0.33491 | 0.40084 | 0.46917 | 0.5448 | 0.62152 | 0.69537 | 0.74967 | 0.78092 | 0.77035 | 0.77511 | 0.70853 | 0.67025 | 0.63713 | 0.55551 | 0.46344 | 0.37544
2015-09-19 | 0.30981 | 0.26644 | 0.24162 | 0.2263 | 0.22356 | 0.24562 | 0.30128 | 0.32629 | 0.35925 | 0.43353 | 0.50014 | 0.54367 | 0.55692 | 0.53519 | 0.49918 | 0.48274 | 0.46793 | 0.45354 | 0.43669 | 0.44303 | 0.43579 | 0.39959 | 0.35038 | 0.2992
2015-09-20 | 0.25152 | 0.2213 | 0.20233 | 0.19219 | 0.18712 | 0.19215 | 0.20781 | 0.22897 | 0.27126 | 0.34215 | 0.41154 | 0.47047 | 0.51628 | 0.54734 | 0.55095 | 0.50307 | 0.46473 | 0.4461 | 0.41746 | 0.42367 | 0.41746 | 0.37599 | 0.32841 | 0.28136
2015-09-21 | 0.23993 | 0.20805 | 0.18837 | 0.17613 | 0.17098 | 0.17229 | 0.18193 | 0.19322 | 0.23949 | 0.31978 | 0.40284 | 0.4879 | 0.56165 | 0.61606 | 0.65402 | 0.66862 | 0.66656 | 0.63951 | 0.58067 | 0.55444 | 0.52625 | 0.45439 | 0.38277 | 0.30875
2015-09-22 | 0.25492 | 0.22071 | 0.19938 | 0.19081 | 0.19291 | 0.21986 | 0.27258 | 0.29831 | 0.33308 | 0.40016 | 0.47326 | 0.54234 | 0.59708 | 0.60878 | 0.59402 | 0.57546 | 0.56503 | 0.54487 | 0.53248 | 0.53995 | 0.51479 | 0.44821 | 0.37257 | 0.30262
2015-09-23 | 0.24917 | 0.21549 | 0.19426 | 0.18363 | 0.18475 | 0.21269 | 0.27135 | 0.29871 | 0.31293 | 0.35542 | 0.38764 | 0.42773 | 0.45793 | 0.46455 | 0.46793 | 0.4755 | 0.48582 | 0.50275 | 0.49162 | 0.50641 | 0.49346 | 0.43436 | 0.36582 | 0.29571
2015-09-24 | 0.24224 | 0.21007 | 0.19501 | 0.18359 | 0.18243 | 0.20954 | 0.26653 | 0.29311 | 0.31541 | 0.3586 | 0.40233 | 0.44809 | 0.48005 | 0.52037 | 0.56782 | 0.6066 | 0.61026 | 0.59437 | 0.56693 | 0.56646 | 0.55115 | 0.48998 | 0.40778 | 0.3371
2015-09-25 | 0.28141 | 0.24379 | 0.22071 | 0.20678 | 0.20596 | 0.22476 | 0.26891 | 0.29836 | 0.33532 | 0.40663 | 0.48299 | 0.53664 | 0.56646 | 0.59346 | 0.63037 | 0.66126 | 0.639 | 0.58115 | 0.5432 | 0.5373 | 0.51712 | 0.45561 | 0.38338 | 0.32044
2015-09-26 | 0.26756 | 0.2347 | 0.21444 | 0.20282 | 0.20257 | 0.22793 | 0.28299 | 0.31182 | 0.33658 | 0.38585 | 0.45378 | 0.53664 | 0.60337 | 0.67246 | 0.69725 | 0.69959 | 0.67439 | 0.62658 | 0.57868 | 0.57143 | 0.54467 | 0.4901 | 0.42308 | 0.40256
2015-09-27 | 0.3311 | 0.27135 | 0.2489 | 0.23331 | 0.22737 | 0.22996 | 0.24335 | 0.26051 | 0.31968 | 0.41607 | 0.50679 | 0.59904 | 0.67647 | 0.73157 | 0.77115 | 0.77313 | 0.72357 | 0.67306 | 0.60759 | 0.59166 | 0.55484 | 0.50026 | 0.43365 | 0.36484
2015-09-28 | 0.30865 | 0.27074 | 0.24442 | 0.22694 | 0.21906 | 0.22012 | 0.22897 | 0.24451 | 0.29635 | 0.3886 | 0.48199 | 0.57505 | 0.65921 | 0.72203 | 0.76261 | 0.77535 | 0.75781 | 0.70777 | 0.63526 | 0.63382 | 0.60653 | 0.5338 | 0.447 | 0.3637
2015-09-29 | 0.3065 | 0.26412 | 0.24104 | 0.22694 | 0.22699 | 0.25088 | 0.30635 | 0.33162 | 0.36457 | 0.44531 | 0.53975 | 0.6403 | 0.70587 | 0.76301 | 0.79237 | 0.79213 | 0.7721 | 0.7192 | 0.66229 | 0.63958 | 0.57375 | 0.49867 | 0.41229 | 0.33679
2015-09-30 | 0.2774 | 0.24135 | 0.22024 | 0.20809 | 0.20797 | 0.23274 | 0.29404 | 0.31622 | 0.35408 | 0.43205 | 0.51596 | 0.59277 | 0.65767 | 0.67988 | 0.70042 | 0.66833 | 0.66398 | 0.65438 | 0.61889 | 0.62316 | 0.59569 | 0.52638 | 0.43973 | 0.35747
2015-10-01 | 0.29728 | 0.25803 | 0.23681 | 0.22429 | 0.22224 | 0.24881 | 0.31016 | 0.33277 | 0.37262 | 0.45233 | 0.53255 | 0.61698 | 0.68854 | 0.74374 | 0.76806 | 0.81038 | 0.83576 | 0.81014 | 0.75006 | 0.72088 | 0.68219 | 0.59611 | 0.49023 | 0.43949
2015-10-02 | 0.34342 | 0.28868 | 0.2613 | 0.24455 | 0.24033 | 0.26291 | 0.32029 | 0.34189 | 0.38355 | 0.47072 | 0.56721 | 0.65322 | 0.72741 | 0.80705 | 0.85175 | 0.88386 | 0.90288 | 0.87085 | 0.79969 | 0.76458 | 0.71981 | 0.62238 | 0.52187 | 0.4215
2015-10-03 | 0.34926 | 0.30321 | 0.2699 | 0.25161 | 0.24464 | 0.26495 | 0.32029 | 0.34586 | 0.3926 | 0.48632 | 0.58709 | 0.68704 | 0.75899 | 0.84063 | 0.88352 | 0.907 | 0.90588 | 0.83378 | 0.73505 | 0.68309 | 0.61769 | 0.54227 | 0.46283 | 0.38944
2015-10-04 | 0.32609 | 0.28002 | 0.25247 | 0.23409 | 0.2254 | 0.22841 | 0.24202 | 0.25964 | 0.32295 | 0.4163 | 0.49511 | 0.56938 | 0.63605 | 0.67765 | 0.69319 | 0.68391 | 0.6519 | 0.60513 | 0.54694 | 0.53717 | 0.50583 | 0.44875 | 0.3835 | 0.32085
2015-10-05 | 0.26208 | 0.21771 | 0.18712 | 0.16473 | 0.15297 | 0.14992 | 0.15517 | 0.16029 | 0.18834 | 0.23414 | 0.28371 | 0.32157 | 0.36495 | 0.40548 | 0.44081 | 0.46756 | 0.49422 | 0.48368 | 0.44357 | 0.44033 | 0.41846 | 0.36218 | 0.29945 | 0.23927
2015-10-06 | 0.19577 | 0.1676 | 0.15149 | 0.14345 | 0.14534 | 0.17034 | 0.21843 | 0.24117 | 0.26444 | 0.31016 | 0.36011 | 0.40755 | 0.46019 | 0.5009 | 0.54347 | 0.55706 | 0.57225 | 0.55101 | 0.52985 | 0.55188 | 0.5179 | 0.44948 | 0.37854 | 0.3067
2015-10-07 | 0.24967 | 0.21826 | 0.19906 | 0.1872 | 0.18459 | 0.2069 | 0.26236 | 0.2897 | 0.30257 | 0.35091 | 0.40686 | 0.44869 | 0.48431 | 0.51518 | 0.53097 | 0.52376 | 0.52285 | 0.5104 | 0.50097 | 0.52546 | 0.49765 | 0.44984 | 0.3724 | 0.29375
2015-10-08 | 0.24157 | 0.21045 | 0.18947 | 0.17944 | 0.18059 | 0.20592 | 0.2619 | 0.28501 | 0.30976 | 0.37042 | 0.44459 | 0.51149 | 0.57786 | 0.63159 | 0.67706 | 0.69808 | 0.69628 | 0.67387 | 0.63403 | 0.63439 | 0.59834 | 0.52259 | 0.43657 | 0.35757
2015-10-09 | 0.29228 | 0.25429 | 0.2294 | 0.2119 | 0.20921 | 0.20445 | 0.28251 | 0.3054 | 0.33579 | 0.41206 | 0.49175 | 0.56795 | 0.62851 | 0.68944 | 0.73258 | 0.76182 | 0.76703 | 0.73885 | 0.67743 | 0.66428 | 0.62081 | 0.54002 | 0.45604 | 0.36719
2015-10-10 | 0.29935 | 0.25474 | 0.22975 | 0.21256 | 0.20954 | 0.23044 | 0.28395 | 0.30976 | 0.34305 | 0.42097 | 0.50525 | 0.5756 | 0.64131 | 0.69831 | 0.73838 | 0.76608 | 0.77162 | 0.73304 | 0.65738 | 0.63167 | 0.58432 | 0.51615 | 0.44465 | 0.37417
2015-10-11 | 0.31086 | 0.26826 | 0.24268 | 0.22433 | 0.21436 | 0.21486 | 0.22669 | 0.23936 | 0.29463 | 0.39288 | 0.48469 | 0.56911 | 0.63864 | 0.69394 | 0.73281 | 0.75805 | 0.76293 | 0.72988 | 0.6495 | 0.61485 | 0.56782 | 0.49962 | 0.43615 | 0.36599
2015-10-12 | 0.3076 | 0.26402 | 0.23322 | 0.21486 | 0.20629 | 0.20469 | 0.21294 | 0.21927 | 0.27731 | 0.37982 | 0.47431 | 0.56131 | 0.6403 | 0.69402 | 0.7308 | 0.75099 | 0.75326 | 0.72418 | 0.65665 | 0.65096 | 0.60457 | 0.52834 | 0.45433 | 0.37555
2015-10-13 | 0.31526 | 0.27517 | 0.25129 | 0.23764 | 0.23795 | 0.26314 | 0.31657 | 0.34031 | 0.37306 | 0.44736 | 0.53856 | 0.61691 | 0.67469 | 0.72303 | 0.75663 | 0.77901 | 0.77599 | 0.74436 | 0.68555 | 0.68294 | 0.63332 | 0.55639 | 0.46979 | 0.38489
2015-10-14 | 0.31988 | 0.28179 | 0.25959 | 0.24513 | 0.24175 | 0.26798 | 0.32939 | 0.35456 | 0.38798 | 0.46621 | 0.54807 | 0.62138 | 0.67543 | 0.73567 | 0.76925 | 0.77845 | 0.76017 | 0.71385 | 0.6735 | 0.68346 | 0.6283 | 0.54714 | 0.45756 | 0.3707
2015-10-15 | 0.29891 | 0.25661 | 0.233 | 0.21881 | 0.2191 | 0.24304 | 0.29974 | 0.32743 | 0.35677 | 0.42214 | 0.48827 | 0.55524 | 0.48594 | 0.64544 | 0.6568 | 0.66508 | 0.64515 | 0.61393 | 0.57697 | 0.58577 | 0.53803 | 0.46936 | 0.38557 | 0.31106
2015-10-16 | 0.25184 | 0.2159 | 0.19505 | 0.18143 | 0.17552 | 0.19207 | 0.23628 | 0.2527 | 0.26966 | 0.31348 | 0.3579 | 0.39441 | 0.43401 | 0.47612 | 0.51544 | 0.55585 | 0.57937 | 0.56741 | 0.52076 | 0.51647 | 0.47425 | 0.40479 | 0.32934 | 0.2578
2015-10-17 | 0.20282 | 0.16908 | 0.15142 | 0.14155 | 0.13915 | 0.15688 | 0.19829 | 0.21822 | 0.2391 | 0.28045 | 0.32167 | 0.36131 | 0.39583 | 0.43746 | 0.47967 | 0.5192 | 0.53882 | 0.52096 | 0.46645 | 0.44839 | 0.40342 | 0.34511 | 0.2937 | 0.23993
2015-10-18 | 0.19861 | 0.16502 | 0.14562 | 0.1351 | 0.13047 | 0.13464 | 0.14779 | 0.16207 | 0.20079 | 0.25734 | 0.30971 | 0.35633 | 0.40554 | 0.45093 | 0.49403 | 0.52834 | 0.54115 | 0.52122 | 0.46621 | 0.45178 | 0.40871 | 0.35241 | 0.30316 | 0.24922
2015-10-19 | 0.20592 | 0.17488 | 0.15396 | 0.14199 | 0.13713 | 0.13734 | 0.14624 | 0.1551 | 0.19505 | 0.25565 | 0.31495 | 0.36982 | 0.43063 | 0.48005 | 0.52161 | 0.54707 | 0.55591 | 0.53605 | 0.49301 | 0.49657 | 0.4572 | 0.39068 | 0.32717 | 0.26453
2015-10-20 | 0.21498 | 0.18224 | 0.16411 | 0.15503 | 0.15556 | 0.17647 | 0.22152 | 0.24665 | 0.27641 | 0.33899 | 0.40554 | 0.46608 | 0.52031 | 0.56456 | 0.60597 | 0.61833 | 0.60977 | 0.58122 | 0.5537 | 0.56354 | 0.51486 | 0.44321 | 0.36795 | 0.29689
2015-10-21 | 0.24064 | 0.20945 | 0.19235 | 0.18197 | 0.18274 | 0.20625 | 0.2607 | 0.29033 | 0.30207 | 0.34189 | 0.38888 | 0.41869 | 0.43955 | 0.44984 | 0.45233 | 0.45451 | 0.4499 | 0.44099 | 0.44069 | 0.46676 | 0.43383 | 0.38366 | 0.31998 | 0.2532
2015-10-22 | 0.20801 | 0.17993 | 0.16458 | 0.15727 | 0.15899 | 0.17936 | 0.23562 | 0.26546 | 0.27835 | 0.31379 | 0.36147 | 0.41194 | 0.45105 | 0.48588 | 0.51207 | 0.52723 | 0.51836 | 0.49644 | 0.48638 | 0.50314 | 0.46732 | 0.40969 | 0.33894 | 0.27074
2015-10-23 | 0.22012 | 0.1931 | 0.17594 | 0.16594 | 0.16484 | 0.18646 | 0.24122 | 0.27093 | 0.27835 | 0.30845 | 0.34479 | 0.37649 | 0.40382 | 0.42173 | 0.4386 | 0.44646 | 0.44189 | 0.42926 | 0.41992 | 0.43687 | 0.42132 | 0.3735 | 0.31313 | 0.25447
2015-10-24 | 0.20937 | 0.18135 | 0.16601 | 0.15946 | 0.16152 | 0.1817 | 0.22742 | 0.25812 | 0.27759 | 0.31657 | 0.3507 | 0.37593 | 0.38877 | 0.40279 | 0.41368 | 0.42361 | 0.42255 | 0.4094 | 0.39839 | 0.40445 | 0.37461 | 0.33763 | 0.29733 | 0.24643
2015-10-25 | 0.19821 | 0.16671 | 0.14745 | 0.13593 | 0.13194 | 0.13497 | 0.14755 | 0.164 | 0.19853 | 0.25066 | 0.29797 | 0.33527 | 0.36899 | 0.40147 | 0.42655 | 0.44513 | 0.44556 | 0.42326 | 0.38411 | 0.37893 | 0.34501 | 0.3058 | 0.26597 | 0.21927
2015-10-26 | 0.18105 | 0.15506 | 0.14016 | 0.13017 | 0.12617 | 0.12697 | 0.13507 | 0.148 | 0.17867 | 0.22983 | 0.27902 | 0.31856 | 0.35402 | 0.39034 | 0.42068 | 0.44453 | 0.45537 | 0.43979 | 0.40485 | 0.41543 | 0.37887 | 0.32295 | 0.26342 | 0.20522
2015-10-27 | 0.16272 | 0.13814 | 0.12476 | 0.11894 | 0.12097 | 0.14138 | 0.18623 | 0.21419 | 0.22944 | 0.27037 | 0.31465 | 0.35714 | 0.39419 | 0.4352 | 0.47202 | 0.50686 | 0.52533 | 0.51143 | 0.4833 | 0.49511 | 0.44712 | 0.37787 | 0.3066 | 0.23808
2015-10-28 | 0.1903 | 0.16199 | 0.1452 | 0.137 | 0.13744 | 0.15925 | 0.20809 | 0.23475 | 0.25215 | 0.30182 | 0.35145 | 0.40216 | 0.4461 | 0.50295 | 0.54587 | 0.57765 | 0.59319 | 0.57498 | 0.5375 | 0.54754 | 0.49523 | 0.42873 | 0.35118 | 0.27907
2015-10-29 | 0.2269 | 0.19362 | 0.17285 | 0.16185 | 0.16181 | 0.18258 | 0.23654 | 0.26134 | 0.27821 | 0.34031 | 0.3956 | 0.45045 | 0.50506 | 0.55302 | 0.59235 | 0.62716 | 0.63411 | 0.60204 | 0.55309 | 0.55323 | 0.50378 | 0.43538 | 0.3572 | 0.28203
2015-10-30 | 0.22186 | 0.18841 | 0.16745 | 0.15616 | 0.15485 | 0.17495 | 0.22493 | 0.25152 | 0.26784 | 0.32239 | 0.38517 | 0.44027 | 0.48954 | 0.5311 | 0.55585 | 0.57525 | 0.58875 | 0.563 | 0.52887 | 0.53578 | 0.48796 | 0.42808 | 0.35553 | 0.28472
2015-10-31 | 0.22699 | 0.19231 | 0.16978 | 0.15881 | 0.15652 | 0.17643 | 0.22677 | 0.2547 | 0.27295 | 0.32624 | 0.37898 | 0.42968 | 0.46886 | 0.49701 | 0.51836 | 0.53466 | 0.53823 | 0.50448 | 0.44598 | 0.41543 | 0.36049 | 0.31602 | 0.26653 | 0.21611
2015-11-01 | 0.17094 | 0.14311 | 0.1282 | 0.12025 | 0.11739 | 0.12062 | 0.13474 | 0.14992 | 0.18282 | 0.2269 | 0.2618 | 0.27859 | 0.28511 | 0.28491 | 0.28689 | 0.2882 | 0.28405 | 0.26887 | 0.25849 | 0.27343 | 0.25007 | 0.22215 | 0.19057 | 0.16015
2015-11-02 | 0.50808 | 0.11186 | 0.10925 | 0.10904 | 0.11252 | 0.12317 | 0.14301 | 0.1832 | 0.2222 | 0.23892 | 0.24131 | 0.23667 | 0.23244 | 0.22583 | 0.22288 | 0.21974 | 0.22097 | 0.23967 | 0.27869 | 0.26737 | 0.24796 | 0.21649 | 0.1794 | 0.14901
2015-11-03 | 0.12588 | 0.11897 | 0.11517 | 0.11661 | 0.12502 | 0.1557 | 0.2131 | 0.23821 | 0.24491 | 0.25356 | 0.26416 | 0.27225 | 0.27319 | 0.27465 | 0.27159 | 0.26691 | 0.27107 | 0.28951 | 0.33017 | 0.31652 | 0.29068 | 0.2489 | 0.20359 | 0.16389
2015-11-04 | 0.13851 | 0.12333 | 0.1152 | 0.11364 | 0.11748 | 0.14097 | 0.18363 | 0.21712 | 0.24531 | 0.26817 | 0.29116 | 0.31192 | 0.32203 | 0.33131 | 0.33632 | 0.34036 | 0.33391 | 0.34448 | 0.38686 | 0.37345 | 0.343 | 0.29141 | 0.24344 | 0.1989
2015-11-05 | 0.16568 | 0.14455 | 0.13414 | 0.12923 | 0.1325 | 0.15535 | 0.20055 | 0.21704 | 0.26116 | 0.30715 | 0.34432 | 0.37444 | 0.39498 | 0.40525 | 0.40917 | 0.40147 | 0.38871 | 0.39862 | 0.43788 | 0.41805 | 0.38512 | 0.33595 | 0.27607 | 0.22097
2015-11-06 | 0.1812 | 0.1567 | 0.14178 | 0.13418 | 0.13534 | 0.15863 | 0.20237 | 0.2376 | 0.27669 | 0.32346 | 0.37262 | 0.41583 | 0.45045 | 0.47687 | 0.48972 | 0.48878 | 0.46713 | 0.44688 | 0.46849 | 0.43621 | 0.38663 | 0.32629 | 0.2631 | 0.20974
2015-11-07 | 0.16904 | 0.14486 | 0.1306 | 0.12524 | 0.12652 | 0.14648 | 0.19113 | 0.22232 | 0.25867 | 0.30222 | 0.34363 | 0.38249 | 0.41496 | 0.44219 | 0.45409 | 0.45154 | 0.42737 | 0.40825 | 0.42091 | 0.38054 | 0.34052 | 0.29595 | 0.25315 | 0.21136
2015-11-08 | 0.17458 | 0.14985 | 0.13385 | 0.12716 | 0.12582 | 0.13155 | 0.14593 | 0.17609 | 0.2354 | 0.28883 | 0.32841 | 0.36142 | 0.3904 | 0.40279 | 0.40096 | 0.38759 | 0.36883 | 0.37488 | 0.38837 | 0.35461 | 0.32142 | 0.28424 | 0.24688 | 0.20657
2015-11-09 | 0.17465 | 0.14974 | 0.13597 | 0.12901 | 0.1262 | 0.13014 | 0.14006 | 0.16199 | 0.20814 | 0.24764 | 0.27117 | 0.28544 | 0.28723 | 0.28007 | 0.27272 | 0.2613 | 0.25872 | 0.28496 | 0.30895 | 0.29136 | 0.2663 | 0.23183 | 0.19773 | 0.16058
2015-11-10 | 0.13352 | 0.11953 | 0.11237 | 0.10943 | 0.11307 | 0.12978 | 0.1748 | 0.21486 | 0.23414 | 0.25863 | 0.27816 | 0.2959 | 0.30915 | 0.32101 | 0.32691 | 0.33168 | 0.32629 | 0.33485 | 0.36752 | 0.34358 | 0.3077 | 0.26171 | 0.217 | 0.17416
2015-11-11 | 0.13969 | 0.12125 | 0.1118 | 0.10838 | 0.1108 | 0.12489 | 0.15524 | 0.18955 | 0.22237 | 0.2536 | 0.27826 | 0.29664 | 0.31414 | 0.33074 | 0.33862 | 0.34596 | 0.33957 | 0.343 | 0.37483 | 0.35236 | 0.31596 | 0.26957 | 0.22173 | 0.17473
2015-11-12 | 0.13918 | 0.12034 | 0.11213 | 0.10874 | 0.11288 | 0.13319 | 0.17951 | 0.20892 | 0.23057 | 0.25968 | 0.29111 | 0.32055 | 0.3475 | 0.37615 | 0.396 | 0.40325 | 0.39238 | 0.38506 | 0.41258 | 0.38534 | 0.3458 | 0.29694 | 0.24339 | 0.19302
2015-11-13 | 0.15616 | 0.13593 | 0.12425 | 0.12075 | 0.12355 | 0.1441 | 0.1905 | 0.2222 | 0.25233 | 0.29267 | 0.33095 | 0.3606 | 0.39057 | 0.41787 | 0.43033 | 0.43205 | 0.41653 | 0.40813 | 0.43229 | 0.40393 | 0.36212 | 0.30946 | 0.25111 | 0.20067
2015-11-14 | 0.16218 | 0.13884 | 0.12671 | 0.12059 | 0.12204 | 0.1405 | 0.18627 | 0.21902 | 0.24949 | 0.2841 | 0.31602 | 0.33794 | 0.35914 | 0.37494 | 0.38433 | 0.38422 | 0.3679 | 0.36272 | 0.37998 | 0.34905 | 0.31455 | 0.27423 | 0.23659 | 0.19717
2015-11-15 | 0.16451 | 0.1425 | 0.13073 | 0.12454 | 0.124 | 0.13047 | 0.14682 | 0.17435 | 0.22147 | 0.26495 | 0.29517 | 0.31927 | 0.33574 | 0.35049 | 0.35601 | 0.3529 | 0.33946 | 0.33679 | 0.35606 | 0.3265 | 0.2959 | 0.26412 | 0.23235 | 0.19946
2015-11-16 | 0.16804 | 0.14852 | 0.13643 | 0.12991 | 0.128 | 0.13325 | 0.14304 | 0.16561 | 0.22309 | 0.28218 | 0.32877 | 0.3649 | 0.39646 | 0.41688 | 0.42567 | 0.42514 | 0.40871 | 0.40566 | 0.43098 | 0.4033 | 0.36283 | 0.31754 | 0.27244 | 0.22506
2015-11-17 | 0.18888 | 0.16838 | 0.1572 | 0.15244 | 0.15863 | 0.18487 | 0.23808 | 0.27244 | 0.31526 | 0.37732 | 0.44105 | 0.49244 | 0.53077 | 0.55242 | 0.55531 | 0.54594 | 0.52638 | 0.52697 | 0.54674 | 0.50609 | 0.44839 | 0.37832 | 0.31293 | 0.24845
2015-11-18 | 0.20286 | 0.17579 | 0.1582 | 0.1495 | 0.1516 | 0.1715 | 0.22561 | 0.25968 | 0.28893 | 0.32352 | 0.34771 | 0.35236 | 0.34057 | 0.32794 | 0.31132 | 0.29512 | 0.29585 | 0.32862 | 0.36326 | 0.35231 | 0.32624 | 0.28781 | 0.24038 | 0.19926
2015-11-19 | 0.17229 | 0.1608 | 0.15624 | 0.15688 | 0.16767 | 0.20201 | 0.27793 | 0.31465 | 0.33007 | 0.33768 | 0.33355 | 0.3179 | 0.2994 | 0.28598 | 0.27565 | 0.27182 | 0.27826 | 0.31652 | 0.35709 | 0.35043 | 0.33027 | 0.29243 | 0.24679 | 0.20379
2015-11-20 | 0.17526 | 0.16174 | 0.15849 | 0.15986 | 0.17128 | 0.20551 | 0.27338 | 0.30331 | 0.29635 | 0.29625 | 0.2937 | 0.29058 | 0.28569 | 0.28074 | 0.27277 | 0.26891 | 0.27065 | 0.3055 | 0.34564 | 0.33946 | 0.31728 | 0.28098 | 0.23725 | 0.19505
2015-11-21 | 0.16491 | 0.14745 | 0.14161 | 0.13817 | 0.14304 | 0.17639 | 0.22828 | 0.26102 | 0.27295 | 0.28472 | 0.29478 | 0.29708 | 0.28888 | 0.28318 | 0.27631 | 0.27013 | 0.27376 | 0.30163 | 0.31968 | 0.30351 | 0.28251 | 0.2546 | 0.22377 | 0.19053
2015-11-22 | 0.16065 | 0.1427 | 0.13315 | 0.12985 | 0.13106 | 0.13871 | 0.15716 | 0.18374 | 0.23287 | 0.28012 | 0.30915 | 0.32537 | 0.32624 | 0.32521 | 0.32009 | 0.31142 | 0.30986 | 0.33485 | 0.35472 | 0.34131 | 0.32213 | 0.29458 | 0.26463 | 0.22608
2015-11-23 | 0.19188 | 0.17109 | 0.15563 | 0.14713 | 0.14558 | 0.15062 | 0.16145 | 0.18759 | 0.2546 | 0.33043 | 0.38489 | 0.4222 | 0.44664 | 0.46479 | 0.46812 | 0.46191 | 0.43866 | 0.44791 | 0.4773 | 0.45744 | 0.42337 | 0.37527 | 0.32516 | 0.27859
2015-11-24 | 0.22467 | 0.19465 | 0.1786 | 0.17258 | 0.17738 | 0.20249 | 0.25265 | 0.29092 | 0.34453 | 0.40888 | 0.47165 | 0.54101 | 0.59736 | 0.62694 | 0.64109 | 0.63576 | 0.6026 | 0.59062 | 0.61478 | 0.57409 | 0.52233 | 0.44912 | 0.38708 | 0.31561
2015-11-25 | 0.25918 | 0.22339 | 0.20445 | 0.19725 | 0.19902 | 0.2251 | 0.27745 | 0.31586 | 0.3707 | 0.43252 | 0.4901 | 0.53018 | 0.55356 | 0.57075 | 0.56863 | 0.55706 | 0.53242 | 0.54042 | 0.563 | 0.53308 | 0.48544 | 0.43181 | 0.37097 | 0.31515
2015-11-26 | 0.26477 | 0.23296 | 0.21323 | 0.20327 | 0.20335 | 0.21834 | 0.25247 | 0.28713 | 0.33126 | 0.3643 | 0.36659 | 0.35871 | 0.3466 | 0.32805 | 0.30635 | 0.28583 | 0.27498 | 0.29748 | 0.32321 | 0.3083 | 0.28439 | 0.26042 | 0.23018 | 0.19437
2015-11-27 | 0.16414 | 0.14551 | 0.13647 | 0.13421 | 0.13657 | 0.14752 | 0.16919 | 0.20347 | 0.24661 | 0.27707 | 0.29595 | 0.30351 | 0.30301 | 0.29272 | 0.28117 | 0.26356 | 0.24131 | 0.23239 | 0.23879 | 0.22207 | 0.21094 | 0.20116 | 0.18619 | 0.16543
2015-11-28 | 0.14672 | 0.1361 | 0.13194 | 0.13335 | 0.1409 | 0.15741 | 0.18564 | 0.21788 | 0.25079 | 0.27037 | 0.27305 | 0.26421 | 0.25347 | 0.24393 | 0.23523 | 0.22966 | 0.23009 | 0.25913 | 0.29429 | 0.2841 | 0.26873 | 0.2595 | 0.22957 | 0.19781
2015-11-29 | 0.17124 | 0.15763 | 0.15062 | 0.14974 | 0.15385 | 0.16265 | 0.1827 | 0.20983 | 0.24073 | 0.25556 | 0.25748 | 0.25625 | 0.25184 | 0.24697 | 0.24108 | 0.23532 | 0.23027 | 0.25021 | 0.27712 | 0.26486 | 0.24634 | 0.22604 | 0.20002 | 0.17045
2015-11-30 | 0.14352 | 0.12726 | 0.11943 | 0.11652 | 0.11794 | 0.12409 | 0.13637 | 0.15695 | 0.19505 | 0.22677 | 0.24755 | 0.26162 | 0.27211 | 0.27755 | 0.27864 | 0.27498 | 0.26966 | 0.29121 | 0.3311 | 0.31698 | 0.29409 | 0.26088 | 0.22339 | 0.18009
2015-12-01 | 0.14964 | 0.13125 | 0.12254 | 0.11984 | 0.12444 | 0.14817 | 0.19729 | 0.22742 | 0.25483 | 0.2867 | 0.32198 | 0.35075 | 0.36451 | 0.36976 | 0.36321 | 0.35145 | 0.34062 | 0.36555 | 0.40801 | 0.3947 | 0.36424 | 0.31759 | 0.2663 | 0.21215
2015-12-02 | 0.17094 | 0.14745 | 0.13338 | 0.12803 | 0.13171 | 0.15378 | 0.20535 | 0.23462 | 0.25679 | 0.29043 | 0.32449 | 0.34617 | 0.35898 | 0.36708 | 0.3643 | 0.35488 | 0.34226 | 0.3696 | 0.41131 | 0.39594 | 0.36582 | 0.32101 | 0.26714 | 0.21261
2015-12-03 | 0.17042 | 0.14544 | 0.13292 | 0.12716 | 0.12962 | 0.15181 | 0.20789 | 0.23466 | 0.26222 | 0.30371 | 0.33736 | 0.36582 | 0.38787 | 0.39839 | 0.40663 | 0.4105 | 0.39175 | 0.4005 | 0.43854 | 0.41799 | 0.38238 | 0.33287 | 0.27693 | 0.21822
2015-12-04 | 0.17484 | 0.15058 | 0.13744 | 0.13197 | 0.13514 | 0.15845 | 0.20929 | 0.24007 | 0.26705 | 0.3078 | 0.34226 | 0.37229 | 0.39634 | 0.40721 | 0.4145 | 0.41723 | 0.39685 | 0.40652 | 0.44694 | 0.4295 | 0.39617 | 0.34963 | 0.29004 | 0.23139
2015-12-05 | 0.18599 | 0.15767 | 0.14325 | 0.13754 | 0.13975 | 0.16261 | 0.21423 | 0.24562 | 0.27883 | 0.32836 | 0.36763 | 0.39521 | 0.41073 | 0.40928 | 0.40773 | 0.41345 | 0.40577 | 0.41589 | 0.43782 | 0.41108 | 0.3776 | 0.33763 | 0.29424 | 0.24429
2015-12-06 | 0.1991 | 0.1699 | 0.15276 | 0.1425 | 0.13844 | 0.14294 | 0.15756 | 0.18231 | 0.23887 | 0.30123 | 0.35124 | 0.38618 | 0.41061 | 0.42602 | 0.433 | 0.42737 | 0.40233 | 0.39181 | 0.40853 | 0.37031 | 0.3348 | 0.2995 | 0.25789 | 0.21277
2015-12-07 | 0.17079 | 0.14675 | 0.13191 | 0.12267 | 0.12015 | 0.12371 | 0.13322 | 0.15142 | 0.19922 | 0.25292 | 0.29048 | 0.31617 | 0.33002 | 0.33773 | 0.34004 | 0.33002 | 0.31652 | 0.3324 | 0.37477 | 0.3467 | 0.31769 | 0.27778 | 0.22979 | 0.18205
2015-12-08 | 0.14572 | 0.12559 | 0.11606 | 0.11282 | 0.11655 | 0.13821 | 0.18518 | 0.21402 | 0.23414 | 0.25881 | 0.28112 | 0.29615 | 0.3061 | 0.31424 | 0.31805 | 0.32264 | 0.32085 | 0.34363 | 0.38978 | 0.37643 | 0.34041 | 0.29292 | 0.24117 | 0.18673
2015-12-09 | 0.14807 | 0.1293 | 0.12031 | 0.11785 | 0.12188 | 0.14637 | 0.20375 | 0.23357 | 0.24958 | 0.26291 | 0.27098 | 0.27272 | 0.27201 | 0.26891 | 0.26402 | 0.25693 | 0.26042 | 0.29826 | 0.35022 | 0.34437 | 0.32208 | 0.28622 | 0.23821 | 0.19255
2015-12-10 | 0.16062 | 0.14755 | 0.14161 | 0.1451 | 0.15527 | 0.19677 | 0.27783 | 0.32851 | 0.32377 | 0.30785 | 0.29556 | 0.28088 | 0.26863 | 0.26037 | 0.25039 | 0.24661 | 0.25197 | 0.29585 | 0.36039 | 0.36033 | 0.3507 | 0.3183 | 0.27135 | 0.2236
2015-12-11 | 0.19457 | 0.18151 | 0.17852 | 0.17951 | 0.19302 | 0.23821 | 0.33043 | 0.37815 | 0.35757 | 0.33715 | 0.31263 | 0.29674 | 0.28136 | 0.26999 | 0.2595 | 0.25515 | 0.26093 | 0.30301 | 0.35693 | 0.35257 | 0.33925 | 0.30705 | 0.25689 | 0.21107
2015-12-12 | 0.18043 | 0.1655 | 0.1604 | 0.15979 | 0.17258 | 0.21373 | 0.29126 | 0.33287 | 0.3359 | 0.33532 | 0.32495 | 0.31187 | 0.29639 | 0.28357 | 0.27065 | 0.26616 | 0.27324 | 0.31978 | 0.36653 | 0.35774 | 0.34718 | 0.32193 | 0.28641 | 0.24621
2015-12-13 | 0.21219 | 0.19813 | 0.19164 | 0.19243 | 0.1999 | 0.2208 | 0.25492 | 0.29856 | 0.32588 | 0.32423 | 0.3049 | 0.28757 | 0.27498 | 0.26277 | 0.25215 | 0.24665 | 0.24513 | 0.27328 | 0.30941 | 0.29762 | 0.28525 | 0.26742 | 0.24148 | 0.21431
2015-12-14 | 0.1881 | 0.17255 | 0.16734 | 0.16778 | 0.17304 | 0.18853 | 0.21843 | 0.25849 | 0.29777 | 0.30237 | 0.28617 | 0.27413 | 0.26495 | 0.25748 | 0.25251 | 0.24814 | 0.24832 | 0.27807 | 0.33064 | 0.32393 | 0.3087 | 0.28151 | 0.23813 | 0.1991
2015-12-15 | 0.17199 | 0.15899 | 0.15802 | 0.16076 | 0.17594 | 0.21771 | 0.30306 | 0.35231 | 0.34803 | 0.32362 | 0.3062 | 0.29262 | 0.28946 | 0.28443 | 0.27845 | 0.27755 | 0.27897 | 0.31318 | 0.36998 | 0.36408 | 0.34162 | 0.30247 | 0.25251 | 0.20461
2015-12-16 | 0.17154 | 0.15684 | 0.15163 | 0.1535 | 0.16403 | 0.20184 | 0.28122 | 0.32203 | 0.31764 | 0.30138 | 0.29082 | 0.28549 | 0.28371 | 0.28453 | 0.28357 | 0.28482 | 0.28554 | 0.31172 | 0.36223 | 0.35268 | 0.32542 | 0.28174 | 0.23383 | 0.18627
2015-12-17 | 0.15076 | 0.13358 | 0.12707 | 0.12633 | 0.13477 | 0.16506 | 0.22686 | 0.26402 | 0.26789 | 0.27244 | 0.27655 | 0.27897 | 0.28386 | 0.2899 | 0.2963 | 0.30282 | 0.2996 | 0.32357 | 0.36812 | 0.35375 | 0.32418 | 0.2868 | 0.23755 | 0.18747
2015-12-18 | 0.15237 | 0.13464 | 0.12768 | 0.12733 | 0.13524 | 0.16367 | 0.22608 | 0.26467 | 0.27878 | 0.28728 | 0.29087 | 0.28791 | 0.28742 | 0.29659 | 0.30227 | 0.30371 | 0.30078 | 0.32285 | 0.36757 | 0.35338 | 0.3309 | 0.29204 | 0.24491 | 0.19657
2015-12-19 | 0.16167 | 0.1441 | 0.13593 | 0.13467 | 0.14195 | 0.17001 | 0.22699 | 0.26821 | 0.28323 | 0.29194 | 0.2997 | 0.30277 | 0.30242 | 0.30525 | 0.3052 | 0.30406 | 0.29836 | 0.31546 | 0.3529 | 0.33303 | 0.30695 | 0.27574 | 0.24188 | 0.20055
2015-12-20 | 0.16664 | 0.14579 | 0.1356 | 0.13106 | 0.1306 | 0.14043 | 0.16026 | 0.18861 | 0.22901 | 0.26254 | 0.28198 | 0.28554 | 0.30004 | 0.30177 | 0.30351 | 0.30401 | 0.29846 | 0.31359 | 0.3467 | 0.32198 | 0.29556 | 0.26681 | 0.23291 | 0.19422
2015-12-21 | 0.1586 | 0.1357 | 0.12254 | 0.11668 | 0.11588 | 0.12012 | 0.13164 | 0.15206 | 0.19629 | 0.24562 | 0.2784 | 0.2962 | 0.31515 | 0.3209 | 0.31657 | 0.3086 | 0.30217 | 0.32707 | 0.3673 | 0.35081 | 0.3282 | 0.2963 | 0.25447 | 0.20535
2015-12-22 | 0.16506 | 0.14077 | 0.1271 | 0.12059 | 0.12254 | 0.13868 | 0.16926 | 0.20278 | 0.25197 | 0.30391 | 0.35049 | 0.38165 | 0.4033 | 0.41968 | 0.43128 | 0.42549 | 0.40571 | 0.41723 | 0.46221 | 0.43758 | 0.40199 | 0.36114 | 0.30915 | 0.24491
2015-12-23 | 0.19521 | 0.16371 | 0.14507 | 0.13613 | 0.13734 | 0.15424 | 0.18533 | 0.21965 | 0.27394 | 0.3348 | 0.38355 | 0.42003 | 0.44736 | 0.45842 | 0.43377 | 0.40801 | 0.38579 | 0.39441 | 0.43502 | 0.41177 | 0.37943 | 0.35542 | 0.32162 | 0.28021
2015-12-24 | 0.23357 | 0.20035 | 0.18009 | 0.1715 | 0.16956 | 0.1812 | 0.20392 | 0.23462 | 0.29876 | 0.37932 | 0.44797 | 0.49689 | 0.52324 | 0.52789 | 0.53137 | 0.51881 | 0.50538 | 0.51758 | 0.52907 | 0.4709 | 0.41927 | 0.37798 | 0.33983 | 0.28878
2015-12-25 | 0.24108 | 0.20715 | 0.17898 | 0.15871 | 0.14548 | 0.14318 | 0.14856 | 0.16403 | 0.20375 | 0.24863 | 0.27907 | 0.29502 | 0.30068 | 0.29659 | 0.28796 | 0.27018 | 0.25184 | 0.25964 | 0.28179 | 0.27018 | 0.26093 | 0.24674 | 0.22194 | 0.18892
2015-12-26 | 0.15745 | 0.13723 | 0.12845 | 0.12394 | 0.12604 | 0.13774 | 0.15892 | 0.18541 | 0.22156 | 0.25808 | 0.28796 | 0.30073 | 0.30039 | 0.29287 | 0.2883 | 0.28506 | 0.28791 | 0.32147 | 0.35919 | 0.34538 | 0.32029 | 0.29053 | 0.25652 | 0.21423
2015-12-27 | 0.17541 | 0.14964 | 0.13378 | 0.12681 | 0.12684 | 0.13197 | 0.14593 | 0.16228 | 0.204 | 0.26019 | 0.3083 | 0.34141 | 0.36283 | 0.36993 | 0.3702 | 0.35871 | 0.34495 | 0.36087 | 0.39771 | 0.37433 | 0.34189 | 0.30865 | 0.26751 | 0.21969
2015-12-28 | 0.17883 | 0.15114 | 0.13481 | 0.12588 | 0.1216 | 0.12355 | 0.13352 | 0.14707 | 0.19705 | 0.25932 | 0.31031 | 0.35129 | 0.38121 | 0.40284 | 0.4145 | 0.41409 | 0.40147 | 0.39782 | 0.43401 | 0.40566 | 0.36828 | 0.32753 | 0.27874 | 0.22318
2015-12-29 | 0.18047 | 0.15378 | 0.13871 | 0.13233 | 0.13302 | 0.14593 | 0.17465 | 0.20404 | 0.25647 | 0.32285 | 0.38082 | 0.42085 | 0.44249 | 0.45233 | 0.45964 | 0.46338 | 0.44875 | 0.44465 | 0.48708 | 0.4547 | 0.41252 | 0.3586 | 0.30396 | 0.24206
2015-12-30 | 0.19207 | 0.16247 | 0.14568 | 0.13693 | 0.1361 | 0.14918 | 0.17616 | 0.20473 | 0.25012 | 0.3059 | 0.36055 | 0.40825 | 0.43943 | 0.46197 | 0.46818 | 0.46056 | 0.44291 | 0.44273 | 0.4845 | 0.45263 | 0.41461 | 0.3631 | 0.31142 | 0.25338
2015-12-31 | 0.20477 | 0.173 | 0.15492 | 0.14558 | 0.14479 | 0.15656 | 0.18205 | 0.21302 | 0.25748 | 0.30735 | 0.35017 | 0.37627 | 0.3826 | 0.38674 | 0.38545 | 0.37743 | 0.37971 | 0.42021 | 0.45659 | 0.41392 | 0.36555 | 0.31607 | 0.26934 | 0.2337

## Conductor Losses
OPC 012915
FPL RC-16
Conductor Losses - From Handwritten PDF
Dated 10/26/2010
Losses = I2R
I = current/amps
R = resistance of conductor
OH FEEDERS 568.3 kcmil ACAR
22500 | current/amps2
0.03287 | ohm/kft at 40º C
739.575 | w/kft
1000000
0.00073958 | mW/kft
48206 | kft
35.652 | mW/kft
3 | conductors
106.9559 | mW in losses
OH FEEDERS 3/0 AAAC
10000 | current/amps2
0.11378 | ohm/kft at 50º C
1137.8 | w/kft
1000000
0.0011378 | mW/kft
6051 | kft
6.8848 | mW/kft
3 | conductors
20.6545 | mW in losses
OH FEEDERS 1/0 AAAC
5625 | current/amps2
0.18049 | ohm/kft at 50º C
1015.2563 | w/kft
1000000
0.0010153 | mW/kft
3707 | kft
3.7636 | mW/kft
3 | conductors
11.2907 | mW in losses
OH LATERALS 1/0 AAAC
625 | current/amps2
0.18049 | ohm/kft at 50º C
112.8063 | w/kft
1000000
0.00011281 | mW/kft
119563 | kft
13.4875 | mW/kft
1 | conductors
13.4875 | mW in losses
UG FEEDERS 25kV, 1000 kcmil AL
22500 | current/amps2
0.0209 | ohm/kft at 58º C
470.25 | w/kft
1000000
0.00047025 | mW/kft
21268 | kft
10.0013 | mW/kft
3 | conductors
30.0038 | mW in losses
UG FEEDERS 25kV, 1/0 AL
625 | current/amps2
0.1886 | ohm/kft at 58º C
117.875 | w/kft
1000000
0.00011788 | mW/kft
1144 | kft
0.13485 | mW/kft
3 | conductors
0.40455 | mW in losses
UG LATERALS 25kV, 1/0 AL
625 | current/amps2
0.1886 | ohm/kft at 58º C
117.875 | w/kft
1000000
0.00011788 | mW/kft
114546 | kft
13.5021 | mW/kft
1 | conductors
13.5021 | mW in losses
196.2989 | mW in total cable losses