## 2016 Annual Cable Losses Energy
OPC 012916
FPL RC-16
2016 FCST (RC2016) - ESTIMATED PRIMARY LINE (CABLE) ENERGY LOSSES
[10 empty] | 2017 FCST NEL = | 119098.5243 | GWH |  | 1989 NEL = | 69956 | GWH
|  |  | Estimated Annual Cable Losses (GWH) = |  |  |  | 568.3966 |  |  | Cable Losses % NEL = | 0.47725 |  |  | Cable Losses % NEL = | 1.2994
CL = Conductor losses at peak (hour, day, month - mW); conductor losses are proportional to the square of the load current (load). Conductor losses vary with load over time.
CLE = mwh associated to conductor losses: 1 mW at peak = 1 mW p.u. = 1 mWh at the peak hour, varying over time.
CLEF = Hourly factor for energy on conductors. Changes with time over a daily/monthly load cycle. CLEF is the square of the p.u. load.
More generally:
| HL (Hourly Load p.u.) | CLEF (HL^2) | CLEF*CL (Mwh)
| 1 | 1 | 1*CL
| 0.98814 | 0.97642 | 0.9764*CL | [10 empty] | CONDUCTOR LOSSES (CL MW)
| 0.96386 | 0.92902 | 0.9290*CL | [10 empty] | Total | 196
| 0.91823 | 0.84314 | 0.8431*CL
| . | . | .
| . | . | .
| . | . | .
Hourly Energy (CLE) = CLEF*CL
Peak = Summer Peak (April to October)
Hourly Energy
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | MWH/Day
2016-01-01 | 33.082 | 30.7186 | 27.6212 | 25.6021 | 24.7468 | 25.1638 | 26.49 | 27.6088 | 32.8458 | 42.0436 | 51.6801 | 58.8516 | 63.3163 | 65.1156 | 64.576 | 62.9333 | 61.2566 | 62.691 | 68.9264 | 65.182 | 59.7114 | 53.9008 | 46.6373 | 38.2386 | 1118.9396
2016-01-02 | 31.1305 | 26.9579 | 24.3217 | 23.1081 | 22.7703 | 24.1712 | 29.916 | 35.0302 | 43.3727 | 54.3246 | 64.0292 | 71.14 | 76.4512 | 80.2597 | 81.9962 | 81.115 | 77.8763 | 76.5232 | 82.3159 | 76.1637 | 68.2643 | 59.9661 | 51.3089 | 42.0284 | 1304.5411
2016-01-03 | 34.0012 | 28.7824 | 25.7629 | 24.3565 | 24.2406 | 25.8704 | 30.9602 | 36.1594 | 42.7325 | 48.7398 | 52.3499 | 53.5475 | 53.5561 | 52.5713 | 51.5872 | 50.981 | 50.6709 | 55.6321 | 63.541 | 61.3394 | 56.9462 | 51.8493 | 45.322 | 38.3259 | 1059.8256
2016-01-04 | 32.5701 | 28.9782 | 26.9274 | 26.0621 | 26.1703 | 27.4854 | 30.4002 | 34.4689 | 41.2395 | 47.7274 | 51.7393 | 52.6395 | 51.79 | 50.4452 | 48.748 | 47.1929 | 47.5165 | 52.4265 | 56.9196 | 53.8663 | 50.0951 | 45.655 | 40.3759 | 34.5587 | 1005.998
2016-01-05 | 29.0796 | 25.4417 | 23.2723 | 22.0689 | 21.8266 | 22.8601 | 25.4002 | 28.4992 | 35.0372 | 42.0512 | 50.3784 | 55.8954 | 58.8696 | 59.8205 | 59.7387 | 58.6263 | 57.106 | 58.3835 | 65.7527 | 61.9486 | 56.8132 | 49.4647 | 41.5117 | 33.748 | 1043.5946
2016-01-06 | 26.763 | 23.261 | 21.2917 | 20.6083 | 21.1509 | 24.432 | 31.9691 | 37.2491 | 42.3873 | 49.8126 | 58.0875 | 63.6628 | 68.2255 | 70.7241 | 69.9452 | 66.9978 | 64.2646 | 68.3809 | 75.5595 | 71.3881 | 62.5143 | 52.401 | 44.5889 | 36.6916 | 1172.3568
2016-01-07 | 31.1698 | 28.305 | 27.5965 | 28.1613 | 30.8817 | 37.4935 | 51.5618 | 62.896 | 68.2643 | 71.5471 | 70.2405 | 66.6327 | 63.2601 | 60.0025 | 57.4976 | 57.3373 | 60.7699 | 72.4148 | 86.8237 | 87.8565 | 84.0852 | 74.7341 | 63.8224 | 53.8835 | 1397.2379
2016-01-08 | 46.8141 | 43.3108 | 42.0894 | 41.5496 | 42.8478 | 48.9123 | 61.3394 | 67.8473 | 67.1808 | 67.1808 | 66.3547 | 63.0453 | 58.6533 | 54.6369 | 51.2921 | 50.0036 | 50.9474 | 56.7512 | 63.907 | 61.5975 | 56.3887 | 48.4366 | 39.966 | 31.9093 | 1282.9619
2016-01-09 | 26.0261 | 23.2213 | 21.9531 | 21.4983 | 22.4015 | 26.345 | 35.365 | 41.9979 | 44.1973 | 48.2894 | 51.1995 | 52.8102 | 52.9556 | 52.1799 | 51.1995 | 50.8552 | 51.469 | 56.4505 | 64.3777 | 62.8401 | 57.9979 | 50.7044 | 42.6096 | 34.1521 | 1043.0962
2016-01-10 | 27.4423 | 23.5796 | 21.4929 | 20.7312 | 21.1833 | 24.4553 | 32.691 | 38.859 | 43.8774 | 50.3534 | 55.7988 | 59.412 | 61.4684 | 63.0359 | 63.0919 | 62.7469 | 62.2636 | 63.0079 | 69.8175 | 65.9722 | 60.0845 | 53.1182 | 46.3327 | 39.138 | 1129.9539
2016-01-11 | 31.4989 | 27.1353 | 24.3681 | 23.0799 | 22.8152 | 24.0673 | 26.9946 | 30.9405 | 40.7427 | 52.648 | 61.8006 | 67.857 | 72.5349 | 75.4472 | 76.6466 | 75.9893 | 72.7554 | 70.1715 | 74.4193 | 68.9557 | 62.1616 | 54.5761 | 47.2333 | 39.6323 | 1224.4714
2016-01-12 | 32.1955 | 27.3931 | 24.5891 | 23.0291 | 22.2682 | 22.731 | 24.6125 | 27.2211 | 34.1453 | 42.0741 | 48.1996 | 51.8916 | 55.2556 | 57.4352 | 58.0516 | 57.3284 | 55.6584 | 54.5067 | 61.0819 | 58.7344 | 53.5303 | 46.6453 | 39.3958 | 31.7369 | 1009.7105
2016-01-13 | 26.0261 | 23.1025 | 21.7991 | 21.6676 | 22.8714 | 27.7016 | 38.0353 | 44.9981 | 47.9144 | 51.9509 | 55.6496 | 58.4914 | 61.1462 | 63.2321 | 64.5854 | 65.5622 | 64.9923 | 66.1442 | 74.602 | 72.6852 | 65.3435 | 55.8076 | 46.2287 | 36.4925 | 1177.0296
2016-01-14 | 28.9845 | 24.8346 | 22.7535 | 21.7224 | 22.1297 | 25.8107 | 34.7525 | 40.7052 | 45.814 | 53.2726 | 59.9024 | 63.9352 | 66.0486 | 66.1537 | 65.2485 | 62.8401 | 62.1894 | 65.1156 | 73.1671 | 71.0111 | 64.5193 | 55.7549 | 45.7504 | 36.0605 | 1178.4762
2016-01-15 | 28.6627 | 24.8991 | 22.8995 | 22.2405 | 22.6918 | 26.8421 | 36.5919 | 42.9556 | 45.3299 | 48.5758 | 50.3034 | 50.4285 | 49.0522 | 47.7112 | 46.2367 | 45.5439 | 46.2687 | 51.545 | 58.8696 | 57.1771 | 52.759 | 46.2127 | 38.4862 | 30.7838 | 993.0667
2016-01-16 | 25.614 | 23.0516 | 22.3182 | 22.5911 | 24.2233 | 30.1092 | 42.7709 | 52.1375 | 53.8231 | 54.4373 | 54.4199 | 52.8017 | 50.3701 | 47.8574 | 45.7186 | 44.6832 | 45.7424 | 52.4265 | 68.1478 | 71.4079 | 70.6549 | 66.1537 | 59.2038 | 51.917 | 1132.581
2016-01-17 | 47.0557 | 45.2033 | 45.4725 | 47.0557 | 50.6793 | 60.4678 | 79.8915 | 92.9418 | 91.025 | 81.7728 | 72.155 | 62.9146 | 55.7198 | 50.22 | 46.541 | 44.5732 | 44.9271 | 50.6291 | 60.5135 | 59.766 | 57.3729 | 52.7846 | 47.7274 | 41.9446 | 1389.3541
2016-01-18 | 36.7414 | 34.538 | 33.8984 | 34.1727 | 35.6873 | 39.2705 | 45.7186 | 54.663 | 61.1278 | 61.8654 | 59.5662 | 54.9851 | 50.3617 | 46.3807 | 42.9865 | 41.1942 | 41.2168 | 46.0371 | 57.5957 | 59.7569 | 59.7478 | 58.7704 | 56.2211 | 52.6736 | 1165.1769
2016-01-19 | 50.2034 | 49.3738 | 50.012 | 51.9339 | 55.0985 | 60.413 | 69.1315 | 80.4283 | 87.2625 | 81.9111 | 70.8131 | 60.7699 | 53.2983 | 48.1099 | 44.127 | 41.0434 | 40.1446 | 42.7709 | 52.5116 | 51.8662 | 49.4317 | 44.6753 | 40.0776 | 34.0286 | 1309.436
2016-01-20 | 29.916 | 28.0616 | 27.6459 | 28.1738 | 30.4326 | 35.1765 | 43.7063 | 52.5883 | 56.0185 | 54.4633 | 52.3839 | 50.4202 | 48.1507 | 46.4368 | 45.148 | 44.4399 | 44.5654 | 47.6219 | 56.769 | 56.0097 | 51.149 | 44.4242 | 36.7913 | 29.4038 | 1039.8966
2016-01-21 | 24.3855 | 21.9421 | 20.9728 | 20.9674 | 22.0689 | 26.7995 | 37.2491 | 44.1582 | 45.7265 | 46.2127 | 46.7095 | 46.6935 | 46.5009 | 45.6471 | 44.9035 | 44.1504 | 44.4399 | 48.453 | 56.8576 | 56.5389 | 51.9339 | 44.9744 | 37.3784 | 30.3354 | 955.9991
2016-01-22 | 25.2937 | 23.5168 | 23.2326 | 24.125 | 26.8787 | 34.3034 | 49.738 | 60.8432 | 59.1224 | 61.2566 | 59.7478 | 56.7778 | 53.4787 | 49.7628 | 47.2252 | 45.8777 | 46.798 | 53.2468 | 68.9459 | 73.6001 | 73.459 | 69.0045 | 62.3193 | 54.7761 | 1203.3301
2016-01-23 | 50.4786 | 49.4647 | 50.5371 | 52.9641 | 57.6136 | 69.8273 | 93.2026 | 105.706 | 98.5082 | 87.0649 | 76.832 | 66.2398 | 57.9889 | 51.5281 | 47.4031 | 45.3536 | 45.5201 | 50.4202 | 63.148 | 65.6193 | 63.5597 | 57.9531 | 49.6799 | 42.0665 | 1498.6795
2016-01-24 | 36.8984 | 35.1556 | 35.0441 | 35.997 | 38.8883 | 47.4112 | 64.4155 | 74.3585 | 74.2572 | 70.9715 | 66.8632 | 61.1186 | 56.2299 | 52.1884 | 48.9781 | 47.1686 | 47.6381 | 52.0102 | 62.4493 | 62.7097 | 59.9115 | 55.3343 | 49.8375 | 43.3882 | 1279.2229
2016-01-25 | 38.355 | 35.9336 | 34.9815 | 35.2532 | 36.5422 | 39.6249 | 45.3299 | 53.024 | 60.7516 | 60.2943 | 55.79 | 51.065 | 47.4355 | 44.6596 | 42.5789 | 41.0359 | 40.3684 | 42.3644 | 49.5226 | 48.7562 | 45.4963 | 41.6558 | 36.6845 | 31.3934 | 1058.8965
2016-01-26 | 27.1659 | 24.5425 | 23.4598 | 23.0065 | 23.3518 | 24.993 | 28.2613 | 33.082 | 40.473 | 44.5575 | 46.4528 | 46.2527 | 46.1408 | 46.0371 | 45.4249 | 44.7775 | 44.6517 | 46.9348 | 54.5327 | 54.2726 | 49.5475 | 43.2103 | 36.3789 | 29.143 | 926.6507
2016-01-27 | 23.7798 | 20.8545 | 19.6328 | 19.3112 | 20.406 | 24.5192 | 34.2828 | 40.4207 | 43.1176 | 46.3807 | 50.2283 | 52.8359 | 55.0112 | 56.831 | 57.676 | 58.7524 | 59.24 | 60.1392 | 67.5571 | 66.6807 | 59.8751 | 50.4035 | 40.8328 | 31.5319 | 1060.3004
2016-01-28 | 24.6475 | 21.2266 | 19.6484 | 19.0383 | 19.7946 | 23.6824 | 32.7112 | 39.1306 | 42.1657 | 46.4288 | 51.0314 | 54.4026 | 57.6225 | 60.3673 | 62.4214 | 64.001 | 64.5476 | 64.8029 | 71.3781 | 70.1912 | 63.8224 | 53.8922 | 44.4321 | 34.9955 | 1106.3823
2016-01-29 | 27.6583 | 23.9003 | 22.1685 | 21.5638 | 22.3904 | 26.7508 | 36.3647 | 43.6053 | 46.9267 | 51.6463 | 55.2819 | 58.3835 | 44.8326 | 57.8547 | 56.6362 | 57.1238 | 58.9327 | 63.8036 | 70.2011 | 68.595 | 64.2363 | 56.4417 | 47.5732 | 38.3623 | 1121.2337
2016-01-30 | 32.2155 | 28.7824 | 27.1353 | 26.7812 | 28.0429 | 33.2106 | 45.1717 | 53.3069 | 57.6046 | 61.8284 | 64.2081 | 63.8976 | 62.5329 | 60.9441 | 59.1948 | 58.195 | 58.8696 | 62.9706 | 70.5463 | 69.337 | 63.9446 | 56.4505 | 46.7819 | 37.717 | 1229.6693
2016-01-31 | 31.5781 | 28.2675 | 26.9641 | 26.4174 | 27.264 | 32.0755 | 43.0559 | 50.3951 | 53.4873 | 57.5779 | 60.6508 | 62.3843 | 62.7469 | 62.2822 | 61.4223 | 61.9208 | 61.2106 | 62.3471 | 67.8183 | 65.6765 | 59.9934 | 53.1354 | 45.6788 | 37.7386 | 1202.0887
2016-02-01 | 31.0256 | 26.8421 | 24.3681 | 23.1138 | 22.8882 | 23.9866 | 27.0129 | 31.7104 | 41.0736 | 50.9558 | 58.1233 | 62.245 | 65.372 | 67.2868 | 68.4976 | 68.9264 | 67.8764 | 65.3244 | 68.3032 | 65.6384 | 58.9327 | 51.7985 | 44.5968 | 36.9984 | 1152.8971
2016-02-02 | 30.206 | 26.0081 | 23.4883 | 22.1297 | 21.6621 | 22.0966 | 23.9809 | 27.4423 | 37.2348 | 47.5408 | 54.524 | 59.1767 | 65.22 | 69.6604 | 72.8757 | 74.3788 | 74.1964 | 71.3086 | 71.259 | 64.7461 | 58.9057 | 55.4743 | 50.9894 | 40.8403 | 1165.345
2016-02-03 | 32.6238 | 26.496 | 24.2812 | 23.3688 | 23.9521 | 27.9248 | 36.8555 | 42.9171 | 48.8301 | 56.893 | 65.5622 | 71.9255 | 77.0692 | 81.1786 | 84.2362 | 85.4925 | 83.3645 | 80.5232 | 84.9607 | 82.7645 | 73.6909 | 63.8788 | 52.6395 | 41.7013 | 1373.1298
2016-02-04 | 33.3734 | 28.896 | 26.357 | 25.1638 | 25.4239 | 29.0162 | 38.1151 | 44.0723 | 49.6468 | 58.2578 | 66.5655 | 73.0163 | 78.2606 | 81.6453 | 83.9559 | 85.2969 | 84.0529 | 80.6076 | 85.1233 | 84.2686 | 76.2355 | 65.7146 | 54.9415 | 43.8229 | 1401.8297
2016-02-05 | 35.4 | 30.3354 | 27.7697 | 26.4597 | 26.684 | 30.7838 | 40.6302 | 46.8141 | 52.6139 | 61.9116 | 70.6352 | 77.5136 | 81.9856 | 85.1884 | 87.1856 | 86.266 | 82.6575 | 79.6919 | 83.7621 | 81.5285 | 73.6102 | 63.5128 | 52.2734 | 41.4284 | 1426.6416
2016-02-06 | 33.2038 | 28.1426 | 25.6616 | 24.432 | 24.7819 | 28.4177 | 37.8036 | 43.8151 | 49.6551 | 56.8221 | 63.4473 | 68.5074 | 72.7554 | 76.8217 | 78.5521 | 79.608 | 78.6042 | 77.3378 | 81.8153 | 80.6815 | 72.946 | 63.0639 | 52.0866 | 40.9381 | 1339.9008
2016-02-07 | 32.5701 | 27.9248 | 24.946 | 23.631 | 23.8314 | 27.4916 | 36.6275 | 42.8786 | 47.1041 | 52.8444 | 58.5813 | 64.1704 | 67.5958 | 68.1672 | 72.7253 | 74.0344 | 73.6606 | 72.7052 | 73.1771 | 69.3761 | 64.001 | 55.4831 | 48.0936 | 39.6545 | 1241.2752
2016-02-08 | 32.6372 | 27.7883 | 25.0813 | 23.7683 | 23.671 | 24.7468 | 27.8503 | 32.4964 | 42.0665 | 53.1354 | 62.2358 | 68.1575 | 72.2548 | 74.2875 | 75.5902 | 74.7747 | 72.9661 | 70.3391 | 71.9853 | 68.6437 | 61.9486 | 54.7761 | 47.4112 | 40.0255 | 1228.6374
2016-02-09 | 32.9199 | 28.1364 | 25.418 | 24.0558 | 23.7569 | 24.6708 | 26.8908 | 30.491 | 37.6592 | 44.8641 | 49.9704 | 52.7163 | 55.3168 | 56.9196 | 57.6314 | 57.035 | 55.6233 | 55.1945 | 60.3856 | 61.1922 | 55.3343 | 47.9469 | 40.6003 | 32.2088 | 1036.9384
2016-02-10 | 25.9902 | 22.7703 | 21.4983 | 21.2971 | 22.3237 | 26.8604 | 37.0056 | 43.6363 | 46.6453 | 50.5287 | 55.0025 | 58.0158 | 60.8799 | 63.1573 | 64.1139 | 65.1156 | 65.2959 | 64.576 | 69.788 | 71.1102 | 64.2457 | 55.0636 | 45.1164 | 35.421 | 1155.4577
2016-02-11 | 28.493 | 24.5484 | 22.7422 | 22.1629 | 22.9164 | 27.2333 | 37.4359 | 44.0567 | 47.6219 | 52.6054 | 57.2928 | 61.7729 | 65.667 | 69.2 | 71.3781 | 73.6606 | 74.3281 | 73.0264 | 77.0073 | 77.5136 | 71.1102 | 59.5118 | 48.3385 | 37.6087 | 1247.232
2016-02-12 | 29.3974 | 25.2759 | 22.9051 | 21.9476 | 22.4516 | 26.2124 | 35.6101 | 41.3755 | 46.1249 | 52.5713 | 58.5273 | 63.5597 | 67.4316 | 70.6747 | 71.5173 | 70.2109 | 68.4685 | 68.7899 | 75.2941 | 73.6506 | 66.8824 | 57.4263 | 45.4012 | 34.6347 | 1216.3409
2016-02-13 | 27.7201 | 23.7454 | 21.9972 | 21.3351 | 22.1021 | 26.2064 | 36.0605 | 42.9171 | 46.7578 | 49.2913 | 51.6125 | 52.4435 | 52.9042 | 52.7675 | 52.2989 | 51.5703 | 50.8468 | 50.8636 | 56.9462 | 59.3939 | 55.6759 | 49.5392 | 41.8685 | 33.8847 | 1030.7487
2016-02-14 | 28.1863 | 25.5604 | 24.7059 | 24.993 | 26.8726 | 33.3666 | 47.7518 | 58.2309 | 58.0158 | 55.3256 | 53.1954 | 49.7048 | 47.0073 | 45.2033 | 44.0801 | 44.0411 | 44.0099 | 44.8405 | 50.6207 | 51.79 | 48.1588 | 43.4424 | 38.4205 | 32.8256 | 1020.3494
2016-02-15 | 28.3238 | 25.6318 | 24.258 | 23.7626 | 23.9751 | 25.6735 | 29.162 | 34.4551 | 40.6902 | 44.9429 | 47.4436 | 47.703 | 46.541 | 45.3774 | 44.3616 | 43.9865 | 43.7762 | 44.3381 | 48.7891 | 49.8624 | 46.4528 | 42.1199 | 37.3281 | 31.5517 | 920.5063
2016-02-16 | 27.0557 | 24.6592 | 24.3507 | 24.63 | 25.1992 | 27.7573 | 32.5634 | 39.6841 | 45.9414 | 47.8493 | 46.9348 | 44.8405 | 43.6752 | 42.8324 | 42.4486 | 42.5866 | 43.0559 | 43.9397 | 49.0028 | 50.83 | 46.8221 | 41.6861 | 36.5635 | 30.2383 | 925.1468
2016-02-17 | 25.6378 | 23.3063 | 22.5632 | 22.7983 | 24.2869 | 28.606 | 36.5067 | 44.5183 | 49.2995 | 51.1911 | 52.0526 | 52.2564 | 52.5713 | 53.1525 | 53.7628 | 54.6543 | 55.1246 | 55.3868 | 59.8387 | 61.3486 | 55.3956 | 47.5489 | 38.6614 | 30.7773 | 1051.246
2016-02-18 | 24.6767 | 21.4547 | 20.3795 | 20.1044 | 21.2104 | 25.6318 | 35.8561 | 43.0636 | 45.9813 | 48.9205 | 51.7393 | 54.1081 | 56.2123 | 58.4914 | 60.66 | 62.7562 | 63.5128 | 62.3657 | 65.448 | 66.969 | 60.3947 | 50.9474 | 41.8152 | 32.2889 | 1094.988
2016-02-19 | 25.6497 | 22.0303 | 20.4857 | 19.8732 | 20.6083 | 24.5658 | 34.008 | 40.0925 | 43.9242 | 48.5021 | 53.3498 | 57.6671 | 61.1646 | 64.6232 | 68.012 | 71.3186 | 72.135 | 70.142 | 71.9753 | 72.8055 | 66.0868 | 56.424 | 46.1808 | 36.0747 | 1167.6991
2016-02-20 | 28.3676 | 24.3275 | 22.2128 | 21.1238 | 21.4275 | 25.2641 | 34.4551 | 40.7577 | 46.3967 | 53.4443 | 60.5227 | 65.5812 | 70.3982 | 74.2673 | 77.0485 | 79.4927 | 79.8284 | 77.5033 | 80.1859 | 81.5709 | 74.9171 | 65.6384 | 54.5327 | 44.1035 | 1303.3681
2016-02-21 | 35.456 | 29.8967 | 27.1659 | 25.8525 | 25.9303 | 29.4739 | 38.9763 | 45.6868 | 54.4806 | 64.5193 | 73.6707 | 80.7343 | 85.7644 | 89.095 | 89.506 | 88.5631 | 83.1285 | 78.7711 | 80.6604 | 78.2606 | 70.8428 | 61.7637 | 53.4615 | 44.0021 | 1435.6625
2016-02-22 | 35.7998 | 29.9481 | 26.9946 | 25.1815 | 24.7176 | 25.3114 | 28.0554 | 33.0753 | 44.935 | 57.2305 | 66.9401 | 74.5005 | 80.6709 | 84.1283 | 85.4925 | 86.1023 | 83.8913 | 78.3126 | 77.3895 | 75.2329 | 67.1422 | 58.9869 | 50.7128 | 41.8457 | 1342.5974
2016-02-23 | 34.1384 | 29.0225 | 25.9542 | 24.2406 | 23.4826 | 23.7569 | 25.4595 | 29.5889 | 40.4057 | 52.6395 | 63.204 | 71.766 | 82.3052 | 84.0636 | 85.5794 | 86.9552 | 85.6556 | 82.1027 | 82.0601 | 82.3265 | 74.6934 | 62.9893 | 52.947 | 41.8457 | 1347.1827
2016-02-24 | 32.9199 | 28.5558 | 25.8585 | 24.3681 | 24.5484 | 28.1801 | 36.2372 | 42.8478 | 49.7877 | 58.8606 | 67.8473 | 74.5614 | 81.4224 | 86.2769 | 89.3282 | 91.7105 | 89.5839 | 86.2769 | 89.4504 | 90.0965 | 79.8284 | 67.6634 | 54.7935 | 42.8555 | 1443.8592
2016-02-25 | 33.6388 | 28.493 | 25.6021 | 24.0731 | 24.1886 | 27.8379 | 36.9198 | 42.6019 | 48.8959 | 56.5831 | 63.9258 | 70.3686 | 76.7702 | 82.5721 | 87.2405 | 90.0184 | 89.1949 | 84.4089 | 85.3621 | 85.3947 | 76.4306 | 64.491 | 52.8102 | 40.9305 | 1398.7524
2016-02-26 | 32.0289 | 26.9702 | 24.0673 | 22.7703 | 22.8658 | 25.9602 | 34.4206 | 40.4132 | 45.7345 | 52.0357 | 60.9717 | 67.2965 | 73.1972 | 77.3584 | 80.0702 | 80.6287 | 78.2086 | 76.554 | 80.9034 | 80.766 | 73.3885 | 63.6066 | 52.4605 | 41.7924 | 1314.4693
2016-02-27 | 33.4958 | 29.1049 | 26.8787 | 25.8645 | 26.1823 | 29.8132 | 39.2116 | 44.8956 | 48.453 | 53.0497 | 58.2937 | 57.1682 | 62.5608 | 63.3163 | 63.0359 | 62.3471 | 60.8616 | 63.2975 | 67.9151 | 68.7509 | 63.0919 | 53.8835 | 43.9787 | 35.0441 | 1180.4946
2016-02-28 | 28.2425 | 24.6708 | 23.0968 | 22.6135 | 23.329 | 27.5841 | 37.7675 | 44.2911 | 46.4368 | 47.7761 | 48.8466 | 49.1758 | 49.2418 | 49.7794 | 50.3701 | 51.1995 | 51.7224 | 51.0398 | 53.4443 | 54.8979 | 50.2867 | 44.5261 | 38.1296 | 31.4461 | 999.9144
2016-02-29 | 26.0081 | 22.8433 | 21.1995 | 20.5017 | 20.7741 | 22.4851 | 25.9722 | 31.0715 | 38.1151 | 43.133 | 46.4528 | 48.216 | 49.9288 | 51.6463 | 52.9385 | 54.6196 | 54.8283 | 53.41 | 53.5303 | 55.5181 | 50.2117 | 44.5732 | 38.508 | 31.7501 | 958.2352
2016-03-01 | 26.0081 | 22.8433 | 21.1995 | 20.5017 | 20.7741 | 22.4851 | 25.9722 | 31.0715 | 38.1151 | 43.133 | 46.4528 | 48.216 | 49.9288 | 51.6463 | 52.9385 | 54.6196 | 54.8283 | 53.41 | 53.5303 | 55.5181 | 50.2117 | 44.5732 | 38.508 | 31.7501 | 958.2352
2016-03-02 | 26.3208 | 23.1477 | 21.4384 | 19.9624 | 19.7476 | 20.5656 | 22.6358 | 26.4658 | 34.7594 | 42.5022 | 47.7599 | 51.7477 | 54.9066 | 58.0875 | 60.3582 | 62.3843 | 63.0453 | 61.4868 | 62.1153 | 64.3966 | 57.9979 | 49.8707 | 41.3075 | 32.7919 | 1025.8018
2016-03-03 | 27.0863 | 22.7759 | 20.5816 | 19.7894 | 20.2417 | 23.8429 | 32.0489 | 37.8326 | 43.4269 | 50.0868 | 56.6804 | 61.7544 | 66.9305 | 72.135 | 75.5391 | 78.6563 | 79.5975 | 77.2551 | 77.2241 | 78.6876 | 69.8568 | 58.6173 | 47.395 | 36.2939 | 1234.3359
2016-03-04 | 28.3739 | 23.8199 | 21.4983 | 20.3689 | 20.6136 | 23.9463 | 32.1955 | 38.2095 | 43.5122 | 50.0951 | 56.3975 | 61.8099 | 66.9016 | 71.7859 | 76.0713 | 79.325 | 80.1228 | 77.6586 | 77.9074 | 78.8546 | 71.1102 | 61.0911 | 49.7628 | 38.903 | 1250.3351
2016-03-05 | 30.5624 | 26.2184 | 23.8486 | 22.8995 | 23.2836 | 26.8421 | 36.1453 | 42.4486 | 47.6787 | 55.4831 | 62.6724 | 69.1706 | 74.8154 | 78.5625 | 80.0807 | 80.5759 | 78.6251 | 76.1124 | 77.8452 | 78.7189 | 71.9953 | 62.1987 | 51.2416 | 40.234 | 1318.259
2016-03-06 | 32.0356 | 27.6645 | 25.0872 | 24.0385 | 24.2059 | 27.683 | 36.5209 | 42.8017 | 50.17 | 58.2668 | 64.6138 | 70.0928 | 73.8525 | 73.0766 | 71.3285 | 61.2658 | 56.6273 | 57.3818 | 62.6817 | 63.7848 | 58.7524 | 51.1238 | 42.8863 | 34.3792 | 1190.3212
2016-03-07 | 27.7511 | 23.9981 | 22.513 | 21.8431 | 22.4628 | 26.2365 | 35.2672 | 41.4436 | 47.4274 | 52.648 | 57.1149 | 59.1857 | 60.276 | 60.3764 | 60.2851 | 60.3673 | 59.5753 | 57.4709 | 58.5363 | 59.3034 | 54.9241 | 47.7436 | 40.6527 | 32.3625 | 1089.765
2016-03-08 | 27.2824 | 23.7855 | 22.2516 | 21.7005 | 22.1187 | 23.5624 | 27.4115 | 33.2581 | 39.9215 | 43.9943 | 45.1954 | 45.1006 | 44.9035 | 44.8247 | 45.4328 | 46.3407 | 46.8301 | 46.3807 | 47.7599 | 50.245 | 46.0052 | 41.1339 | 35.512 | 30.2513 | 901.2023
2016-03-09 | 24.7995 | 0 | 21.9586 | 20.4911 | 19.9834 | 20.6457 | 22.5688 | 25.501 | 30.0898 | 36.2443 | 41.6633 | 44.1582 | 47.6462 | 49.6302 | 51.107 | 53.2897 | 55.5882 | 56.707 | 55.0374 | 55.5181 | 58.1771 | 51.6801 | 43.7762 | 33.6184 | 919.8794
2016-03-10 | 26.2064 | 21.7937 | 19.7999 | 19.1977 | 19.9046 | 23.2439 | 31.3868 | 38.1659 | 40.3161 | 44.6989 | 50.2617 | 53.7542 | 57.8279 | 60.6142 | 64.8881 | 69.1609 | 72.7855 | 73.0364 | 70.0239 | 69.2293 | 70.4278 | 60.5044 | 50.3367 | 38.8737 | 1146.4385
2016-03-11 | 29.557 | 24.4146 | 21.7772 | 20.523 | 20.5177 | 23.774 | 31.9159 | 38.4643 | 40.331 | 45.4963 | 50.3451 | 55.0636 | 59.3305 | 63.3818 | 67.3061 | 71.8357 | 75.764 | 76.9351 | 74.2268 | 72.8958 | 74.247 | 65.4005 | 54.2899 | 41.3982 | 1199.191
2016-03-12 | 32.5165 | 27.0435 | 24.403 | 23.278 | 23.5282 | 27.0374 | 36.0747 | 35.6803 | 44.6125 | 51.1574 | 59.7296 | 67.0556 | 73.0163 | 77.2034 | 79.5031 | 84.0313 | 86.8128 | 85.5142 | 80.9563 | 79.0948 | 79.8915 | 70.418 | 59.3034 | 46.967 | 1354.8285
2016-03-13 | 36.8199 | 30.7186 | 27.3439 | 25.6259 | 25.1874 | 27.8875 | 35.6522 | 41.0133 | 42.648 | 47.6543 | 51.5618 | 53.9181 | 55.2469 | 56.089 | 56.6716 | 57.2839 | 58.4824 | 58.195 | 54.9415 | 54.5501 | 56.7335 | 50.0618 | 41.762 | 32.7448 | 1078.7933
2016-03-14 | 26.0141 | 22.552 | 20.7312 | 20.2893 | 21.1833 | 25.2346 | 35.568 | 44.0567 | 46.077 | 47.9062 | 49.3243 | 49.6717 | 49.5226 | 49.8956 | 50.3784 | 51.2668 | 52.5542 | 52.4776 | 50.4953 | 50.3284 | 52.1629 | 47.1041 | 40.4955 | 33.5026 | 988.7926
2016-03-15 | 26.5445 | 22.7703 | 20.6083 | 19.6693 | 19.847 | 21.14 | 23.9751 | 29.124 | 35.505 | 41.8913 | 47.1041 | 50.22 | 52.5202 | 54.4806 | 56.8221 | 59.2762 | 61.9856 | 62.4586 | 59.4392 | 56.5831 | 57.2305 | 51.1827 | 44.6753 | 36.2514 | 1011.3042
2016-03-16 | 29.5122 | 25.2346 | 22.6694 | 21.2917 | 20.7473 | 21.0968 | 22.9164 | 25.9063 | 32.4562 | 42.0131 | 49.4647 | 55.2906 | 60.1301 | 63.9634 | 67.7892 | 70.4673 | 71.7262 | 71.2888 | 67.8086 | 66.508 | 68.8289 | 61.699 | 53.2554 | 42.4027 | 1134.4668
2016-03-17 | 33.8847 | 28.7761 | 26.0922 | 25.152 | 25.6616 | 29.4867 | 38.195 | 45.4328 | 49.5806 | 58.2758 | 68.4879 | 75.9279 | 81.5179 | 84.4305 | 85.9714 | 87.0649 | 87.3943 | 84.9823 | 82.2732 | 83.8805 | 83.7621 | 74.9782 | 65.1915 | 52.8444 | 1459.2443
2016-03-18 | 42.9633 | 37.0413 | 34.1934 | 32.8593 | 32.6507 | 35.6733 | 43.9553 | 49.2418 | 48.3221 | 51.3257 | 54.3419 | 56.0185 | 57.4709 | 59.5118 | 62.2265 | 65.1725 | 68.3421 | 69.337 | 66.6039 | 65.2674 | 66.8824 | 58.8516 | 48.666 | 37.3928 | 1244.3113
2016-03-19 | 28.7004 | 24.05 | 21.7278 | 20.7312 | 20.9944 | 24.3507 | 32.6037 | 38.8517 | 41.5799 | 47.1686 | 53.0155 | 57.5333 | 60.6142 | 64.4721 | 68.3809 | 72.2449 | 74.7137 | 74.8662 | 70.8923 | 68.2546 | 70.0829 | 62.0782 | 52.0781 | 40.6452 | 1190.6306
2016-03-20 | 31.9957 | 26.836 | 24.2869 | 22.8995 | 22.984 | 26.1703 | 34.3861 | 40.9005 | 43.893 | 49.3986 | 55.4919 | 60.2669 | 64.1327 | 68.2838 | 72.155 | 75.3043 | 77.3998 | 76.6569 | 73.0666 | 70.1814 | 71.6963 | 62.375 | 51.7562 | 40.6827 | 1243.1998
2016-03-21 | 31.2815 | 25.8645 | 22.7759 | 21.1563 | 21.1184 | 23.6252 | 30.1027 | 36.4215 | 40.6827 | 47.4841 | 54.8631 | 61.0176 | 66.1346 | 71.4278 | 76.6363 | 80.9986 | 82.7324 | 81.0303 | 75.1004 | 70.8527 | 71.1995 | 63.1293 | 54.8892 | 45.4249 | 1255.9495
2016-03-22 | 36.7129 | 31.3802 | 27.9621 | 26.0081 | 25.2405 | 26.0561 | 28.6438 | 32.1888 | 38.6322 | 49.7214 | 58.8696 | 64.001 | 68.6534 | 72.2848 | 74.8255 | 77.6275 | 81.2951 | 81.2209 | 76.5643 | 71.1003 | 70.4772 | 62.2636 | 53.0497 | 42.9094 | 1277.6885
2016-03-23 | 34.3586 | 28.5055 | 25.2405 | 23.42 | 22.5744 | 22.9333 | 24.595 | 27.264 | 33.6252 | 44.2364 | 54.5761 | 63.0546 | 71.6565 | 79.5346 | 85.1016 | 89.8846 | 91.9922 | 91.7556 | 87.5922 | 82.6469 | 83.4396 | 73.0766 | 61.8746 | 49.1428 | 1352.0811
2016-03-24 | 39.0498 | 32.5232 | 28.4867 | 26.8787 | 26.6718 | 29.4038 | 35.7295 | 41.7165 | 46.1967 | 52.8957 | 58.4644 | 62.4678 | 64.0386 | 63.86 | 62.1987 | 61.1186 | 61.229 | 61.8931 | 61.7822 | 62.4493 | 61.4684 | 54.0131 | 45.9972 | 36.5067 | 1177.0392
2016-03-25 | 29.3273 | 24.5192 | 21.7005 | 20.7098 | 20.9944 | 23.6653 | 30.4585 | 36.4428 | 40.2937 | 46.3087 | 50.763 | 55.4043 | 59.1676 | 61.8469 | 64.3777 | 66.4217 | 68.2061 | 68.3518 | 65.6384 | 62.4493 | 63.616 | 55.3256 | 45.0296 | 34.4206 | 1115.4387
2016-03-26 | 26.2124 | 21.9586 | 19.7267 | 18.982 | 19.5652 | 22.7703 | 30.6275 | 38.1877 | 42.9094 | 45.417 | 47.4517 | 47.4679 | 46.4929 | 45.3141 | 44.5575 | 44.1348 | 44.8956 | 45.4249 | 45.1559 | 47.7436 | 51.6885 | 46.7095 | 39.3663 | 32.0289 | 914.7889
2016-03-27 | 26.0201 | 22.7535 | 21.1509 | 20.7848 | 21.5038 | 24.7995 | 32.5232 | 38.5956 | 41.7924 | 46.4929 | 48.8877 | 50.0868 | 50.6458 | 51.107 | 51.0482 | 50.939 | 51.1238 | 50.9978 | 50.3617 | 52.6566 | 54.8196 | 49.5144 | 42.2573 | 34.2002 | 985.0625
2016-03-28 | 27.615 | 23.551 | 21.5528 | 20.523 | 20.9298 | 23.7282 | 30.2771 | 36.2868 | 40.908 | 47.6057 | 54.7848 | 59.249 | 62.4214 | 64.3117 | 65.8672 | 66.844 | 66.6711 | 64.6138 | 61.6436 | 61.6713 | 62.896 | 57.4709 | 50.8468 | 42.6249 | 1134.8938
2016-03-29 | 35.351 | 30.6991 | 27.8441 | 26.4174 | 26.1222 | 27.1169 | 29.8324 | 34.008 | 40.7277 | 50.83 | 60.3399 | 67.3254 | 70.4969 | 72.2149 | 71.8557 | 70.1223 | 67.8764 | 65.5622 | 62.0134 | 61.0176 | 58.5723 | 51.3763 | 45.0375 | 37.4575 | 1190.2171
2016-03-30 | 30.517 | 26.0201 | 23.0742 | 21.6786 | 21.1779 | 21.7005 | 23.8486 | 26.6597 | 32.2088 | 40.1744 | 46.1808 | 49.3491 | 50.8216 | 51.9424 | 53.0155 | 53.9267 | 54.8544 | 54.6456 | 52.452 | 50.9307 | 53.7887 | 47.3303 | 39.3147 | 30.452 | 956.0642
2016-03-31 | 23.8371 | 20.6243 | 18.6759 | 18.0662 | 18.7725 | 23.0009 | 31.6442 | 37.8253 | 40.033 | 43.1948 | 46.5811 | 49.3738 | 51.4184 | 53.9008 | 56.133 | 58.0248 | 58.9237 | 57.9531 | 56.8398 | 58.213 | 60.7607 | 53.1182 | 43.8696 | 33.7412 | 1014.5256
2016-04-01 | 26.1703 | 22.1297 | 20.1994 | 19.4354 | 19.9571 | 23.5396 | 33.1091 | 39.7138 | 42.2191 | 45.7424 | 49.2913 | 52.452 | 55.0548 | 58.5093 | 62.8028 | 67.7989 | 72.5049 | 74.2268 | 71.6167 | 67.0845 | 68.1381 | 59.4846 | 47.7436 | 36.3718 | 1135.296
2016-04-02 | 27.9621 | 23.3177 | 20.9674 | 19.8051 | 20.1044 | 23.711 | 32.4562 | 37.9339 | 40.6078 | 45.8379 | 50.4703 | 54.8457 | 57.9263 | 61.8284 | 67.9829 | 73.7313 | 78.1982 | 80.1017 | 76.5335 | 71.7959 | 72.7554 | 63.7661 | 51.4522 | 39.5214 | 1193.6125
2016-04-03 | 30.3678 | 25.1933 | 22.4739 | 21.3949 | 21.6293 | 25.3943 | 33.6047 | 39.0277 | 42.8786 | 49.0028 | 55.1334 | 60.4678 | 65.448 | 70.3785 | 77.4101 | 82.2092 | 85.6665 | 84.2793 | 80.4599 | 75.0291 | 77.8452 | 68.2158 | 55.2382 | 42.6326 | 1291.381
2016-04-04 | 32.893 | 27.467 | 24.3507 | 22.8882 | 22.7254 | 26.0441 | 35.0094 | 40.2639 | 44.5575 | 51.7731 | 59.1767 | 65.6003 | 70.7439 | 76.2047 | 81.6347 | 86.5064 | 90.5322 | 90.1523 | 85.2535 | 77.0485 | 75.3553 | 67.0845 | 56.9196 | 46.0451 | 1356.2298
2016-04-05 | 36.6062 | 30.504 | 26.8299 | 24.665 | 23.8142 | 24.1134 | 26.6415 | 29.9996 | 38.7638 | 50.0951 | 59.7296 | 68.012 | 75.1309 | 82.7003 | 88.0991 | 92.184 | 93.7482 | 92.7266 | 85.9823 | 77.4412 | 76.5232 | 67.8183 | 58.0337 | 47.6543 | 1377.8164
2016-04-06 | 37.9556 | 31.5121 | 27.2333 | 24.817 | 23.8429 | 23.9866 | 25.6735 | 28.1364 | 37.0843 | 49.0275 | 59.6751 | 67.9442 | 75.8869 | 83.1714 | 90.1411 | 94.7297 | 96.9972 | 96.8352 | 91.3843 | 84.247 | 84.4953 | 73.8929 | 61.6436 | 47.8737 | 1418.1868
2016-04-07 | 38.3841 | 32.4026 | 29.3273 | 27.8875 | 28.28 | 32.3758 | 41.7545 | 47.5975 | 53.1011 | 64.0292 | 75.7947 | 86.769 | 96.3499 | 105.2472 | 112.5082 | 118.1384 | 121.6525 | 120.2433 | 113.3953 | 107.5512 | 105.8269 | 92.263 | 76.7187 | 62.0504 | 1789.6484
2016-04-08 | 50.8133 | 43.0867 | 37.8036 | 35.1695 | 35.2114 | 39.0277 | 49.5806 | 55.6759 | 60.9258 | 68.7119 | 78.3126 | 86.7252 | 91.8457 | 94.5696 | 94.0216 | 91.1485 | 92.6926 | 86.5829 | 75.4267 | 70.2898 | 70.9715 | 61.736 | 49.8873 | 38.5956 | 1558.8119
2016-04-09 | 30.8425 | 26.1342 | 23.5796 | 22.3404 | 22.2571 | 25.4239 | 33.8095 | 38.1659 | 40.488 | 45.3616 | 49.3325 | 51.5112 | 52.8273 | 53.9353 | 55.7549 | 58.0158 | 60.2121 | 61.6344 | 60.1027 | 57.971 | 61.2382 | 54.1168 | 43.551 | 33.6115 | 1062.2175
2016-04-10 | 26.2967 | 22.4015 | 20.2788 | 19.5184 | 19.8836 | 23.295 | 31.9159 | 37.0056 | 39.5435 | 43.9164 | 48.1425 | 51.3173 | 53.5217 | 56.1066 | 58.9689 | 62.1523 | 64.3966 | 64.34 | 62.1338 | 60.605 | 63.8318 | 56.0713 | 46.0291 | 35.5891 | 1067.2615
2016-04-11 | 28.018 | 23.4086 | 21.1671 | 20.247 | 20.5496 | 23.6767 | 32.0556 | 37.3065 | 41.1565 | 47.7843 | 54.1514 | 58.7073 | 61.9579 | 65.2769 | 68.3712 | 69.5231 | 69.8862 | 68.1187 | 64.907 | 62.4864 | 64.161 | 58.3745 | 50.7714 | 41.8457 | 1153.9087
2016-04-12 | 33.8916 | 28.7697 | 25.3824 | 23.5339 | 22.7759 | 23.3574 | 26.0861 | 29.6849 | 38.4497 | 49.2913 | 58.4284 | 65.9626 | 71.2788 | 76.1739 | 79.1785 | 81.9643 | 83.0106 | 81.8472 | 75.7845 | 69.0436 | 68.9948 | 62.6073 | 53.2297 | 44.3537 | 1273.0811
2016-04-13 | 36.3718 | 30.6795 | 27.35 | 25.211 | 24.3391 | 24.6592 | 26.5021 | 29.2256 | 36.977 | 47.5327 | 56.3269 | 63.0359 | 69.1804 | 73.3885 | 75.1819 | 76.6363 | 77.0176 | 76.2971 | 72.8858 | 71.8756 | 74.9578 | 67.4219 | 57.3195 | 45.7663 | 1266.1394
2016-04-14 | 36.6845 | 31.2947 | 28.4804 | 26.9274 | 27.0679 | 30.5624 | 39.7212 | 45.4408 | 52.0187 | 62.8214 | 73.6304 | 83.633 | 92.105 | 100.773 | 107.905 | 114.1225 | 117.4367 | 116.3436 | 109.4492 | 101.0447 | 99.9016 | 87.8675 | 72.4348 | 56.7247 | 1714.3912
2016-04-15 | 44.7854 | 37.8398 | 33.8095 | 31.1567 | 30.66 | 33.9395 | 43.4114 | 48.8712 | 57.1149 | 69.6996 | 81.0938 | 92.1727 | 100.6197 | 106.8574 | 109.3632 | 111.3143 | 109.8925 | 101.4587 | 97.2637 | 91.5755 | 91.9922 | 81.4966 | 66.7383 | 52.2989 | 1725.4254
2016-04-16 | 41.6406 | 35.0511 | 31.1961 | 29.2891 | 28.896 | 31.9292 | 40.3983 | 44.9271 | 48.314 | 53.7628 | 58.5363 | 61.9208 | 65.5337 | 69.8175 | 72.9962 | 75.4165 | 76.9041 | 76.3587 | 73.8222 | 73.2274 | 76.0098 | 69.7389 | 58.5363 | 46.2447 | 1340.4675
2016-04-17 | 37.4 | 32.1088 | 29.2001 | 27.7325 | 27.9372 | 31.5583 | 40.6153 | 46.2767 | 51.545 | 59.9206 | 67.7795 | 73.0867 | 74.8967 | 76.3074 | 76.8423 | 76.0303 | 74.8052 | 72.2748 | 69.9551 | 68.5658 | 70.3095 | 65.1345 | 56.3358 | 45.9334 | 1352.5514
2016-04-18 | 37.4431 | 31.9957 | 28.6878 | 26.9457 | 26.6779 | 29.4484 | 35.547 | 41.1037 | 49.0604 | 59.9388 | 69.5623 | 76.3382 | 80.6709 | 85.5033 | 87.9006 | 87.4712 | 86.5173 | 85.3947 | 80.7343 | 75.3859 | 75.672 | 69.5035 | 61.1278 | 51.9424 | 1440.5729
2016-04-19 | 42.7786 | 37.1774 | 33.4958 | 31.1961 | 30.4326 | 31.1436 | 32.5299 | 34.6832 | 41.247 | 53.3412 | 64.3211 | 72.4348 | 79.3146 | 84.5386 | 87.4602 | 89.4615 | 89.1394 | 85.1341 | 77.5964 | 68.8289 | 67.3254 | 59.9024 | 51.6801 | 41.1942 | 1386.3572
2016-04-20 | 32.7112 | 27.0068 | 23.4314 | 21.6676 | 20.9459 | 21.3242 | 23.0968 | 25.2818 | 31.9824 | 39.7582 | 44.4242 | 48.4284 | 51.2079 | 53.2554 | 54.6543 | 55.7637 | 56.4859 | 55.7286 | 53.8404 | 52.7761 | 56.5477 | 52.3414 | 44.3851 | 34.8843 | 981.9296
2016-04-21 | 27.467 | 23.0855 | 20.9029 | 19.8784 | 20.1941 | 23.4541 | 31.1239 | 35.6803 | 39.6545 | 45.0375 | 50.3701 | 54.6196 | 59.0863 | 62.8121 | 67.1615 | 70.7043 | 73.6203 | 73.3583 | 71.1201 | 68.0702 | 70.4081 | 62.3007 | 51.0398 | 40.0404 | 1161.19
2016-04-22 | 30.9471 | 25.5188 | 23.0742 | 21.6348 | 21.6621 | 25.3292 | 33.6729 | 37.6737 | 41.9827 | 47.5813 | 53.7628 | 60.2395 | 65.3435 | 69.6408 | 74.2166 | 79.944 | 84.0205 | 84.7982 | 81.6559 | 76.9866 | 79.0739 | 70.0141 | 56.645 | 43.4734 | 1288.8916
2016-04-23 | 33.9053 | 28.4428 | 25.2464 | 23.4029 | 23.1138 | 26.2004 | 33.9737 | 29.4867 | 43.6596 | 50.2117 | 56.8842 | 62.0967 | 68.595 | 76.8217 | 86.0477 | 93.2935 | 98.695 | 100.078 | 95.8428 | 87.9888 | 87.1856 | 78.9903 | 64.9923 | 48.2813 | 1423.4361
2016-04-24 | 38.224 | 32.1288 | 26.9335 | 24.8463 | 24.9108 | 26.8421 | 34.4827 | 39.4327 | 45.2508 | 54.1947 | 63.9164 | 72.6651 | 81.1256 | 89.0173 | 95.9119 | 102.8847 | 107.0276 | 106.481 | 100.4311 | 91.3057 | 90.5658 | 80.5337 | 65.7337 | 51.5281 | 1546.374
2016-04-25 | 40.2863 | 33.0144 | 28.8139 | 26.5081 | 25.9842 | 28.9339 | 36.7699 | 41.6027 | 48.0284 | 57.5422 | 68.5268 | 78.865 | 88.4304 | 97.6931 | 106.0326 | 113.3327 | 117.4239 | 116.3056 | 107.844 | 95.9925 | 92.8172 | 82.85 | 69.6015 | 56.3358 | 1659.5352
2016-04-26 | 44.3616 | 36.2868 | 31.4329 | 28.4679 | 26.8299 | 26.9396 | 28.7761 | 32.5433 | 42.9094 | 56.0097 | 69.2978 | 81.7728 | 92.2178 | 100.5136 | 105.6577 | 110.3366 | 112.7827 | 111.3267 | 103.3144 | 91.6092 | 88.4525 | 79.4717 | 68.0508 | 56.4594 | 1625.8208
2016-04-27 | 46.1808 | 38.8077 | 33.6797 | 30.7773 | 28.9782 | 28.6689 | 29.6849 | 32.644 | 44.1504 | 59.2309 | 73.4187 | 85.9278 | 96.2691 | 105.0543 | 111.0911 | 116.369 | 118.4965 | 117.0675 | 109.7077 | 99.6081 | 98.1818 | 87.8455 | 72.7153 | 58.8876 | 1723.4428
2016-04-28 | 47.9632 | 41.1037 | 36.9984 | 34.538 | 34.331 | 38.2386 | 47.201 | 52.8871 | 60.9258 | 72.9259 | 87.6252 | 100.8793 | 111.4259 | 120.8112 | 128.8486 | 135.1833 | 136.8835 | 136.2104 | 128.7286 | 117.7809 | 114.7262 | 101.1274 | 82.9892 | 66.4888 | 2036.8211
2016-04-29 | 54.3246 | 46.4608 | 41.6558 | 38.991 | 38.5518 | 42.2115 | 51.023 | 56.8044 | 66.7383 | 80.2386 | 94.7411 | 107.8318 | 117.9468 | 126.3785 | 132.3957 | 136.746 | 135.8402 | 132.6935 | 126.5504 | 116.7751 | 113.145 | 100.384 | 82.8929 | 66.4217 | 2107.7423
2016-04-30 | 53.944 | 46.7578 | 42.3414 | 39.966 | 39.8175 | 43.4812 | 52.631 | 58.4464 | 68.1478 | 81.7622 | 96.1769 | 108.3084 | 117.7044 | 126.1407 | 131.4235 | 135.1149 | 133.195 | 122.9005 | 115.4829 | 107.7463 | 107.2223 | 96.0501 | 79.6814 | 64.2269 | 2068.6696
2016-05-01 | 52.0611 | 44.7618 | 40.1819 | 37.8253 | 37.1702 | 41.0736 | 50.5371 | 56.53 | 65.1915 | 78.6563 | 93.6117 | 105.6577 | 115.6725 | 124.535 | 130.3207 | 133.2628 | 131.7877 | 124.0894 | 112.7327 | 104.2966 | 103.5296 | 91.6205 | 76.6158 | 62.1245 | 2013.846
2016-05-02 | 50.9474 | 43.7607 | 39.418 | 36.8698 | 36.216 | 39.8621 | 48.863 | 54.9241 | 62.5329 | 74.3788 | 85.2426 | 93.8393 | 98.9989 | 105.1146 | 109.6092 | 111.9975 | 110.5095 | 106.0689 | 99.4087 | 90.6889 | 90.521 | 78.7711 | 67.7311 | 56.7335 | 1793.0076
2016-05-03 | 46.806 | 39.8769 | 35.533 | 33.0144 | 31.7634 | 32.4495 | 34.8426 | 38.7492 | 46.9912 | 58.1233 | 67.9636 | 75.08 | 78.4584 | 80.1017 | 79.1785 | 75.0189 | 65.829 | 62.4214 | 59.3577 | 58.5273 | 60.5959 | 56.8132 | 50.6876 | 43.4192 | 1311.6019
2016-05-04 | 36.5209 | 31.5055 | 28.5683 | 26.6597 | 26.0741 | 26.0861 | 26.7934 | 27.6645 | 34.4551 | 43.0096 | 50.3284 | 55.8866 | 61.8099 | 67.1134 | 71.8656 | 77.3481 | 81.7409 | 84.0098 | 82.0494 | 75.2023 | 72.946 | 64.5854 | 54.472 | 41.7696 | 1248.4646
2016-05-05 | 32.8795 | 26.6475 | 24.403 | 22.8489 | 22.8939 | 26.1763 | 33.2648 | 38.0498 | 44.0645 | 52.5798 | 62.0412 | 70.5166 | 79.0008 | 87.1746 | 95.0274 | 101.8617 | 108.0272 | 108.9087 | 103.9247 | 88.4636 | 88.8843 | 78.0216 | 59.2852 | 48.2241 | 1503.1698
2016-05-06 | 37.3568 | 31.2289 | 27.4177 | 25.27 | 24.776 | 27.7016 | 35.0859 | 40.0106 | 46.3407 | 55.913 | 66.2972 | 77.1621 | 88.066 | 96.7542 | 105.3316 | 113.0075 | 118.0234 | 117.6916 | 111.5004 | 95.7623 | 97.6351 | 86.5392 | 70.9121 | 55.0548 | 1650.8389
2016-05-07 | 43.8696 | 36.9341 | 33.1768 | 30.7903 | 30.2836 | 33.3463 | 41.2923 | 46.541 | 54.5501 | 64.9734 | 77.2964 | 88.2095 | 98.4499 | 108.2595 | 117.4876 | 122.1718 | 125.679 | 124.6925 | 117.0675 | 106.3718 | 103.8528 | 93.9532 | 77.2757 | 61.6713 | 1838.196
2016-05-08 | 49.2253 | 42.097 | 37.847 | 34.8912 | 34.214 | 37.2419 | 45.3457 | 50.4118 | 59.2129 | 70.4969 | 82.7538 | 93.4752 | 103.0159 | 112.3835 | 119.8697 | 126.6694 | 130.8716 | 129.7041 | 123.0309 | 111.3267 | 106.9911 | 95.9234 | 80.1649 | 64.9923 | 1942.1562
2016-05-09 | 50.9307 | 42.9402 | 38.7199 | 35.6382 | 34.8982 | 38.0716 | 46.2207 | 51.4437 | 59.8478 | 71.2987 | 83.2035 | 93.5207 | 102.837 | 111.4756 | 119.4968 | 125.5868 | 128.6886 | 125.6131 | 116.2675 | 103.6971 | 98.6366 | 88.7735 | 76.6878 | 64.2929 | 1908.787
2016-05-10 | 52.9812 | 45.5915 | 40.9305 | 37.7458 | 36.2585 | 36.6346 | 38.195 | 42.418 | 54.7761 | 68.9752 | 80.3123 | 89.4949 | 99.2681 | 105.8874 | 110.2748 | 113.5581 | 113.3702 | 110.9549 | 104.2005 | 92.7379 | 93.8165 | 85.6229 | 75.3859 | 63.8412 | 1793.2321
2016-05-11 | 53.2726 | 46.1089 | 41.1565 | 38.1151 | 36.6702 | 36.301 | 36.877 | 39.4327 | 48.9699 | 61.8469 | 73.0465 | 82.2626 | 90.7673 | 98.2633 | 103.9487 | 106.8209 | 107.905 | 104.9338 | 98.8586 | 90.3868 | 90.5434 | 84.9607 | 72.9862 | 59.0772 | 1703.5116
2016-05-12 | 47.4436 | 40.5329 | 36.5067 | 34.4758 | 34.3034 | 37.876 | 46.1728 | 51.4269 | 59.1767 | 71.1102 | 84.1499 | 95.3027 | 104.8857 | 112.6703 | 118.5093 | 123.7099 | 125.6658 | 124.037 | 118.6245 | 110.6702 | 108.5043 | 96.5 | 80.0702 | 64.9355 | 1927.26
2016-05-13 | 52.9128 | 45.8618 | 41.164 | 38.406 | 37.8181 | 41.3679 | 49.8375 | 55.02 | 62.6166 | 74.6731 | 86.8676 | 96.6502 | 105.9358 | 112.2714 | 117.0548 | 121.0956 | 123.2005 | 120.8629 | 114.1351 | 105.2713 | 103.9247 | 94.7068 | 79.2936 | 63.6816 | 1944.6295
2016-05-14 | 52.8102 | 45.806 | 40.8779 | 38.1369 | 37.6232 | 39.0498 | 50.5622 | 54.7413 | 63.1573 | 76.4923 | 88.8289 | 101.021 | 110.1267 | 116.0648 | 120.3335 | 120.2046 | 118.9576 | 116.2802 | 109.1543 | 100.9856 | 101.5653 | 92.0824 | 77.8659 | 62.6724 | 1935.4004
2016-05-15 | 50.8384 | 43.714 | 39.2116 | 36.8413 | 36.7557 | 40.2117 | 48.707 | 53.7369 | 60.7149 | 73.1168 | 84.8956 | 91.3618 | 93.8165 | 93.3275 | 89.4171 | 84.9607 | 83.7621 | 83.59 | 81.3163 | 77.6482 | 77.6482 | 71.9653 | 60.8065 | 49.4813 | 1607.8456
2016-05-16 | 40.1297 | 34.6832 | 31.3802 | 29.3719 | 29.0732 | 32.6171 | 40.5778 | 44.3381 | 47.2413 | 52.7078 | 57.5957 | 61.1738 | 62.8028 | 63.9258 | 66.2781 | 67.6441 | 69.1902 | 67.5764 | 63.4379 | 58.2488 | 56.1506 | 51.7308 | 44.636 | 36.3293 | 1208.8407
2016-05-17 | 29.1684 | 24.8639 | 22.091 | 20.5976 | 20.1572 | 20.6564 | 22.2737 | 25.507 | 33.0415 | 41.8761 | 49.796 | 56.2828 | 61.2474 | 65.9626 | 70.645 | 74.4396 | 76.8732 | 76.4101 | 71.9554 | 64.6138 | 62.4864 | 58.4464 | 50.2783 | 41.8761 | 1141.5459
2016-05-18 | 34.4206 | 29.2637 | 25.9243 | 23.7683 | 22.8264 | 23.0178 | 23.591 | 26.2666 | 34.4551 | 45.1875 | 54.7413 | 62.5329 | 69.3565 | 75.1207 | 80.5126 | 84.5278 | 87.4712 | 86.8018 | 81.3269 | 73.8424 | 73.0063 | 67.7021 | 56.9551 | 45.322 | 1287.941
2016-05-19 | 36.1806 | 30.465 | 27.1291 | 25.5545 | 25.6259 | 28.7508 | 35.997 | 40.6078 | 47.9469 | 57.3729 | 66.8343 | 75.3859 | 83.0213 | 90.9241 | 96.3961 | 101.8142 | 104.8014 | 104.3206 | 99.397 | 90.1523 | 86.9991 | 79.0008 | 65.6574 | 51.3426 | 1551.6778
2016-05-20 | 40.6902 | 34.0972 | 30.5494 | 28.4804 | 27.8999 | 30.6405 | 37.6159 | 43.2103 | 50.6709 | 60.5501 | 71.0309 | 80.1754 | 87.8234 | 94.421 | 99.233 | 103.171 | 105.5006 | 104.4647 | 100.2662 | 90.7337 | 87.9006 | 79.0217 | 65.3149 | 51.545 | 1605.0071
2016-05-21 | 40.8629 | 34.1727 | 30.2254 | 27.8193 | 27.1781 | 29.8903 | 37.0199 | 42.4027 | 48.9041 | 57.7385 | 67.1037 | 75.8459 | 83.5041 | 92.0599 | 100.5136 | 106.4446 | 110.1021 | 108.59 | 102.3725 | 92.3534 | 87.8896 | 80.0386 | 66.4313 | 52.1205 | 1601.5835
2016-05-22 | 40.3609 | 33.4958 | 29.0415 | 26.8665 | 26.49 | 29.3655 | 36.5138 | 41.5117 | 49.044 | 58.7524 | 69.9354 | 81.3693 | 92.5908 | 104.0086 | 112.9076 | 120.6562 | 125.6263 | 124.0894 | 117.0675 | 105.1266 | 98.5782 | 90.3198 | 73.802 | 57.8279 | 1745.3476
2016-05-23 | 45.0691 | 37.3496 | 32.4562 | 29.7298 | 28.6627 | 31.1174 | 37.5367 | 44.0255 | 53.2897 | 65.4766 | 79.2413 | 93.9304 | 107.2344 | 121.3933 | 132.1658 | 139.4399 | 141.8098 | 138.6082 | 128.902 | 112.8326 | 106.3597 | 97.4725 | 82.7431 | 68.0314 | 1954.8777
2016-05-24 | 55.2731 | 46.5089 | 40.1521 | 36.0464 | 33.9053 | 33.3327 | 33.8779 | 38.2168 | 50.939 | 66.9209 | 82.9999 | 99.1627 | 113.7712 | 124.3777 | 131.033 | 134.6371 | 134.4734 | 131.4101 | 121.1474 | 108.3941 | 103.1591 | 94.147 | 81.1786 | 68.0023 | 1963.0665
2016-05-25 | 56.6716 | 47.8656 | 41.6785 | 37.8109 | 35.54 | 34.697 | 35.0511 | 37.8109 | 47.8656 | 61.8931 | 78.7398 | 93.3502 | 107.1736 | 116.8005 | 122.6791 | 126.1011 | 127.2523 | 122.5229 | 112.8326 | 102.111 | 98.8469 | 90.8793 | 77.7311 | 65.4766 | 1879.3812
2016-05-26 | 53.8059 | 46.2207 | 40.9757 | 37.7025 | 35.9618 | 35.99 | 36.7557 | 40.4506 | 53.0925 | 70.142 | 87.2734 | 100.6197 | 112.5082 | 121.0439 | 125.9296 | 128.5019 | 128.5819 | 124.6138 | 115.079 | 104.2005 | 101.9685 | 92.6926 | 78.219 | 63.0453 | 1935.3746
2016-05-27 | 51.5787 | 43.9943 | 39.3368 | 36.6133 | 35.7225 | 39.0939 | 46.549 | 53.5733 | 63.7285 | 77.3481 | 91.598 | 105.2351 | 115.8116 | 124.2335 | 129.2493 | 131.6393 | 127.8365 | 118.1256 | 109.2894 | 100.9738 | 100.0309 | 91.5417 | 77.2964 | 61.4868 | 1971.8863
2016-05-28 | 49.987 | 42.7555 | 38.4716 | 35.8983 | 35.2882 | 38.581 | 46.3087 | 52.4265 | 61.7822 | 73.9333 | 87.4602 | 102.2536 | 113.3452 | 122.8223 | 128.1157 | 129.6372 | 129.49 | 124.3645 | 116.5085 | 108.0639 | 105.4161 | 96.0847 | 81.0727 | 65.7623 | 1985.8292
2016-05-29 | 53.2554 | 45.0612 | 40.4805 | 37.7964 | 36.8698 | 39.9215 | 47.5327 | 53.6594 | 61.6159 | 72.2748 | 84.1607 | 93.0665 | 98.6249 | 102.3488 | 99.7489 | 96.9162 | 95.1306 | 92.8965 | 90.8681 | 84.8523 | 84.2793 | 78.6772 | 67.6634 | 55.177 | 1712.8781
2016-05-30 | 44.0021 | 36.7272 | 33.387 | 31.3934 | 31.0322 | 33.9326 | 40.7802 | 46.6373 | 55.3781 | 69.2 | 82.5934 | 94.2954 | 103.9726 | 111.7364 | 116.4197 | 119.4711 | 118.6117 | 112.234 | 101.222 | 92.5568 | 90.0407 | 82.7217 | 71.9155 | 61.0268 | 1781.2878
2016-05-31 | 51.0734 | 43.218 | 38.1296 | 34.9746 | 33.7958 | 33.5911 | 34.9746 | 39.6175 | 52.3244 | 68.4004 | 84.2362 | 97.4841 | 106.4567 | 112.3711 | 113.3702 | 112.4583 | 109.1543 | 102.0873 | 94.1813 | 86.1568 | 85.1016 | 79.923 | 70.9517 | 60.1209 | 1744.1527
2016-06-01 | 51.0146 | 43.4657 | 38.837 | 35.7435 | 34.1041 | 34.0217 | 34.6555 | 37.9049 | 48.3957 | 62.7935 | 77.3791 | 89.1949 | 99.4791 | 106.8088 | 110.6579 | 109.6954 | 105.0784 | 97.3333 | 89.0506 | 83.5685 | 83.4611 | 79.7654 | 70.0436 | 58.0785 | 1680.5307
2016-06-02 | 48.1915 | 41.8685 | 38.4205 | 36.5564 | 36.7842 | 40.8779 | 48.666 | 54.2379 | 59.6479 | 66.2015 | 72.7654 | 76.6055 | 80.4493 | 83.0642 | 84.8415 | 84.7549 | 84.3441 | 82.3159 | 80.2597 | 78.0216 | 78.7293 | 74.3889 | 63.7285 | 52.129 | 1547.8501
2016-06-03 | 42.5022 | 36.5209 | 33.0415 | 31.0322 | 30.9144 | 34.3517 | 41.7848 | 46.8623 | 51.9594 | 59.5843 | 67.7118 | 74.9578 | 80.4283 | 84.4953 | 86.2223 | 86.7909 | 84.6791 | 82.4226 | 78.6251 | 75.3859 | 76.4409 | 70.9517 | 60.7974 | 49.0604 | 1467.5231
2016-06-04 | 39.4106 | 33.5162 | 30.064 | 28.3363 | 28.3113 | 31.5187 | 38.4278 | 39.514 | 49.738 | 59.957 | 69.0827 | 76.6775 | 82.0814 | 88.7513 | 93.6913 | 97.0898 | 99.7137 | 100.2427 | 96.8467 | 89.1394 | 85.4272 | 79.325 | 67.9248 | 54.5588 | 1559.3462
2016-06-05 | 43.6985 | 37.0413 | 32.8323 | 30.3548 | 29.5825 | 32.2889 | 38.3477 | 45.2508 | 55.5094 | 67.8667 | 81.709 | 94.9587 | 105.6939 | 116.0015 | 123.344 | 128.7286 | 131.0061 | 129.9988 | 123.6707 | 111.2027 | 104.4287 | 94.1014 | 78.8024 | 62.4028 | 1898.8222
2016-06-06 | 50.5204 | 42.0894 | 36.7771 | 33.5911 | 32.1555 | 34.3448 | 39.2705 | 46.3247 | 58.5993 | 73.5295 | 90.4427 | 107.2466 | 121.6007 | 132.9373 | 141.1247 | 145.771 | 147.308 | 144.4964 | 135.5799 | 121.8471 | 113.17 | 103.757 | 88.8067 | 74.4396 | 2115.73
2016-06-07 | 61.4868 | 52.1714 | 45.9334 | 42.1886 | 39.6915 | 38.8297 | 39.5509 | 44.534 | 58.4284 | 75.1106 | 93.8621 | 111.6743 | 124.0108 | 132.9238 | 138.29 | 139.7454 | 134.7462 | 127.2523 | 117.5386 | 107.9295 | 101.5534 | 93.1686 | 80.6181 | 67.8086 | 2069.0471
2016-06-08 | 56.6893 | 48.2568 | 42.5636 | 37.876 | 36.4428 | 35.8983 | 35.997 | 39.0865 | 50.4369 | 67.6248 | 85.9278 | 102.8966 | 113.4954 | 115.9761 | 113.1826 | 111.4508 | 108.1983 | 104.7653 | 98.2983 | 90.7113 | 86.5392 | 80.2281 | 67.5281 | 56.1066 | 1786.1762
2016-06-09 | 45.3062 | 38.3987 | 33.8984 | 31.6839 | 31.3802 | 34.1865 | 39.6693 | 46.1009 | 56.2123 | 69.7487 | 85.9496 | 103.8049 | 118.3429 | 130.9388 | 137.8618 | 135.7717 | 132.0848 | 122.9005 | 112.4209 | 103.422 | 98.4966 | 90.2416 | 75.8664 | 61.4131 | 1936.1006
2016-06-10 | 49.5888 | 42.0208 | 37.6448 | 34.9955 | 34.3241 | 37.1846 | 42.9248 | 50.83 | 62.8774 | 76.8423 | 90.9353 | 104.5368 | 115.5587 | 121.8341 | 121.497 | 113.2826 | 106.081 | 102.7535 | 101.8854 | 95.7393 | 93.7368 | 84.9715 | 71.1598 | 57.6582 | 1850.8632
2016-06-11 | 47.306 | 40.3534 | 35.7506 | 33.3666 | 32.8323 | 35.2951 | 41.1716 | 48.0528 | 58.7434 | 73.7111 | 88.3531 | 101.4468 | 109.9911 | 115.3819 | 109.9911 | 100.7848 | 96.2345 | 94.8327 | 92.8511 | 86.9662 | 84.2038 | 78.5834 | 66.8055 | 54.5588 | 1727.5677
2016-06-12 | 44.5105 | 37.7531 | 33.7002 | 31.2947 | 30.7642 | 33.0482 | 38.6102 | 43.7685 | 49.5723 | 57.7117 | 68.7801 | 81.6665 | 96.4538 | 110.4601 | 120.166 | 122.3407 | 116.2422 | 106.8695 | 99.9486 | 93.0211 | 89.4171 | 81.8685 | 67.9442 | 55.02 | 1710.932
2016-06-13 | 44.6046 | 37.7892 | 33.6184 | 31.0322 | 30.5559 | 32.7986 | 37.6376 | 44.6439 | 55.7812 | 68.5171 | 81.8791 | 95.6933 | 107.0154 | 112.9575 | 112.8201 | 106.3354 | 99.8546 | 93.1346 | 87.3064 | 79.1053 | 74.3078 | 69.6113 | 61.0084 | 50.9307 | 1648.9387
2016-06-14 | 42.2573 | 36.0958 | 32.0356 | 29.7106 | 28.7004 | 29.1049 | 30.5235 | 34.7247 | 45.077 | 59.005 | 73.7515 | 88.077 | 99.7489 | 109.6954 | 114.399 | 114.0346 | 108.015 | 102.111 | 93.1459 | 83.7836 | 80.3229 | 74.5512 | 65.2105 | 55.1596 | 1629.2408
2016-06-15 | 46.2687 | 40.167 | 35.5891 | 32.9469 | 32.2022 | 32.866 | 34.0766 | 38.195 | 49.7711 | 65.3244 | 80.6815 | 95.7278 | 108.6635 | 117.2457 | 122.3147 | 120.398 | 113.7461 | 105.6214 | 97.2637 | 88.8621 | 87.2295 | 83.3967 | 72.4949 | 61.1278 | 1762.1803
2016-06-16 | 50.012 | 43.218 | 39.1159 | 36.6417 | 35.8139 | 38.4643 | 43.8696 | 49.8043 | 57.9621 | 68.8581 | 84.2254 | 100.1368 | 111.6743 | 122.2757 | 129.8514 | 134.4053 | 137.1587 | 135.2106 | 125.5604 | 109.7077 | 102.5391 | 93.7596 | 78.865 | 64.2363 | 1993.3662
2016-06-17 | 52.0696 | 44.4634 | 39.138 | 36.1665 | 35.1416 | 37.3928 | 42.9017 | 49.3243 | 57.7922 | 67.5474 | 77.5654 | 87.2185 | 95.8889 | 103.757 | 106.481 | 106.4325 | 104.3446 | 102.4677 | 98.6833 | 92.5568 | 88.9841 | 84.3657 | 70.2306 | 56.8487 | 1737.7622
2016-06-18 | 45.6868 | 39.0204 | 34.9955 | 32.5433 | 32.1488 | 34.6763 | 40.5553 | 46.9831 | 56.4064 | 67.7892 | 81.1468 | 94.6153 | 102.2774 | 105.0543 | 103.2427 | 98.3916 | 93.0098 | 88.5189 | 84.2038 | 79.986 | 78.3751 | 74.3078 | 63.3443 | 51.6632 | 1628.942
2016-06-19 | 41.8457 | 35.99 | 32.5902 | 30.6535 | 30.1608 | 32.6574 | 38.2095 | 44.3459 | 54.2726 | 66.7863 | 81.2845 | 93.5889 | 104.2485 | 112.2714 | 112.9326 | 105.9479 | 99.5846 | 93.248 | 87.043 | 81.3269 | 78.3647 | 72.2249 | 62.0319 | 50.3617 | 1641.9714
2016-06-20 | 40.7727 | 34.7663 | 31.0977 | 29.1493 | 28.6627 | 30.7773 | 35.7506 | 42.1046 | 52.3329 | 66.1346 | 80.4072 | 94.4324 | 105.7785 | 112.4583 | 110.5095 | 100.962 | 95.1077 | 90.0072 | 85.7753 | 80.3545 | 77.2137 | 73.3985 | 64.5004 | 54.16 | 1616.614
2016-06-21 | 44.4477 | 38.195 | 34.008 | 31.6574 | 30.647 | 31.0453 | 32.0422 | 37.1129 | 50.5956 | 67.4219 | 82.6041 | 97.6815 | 110.3242 | 117.9596 | 115.6472 | 107.5268 | 100.7258 | 95.3256 | 88.9508 | 82.4866 | 79.3355 | 75.6515 | 66.9016 | 56.1418 | 1674.4359
2016-06-22 | 46.3967 | 40.473 | 35.9759 | 33.2852 | 31.7965 | 31.7104 | 32.1022 | 37.1272 | 49.9288 | 67.1422 | 83.225 | 96.4076 | 109.4 | 119.3426 | 125.8768 | 126.8945 | 122.614 | 113.1951 | 101.7431 | 92.2404 | 88.4968 | 83.0642 | 72.135 | 58.9779 | 1799.551
2016-06-23 | 47.8412 | 41.6178 | 37.4503 | 35.0372 | 34.5241 | 37.2778 | 42.9094 | 50.245 | 61.8469 | 75.9688 | 92.4212 | 108.1739 | 122.8745 | 135.1969 | 142.4265 | 144.0869 | 141.1945 | 134.992 | 126.1539 | 114.3236 | 106.7845 | 97.0898 | 82.4973 | 66.2876 | 2079.2216
2016-06-24 | 53.8663 | 45.822 | 40.8478 | 37.7531 | 36.7486 | 39.1674 | 44.7697 | 52.095 | 64.5193 | 79.3774 | 97.1825 | 113.5706 | 128.5286 | 142.3563 | 150.7956 | 155.4947 | 156.3461 | 150.5503 | 143.0585 | 130.549 | 123.9061 | 112.7702 | 95.5783 | 77.897 | 2273.5505
2016-06-25 | 63.8318 | 54.212 | 47.6219 | 43.714 | 42.2803 | 44.5497 | 50.17 | 57.7475 | 70.7637 | 87.9226 | 107.4537 | 123.3832 | 138.4421 | 150.7235 | 158.544 | 159.3295 | 152.7944 | 144.454 | 134.2418 | 121.3674 | 113.7335 | 104.1525 | 89.8846 | 73.2576 | 2334.5753
2016-06-26 | 60.0845 | 50.604 | 44.6282 | 40.9757 | 39.5953 | 41.4966 | 47.1202 | 54.3939 | 67.4412 | 85.1667 | 104.0206 | 119.8697 | 132.707 | 141.4321 | 150.2331 | 153.158 | 153.2307 | 148.638 | 140.469 | 127.584 | 118.7013 | 108.2595 | 92.1501 | 74.9171 | 2296.8765
2016-06-27 | 61.0543 | 52.2394 | 46.3007 | 42.7171 | 41.5648 | 43.9865 | 48.7398 | 55.9218 | 68.9362 | 85.6338 | 102.1348 | 117.7937 | 128.0758 | 137.0348 | 144.9348 | 145.7994 | 142.7494 | 135.3884 | 122.5229 | 109.6338 | 102.7416 | 93.407 | 82.156 | 68.6242 | 2180.0909
2016-06-28 | 55.711 | 47.1686 | 41.7848 | 37.9339 | 35.6803 | 33.8984 | 38.8737 | 42.0208 | 55.9482 | 74.2774 | 90.4651 | 108.3084 | 123.5792 | 133.4801 | 139.6899 | 144.3975 | 143.833 | 140.5387 | 130.9657 | 118.1768 | 111.2027 | 102.8966 | 89.762 | 75.0291 | 2115.6217
2016-06-29 | 62.44 | 53.5905 | 47.4274 | 43.2798 | 40.9681 | 40.085 | 39.8027 | 43.4037 | 57.8905 | 77.7104 | 97.9955 | 117.6916 | 133.8062 | 141.9219 | 142.2862 | 136.856 | 132.6528 | 126.0219 | 113.2951 | 102.016 | 95.5208 | 89.0728 | 77.2137 | 63.6535 | 2076.6024
2016-06-30 | 52.759 | 45.2112 | 40.4207 | 37.7097 | 37.3784 | 40.3161 | 45.9653 | 52.112 | 63.1013 | 78.8754 | 94.9014 | 109.7816 | 122.3667 | 133.548 | 140.5666 | 144.0586 | 140.9571 | 129.383 | 118.4453 | 108.7125 | 103.4817 | 95.8198 | 83.5041 | 68.7509 | 2088.1265
2016-07-01 | 56.5477 | 48.6496 | 44.0489 | 41.3679 | 40.7427 | 43.7996 | 50.2367 | 55.8251 | 63.2695 | 74.3788 | 86.5282 | 99.5494 | 108.0883 | 112.0099 | 115.8875 | 117.5641 | 120.5013 | 118.6757 | 113.8339 | 109.4123 | 107.1006 | 98.042 | 83.4826 | 68.7996 | 1978.342
2016-07-02 | 55.7988 | 48.3058 | 43.6208 | 41.164 | 40.3908 | 42.8786 | 48.7316 | 55.0723 | 66.2972 | 81.8153 | 99.9956 | 113.508 | 121.9639 | 123.0178 | 118.049 | 113.4203 | 112.1967 | 110.4354 | 107.0397 | 100.9501 | 98.7534 | 93.9076 | 82.4332 | 67.7699 | 1987.516
2016-07-03 | 57.186 | 49.3491 | 44.9823 | 42.158 | 41.7089 | 44.1738 | 50.0369 | 56.6008 | 68.0702 | 85.1667 | 104.97 | 121.5618 | 133.8606 | 142.8056 | 150.2908 | 154.4848 | 152.7944 | 141.8798 | 130.3878 | 119.4968 | 112.9825 | 105.6697 | 92.6021 | 77.4826 | 2280.702
2016-07-04 | 64.8597 | 55.3256 | 48.7316 | 44.4948 | 42.3185 | 42.265 | 43.1562 | 46.053 | 58.5813 | 78.8546 | 99.655 | 117.2838 | 128.4753 | 134.0648 | 135.9909 | 135.4978 | 122.0418 | 106.4446 | 95.8198 | 86.7142 | 81.1574 | 74.3484 | 70.6846 | 63.2601 | 1976.0787
2016-07-05 | 53.6939 | 46.053 | 41.2546 | 38.2168 | 36.7842 | 36.8413 | 37.7314 | 40.3385 | 50.1534 | 62.4121 | 78.0632 | 89.9849 | 100.3722 | 110.7073 | 112.0224 | 104.3566 | 97.4957 | 92.8511 | 88.3641 | 83.7621 | 80.914 | 76.5849 | 68.5658 | 58.5183 | 1686.0417
2016-07-06 | 49.8126 | 43.218 | 38.903 | 36.0676 | 35.1835 | 35.3301 | 35.9477 | 38.7492 | 49.8873 | 62.3935 | 74.6832 | 79.7234 | 84.9498 | 89.7954 | 94.3068 | 95.0274 | 93.7141 | 90.2528 | 84.8198 | 76.729 | 75.2023 | 72.0352 | 63.3163 | 52.7504 | 1552.7984
2016-07-07 | 44.6125 | 39.0865 | 35.8702 | 34.3172 | 34.2415 | 37.1989 | 42.7478 | 49.1181 | 59.2219 | 70.4969 | 82.7003 | 91.1485 | 95.1879 | 98.3566 | 99.4791 | 102.7416 | 102.7416 | 102.2061 | 99.8429 | 96.8005 | 94.4896 | 89.1061 | 77.1311 | 63.7755 | 1742.6187
2016-07-08 | 52.4605 | 44.8641 | 40.0404 | 37.364 | 36.6204 | 38.9323 | 44.534 | 51.3847 | 62.1245 | 78.1151 | 95.2568 | 111.7364 | 125.4156 | 131.9227 | 130.643 | 123.083 | 115.445 | 108.921 | 102.2774 | 93.7596 | 86.9443 | 79.608 | 68.4198 | 56.707 | 1916.5797
2016-07-09 | 46.6533 | 40.5179 | 36.7486 | 33.2242 | 33.5162 | 36.8555 | 42.6864 | 48.9288 | 60.0298 | 76.1842 | 92.0373 | 108.7003 | 120.0629 | 123.4093 | 113.2826 | 105.4282 | 101.7312 | 96.3961 | 90.1076 | 86.5173 | 83.4074 | 86.1132 | 67.5571 | 56.1418 | 1786.2371
2016-07-10 | 45.6868 | 39.3442 | 35.7295 | 33.748 | 33.17 | 35.6803 | 41.4511 | 48.314 | 59.3215 | 73.8727 | 86.0586 | 94.7755 | 103.0755 | 109.1297 | 108.8842 | 104.8616 | 98.8936 | 92.5681 | 87.4493 | 82.2306 | 80.8083 | 76.4204 | 66.7575 | 55.5707 | 1693.8015
2016-07-11 | 45.5042 | 39.3073 | 35.5751 | 33.6797 | 33.2377 | 35.533 | 40.4955 | 47.4679 | 60.1118 | 75.4574 | 91.6993 | 107.3927 | 119.8826 | 130.3476 | 136.6498 | 138.1933 | 136.856 | 132.1523 | 124.6269 | 113.4954 | 107.1371 | 100.3722 | 87.9557 | 74.3281 | 2047.4584
2016-07-12 | 62.3378 | 53.9612 | 47.9632 | 44.3381 | 41.5951 | 41.6178 | 42.3261 | 45.822 | 57.7207 | 76.0098 | 92.3534 | 108.1372 | 121.5618 | 129.1958 | 131.464 | 131.0061 | 128.9421 | 122.1718 | 113.02 | 100.9738 | 95.1077 | 87.2295 | 76.482 | 65.0207 | 2016.3577
2016-07-13 | 56.3093 | 49.879 | 45.4487 | 42.1123 | 39.9735 | 39.1453 | 39.3147 | 43.0867 | 56.3534 | 73.0465 | 88.5189 | 103.4698 | 114.9529 | 120.9146 | 125.89 | 129.4097 | 128.7553 | 123.9715 | 116.3056 | 106.7237 | 101.6245 | 96.2576 | 84.2362 | 70.8428 | 1996.5424
2016-07-14 | 59.403 | 51.469 | 45.8618 | 42.9017 | 42.1275 | 44.4477 | 50.0702 | 56.5654 | 69.0924 | 85.286 | 102.7059 | 118.2151 | 129.9988 | 133.2493 | 130.8043 | 129.5034 | 128.9688 | 128.7152 | 125.3892 | 114.6506 | 105.3558 | 95.6703 | 81.7197 | 67.2675 | 2139.4386
2016-07-15 | 55.4919 | 47.8737 | 42.971 | 39.9512 | 39.2557 | 41.6254 | 47.5732 | 53.6766 | 63.5972 | 78.6772 | 92.5003 | 105.0182 | 112.9201 | 112.9825 | 109.5723 | 103.5057 | 99.3853 | 96.5346 | 95.3141 | 90.7673 | 89.2504 | 84.4953 | 73.157 | 60.6783 | 1836.7745
2016-07-16 | 50.5873 | 43.365 | 38.7126 | 36.4996 | 36.1877 | 39.2705 | 46.6533 | 53.1697 | 65.258 | 80.481 | 94.1356 | 104.9941 | 111.9602 | 106.6994 | 100.7494 | 95.9695 | 91.7781 | 87.9226 | 85.4164 | 81.2421 | 81.8153 | 78.8232 | 69.1706 | 57.81 | 1738.6711
2016-07-17 | 48.1425 | 42.0589 | 37.5727 | 35.449 | 35.2463 | 38.0571 | 44.1817 | 49.7297 | 62.7655 | 76.7187 | 91.508 | 105.1025 | 105.4402 | 103.1949 | 100.4311 | 104.9459 | 111.1531 | 111.8856 | 110.4848 | 104.7774 | 100.2191 | 93.7596 | 79.629 | 66.4026 | 1858.8556
2016-07-18 | 53.7628 | 46.1009 | 41.315 | 38.2968 | 37.1774 | 39.3737 | 44.4086 | 50.763 | 63.4473 | 80.6815 | 98.1235 | 115.1042 | 129.8648 | 141.2504 | 148.423 | 152.4169 | 152.4314 | 144.8499 | 131.0465 | 117.1947 | 108.8229 | 100.1132 | 86.7799 | 73.4388 | 2195.1871
2016-07-19 | 61.0727 | 52.0866 | 46.1408 | 42.5176 | 40.2713 | 40.1297 | 40.8929 | 44.7461 | 59.3486 | 78.1671 | 96.4191 | 113.2951 | 126.815 | 136.966 | 141.2783 | 142.7634 | 146.2967 | 143.5793 | 132.8425 | 121.6655 | 115.243 | 105.5731 | 91.7443 | 78.3439 | 2198.1986
2016-07-20 | 65.8195 | 56.831 | 50.295 | 45.9255 | 43.4657 | 42.4333 | 42.5482 | 45.0138 | 58.4734 | 78.0112 | 96.1423 | 115.3819 | 130.8581 | 141.5859 | 146.866 | 143.8189 | 141.1107 | 136.8422 | 127.7169 | 116.7751 | 112.3088 | 104.5729 | 91.6655 | 76.2252 | 2210.6869
2016-07-21 | 63.2975 | 54.6891 | 48.8055 | 45.3299 | 44.4869 | 46.8623 | 52.9556 | 58.8786 | 69.9059 | 85.8189 | 103.8768 | 120.0629 | 130.764 | 132.6393 | 126.4314 | 120.2691 | 113.8213 | 108.1494 | 102.4796 | 96.3384 | 95.1535 | 86.8128 | 75.2635 | 62.7655 | 2045.8576
2016-07-22 | 51.6041 | 44.4556 | 40.5853 | 37.9194 | 37.5295 | 40.8629 | 46.7417 | 52.9984 | 64.576 | 78.9485 | 93.0438 | 104.3206 | 111.3887 | 115.4324 | 121.0956 | 124.4563 | 121.899 | 114.4241 | 108.0028 | 101.0328 | 99.0925 | 91.902 | 79.2308 | 66.4026 | 1947.9453
2016-07-23 | 55.7461 | 48.3875 | 43.5587 | 40.6302 | 39.8992 | 42.3261 | 49.184 | 54.8979 | 66.4984 | 79.5031 | 91.8457 | 102.2893 | 110.6084 | 118.7654 | 126.9209 | 131.1945 | 132.8154 | 131.4505 | 130.4013 | 121.1086 | 115.5966 | 107.478 | 91.6655 | 76.5746 | 2109.3461
2016-07-24 | 63.4566 | 54.0822 | 48.1262 | 44.6046 | 43.3882 | 45.6073 | 50.7714 | 56.9995 | 69.3663 | 86.6595 | 103.769 | 88.8621 | 130.3207 | 136.9935 | 140.9851 | 144.8357 | 150.2043 | 147.094 | 142.3002 | 130.9254 | 120.9275 | 111.4632 | 93.7938 | 77.2241 | 2282.7605
2016-07-25 | 64.4532 | 54.6717 | 48.707 | 44.809 | 42.9865 | 45.1717 | 50.295 | 56.8221 | 71.1598 | 88.8843 | 106.2991 | 123.331 | 134.1328 | 140.1627 | 145.7852 | 151.1423 | 151.8803 | 146.4674 | 135.5252 | 122.6009 | 116.0015 | 106.1658 | 92.5342 | 78.6459 | 2318.6346
2016-07-26 | 67.2097 | 58.2758 | 52.7419 | 48.2486 | 45.5915 | 45.1559 | 46.2847 | 49.3738 | 61.7175 | 80.2175 | 98.9989 | 112.4209 | 118.3302 | 121.6396 | 120.6562 | 117.0293 | 117.0675 | 114.399 | 108.5777 | 100.714 | 98.695 | 90.8905 | 79.346 | 69.1804 | 2022.7621
2016-07-27 | 58.8876 | 51.3089 | 46.3487 | 42.8632 | 41.0585 | 40.5478 | 40.9606 | 43.6053 | 58.2758 | 77.4205 | 95.2223 | 112.4458 | 127.0667 | 138.8436 | 146.6666 | 151.9818 | 153.7842 | 151.7355 | 142.7072 | 129.8246 | 124.0894 | 114.7639 | 99.1978 | 83.59 | 2273.1965
2016-07-28 | 69.3663 | 60.4587 | 54.1341 | 50.3451 | 49.2995 | 51.9763 | 57.819 | 63.86 | 77.2654 | 96.0616 | 114.0974 | 132.1388 | 145.0056 | 157.3473 | 168.8001 | 175.3384 | 177.7282 | 175.0739 | 168.4185 | 155.6266 | 148.008 | 135.9635 | 115.0916 | 94.8556 | 2694.0795
2016-07-29 | 78.5313 | 67.8957 | 60.7057 | 56.4859 | 54.663 | 56.6981 | 62.245 | 67.7699 | 81.5072 | 98.8235 | 116.6862 | 133.6975 | 145.4448 | 153.6676 | 157.8047 | 154.5725 | 151.4315 | 140.9571 | 128.6086 | 118.0873 | 113.7837 | 105.0905 | 89.9961 | 76.3895 | 2471.5429
2016-07-30 | 63.8318 | 56.0537 | 50.4285 | 47.2898 | 46.069 | 48.5758 | 55.1945 | 60.6783 | 73.2878 | 88.6295 | 102.2774 | 119.2014 | 134.378 | 148.3085 | 155.8614 | 156.4784 | 147.5221 | 133.29 | 123.4746 | 114.1728 | 108.5043 | 100.2662 | 85.3621 | 71.4775 | 2290.6133
2016-07-31 | 59.1405 | 51.065 | 45.8856 | 42.9325 | 41.9294 | 44.1348 | 50.2617 | 55.212 | 65.8195 | 82.6041 | 102.0635 | 120.9404 | 134.0375 | 143.0023 | 146.1403 | 142.6089 | 131.8282 | 122.0548 | 114.0723 | 105.404 | 102.8489 | 95.6473 | 82.8072 | 69.1902 | 2151.631
2016-08-01 | 58.4284 | 50.9055 | 45.1954 | 42.7478 | 41.4284 | 43.8618 | 49.0769 | 55.9482 | 68.6826 | 86.5829 | 104.0566 | 120.4625 | 133.5208 | 143.0585 | 151.2146 | 155.6706 | 155.0259 | 146.3678 | 133.9695 | 122.3407 | 117.6789 | 108.3574 | 93.0211 | 79.0217 | 2306.6247
2016-08-02 | 66.6999 | 57.3106 | 51.1406 | 47.0557 | 44.8484 | 44.6517 | 45.9414 | 48.8548 | 62.3193 | 80.84 | 98.8703 | 113.721 | 125.8372 | 132.9238 | 139.4121 | 139.1208 | 136.8835 | 131.208 | 121.3415 | 111.6618 | 108.0394 | 100.9383 | 88.077 | 75.9176 | 2173.6146
2016-08-03 | 64.4721 | 56.2299 | 50.4285 | 46.7337 | 44.5889 | 44.3302 | 45.2745 | 46.7015 | 56.9995 | 71.3881 | 83.1607 | 96.6155 | 103.398 | 105.4523 | 106.2021 | 108.0639 | 109.6215 | 107.6853 | 102.6463 | 97.821 | 93.6458 | 86.0368 | 73.802 | 61.321 | 1862.6191
2016-08-04 | 50.5705 | 43.9086 | 39.825 | 37.5007 | 37.3425 | 40.473 | 46.8543 | 51.8831 | 62.2358 | 76.482 | 91.8457 | 105.9963 | 110.0281 | 108.1861 | 101.8024 | 95.4979 | 89.4282 | 82.8929 | 78.8546 | 75.8562 | 77.8659 | 73.0264 | 64.0951 | 54.6543 | 1697.1052
2016-08-05 | 46.1089 | 40.6752 | 37.6448 | 36.0252 | 35.9406 | 38.6687 | 45.4012 | 51.2584 | 62.6352 | 78.4271 | 93.1119 | 107.8806 | 120.282 | 127.996 | 126.4182 | 125.2182 | 126.4049 | 127.5044 | 123.2266 | 113.9468 | 109.8308 | 99.6081 | 84.0421 | 69.8076 | 2028.0634
2016-08-06 | 56.8221 | 49.011 | 43.7374 | 40.5628 | 39.9735 | 42.2497 | 48.216 | 54.3072 | 67.2675 | 84.7765 | 102.0991 | 121.925 | 136.4574 | 149.1687 | 157.2883 | 157.9524 | 150.9689 | 143.5089 | 133.6567 | 124.168 | 119.9598 | 110.0651 | 92.105 | 76.8835 | 2303.1306
2016-08-07 | 63.148 | 54.3939 | 48.9041 | 45.417 | 44.166 | 46.549 | 52.7419 | 58.4464 | 72.6752 | 91.3169 | 109.6338 | 128.3953 | 143.8753 | 154.9674 | 157.303 | 155.9348 | 153.6967 | 149.83 | 139.7593 | 128.6086 | 118.7654 | 105.6939 | 87.1856 | 71.6864 | 2383.0937
2016-08-08 | 58.9959 | 50.1867 | 45.2271 | 42.3491 | 41.0886 | 45.7265 | 49.5557 | 54.9764 | 64.2929 | 79.2518 | 94.3411 | 111.811 | 128.6352 | 143.3258 | 151.1568 | 151.6341 | 149.0395 | 138.1242 | 125.2182 | 113.7085 | 109.6954 | 100.5725 | 87.3284 | 75.8255 | 2212.0666
2016-08-09 | 62.4957 | 54.0217 | 48.0691 | 44.4164 | 42.6787 | 42.6787 | 43.8385 | 47.4436 | 62.2636 | 82.2412 | 101.1392 | 119.0217 | 133.1814 | 142.9601 | 149.8875 | 154.0467 | 153.4636 | 144.6801 | 130.7237 | 117.7809 | 113.02 | 103.1352 | 89.5172 | 77.7104 | 2260.4151
2016-08-10 | 65.7051 | 57.2216 | 50.7128 | 46.7337 | 44.4007 | 43.582 | 43.9553 | 46.1009 | 60.0389 | 79.7129 | 98.8352 | 119.1372 | 134.2281 | 146.0835 | 151.9238 | 153.0852 | 152.0542 | 148.008 | 137.3515 | 124.1942 | 118.3174 | 106.3112 | 89.8734 | 74.3686 | 2291.9354
2016-08-11 | 61.2198 | 52.4265 | 46.7578 | 43.4579 | 42.418 | 45.2508 | 51.3931 | 56.2035 | 68.1769 | 86.7252 | 105.7906 | 126.5239 | 143.354 | 154.514 | 157.421 | 156.6108 | 157.0377 | 154.2803 | 146.1119 | 133.9151 | 129.1424 | 114.5122 | 97.6931 | 79.8284 | 2410.7648
2016-08-12 | 65.667 | 56.7335 | 50.0618 | 46.1728 | 44.9271 | 47.3545 | 53.625 | 58.9779 | 71.398 | 89.2171 | 106.8331 | 124.0632 | 137.2 | 147.7507 | 151.692 | 151.3881 | 153.7551 | 152.1702 | 146.6809 | 135.0056 | 127.996 | 114.4493 | 96.7658 | 80.6815 | 2410.5661
2016-08-13 | 66.2494 | 57.8905 | 51.7731 | 46.967 | 45.7504 | 48.3303 | 54.9328 | 60.5135 | 74.247 | 92.67 | 111.0787 | 131.7607 | 147.6506 | 159.1367 | 165.0788 | 168.1897 | 168.1745 | 160.9213 | 150.0315 | 136.4025 | 130.8985 | 118.4709 | 100.2191 | 83.5793 | 2530.9167
2016-08-14 | 69.9059 | 61.1922 | 55.3868 | 51.7562 | 50.17 | 52.2054 | 58.7975 | 64.0386 | 77.555 | 96.8352 | 116.1155 | 132.3822 | 147.1368 | 155.2309 | 156.3755 | 146.0124 | 131.2484 | 120.4238 | 111.6991 | 104.5248 | 103.0875 | 93.7141 | 81.6347 | 67.5668 | 2304.9951
2016-08-15 | 56.4594 | 49.4647 | 44.3459 | 42.0894 | 41.5041 | 44.5183 | 51.545 | 57.81 | 71.0507 | 86.8566 | 103.3861 | 116.1281 | 126.2332 | 124.0763 | 106.6387 | 96.1538 | 89.4282 | 84.9173 | 79.4298 | 74.3382 | 75.0189 | 69.8273 | 62.8214 | 54.3766 | 1808.418
2016-08-16 | 46.2687 | 41.2395 | 37.9773 | 35.8702 | 34.8149 | 35.1974 | 37.1559 | 40.4655 | 53.0754 | 73.4691 | 92.7379 | 108.125 | 123.4485 | 126.2596 | 134.2963 | 128.1956 | 117.4749 | 106.7966 | 97.1014 | 89.1838 | 87.0539 | 80.9774 | 72.3648 | 61.4131 | 1860.9627
2016-08-17 | 52.2054 | 45.8458 | 41.3528 | 38.3404 | 37.1058 | 37.1631 | 38.5007 | 41.1188 | 53.0925 | 72.4548 | 92.3986 | 110.0281 | 125.6527 | 139.426 | 141.7678 | 139.1208 | 140.469 | 139.954 | 133.8334 | 124.0501 | 121.0309 | 110.4107 | 93.4184 | 75.3145 | 2144.0551
2016-08-18 | 62.9519 | 53.9181 | 48.2241 | 44.9508 | 44.252 | 48.7644 | 56.9817 | 60.834 | 70.5759 | 89.1727 | 108.7248 | 127.9295 | 143.2133 | 156.0669 | 162.0267 | 166.9419 | 167.7326 | 164.5053 | 157.6128 | 145.6149 | 140.9851 | 124.4694 | 102.5629 | 85.0474 | 2534.0592
2016-08-19 | 69.6113 | 60.1118 | 53.7025 | 49.796 | 48.6414 | 52.4861 | 61.2198 | 64.8124 | 75.4165 | 93.8507 | 111.8856 | 130.9792 | 147.1226 | 158.5292 | 165.3961 | 173.8007 | 178.1673 | 173.7077 | 165.4566 | 151.5039 | 146.0124 | 130.2134 | 107.9783 | 89.1061 | 2659.5074
2016-08-20 | 73.5598 | 63.6535 | 57.186 | 52.5457 | 51.0818 | 54.5414 | 62.9519 | 53.4959 | 76.4718 | 95.1535 | 113.1075 | 133.4665 | 147.2937 | 161.2048 | 167.0178 | 168.1745 | 167.7174 | 163.2261 | 153.6967 | 142.2862 | 137.2827 | 123.7622 | 104.0806 | 85.5359 | 2608.4939
2016-08-21 | 72.2648 | 62.5701 | 56.1242 | 52.1629 | 50.5956 | 54.2639 | 63.1667 | 67.3447 | 78.3439 | 95.5323 | 114.5373 | 134.2009 | 149.0108 | 162.3711 | 170.0856 | 178.0732 | 178.3557 | 166.7293 | 154.8942 | 139.2595 | 135.799 | 120.9921 | 102.5034 | 84.1822 | 2643.3636
2016-08-22 | 69.1022 | 60.0845 | 53.9612 | 50.2533 | 48.7809 | 52.1799 | 60.9625 | 64.926 | 75.5493 | 94.1584 | 112.2465 | 130.8312 | 146.3536 | 157.9524 | 162.3561 | 171.9766 | 174.4988 | 167.5956 | 156.6696 | 140.9153 | 132.707 | 117.4367 | 100.8675 | 85.4381 | 2587.8034
2016-08-23 | 71.2292 | 61.9579 | 54.9241 | 50.32 | 47.5651 | 47.3222 | 48.584 | 51.3426 | 65.1251 | 86.8566 | 107.3684 | 127.0799 | 142.9601 | 154.1051 | 159.2257 | 163.4214 | 165.8348 | 162.461 | 151.9673 | 137.1036 | 130.2536 | 118.0107 | 103.733 | 87.9447 | 2496.6961
2016-08-24 | 73.2677 | 63.1947 | 55.8427 | 51.0146 | 48.1751 | 47.1041 | 47.2333 | 48.9452 | 63.4379 | 84.5926 | 103.8049 | 125.2576 | 143.2977 | 156.7727 | 165.1392 | 169.58 | 170.0396 | 167.5348 | 157.6423 | 144.567 | 139.0376 | 122.8875 | 103.5415 | 86.015 | 2537.9253
2016-08-25 | 73.3079 | 63.2134 | 57.6939 | 54.5067 | 54.3246 | 59.2219 | 68.8581 | 72.8256 | 80.4915 | 96.9277 | 114.1853 | 130.0256 | 140.3576 | 144.4964 | 145.4164 | 145.1613 | 145.9982 | 142.7353 | 133.2221 | 124.6794 | 122.5489 | 108.4553 | 92.2404 | 75.3757 | 2446.2693
2016-08-26 | 64.2363 | 56.769 | 51.79 | 48.937 | 48.4284 | 52.7675 | 62.0782 | 65.6479 | 73.7717 | 89.9849 | 105.404 | 120.3851 | 131.4101 | 141.544 | 148.5376 | 154.2511 | 157.2146 | 154.6748 | 146.1261 | 133.5752 | 129.129 | 114.6003 | 94.1014 | 77.5136 | 2422.8778
2016-08-27 | 62.9706 | 54.0822 | 48.0284 | 44.5418 | 43.2798 | 46.8462 | 55.4481 | 58.5363 | 67.4895 | 84.5926 | 100.8557 | 117.6023 | 131.8012 | 143.833 | 153.3908 | 160.37 | 164.5354 | 161.937 | 153.3472 | 139.6065 | 135.2516 | 120.2562 | 100.0662 | 83.3108 | 2431.9794
2016-08-28 | 69.1511 | 60.1027 | 53.7714 | 49.7297 | 48.1017 | 51.8662 | 61.275 | 64.907 | 73.9839 | 88.088 | 99.9369 | 110.559 | 123.2918 | 136.801 | 149.5279 | 157.7161 | 161.354 | 155.1577 | 142.8056 | 133.0594 | 127.2523 | 111.8234 | 94.3296 | 78.6355 | 2403.2268
2016-08-29 | 64.6705 | 56.424 | 51.1154 | 47.5975 | 46.6774 | 50.4786 | 59.8205 | 64.6327 | 75.0291 | 93.6686 | 112.5331 | 127.6372 | 139.093 | 150.334 | 158.4848 | 163.166 | 161.5931 | 151.4026 | 138.802 | 126.7356 | 122.2627 | 109.056 | 94.5124 | 81.7622 | 2447.489
2016-08-30 | 69.9256 | 61.321 | 55.3781 | 51.2331 | 49.473 | 51.149 | 51.7562 | 53.9008 | 65.6193 | 85.8624 | 104.9338 | 124.3121 | 138.0137 | 148.9965 | 157.362 | 161.0257 | 160.5189 | 151.7934 | 136.9523 | 124.7582 | 120.3593 | 107.8562 | 94.5924 | 82.5614 | 2409.6544
2016-08-31 | 70.3193 | 61.0176 | 54.4026 | 50.5622 | 47.9225 | 46.7899 | 47.476 | 49.3821 | 62.691 | 84.2578 | 102.1704 | 119.2655 | 134.1873 | 144.765 | 149.5854 | 151.1568 | 147.8793 | 141.558 | 128.6086 | 116.9022 | 113.5205 | 102.0516 | 88.8621 | 75.8766 | 2291.2103
2016-09-01 | 64.5004 | 57.1594 | 51.8154 | 47.9877 | 46.7658 | 47.4922 | 49.738 | 50.7714 | 63.3911 | 84.7765 | 104.6931 | 125.3761 | 137.4893 | 147.0513 | 155.4947 | 158.4256 | 156.0669 | 150.2043 | 140.4273 | 128.7686 | 125.2576 | 111.0168 | 93.1686 | 77.9074 | 2375.7454
2016-09-02 | 64.7556 | 56.2123 | 50.5287 | 47.306 | 46.2367 | 50.012 | 58.7524 | 62.4121 | 70.7834 | 87.4493 | 103.5535 | 121.2768 | 134.5825 | 143.0445 | 152.3878 | 157.9081 | 159.0773 | 154.0176 | 142.9742 | 131.1541 | 124.4039 | 106.748 | 87.7023 | 70.8428 | 2384.1219
2016-09-03 | 58.0875 | 50.1284 | 45.2666 | 42.2115 | 41.4133 | 45.0375 | 54.0476 | 57.5511 | 65.0302 | 78.959 | 89.4282 | 101.0328 | 112.608 | 125.3629 | 134.8964 | 138.1518 | 140.1348 | 135.5252 | 127.4911 | 117.3475 | 114.311 | 101.293 | 84.7982 | 68.5171 | 2128.6307
2016-09-04 | 56.4594 | 48.6824 | 43.9164 | 41.0962 | 40.3385 | 43.8852 | 53.1268 | 56.4594 | 61.8006 | 73.7717 | 87.4163 | 99.4673 | 110.0404 | 120.398 | 124.8632 | 126.7621 | 129.0489 | 125.6 | 119.4582 | 113.9468 | 112.396 | 99.4439 | 82.9143 | 68.5852 | 2039.877
2016-09-05 | 56.6893 | 49.25 | 44.7854 | 42.097 | 41.6785 | 45.4328 | 55.2644 | 58.9237 | 67.0075 | 83.0963 | 100.078 | 116.4451 | 131.0868 | 142.6511 | 149.3842 | 149.8012 | 143.2836 | 130.5758 | 117.7299 | 109.3509 | 104.5729 | 92.9758 | 80.9774 | 69.9452 | 2183.0827
2016-09-06 | 59.1948 | 52.5883 | 47.7193 | 44.4948 | 42.9787 | 42.9556 | 44.8484 | 48.0202 | 58.7254 | 74.3179 | 87.4932 | 98.1352 | 104.5969 | 103.745 | 101.6957 | 99.034 | 93.9646 | 89.9849 | 85.4381 | 83.1285 | 83.1499 | 76.8114 | 69.3272 | 61.2934 | 1753.6415
2016-09-07 | 52.8957 | 45.8936 | 41.3906 | 38.3987 | 37.2922 | 37.4863 | 39.0057 | 41.0133 | 50.4703 | 64.1233 | 77.6897 | 92.3534 | 105.1507 | 114.3361 | 118.7269 | 115.7231 | 110.5219 | 103.5057 | 93.4298 | 90.2416 | 90.0965 | 81.0198 | 69.0045 | 57.3195 | 1767.0887
2016-09-08 | 48.5103 | 42.9325 | 38.8297 | 36.457 | 36.308 | 40.5928 | 49.4565 | 52.9641 | 58.9057 | 74.0648 | 91.0026 | 107.1006 | 120.6562 | 131.3966 | 139.5093 | 142.9742 | 142.5949 | 139.4815 | 128.3021 | 122.1328 | 117.9213 | 103.2308 | 86.3424 | 70.9319 | 2122.5984
2016-09-09 | 58.7254 | 50.6207 | 45.814 | 42.8709 | 41.6861 | 45.1796 | 54.2466 | 57.6939 | 63.9352 | 78.0216 | 94.0672 | 109.5477 | 123.3179 | 135.8676 | 141.7538 | 148.0938 | 146.5385 | 139.8566 | 129.276 | 120.9792 | 115.344 | 99.3032 | 82.1453 | 67.2965 | 2192.1814
2016-09-10 | 56.1858 | 49.3986 | 45.077 | 42.1199 | 41.4966 | 45.5121 | 54.7935 | 58.0068 | 64.161 | 76.5952 | 92.0824 | 105.561 | 118.0873 | 129.3696 | 136.1143 | 139.2872 | 138.0413 | 132.3957 | 123.2266 | 116.5085 | 112.5581 | 96.9393 | 80.7026 | 65.7527 | 2119.9731
2016-09-11 | 54.3766 | 47.5165 | 42.8863 | 40.0925 | 39.4696 | 43.1794 | 52.3924 | 55.9042 | 61.4407 | 74.6528 | 87.7243 | 99.655 | 108.8351 | 115.5714 | 117.9213 | 118.6501 | 114.2482 | 105.7785 | 98.275 | 94.147 | 92.105 | 81.6772 | 70.5858 | 58.2937 | 1875.3785
2016-09-12 | 47.0154 | 41.7469 | 38.1659 | 36.4002 | 36.4002 | 40.4431 | 50.195 | 53.1868 | 59.5843 | 70.922 | 82.092 | 92.026 | 102.2774 | 112.4209 | 115.0033 | 114.0095 | 114.7262 | 115.584 | 107.7708 | 99.2564 | 95.9119 | 86.2878 | 76.0816 | 64.4626 | 1851.9703
2016-09-13 | 52.8444 | 45.7265 | 40.9907 | 37.3496 | 35.9124 | 35.7787 | 37.7314 | 40.4655 | 49.2335 | 63.2227 | 79.629 | 95.7048 | 108.8719 | 117.3857 | 120.8887 | 120.4883 | 115.5335 | 108.6268 | 97.3913 | 91.8682 | 88.4747 | 78.1878 | 66.7287 | 55.7812 | 1784.8161
2016-09-14 | 47.6381 | 41.4814 | 37.3065 | 34.6071 | 33.0482 | 32.7919 | 33.8437 | 35.3301 | 45.4012 | 60.6966 | 76.8011 | 93.214 | 106.3112 | 115.4324 | 120.166 | 121.7693 | 122.0159 | 115.8369 | 105.199 | 99.1627 | 95.9925 | 84.6251 | 71.8059 | 58.3566 | 1788.8331
2016-09-15 | 49.044 | 42.6864 | 38.9543 | 36.9269 | 36.8484 | 40.7953 | 49.6302 | 53.3584 | 59.9843 | 74.7036 | 94.2497 | 110.2131 | 124.2204 | 136.9523 | 146.1829 | 152.4749 | 153.6093 | 149.4417 | 139.0792 | 131.4101 | 125.8372 | 108.9824 | 91.5192 | 72.7052 | 2219.8094
2016-09-16 | 59.4574 | 51.7646 | 46.1648 | 42.7632 | 41.8305 | 45.235 | 54.3766 | 57.8547 | 64.3494 | 78.2606 | 94.8327 | 111.1779 | 124.2859 | 134.4053 | 132.5851 | 127.0402 | 122.5749 | 117.4367 | 111.7364 | 109.523 | 105.211 | 91.553 | 77.0279 | 63.0639 | 2064.5106
2016-09-17 | 51.3257 | 44.6596 | 40.2191 | 37.5367 | 37.3209 | 41.3982 | 50.9223 | 54.3332 | 59.6479 | 70.2306 | 84.6791 | 96.4538 | 105.3799 | 110.2625 | 115.7357 | 115.4071 | 107.6975 | 99.1159 | 93.3843 | 94.3411 | 92.7266 | 82.7645 | 69.4153 | 56.1418 | 1811.0993
2016-09-18 | 46.8623 | 40.4057 | 37.1917 | 35.0511 | 34.8704 | 38.7638 | 48.1017 | 51.469 | 56.8487 | 68.0411 | 79.6395 | 92.4777 | 105.5006 | 118.0362 | 127.2523 | 132.5581 | 130.764 | 131.5718 | 120.2691 | 113.7712 | 108.1494 | 94.2954 | 78.6668 | 63.7285 | 1954.2861
2016-09-19 | 52.5883 | 45.2271 | 41.0133 | 38.4133 | 37.9484 | 41.6937 | 51.1406 | 55.3868 | 60.9808 | 73.59 | 84.8956 | 92.2856 | 94.5353 | 90.8457 | 84.7332 | 81.943 | 79.4298 | 76.9866 | 74.1255 | 75.2023 | 73.9738 | 67.8279 | 59.4755 | 50.7881 | 1585.0303
2016-09-20 | 42.6941 | 37.5655 | 34.3448 | 32.6238 | 31.7634 | 32.6171 | 35.2742 | 38.8663 | 46.0451 | 58.0785 | 69.8568 | 79.8599 | 87.6362 | 92.9078 | 93.5207 | 85.3947 | 78.8859 | 75.7231 | 70.8626 | 71.9155 | 70.8626 | 63.8224 | 55.7461 | 47.7599 | 1434.6268
2016-09-21 | 40.7277 | 35.3161 | 31.9757 | 29.8967 | 29.0225 | 29.2446 | 30.8817 | 32.7986 | 40.6527 | 54.2812 | 68.3809 | 82.8179 | 95.3371 | 104.5729 | 111.0168 | 113.4954 | 113.145 | 108.5532 | 98.5666 | 94.1128 | 89.3282 | 77.1311 | 64.9734 | 52.4095 | 1628.6386
2016-09-22 | 43.2721 | 37.4647 | 33.8437 | 32.3892 | 32.7448 | 37.3209 | 46.2687 | 50.6374 | 56.5389 | 67.9248 | 80.3334 | 92.0599 | 101.3521 | 103.3383 | 100.8321 | 97.6815 | 95.9119 | 92.489 | 90.3868 | 91.6542 | 87.3833 | 76.0816 | 63.2414 | 51.3679 | 1662.5186
2016-09-23 | 42.2955 | 36.5777 | 32.9739 | 31.1698 | 31.3605 | 36.1029 | 46.061 | 50.7044 | 53.1182 | 60.3308 | 65.8004 | 72.605 | 77.7311 | 78.8546 | 79.4298 | 80.7132 | 82.4653 | 85.3403 | 83.4504 | 85.9605 | 83.7621 | 73.7313 | 62.0967 | 50.195 | 1482.8305
2016-09-24 | 41.1188 | 35.6593 | 33.1023 | 31.1633 | 30.9667 | 35.568 | 45.2429 | 49.7546 | 53.5389 | 60.8707 | 68.2935 | 76.0611 | 81.486 | 88.331 | 96.3845 | 102.9681 | 103.5894 | 100.8911 | 96.2345 | 96.1538 | 93.5548 | 83.1714 | 69.2195 | 57.2216 | 1630.5458
2016-09-25 | 47.768 | 41.3831 | 37.4647 | 35.0998 | 34.9607 | 38.1514 | 45.6471 | 50.6458 | 56.9196 | 69.0241 | 81.9856 | 91.0924 | 96.1538 | 100.7376 | 107.0032 | 112.2465 | 108.4675 | 98.6483 | 92.2066 | 91.2046 | 87.7794 | 77.3378 | 65.0776 | 54.3939 | 1721.3989
2016-09-26 | 45.417 | 39.8398 | 36.4002 | 34.4275 | 34.3861 | 38.6906 | 48.0365 | 52.9299 | 57.1327 | 65.4956 | 77.0279 | 91.0924 | 102.4201 | 114.1476 | 118.3557 | 118.7526 | 114.4744 | 106.3597 | 98.2284 | 96.9972 | 92.4551 | 83.1928 | 71.8158 | 68.3323 | 1806.4081
2016-09-27 | 56.2035 | 46.061 | 42.2497 | 39.6027 | 38.5956 | 39.0351 | 41.3075 | 44.2207 | 54.2639 | 70.6253 | 86.0259 | 101.6838 | 114.8269 | 124.1811 | 130.8985 | 131.2349 | 122.8223 | 114.2482 | 103.1352 | 100.4311 | 94.1813 | 84.9173 | 73.6102 | 61.9301 | 1916.2917
2016-09-28 | 52.3924 | 45.9573 | 41.489 | 38.5226 | 37.1846 | 37.364 | 38.8663 | 41.5041 | 50.3034 | 65.9626 | 81.8153 | 97.6118 | 111.898 | 122.5619 | 129.4499 | 131.6123 | 128.6352 | 120.1402 | 107.8318 | 107.5878 | 102.9562 | 90.6105 | 75.8766 | 61.736 | 1919.8699
2016-09-29 | 52.0272 | 44.8326 | 40.9155 | 38.5226 | 38.5299 | 42.5866 | 52.0017 | 56.2916 | 61.8838 | 75.5902 | 91.6205 | 108.688 | 119.8183 | 129.5167 | 134.5007 | 134.4598 | 131.0599 | 122.0808 | 112.4209 | 108.5655 | 97.3913 | 84.6467 | 69.9846 | 57.1682 | 2005.1037
2016-09-30 | 47.0879 | 40.9681 | 37.3856 | 35.3231 | 35.3021 | 39.5066 | 49.9122 | 53.6766 | 60.1027 | 73.3381 | 87.5812 | 100.6197 | 111.637 | 115.4071 | 118.8935 | 113.4454 | 112.7078 | 111.0787 | 105.0543 | 105.7785 | 101.1156 | 89.3504 | 74.6426 | 60.6783 | 1880.5932
2016-10-01 | 50.4619 | 43.7996 | 40.1968 | 38.0716 | 37.7242 | 42.2344 | 52.648 | 56.4859 | 63.2508 | 76.7805 | 90.398 | 104.7292 | 116.8768 | 126.2464 | 130.3744 | 137.5583 | 141.8658 | 137.5169 | 127.3186 | 122.3667 | 115.799 | 101.1865 | 83.2143 | 74.602 | 2111.7065
2016-10-02 | 58.2937 | 49.0028 | 44.3537 | 41.5117 | 40.7953 | 44.6282 | 54.3679 | 58.0337 | 65.1061 | 79.902 | 96.2807 | 110.8806 | 123.4746 | 136.9935 | 144.5812 | 150.0315 | 153.2598 | 147.8221 | 135.7443 | 129.7845 | 122.1848 | 105.6456 | 88.5853 | 71.5471 | 2252.8105
2016-10-03 | 59.2852 | 51.469 | 45.814 | 42.7094 | 41.5269 | 44.9744 | 54.3679 | 58.7073 | 66.6423 | 82.5507 | 99.655 | 116.6227 | 128.8353 | 142.6932 | 149.9739 | 153.9592 | 153.7696 | 141.53 | 124.7713 | 115.9508 | 104.8496 | 92.0486 | 78.5625 | 66.1059 | 2217.3748
2016-10-04 | 55.3518 | 47.5327 | 42.8555 | 39.736 | 38.2604 | 38.7711 | 41.0811 | 44.0723 | 54.8196 | 70.6648 | 84.0421 | 96.6502 | 107.9661 | 115.0286 | 117.6661 | 116.0901 | 110.6579 | 102.7178 | 92.8398 | 91.1821 | 85.8624 | 76.1739 | 65.0966 | 54.4633 | 1789.5823
2016-10-05 | 44.4869 | 36.9555 | 31.7634 | 27.9621 | 25.9662 | 25.4476 | 26.3389 | 27.2088 | 31.9691 | 39.7434 | 48.1588 | 54.5848 | 61.9486 | 68.8289 | 74.8255 | 79.3669 | 83.8913 | 82.1027 | 75.2941 | 74.7442 | 71.0309 | 61.4776 | 50.83 | 40.6153 | 1245.5415
2016-10-06 | 33.2309 | 28.4491 | 25.7152 | 24.3507 | 24.6708 | 28.915 | 37.0771 | 40.9381 | 44.8877 | 52.648 | 61.1278 | 69.1804 | 78.1151 | 85.0257 | 92.2517 | 94.5581 | 97.1362 | 93.5321 | 89.9403 | 93.6799 | 87.9116 | 76.2971 | 64.2552 | 52.0611 | 1475.955
2016-10-07 | 42.3797 | 37.0485 | 33.789 | 31.7766 | 31.3341 | 35.1207 | 44.534 | 49.1758 | 51.3594 | 59.5662 | 69.0631 | 76.1637 | 82.2092 | 87.4493 | 90.13 | 88.9064 | 88.7513 | 86.6376 | 85.0365 | 89.1949 | 84.4737 | 76.3587 | 63.2134 | 49.8624 | 1533.5343
2016-10-08 | 41.0058 | 35.7225 | 32.1621 | 30.4585 | 30.6535 | 34.9537 | 44.4556 | 48.3794 | 52.5798 | 62.8774 | 75.4676 | 86.8237 | 98.0886 | 107.2101 | 114.9277 | 118.4965 | 118.1895 | 114.3864 | 107.6244 | 107.6853 | 101.5653 | 88.707 | 74.1053 | 60.6966 | 1787.2222
2016-10-09 | 49.6137 | 43.1639 | 38.9397 | 35.9688 | 35.512 | 34.704 | 47.9551 | 51.8408 | 56.9995 | 69.9452 | 83.4718 | 96.4076 | 106.6873 | 117.0293 | 124.3514 | 129.3161 | 130.2 | 125.4156 | 114.9907 | 112.7577 | 105.3799 | 91.6655 | 77.4101 | 62.3286 | 1942.0544
2016-10-10 | 50.8133 | 43.2412 | 38.9984 | 36.0817 | 35.568 | 39.1159 | 48.1996 | 52.5798 | 58.2309 | 71.4576 | 85.7644 | 97.7048 | 108.8597 | 118.5349 | 125.3366 | 130.0391 | 130.9792 | 124.4301 | 111.5873 | 107.2223 | 99.1861 | 87.6142 | 75.4778 | 63.5128 | 1940.5357
2016-10-11 | 52.7675 | 45.5359 | 41.1942 | 38.0788 | 36.386 | 36.4712 | 38.4789 | 40.6302 | 50.012 | 66.6903 | 82.2732 | 96.6039 | 108.4063 | 117.7937 | 124.3908 | 128.6752 | 129.5034 | 123.893 | 110.2501 | 104.3686 | 96.3845 | 84.809 | 74.0344 | 62.1245 | 1889.7557
2016-10-12 | 52.2139 | 44.8169 | 39.5879 | 36.4712 | 35.0163 | 34.7455 | 36.1453 | 37.2204 | 47.0718 | 64.4721 | 80.5126 | 95.2797 | 108.688 | 117.8064 | 124.0501 | 127.4778 | 127.863 | 122.9266 | 111.4632 | 110.4972 | 102.6225 | 89.6841 | 77.1208 | 63.7473 | 1887.5006
2016-10-13 | 53.5131 | 46.7095 | 42.6557 | 40.3385 | 40.3908 | 44.6675 | 53.7369 | 57.7653 | 63.3256 | 75.9381 | 91.418 | 104.7172 | 114.5248 | 122.7311 | 128.4353 | 132.2334 | 131.7202 | 126.3521 | 116.369 | 115.9255 | 107.5024 | 94.4438 | 79.7444 | 65.3339 | 2050.4923
2016-10-14 | 54.2986 | 47.833 | 44.0645 | 41.6102 | 41.0359 | 45.4883 | 55.913 | 60.1848 | 65.8576 | 79.1367 | 93.0325 | 105.4765 | 114.6506 | 124.8764 | 130.5758 | 132.1388 | 129.0355 | 121.1733 | 114.3236 | 116.0141 | 106.6509 | 92.8738 | 77.6689 | 62.924 | 2056.8373
2016-10-15 | 50.7379 | 43.5587 | 39.5509 | 37.1416 | 37.1917 | 41.2546 | 50.8803 | 55.5795 | 60.5593 | 71.6565 | 82.8822 | 94.2497 | 82.4866 | 109.56 | 111.488 | 112.8951 | 109.5107 | 104.2125 | 97.9373 | 99.4322 | 91.3281 | 79.6709 | 65.448 | 52.8017 | 1782.014
2016-10-16 | 42.7478 | 36.6489 | 33.1091 | 30.7969 | 29.7939 | 32.6037 | 40.1074 | 42.894 | 45.7742 | 53.2125 | 60.7516 | 66.9497 | 73.6707 | 80.8188 | 87.4932 | 94.3525 | 98.3449 | 96.3153 | 88.3973 | 87.6693 | 80.5021 | 68.7119 | 55.9042 | 43.7607 | 1471.3305
2016-10-17 | 34.4275 | 28.7004 | 25.7033 | 24.0269 | 23.6195 | 26.6293 | 33.6593 | 37.0413 | 40.5853 | 47.6057 | 54.6022 | 61.3302 | 67.1904 | 74.2572 | 81.4224 | 88.1322 | 91.463 | 88.4304 | 79.1785 | 76.1124 | 68.4782 | 58.5813 | 49.8541 | 40.7277 | 1301.7587
2016-10-18 | 33.7139 | 28.0118 | 24.7176 | 22.9333 | 22.1463 | 22.8545 | 25.0872 | 27.5101 | 34.0835 | 43.683 | 52.5713 | 60.4861 | 68.8386 | 76.5437 | 83.859 | 89.6841 | 91.8569 | 88.4747 | 79.1367 | 76.6878 | 69.3761 | 59.8205 | 51.4606 | 42.3032 | 1275.8403
2016-10-19 | 34.9537 | 29.6849 | 26.1342 | 24.1019 | 23.278 | 23.312 | 24.8229 | 26.3269 | 33.1091 | 43.3959 | 53.4615 | 62.7748 | 73.0967 | 81.486 | 88.541 | 92.8625 | 94.3639 | 90.9914 | 83.6868 | 84.2901 | 77.6068 | 66.3164 | 55.5356 | 44.9035 | 1339.0366
2016-10-20 | 36.4925 | 30.934 | 27.8565 | 26.3148 | 26.4054 | 29.9546 | 37.6015 | 41.8685 | 46.9187 | 57.5422 | 68.8386 | 79.1158 | 88.3199 | 95.8313 | 102.8608 | 104.9579 | 103.5057 | 98.66 | 93.9874 | 95.6588 | 87.3943 | 75.2329 | 62.4586 | 50.3951 | 1569.1055
2016-10-21 | 40.8478 | 35.554 | 32.6507 | 30.8883 | 31.0191 | 35.0094 | 44.252 | 49.283 | 51.2752 | 58.0337 | 66.0104 | 71.0706 | 74.6121 | 76.3587 | 76.7805 | 77.1518 | 76.369 | 74.8561 | 74.8052 | 79.2308 | 73.6405 | 65.1251 | 54.3159 | 42.9787 | 1392.1185
2016-10-22 | 35.3091 | 30.5429 | 27.9372 | 26.6961 | 26.9885 | 30.4456 | 39.9958 | 45.0612 | 47.2494 | 53.264 | 61.3578 | 69.9256 | 76.5643 | 82.4759 | 86.9224 | 89.4949 | 87.9888 | 84.2686 | 82.5614 | 85.4055 | 79.325 | 69.5427 | 57.5333 | 45.9573 | 1422.8132
2016-10-23 | 37.364 | 32.7784 | 29.8646 | 28.1676 | 27.9807 | 31.6508 | 40.9456 | 45.9892 | 47.2494 | 52.3584 | 58.5273 | 63.907 | 68.5463 | 71.5869 | 74.4498 | 75.7845 | 75.0087 | 72.8657 | 71.2788 | 74.1559 | 71.5173 | 63.4005 | 53.1525 | 43.1948 | 1311.7247
2016-10-24 | 35.54 | 30.7838 | 28.1801 | 27.0679 | 27.4177 | 30.8425 | 38.6029 | 43.8151 | 47.1202 | 53.7369 | 59.5299 | 63.813 | 65.9913 | 68.3712 | 70.2208 | 71.9055 | 71.7262 | 69.4937 | 67.6248 | 68.6534 | 63.5878 | 57.3106 | 50.4703 | 41.8305 | 1253.6361
2016-10-25 | 33.6456 | 28.2988 | 25.0283 | 23.0742 | 22.396 | 22.9107 | 25.046 | 27.8379 | 33.7002 | 42.5482 | 50.5789 | 56.9108 | 62.6352 | 68.1478 | 72.4048 | 75.5595 | 75.6311 | 71.8457 | 65.201 | 64.3211 | 58.5633 | 51.9085 | 45.148 | 37.2204 | 1140.5621
2016-10-26 | 30.7316 | 26.3208 | 23.7912 | 22.0966 | 21.4166 | 21.5528 | 22.9276 | 25.1225 | 30.3289 | 39.0131 | 47.3626 | 54.0736 | 60.0936 | 66.2589 | 71.4079 | 75.4574 | 77.2964 | 74.6528 | 68.7216 | 70.5166 | 64.3117 | 54.8196 | 44.7146 | 34.8357 | 1127.8249
2016-10-27 | 27.6212 | 23.4484 | 21.1779 | 20.1889 | 20.5337 | 23.9981 | 31.6111 | 36.3576 | 38.947 | 45.8936 | 53.41 | 60.6233 | 66.9113 | 73.8727 | 80.1228 | 86.0368 | 89.1727 | 86.8128 | 82.0388 | 84.0421 | 75.8971 | 64.1421 | 52.0441 | 40.4132 | 1285.3174
2016-10-28 | 32.3023 | 27.4978 | 24.6475 | 23.2553 | 23.329 | 27.0312 | 35.3231 | 39.8472 | 42.8017 | 51.2331 | 59.657 | 68.2643 | 75.7231 | 85.3729 | 92.6587 | 98.0537 | 100.6904 | 97.6002 | 91.2383 | 92.9418 | 84.0636 | 72.7754 | 59.6116 | 47.3707 | 1453.2899
2016-10-29 | 38.5153 | 32.866 | 29.3401 | 27.4731 | 27.467 | 30.9929 | 40.1521 | 44.3616 | 47.2252 | 57.7653 | 67.1519 | 76.4615 | 85.7318 | 93.8735 | 100.5489 | 106.4567 | 107.6365 | 102.1942 | 93.8849 | 93.9076 | 85.5142 | 73.903 | 60.6325 | 47.8737 | 1571.9294
2016-10-30 | 37.6592 | 31.9824 | 28.424 | 26.5081 | 26.2847 | 29.6977 | 38.1804 | 42.6941 | 45.4645 | 54.7239 | 65.3815 | 74.7341 | 83.0963 | 90.1523 | 94.3525 | 97.6467 | 99.9369 | 95.5668 | 89.7732 | 90.9465 | 82.8286 | 72.6651 | 60.349 | 48.3303 | 1507.3789
2016-10-31 | 38.5299 | 32.644 | 28.8202 | 26.9579 | 26.5687 | 29.9481 | 38.4934 | 43.2335 | 46.3327 | 55.3781 | 64.3306 | 72.936 | 79.587 | 84.3657 | 87.9888 | 90.7561 | 91.3618 | 85.6338 | 75.7027 | 70.5166 | 61.1922 | 53.6422 | 45.2429 | 36.6845 | 1366.8473
2016-11-01 | 29.0162 | 24.2927 | 21.7607 | 20.4113 | 19.9256 | 20.4751 | 22.8714 | 25.4476 | 31.0322 | 38.5153 | 44.4399 | 47.2898 | 48.3957 | 48.363 | 48.6988 | 48.9205 | 48.216 | 45.6391 | 43.8774 | 46.4127 | 42.4486 | 37.7097 | 32.3491 | 27.1843 | 863.6929
2016-11-02 | 86.2441 | 18.9871 | 18.544 | 18.5086 | 19.1 | 20.9083 | 24.2754 | 31.0977 | 37.717 | 40.5553 | 40.9606 | 40.1744 | 39.4549 | 38.3331 | 37.8326 | 37.2994 | 37.5079 | 40.6827 | 47.306 | 45.3853 | 42.0894 | 36.7486 | 30.452 | 25.2937 | 855.458
2016-11-03 | 21.3677 | 20.1941 | 19.5496 | 19.7946 | 21.2212 | 26.4295 | 36.1736 | 40.4356 | 41.5723 | 43.0404 | 44.8405 | 46.2127 | 46.3727 | 46.6212 | 46.1009 | 45.3062 | 46.0131 | 49.1428 | 56.0449 | 53.7283 | 49.3408 | 42.2497 | 34.5587 | 27.8193 | 924.1305
2016-11-04 | 23.5111 | 20.9351 | 19.5548 | 19.2905 | 19.9414 | 23.9291 | 31.1698 | 36.8555 | 41.6406 | 45.5201 | 49.4234 | 52.947 | 54.663 | 56.2387 | 57.0883 | 57.7743 | 56.6804 | 58.4734 | 65.667 | 63.3911 | 58.2219 | 49.4647 | 41.3226 | 33.7617 | 1037.4654
2016-11-05 | 28.1239 | 24.5367 | 22.7703 | 21.9366 | 22.4907 | 26.3691 | 34.0423 | 36.8413 | 44.3302 | 52.1375 | 58.4464 | 63.5597 | 67.046 | 68.7899 | 69.4545 | 68.1478 | 65.9817 | 67.6634 | 74.3281 | 70.9616 | 65.372 | 57.0261 | 46.8623 | 37.5079 | 1194.7259
2016-11-06 | 30.7577 | 26.599 | 24.0673 | 22.7759 | 22.9727 | 26.9274 | 34.3517 | 40.331 | 46.967 | 54.9066 | 63.2508 | 70.5858 | 76.4615 | 80.9457 | 83.1285 | 82.9678 | 79.2936 | 75.8562 | 79.5241 | 74.0446 | 65.6289 | 55.3868 | 44.6596 | 35.6031 | 1297.9933
2016-11-07 | 28.6941 | 24.5891 | 22.1685 | 21.2591 | 21.4765 | 24.8639 | 32.4428 | 37.7386 | 43.9086 | 51.3005 | 58.3296 | 64.926 | 70.4377 | 75.0596 | 77.0795 | 76.6466 | 72.5449 | 69.2978 | 71.4477 | 64.5949 | 57.8011 | 50.2367 | 42.971 | 35.8772 | 1195.6921
2016-11-08 | 29.6337 | 25.4358 | 22.7198 | 21.5856 | 21.3568 | 22.3293 | 24.7702 | 29.8903 | 39.9586 | 49.0275 | 55.7461 | 61.3486 | 66.2685 | 68.3712 | 68.0605 | 65.7909 | 62.6073 | 63.6347 | 65.9244 | 60.1939 | 54.5588 | 48.2486 | 41.9065 | 35.065 | 1104.4326
2016-11-09 | 29.6465 | 25.418 | 23.0799 | 21.8981 | 21.4221 | 22.091 | 23.774 | 27.4978 | 35.3301 | 42.036 | 46.0291 | 48.453 | 48.7562 | 47.5408 | 46.2927 | 44.3537 | 43.9164 | 48.3712 | 52.4435 | 49.4565 | 45.2033 | 39.3516 | 33.5638 | 27.2579 | 893.183
2016-11-10 | 22.6638 | 20.2893 | 19.0743 | 18.5744 | 19.1925 | 22.0303 | 29.6721 | 36.4712 | 39.7434 | 43.9008 | 47.2171 | 50.2283 | 52.4776 | 54.4893 | 55.4919 | 56.3005 | 55.3868 | 56.8398 | 62.3843 | 58.3207 | 52.2309 | 44.4242 | 36.8341 | 29.5634 | 983.8009
2016-11-11 | 23.711 | 20.5816 | 18.9768 | 18.3975 | 18.8082 | 21.1995 | 26.351 | 32.1755 | 37.7458 | 43.0481 | 47.2333 | 50.3534 | 53.3241 | 56.1418 | 57.4798 | 58.7254 | 57.6403 | 58.2219 | 63.6253 | 59.8114 | 53.6336 | 45.7583 | 37.6376 | 29.6593 | 990.2407
2016-11-12 | 23.6252 | 20.4273 | 19.0332 | 18.4581 | 19.1617 | 22.6079 | 30.4715 | 35.463 | 39.138 | 44.0801 | 49.4151 | 54.4112 | 58.9869 | 63.8506 | 67.2193 | 68.449 | 66.6039 | 65.3625 | 70.0337 | 65.41 | 58.6983 | 50.4035 | 41.315 | 32.765 | 1085.39
2016-11-13 | 26.5081 | 23.0742 | 21.0914 | 20.4964 | 20.9728 | 24.4611 | 32.3357 | 37.717 | 42.8324 | 49.6799 | 56.177 | 61.2106 | 66.2972 | 70.9319 | 73.0465 | 73.3381 | 70.7043 | 69.2782 | 73.3784 | 68.5658 | 61.4684 | 52.5287 | 42.6249 | 34.0629 | 1172.7821
2016-11-14 | 27.5286 | 23.5681 | 21.5092 | 20.4698 | 20.7152 | 23.8486 | 31.6178 | 37.1774 | 42.3491 | 48.2241 | 53.6422 | 57.364 | 60.9625 | 63.6441 | 65.239 | 65.22 | 62.4493 | 61.5698 | 64.5004 | 59.249 | 53.3928 | 46.549 | 40.1595 | 33.4686 | 1084.4179
2016-11-15 | 27.9248 | 24.1886 | 22.1906 | 21.14 | 21.0483 | 22.1463 | 24.9226 | 29.5953 | 37.5943 | 44.9744 | 50.1034 | 54.1947 | 56.9906 | 59.4936 | 60.4313 | 59.9024 | 57.6225 | 57.1682 | 60.4404 | 55.4218 | 50.2283 | 44.8326 | 39.4401 | 33.8574 | 1015.8525
2016-11-16 | 28.5244 | 25.211 | 23.159 | 22.0524 | 21.7278 | 22.6191 | 24.2812 | 28.1115 | 37.8687 | 47.8981 | 55.8076 | 61.9393 | 67.2965 | 70.7637 | 72.2548 | 72.1649 | 69.3761 | 68.8581 | 73.157 | 68.4587 | 61.5883 | 53.9008 | 46.2447 | 38.2022 | 1161.4659
2016-11-17 | 32.0622 | 28.5809 | 26.684 | 25.8764 | 26.9274 | 31.3802 | 40.4132 | 46.2447 | 53.5131 | 64.048 | 74.8662 | 83.59 | 90.0965 | 93.771 | 94.2611 | 92.67 | 89.3504 | 89.4504 | 92.8058 | 85.906 | 76.1124 | 64.2175 | 53.1182 | 42.1733 | 1498.119
2016-11-18 | 34.4344 | 29.8389 | 26.8543 | 25.3765 | 25.7331 | 29.1113 | 38.2968 | 44.0801 | 49.044 | 54.9154 | 59.023 | 59.8114 | 57.81 | 55.6671 | 52.8444 | 50.0951 | 50.22 | 55.7812 | 61.6621 | 59.8023 | 55.3781 | 48.8548 | 40.8028 | 33.8232 | 1099.2602
2016-11-19 | 29.2446 | 27.2947 | 26.5203 | 26.6293 | 28.4616 | 34.2897 | 47.1767 | 53.41 | 56.0273 | 57.3195 | 56.6185 | 53.9612 | 50.8216 | 48.543 | 46.7899 | 46.1408 | 47.2333 | 53.7283 | 60.6142 | 59.4846 | 56.0625 | 49.6385 | 41.8913 | 34.5932 | 1092.4948
2016-11-20 | 29.749 | 27.4546 | 26.903 | 27.1353 | 29.0732 | 34.8843 | 46.4047 | 51.4859 | 50.3034 | 50.2867 | 49.8541 | 49.3243 | 48.4939 | 47.6543 | 46.3007 | 45.6471 | 45.9414 | 51.8577 | 58.6713 | 57.6225 | 53.8577 | 47.6949 | 40.2713 | 33.1091 | 1049.9804
2016-11-21 | 27.9932 | 25.0283 | 24.0385 | 23.4541 | 24.2812 | 29.9417 | 38.7492 | 44.3068 | 46.3327 | 48.3303 | 50.0369 | 50.4285 | 49.0357 | 48.0691 | 46.9026 | 45.8538 | 46.4688 | 51.1995 | 54.2639 | 51.5196 | 47.9551 | 43.218 | 37.9846 | 32.3424 | 987.7344
2016-11-22 | 27.2701 | 24.2233 | 22.6023 | 22.0413 | 22.246 | 23.5453 | 26.6779 | 31.1895 | 39.5288 | 47.5489 | 52.4776 | 55.2294 | 55.3781 | 55.2032 | 54.3332 | 52.8615 | 52.5969 | 56.8398 | 60.2121 | 57.9352 | 54.6804 | 50.0036 | 44.9192 | 38.3768 | 1027.9206
2016-11-23 | 32.5701 | 29.0415 | 26.4174 | 24.9754 | 24.7117 | 25.5664 | 27.4054 | 31.8429 | 43.218 | 56.089 | 65.3339 | 71.6665 | 75.8152 | 78.8963 | 79.4612 | 78.4063 | 74.4599 | 76.0303 | 81.0198 | 77.6482 | 71.8656 | 63.7004 | 55.1945 | 47.2898 | 1318.6258
2016-11-24 | 38.1369 | 33.0415 | 30.316 | 29.2955 | 30.1092 | 34.3723 | 42.8863 | 49.3821 | 58.4824 | 69.4055 | 80.0597 | 91.8344 | 101.3995 | 106.4203 | 108.8229 | 107.9173 | 102.2893 | 100.2544 | 104.3566 | 97.4493 | 88.6627 | 76.2355 | 65.7051 | 53.5733 | 1700.4078
2016-11-25 | 43.9943 | 37.9194 | 34.704 | 33.4822 | 33.7821 | 38.2095 | 47.096 | 53.6164 | 62.924 | 73.4187 | 83.1928 | 89.9961 | 93.9646 | 96.8815 | 96.5231 | 94.5581 | 90.3757 | 91.733 | 95.5668 | 90.4875 | 82.4012 | 73.2979 | 62.9706 | 53.4959 | 1654.5912
2016-11-26 | 44.9429 | 39.5435 | 36.1948 | 34.5034 | 34.5172 | 37.0628 | 42.8555 | 48.7398 | 56.2299 | 61.8376 | 62.2265 | 60.8891 | 58.8335 | 55.6847 | 52.0017 | 48.5185 | 46.6774 | 50.4953 | 54.8631 | 52.3329 | 48.2731 | 44.2051 | 39.0718 | 32.9942 | 1143.4944
2016-11-27 | 27.8627 | 24.7 | 23.1647 | 22.7815 | 23.1816 | 25.0401 | 28.7193 | 34.538 | 41.8609 | 47.0315 | 50.2367 | 51.5196 | 51.4353 | 49.6882 | 47.7274 | 44.7382 | 40.9606 | 39.4475 | 40.5329 | 37.6953 | 35.8068 | 34.1453 | 31.6045 | 28.0803 | 882.4989
2016-11-28 | 24.905 | 23.1025 | 22.396 | 22.6358 | 23.9176 | 26.7204 | 31.5121 | 36.9841 | 42.5712 | 45.8936 | 46.3487 | 44.8484 | 43.025 | 41.4057 | 39.9289 | 38.9837 | 39.0571 | 43.9865 | 49.9538 | 48.2241 | 45.6153 | 44.0489 | 38.969 | 33.5775 | 898.6108
2016-11-29 | 29.0669 | 26.7569 | 25.5664 | 25.418 | 26.1162 | 27.6088 | 31.0125 | 35.6171 | 40.8629 | 43.3805 | 43.7063 | 43.4967 | 42.7478 | 41.9217 | 40.923 | 39.9438 | 39.0865 | 42.4716 | 47.0396 | 44.9586 | 41.8152 | 38.3696 | 33.9532 | 28.9339 | 880.7737
2016-11-30 | 24.3623 | 21.602 | 20.2735 | 19.7789 | 20.0202 | 21.0644 | 23.1477 | 26.6415 | 33.1091 | 38.4934 | 42.0208 | 44.4086 | 46.1888 | 47.1121 | 47.2979 | 46.6774 | 45.7742 | 49.4317 | 56.2035 | 53.8059 | 49.9205 | 44.2833 | 37.9194 | 30.5689 | 890.106
2016-12-01 | 25.4002 | 22.2793 | 20.8009 | 20.3423 | 21.1238 | 25.152 | 33.489 | 38.6029 | 43.2567 | 48.666 | 54.6543 | 59.539 | 61.8746 | 62.7655 | 61.6529 | 59.657 | 57.819 | 62.0504 | 69.2587 | 66.9978 | 61.8284 | 53.9094 | 45.2033 | 36.0111 | 1112.3344
2016-12-02 | 29.0162 | 25.0283 | 22.6414 | 21.7333 | 22.357 | 26.1042 | 34.8565 | 39.825 | 43.5898 | 49.2995 | 55.081 | 58.7614 | 60.935 | 62.31 | 61.8376 | 60.2395 | 58.0964 | 62.7376 | 69.8175 | 67.2097 | 62.0967 | 54.4893 | 45.3457 | 36.0888 | 1129.4974
2016-12-03 | 28.9276 | 24.6884 | 22.5632 | 21.5856 | 22.0027 | 25.7689 | 35.2882 | 39.8324 | 44.5105 | 51.5534 | 57.2661 | 62.0967 | 65.8385 | 67.6248 | 69.0241 | 69.68 | 66.4984 | 67.9829 | 74.4396 | 70.9517 | 64.907 | 56.5035 | 47.0073 | 37.0413 | 1193.5827
2016-12-04 | 29.6785 | 25.5604 | 23.329 | 22.4015 | 22.9389 | 26.8969 | 35.526 | 40.7502 | 45.3299 | 52.2479 | 58.0964 | 63.1947 | 67.2772 | 69.1218 | 70.3588 | 70.823 | 67.364 | 69.0045 | 75.8664 | 72.9059 | 67.2483 | 59.3486 | 49.2335 | 39.2778 | 1223.7802
2016-12-05 | 31.5715 | 26.763 | 24.3159 | 23.3461 | 23.7225 | 27.6027 | 36.3647 | 41.6937 | 47.3303 | 55.7373 | 62.4028 | 67.0845 | 69.7193 | 69.4741 | 69.2098 | 70.1814 | 68.8776 | 70.5956 | 74.3179 | 69.7782 | 64.0951 | 57.3106 | 49.9455 | 41.4663 | 1242.9062
2016-12-06 | 33.7958 | 28.8392 | 25.9303 | 24.1886 | 23.4997 | 24.2638 | 26.7447 | 30.9471 | 40.5478 | 51.1322 | 59.6206 | 65.5527 | 69.6996 | 72.3148 | 73.4993 | 72.5449 | 68.2935 | 66.508 | 69.3468 | 62.8587 | 56.831 | 50.8384 | 43.7762 | 36.117 | 1177.6907
2016-12-07 | 28.9909 | 24.9108 | 22.3904 | 20.8223 | 20.3954 | 20.9997 | 22.6135 | 25.7033 | 33.8163 | 42.9325 | 49.3078 | 53.668 | 56.0185 | 57.3284 | 57.7207 | 56.0185 | 53.7283 | 56.424 | 63.616 | 58.8516 | 53.9267 | 47.1525 | 39.0057 | 30.9013 | 997.2432
2016-12-08 | 24.7351 | 21.3188 | 19.7006 | 19.1514 | 19.7842 | 23.4598 | 31.4329 | 36.3293 | 39.7434 | 43.9319 | 47.7193 | 50.27 | 51.9594 | 53.3412 | 53.9871 | 54.7674 | 54.4633 | 58.3296 | 66.1633 | 63.8976 | 57.7832 | 49.7214 | 40.9381 | 31.6971 | 1014.6254
2016-12-09 | 25.1343 | 21.9476 | 20.4219 | 20.0044 | 20.6884 | 24.8463 | 34.5863 | 39.6471 | 42.3644 | 44.6282 | 45.9972 | 46.2927 | 46.1728 | 45.6471 | 44.8169 | 43.6131 | 44.2051 | 50.6291 | 59.4483 | 58.4554 | 54.6717 | 48.584 | 40.4356 | 32.6843 | 955.9221
2016-12-10 | 27.264 | 25.046 | 24.0385 | 24.63 | 26.357 | 33.4006 | 47.1606 | 55.7637 | 54.9589 | 52.2564 | 50.17 | 47.6787 | 45.5994 | 44.1973 | 42.5022 | 41.8609 | 42.7709 | 50.22 | 61.1738 | 61.1646 | 59.5299 | 54.0303 | 46.061 | 37.9556 | 1055.7902
2016-12-11 | 33.0279 | 30.8099 | 30.303 | 30.4715 | 32.765 | 40.4356 | 56.089 | 64.1892 | 60.6966 | 57.2305 | 53.0668 | 50.3701 | 47.7599 | 45.8299 | 44.0489 | 43.3108 | 44.2911 | 51.4353 | 60.5867 | 59.8478 | 57.5868 | 52.1205 | 43.6053 | 35.8279 | 1125.7061
2016-12-12 | 30.6275 | 28.0928 | 27.2272 | 27.123 | 29.2955 | 36.2797 | 49.4399 | 56.5035 | 57.0172 | 56.9196 | 55.1596 | 52.9385 | 50.3117 | 48.1344 | 45.9414 | 45.1796 | 46.3807 | 54.2812 | 62.2172 | 60.7241 | 58.9327 | 54.6456 | 48.6168 | 41.7924 | 1123.7819
2016-12-13 | 36.0182 | 33.632 | 32.5299 | 32.6641 | 33.9326 | 37.4791 | 43.2721 | 50.6793 | 55.3168 | 55.0374 | 51.7562 | 48.8137 | 46.6774 | 44.6046 | 42.8017 | 41.8685 | 41.6102 | 46.3887 | 52.5202 | 50.5204 | 48.4202 | 45.3932 | 40.9907 | 36.3789 | 1049.3062
2016-12-14 | 31.9292 | 29.2891 | 28.4052 | 28.4804 | 29.3719 | 32.0023 | 37.0771 | 43.8774 | 50.5455 | 51.3257 | 48.5758 | 46.533 | 44.9744 | 43.7063 | 42.8632 | 42.1199 | 42.1504 | 47.201 | 56.1242 | 54.9851 | 52.401 | 47.7843 | 40.4207 | 33.7958 | 1005.9388
2016-12-15 | 29.1938 | 26.9885 | 26.8238 | 27.2886 | 29.8646 | 36.9555 | 51.4437 | 59.8023 | 59.0772 | 54.9328 | 51.9763 | 49.6717 | 49.1346 | 48.2813 | 47.2656 | 47.1121 | 47.3545 | 53.1611 | 62.8028 | 61.8006 | 57.9889 | 51.3426 | 42.8632 | 34.7317 | 1107.8578
2016-12-16 | 29.1176 | 26.6233 | 25.7391 | 26.0561 | 27.8441 | 34.2621 | 47.7355 | 54.663 | 53.9181 | 51.1574 | 49.3656 | 48.4612 | 48.1588 | 48.2976 | 48.1344 | 48.3467 | 48.4693 | 52.9128 | 61.4868 | 59.866 | 55.2382 | 47.8249 | 39.6915 | 31.6178 | 1064.9878
2016-12-17 | 25.5902 | 22.675 | 21.5692 | 21.4438 | 22.877 | 28.018 | 38.508 | 44.8169 | 45.4725 | 46.2447 | 46.9428 | 47.3545 | 48.1833 | 49.2088 | 50.295 | 51.4016 | 50.8552 | 54.9241 | 62.4864 | 60.048 | 55.0287 | 48.6824 | 40.3236 | 31.823 | 1014.7727
2016-12-18 | 25.8645 | 22.8545 | 21.6731 | 21.6129 | 22.9558 | 27.7821 | 38.3768 | 44.9271 | 47.3222 | 48.7644 | 49.3738 | 48.8712 | 48.7891 | 50.3451 | 51.3089 | 51.5534 | 51.0566 | 54.8022 | 62.3935 | 59.9843 | 56.1682 | 49.5723 | 41.5723 | 33.3666 | 1031.2909
2016-12-19 | 27.4423 | 24.4611 | 23.0742 | 22.8601 | 24.0961 | 28.8581 | 38.5299 | 45.528 | 48.0773 | 49.5557 | 50.8719 | 51.3931 | 51.3342 | 51.8154 | 51.8069 | 51.6125 | 50.6458 | 53.5475 | 59.9024 | 56.53 | 52.1035 | 46.806 | 41.0585 | 34.0423 | 1035.953
2016-12-20 | 28.2863 | 24.7468 | 23.0178 | 22.246 | 22.1685 | 23.8371 | 27.2027 | 32.0156 | 38.8737 | 44.5654 | 47.8656 | 48.4693 | 50.9307 | 51.2247 | 51.5196 | 51.6041 | 50.6625 | 53.2297 | 58.8516 | 54.6543 | 50.17 | 45.2903 | 39.5361 | 32.9672 | 973.9355
2016-12-21 | 26.9213 | 23.0347 | 20.8009 | 19.8051 | 19.6693 | 20.3901 | 22.3459 | 25.8107 | 33.3191 | 41.6937 | 47.2575 | 50.2783 | 53.4959 | 54.472 | 53.7369 | 52.3839 | 51.2921 | 55.5181 | 62.3471 | 59.548 | 55.711 | 50.295 | 43.1948 | 34.8565 | 978.1781
2016-12-22 | 28.018 | 23.8946 | 21.5747 | 20.4698 | 20.8009 | 23.5396 | 28.7319 | 34.4206 | 42.7709 | 51.5872 | 59.4936 | 64.784 | 68.4587 | 71.2391 | 73.2073 | 72.2249 | 68.8679 | 70.823 | 78.4584 | 74.2774 | 68.2352 | 61.3026 | 52.4776 | 41.5723 | 1221.2302
2016-12-23 | 33.1361 | 27.7883 | 24.6241 | 23.1081 | 23.312 | 26.1823 | 31.4593 | 37.285 | 46.5009 | 56.831 | 65.1061 | 71.2987 | 75.9381 | 77.8141 | 73.6304 | 69.2587 | 65.4861 | 66.9497 | 73.8424 | 69.8961 | 64.406 | 60.3308 | 54.5935 | 47.5651 | 1266.3428
2016-12-24 | 39.6471 | 34.008 | 30.5689 | 29.1113 | 28.7824 | 30.7577 | 34.614 | 39.825 | 50.7128 | 64.3872 | 76.0406 | 84.3441 | 88.8178 | 89.6062 | 90.1969 | 88.066 | 85.7862 | 87.8565 | 89.8066 | 79.9335 | 71.1697 | 64.161 | 57.685 | 49.0193 | 1484.9035
2016-12-25 | 40.923 | 35.1626 | 30.3807 | 26.9396 | 24.6942 | 24.3043 | 25.2169 | 27.8441 | 34.5863 | 42.2039 | 47.3707 | 50.0785 | 51.0398 | 50.3451 | 48.8794 | 45.8618 | 42.7478 | 44.0723 | 47.833 | 45.8618 | 44.2911 | 41.8837 | 37.6737 | 32.0689 | 942.2631
2016-12-26 | 26.7265 | 23.295 | 21.8046 | 21.0375 | 21.3949 | 23.3802 | 26.9763 | 31.4725 | 37.6087 | 43.8074 | 48.8794 | 51.0482 | 50.9894 | 49.7131 | 48.937 | 48.3875 | 48.8712 | 54.5674 | 60.9717 | 58.6263 | 54.3679 | 49.316 | 43.5432 | 36.3647 | 982.0866
2016-12-27 | 29.7747 | 25.4002 | 22.7086 | 21.5256 | 21.531 | 22.4015 | 24.7702 | 27.5471 | 34.6278 | 44.166 | 52.3329 | 57.9531 | 61.5883 | 62.7935 | 62.8401 | 60.8891 | 58.5543 | 61.2566 | 67.5088 | 63.541 | 58.0337 | 52.3924 | 45.4091 | 37.2922 | 1076.8378
2016-12-28 | 30.3548 | 25.6556 | 22.8826 | 21.3677 | 20.6403 | 20.9728 | 22.6638 | 24.9637 | 33.4482 | 44.0177 | 52.6736 | 59.6297 | 64.7083 | 68.3809 | 70.3588 | 70.2898 | 68.1478 | 67.5281 | 73.6707 | 68.8581 | 62.5143 | 55.597 | 47.3141 | 37.8832 | 1134.5218
2016-12-29 | 30.634 | 26.1042 | 23.5453 | 22.4628 | 22.5799 | 24.7702 | 29.6465 | 34.6347 | 43.5354 | 54.8022 | 64.6421 | 71.4377 | 75.1106 | 76.7805 | 78.0216 | 78.6563 | 76.1739 | 75.4778 | 82.6789 | 77.1828 | 70.0239 | 60.8707 | 51.5956 | 41.0886 | 1292.4563
2016-12-30 | 32.6037 | 27.578 | 24.7293 | 23.2439 | 23.1025 | 25.3232 | 29.9031 | 34.7525 | 42.4563 | 51.9255 | 61.2014 | 69.2978 | 74.5918 | 78.4167 | 79.4717 | 78.1775 | 75.1819 | 75.1513 | 82.2412 | 76.832 | 70.3785 | 61.6344 | 52.8615 | 43.0096 | 1294.0651
2016-12-31 | 34.7594 | 29.3655 | 26.2967 | 24.7117 | 24.5775 | 26.5748 | 30.9013 | 36.1594 | 43.7063 | 52.1714 | 59.4392 | 63.8694 | 64.9449 | 65.6479 | 65.429 | 64.0668 | 64.4532 | 71.3285 | 77.5033 | 70.2602 | 62.0504 | 53.6508 | 45.7186 | 39.6693 | 1197.2556
[25 empty] | 568396.5565 | Annual MWHs
Note on L5: AJZ: Taken from Load Forecast (FNG)
Note on A13: AJZ: NOTES: Variable losses vary with the amount of electricity distributed and are, more precisely, proportional to the square of the current. Consequently, a 1% increase in current leads to an increase in losses of more than 1%. - Electrical Engineering Portal

## 2016 Hourly Load - RC2016
OPC 012917
FPL RC-16
2017 FORECASTED Hourly Loads - RC2016
BASED ON 2014 RAW DATA
FORECASTED
SUMMER PEAK |  | 24336.0406
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | MAX | 2014 Hourly Load | 116299005
2016-01-01 | 9998.1094 | 9634.356 | 9135.7278 | 8795.4753 | 8647.3173 | 8719.8636 | 8946.6986 | 9133.6842 | 9962.3471 | 11271.2463 | 12496.3595 | 13335.2402 | 13831.8249 | 14026.9847 | 13968.7433 | 13789.932 | 13604.9899 | 13763.3657 | 14431.6093 | 14034.1372 | 13432.3093 | 12762.0221 | 11871.0306 | 10749.1171 | 14431.6093 | 2016 Forecasted (FNG) NEL | 119624759.6915
2016-01-02 | 9698.7281 | 9025.3756 | 8572.7274 | 8356.1102 | 8294.8035 | 8546.1612 | 9507.6554 | 10288.2947 | 11448.0141 | 12812.0893 | 13909.4801 | 14661.5096 | 15198.9655 | 15572.9367 | 15740.5084 | 15655.7008 | 15339.971 | 15206.1179 | 15771.1618 | 15170.3557 | 14362.1283 | 13460.9191 | 12451.4012 | 11269.2027 | 15771.1618
2016-01-03 | 10136.0496 | 9325.7787 | 8823.0633 | 8578.8581 | 8558.4225 | 8841.4553 | 9672.1618 | 10452.8011 | 11363.2064 | 12135.6715 | 12577.0801 | 12720.1292 | 12721.1509 | 12603.6463 | 12485.1199 | 12411.5518 | 12373.746 | 12965.3562 | 13856.3476 | 13614.1859 | 13117.6013 | 12516.7951 | 11702.4371 | 10761.3784 | 13856.3476 | Ratio 2014 to 2016 | 1.0286
2016-01-04 | 9920.4542 | 9357.4538 | 9020.2667 | 8874.1523 | 8892.5443 | 9113.2486 | 9584.2888 | 10205.5306 | 11162.9377 | 12008.9708 | 12503.512 | 12611.8206 | 12509.6426 | 12346.158 | 12136.6932 | 11941.5334 | 11982.4046 | 12586.2761 | 13114.5359 | 12757.935 | 12303.2432 | 11745.3518 | 11045.4331 | 10218.8137 | 13114.5359
2016-01-05 | 9373.8023 | 8767.8872 | 8385.7418 | 8166.0593 | 8121.101 | 8311.1519 | 8760.7348 | 9279.7986 | 10289.3165 | 11272.268 | 12337.9837 | 12996.0095 | 13337.2838 | 13444.5706 | 13435.3746 | 13309.6957 | 13135.9933 | 13282.1077 | 14095.4439 | 13681.6234 | 13102.2746 | 12225.588 | 11199.7217 | 10098.2437 | 14095.4439 | Applied above ratio to 2013 historical hourly loads
2016-01-06 | 8992.6787 | 8383.6983 | 8020.9667 | 7891.2007 | 7994.4004 | 8592.1412 | 9828.494 | 10609.1333 | 11317.2263 | 12268.5028 | 13248.389 | 13869.6307 | 14358.0412 | 14618.5949 | 14537.8743 | 14228.2752 | 13935.0246 | 14374.3897 | 15110.0707 | 14687.0541 | 13743.9519 | 12583.2107 | 11607.4116 | 10529.4346 | 15110.0707
2016-01-07 | 9704.8588 | 9248.1235 | 9131.6406 | 9224.6225 | 9659.9005 | 10643.8738 | 12482.0546 | 13785.8449 | 14362.1283 | 14703.4026 | 14568.5277 | 14189.4476 | 13825.6942 | 13465.0062 | 13180.9516 | 13162.5595 | 13550.8356 | 14792.2974 | 16197.2437 | 16293.291 | 15939.7554 | 15027.3066 | 13887.001 | 12759.9785 | 16293.291 | Resulting Total Hourly Load | 119098524.3114
2016-01-08 | 11893.5098 | 11439.8398 | 11277.3769 | 11204.8306 | 11378.5331 | 12157.1288 | 13614.1859 | 14318.1918 | 14247.689 | 14247.689 | 14159.816 | 13802.1933 | 13312.7611 | 12848.8733 | 12449.3577 | 12292.0037 | 12407.4647 | 13095.1221 | 13896.197 | 13642.7958 | 13053.2292 | 12097.8656 | 10989.2352 | 9819.298 | 14318.1918
2016-01-09 | 8868.0216 | 8376.5458 | 8144.6019 | 8059.7943 | 8227.366 | 8922.1759 | 10337.3401 | 11265.1156 | 11556.3227 | 12079.4736 | 12438.1181 | 12632.2561 | 12649.6264 | 12556.6445 | 12438.1181 | 12396.2252 | 12470.815 | 13060.3816 | 13947.286 | 13779.7142 | 13238.1712 | 12377.8331 | 11346.8579 | 10158.5287 | 13947.286
2016-01-10 | 9106.0962 | 8440.9179 | 8058.7725 | 7914.7016 | 8000.5311 | 8596.2283 | 9938.8462 | 10835.9683 | 11514.4297 | 12334.9184 | 12984.77 | 13398.5905 | 13628.4909 | 13801.1715 | 13807.3022 | 13769.4964 | 13716.3639 | 13798.1062 | 14524.5912 | 14118.9449 | 13474.2022 | 12669.0402 | 11832.203 | 10874.7959 | 14524.5912
2016-01-11 | 9755.9477 | 9055.0072 | 8580.9016 | 8351.0013 | 8302.9777 | 8527.7691 | 9031.5063 | 9669.0965 | 11095.5002 | 12612.8423 | 13665.2749 | 14319.2136 | 14804.5587 | 15098.8311 | 15218.3793 | 15152.9854 | 14827.0378 | 14561.3753 | 14995.6314 | 14434.6746 | 13705.1243 | 12841.7209 | 11946.6423 | 10943.2551 | 15218.3793
2016-01-12 | 9863.2345 | 9097.9219 | 8619.7293 | 8341.8053 | 8202.8433 | 8287.651 | 8623.8164 | 9069.3121 | 10157.5069 | 11275.3334 | 12068.234 | 12521.904 | 12921.4197 | 13173.7991 | 13244.3019 | 13161.5378 | 12968.4215 | 12833.5466 | 13585.5761 | 13321.9571 | 12718.0856 | 11872.0524 | 10910.5582 | 9792.7318 | 13585.5761
2016-01-13 | 8868.0216 | 8355.0884 | 8115.9921 | 8091.4694 | 8313.1955 | 9149.0109 | 10720.5073 | 11660.5441 | 12032.4718 | 12529.0564 | 12967.3997 | 13294.3691 | 13592.7286 | 13822.6289 | 13969.7651 | 14075.0084 | 14013.7016 | 14137.3369 | 15014.0234 | 14819.8854 | 14051.5074 | 12985.7917 | 11818.9199 | 10500.8248 | 15014.0234 | 2014 Historical Summer Peak | 22720
2016-01-14 | 9358.4756 | 8662.644 | 8291.7381 | 8101.6872 | 8177.2989 | 8831.2376 | 10247.4235 | 11090.3913 | 11765.7874 | 12687.4322 | 13453.7666 | 13899.2623 | 14127.1191 | 14138.3587 | 14041.2896 | 13779.7142 | 13708.1896 | 14026.9847 | 14868.9308 | 14648.2265 | 13962.6127 | 12979.6611 | 11757.6132 | 10438.4962 | 14868.9308
2016-01-15 | 9306.3649 | 8673.8836 | 8318.3044 | 8197.7345 | 8280.4986 | 9005.9618 | 10515.1297 | 11392.838 | 11703.4589 | 12115.2359 | 12328.7877 | 12344.1144 | 12174.4991 | 12006.9273 | 11819.9417 | 11731.0469 | 11824.0288 | 12480.011 | 13337.2838 | 13144.1675 | 12626.1255 | 11816.8763 | 10783.8576 | 9644.5738 | 13337.2838 | Ratioed 2017 Projected Summer Peak | 23214.8232
2016-01-16 | 8797.5188 | 8345.8924 | 8212.0394 | 8262.1065 | 8555.3572 | 9538.3088 | 11368.3153 | 12551.5356 | 12752.8261 | 12825.3724 | 12823.3289 | 12631.2344 | 12336.962 | 12025.3193 | 11753.526 | 11619.673 | 11756.5914 | 12586.2761 | 14349.867 | 14689.0977 | 14611.4424 | 14138.3587 | 13375.0896 | 12524.9693 | 14689.0977
2016-01-17 | 11924.1632 | 11687.1104 | 11721.8509 | 11924.1632 | 12374.7678 | 13517.1169 | 15537.1744 | 16758.2005 | 16584.4981 | 15719.0511 | 14765.7311 | 13787.8884 | 12975.574 | 12318.5699 | 11858.7693 | 11605.3681 | 11651.3481 | 12368.6371 | 13522.2258 | 13438.4399 | 13166.6467 | 12629.1908 | 12008.9708 | 11257.9631 | 16758.2005 | FNG Forecasted Summer Peak | 24336.0406
2016-01-18 | 10536.587 | 10215.7484 | 10120.7229 | 10161.5941 | 10384.3419 | 10893.188 | 11753.526 | 12851.9387 | 13590.685 | 13672.4274 | 13415.9608 | 12889.7445 | 12335.9402 | 11838.3337 | 11396.9251 | 11156.807 | 11159.8723 | 11794.3972 | 13192.1911 | 13437.4181 | 13436.3964 | 13326.0442 | 13033.8154 | 12615.9077 | 13672.4274
2016-01-19 | 12316.5264 | 12214.3485 | 12293.0255 | 12527.0129 | 12903.0276 | 13510.9862 | 14453.0667 | 15589.2851 | 16238.1149 | 15732.3342 | 14627.7909 | 13550.8356 | 12690.4976 | 12056.9945 | 11547.1266 | 11136.3714 | 11013.7579 | 11368.3153 | 12596.4939 | 12518.8387 | 12221.5009 | 11618.6512 | 11004.5619 | 10140.1367 | 16238.1149
2016-01-20 | 9507.6554 | 9208.2741 | 9139.8149 | 9226.6661 | 9589.3977 | 10309.752 | 11491.9506 | 12605.6899 | 13010.3144 | 12828.4377 | 12581.1672 | 12343.0926 | 12062.1034 | 11845.4862 | 11679.9579 | 11587.9978 | 11604.3463 | 11995.6877 | 13097.1657 | 13009.2927 | 12431.9874 | 11585.9543 | 10543.7395 | 9425.913 | 13097.1657
2016-01-21 | 8583.967 | 8142.5584 | 7960.6817 | 7959.6599 | 8166.0593 | 8998.8093 | 10609.1333 | 11551.2138 | 11754.5478 | 11816.8763 | 11880.2267 | 11878.1831 | 11853.6604 | 11744.33 | 11648.2828 | 11550.192 | 11587.9978 | 12099.9092 | 13107.3835 | 13070.5994 | 12527.0129 | 11657.4788 | 10627.5254 | 9574.071 | 13107.3835
2016-01-22 | 8742.3428 | 8429.6783 | 8378.5894 | 8537.9869 | 9012.0925 | 10181.0079 | 12259.3067 | 13559.0099 | 13365.8936 | 13604.9899 | 13436.3964 | 13098.1875 | 12711.9549 | 12262.3721 | 11945.6205 | 11773.9616 | 11891.4662 | 12684.3669 | 14433.6529 | 14912.8673 | 14898.5624 | 14439.7835 | 13722.4945 | 12865.2218 | 14912.8673
2016-01-23 | 12350.2451 | 12225.588 | 12357.3975 | 12650.6482 | 13194.2347 | 14525.613 | 16781.7014 | 17871.9398 | 17252.7416 | 16219.7229 | 15236.7713 | 14147.5547 | 13237.1494 | 12477.9675 | 11968.0997 | 11706.5242 | 11727.9816 | 12343.0926 | 13813.4329 | 14081.139 | 13858.3912 | 13233.0623 | 12252.1543 | 11274.3116 | 17871.9398
2016-01-24 | 10559.0662 | 10306.6867 | 10290.3382 | 10429.3002 | 10840.0554 | 11969.1214 | 13951.3731 | 14989.5007 | 14979.2829 | 14644.1394 | 14213.9703 | 13589.6632 | 13034.8371 | 12557.6663 | 12165.3031 | 11938.4681 | 11997.7313 | 12536.2089 | 13736.7994 | 13765.4093 | 13454.7884 | 12930.6157 | 12271.5681 | 11450.0576 | 14989.5007
2016-01-25 | 10765.4656 | 10420.1042 | 10281.1422 | 10320.9916 | 10507.9772 | 10942.2334 | 11703.4589 | 12657.8006 | 13548.7921 | 13497.7031 | 12983.7482 | 12421.7696 | 11972.1868 | 11616.6076 | 11342.7708 | 11135.3496 | 11044.4113 | 11314.161 | 12232.7405 | 12137.715 | 11724.9162 | 11219.1355 | 10528.4128 | 9739.5993 | 13548.7921
2016-01-26 | 9060.1161 | 8611.555 | 8419.4605 | 8337.7182 | 8400.0467 | 8690.232 | 9240.971 | 9998.1094 | 11058.7162 | 11603.3245 | 11847.5297 | 11821.9852 | 11807.6803 | 11794.3972 | 11715.7202 | 11631.9343 | 11615.5858 | 11908.8365 | 12836.612 | 12805.9586 | 12235.8058 | 11426.5567 | 10484.4763 | 9384.0201 | 12836.612
2016-01-27 | 8476.6802 | 7938.2025 | 7702.1715 | 7638.8212 | 7852.3731 | 8607.4679 | 10177.9425 | 11051.5637 | 11414.2953 | 11838.3337 | 12319.5917 | 12635.3215 | 12892.8098 | 13104.3181 | 13201.3872 | 13324.0007 | 13379.1767 | 13480.3329 | 14287.5384 | 14194.5565 | 13450.7013 | 12341.0491 | 11107.7616 | 9761.0566 | 14287.5384
2016-01-28 | 8629.9471 | 8008.7053 | 7705.2369 | 7584.6669 | 7733.8467 | 8459.3099 | 9941.9115 | 10873.7742 | 11287.5947 | 11844.4644 | 12417.6825 | 12821.2853 | 13195.2565 | 13505.8774 | 13733.7341 | 13906.4148 | 13965.678 | 13993.266 | 14686.0323 | 14563.4188 | 13887.001 | 12761.0003 | 11586.976 | 10283.1858 | 14686.0323
2016-01-29 | 9141.8584 | 8498.1375 | 8184.4513 | 8072.0556 | 8225.3225 | 8990.6351 | 10482.4327 | 11478.6674 | 11907.8147 | 12492.2724 | 12924.485 | 13282.1077 | 11639.0868 | 13221.8227 | 13081.839 | 13138.0368 | 13344.4362 | 13884.9574 | 14564.4406 | 14396.8688 | 13931.9593 | 13059.3598 | 11989.557 | 10766.4873 | 14564.4406
2016-01-30 | 9866.2999 | 9325.7787 | 9055.0072 | 8995.744 | 9205.2087 | 10017.5232 | 11683.0233 | 12691.5193 | 13193.2129 | 13668.3402 | 13928.8939 | 13895.1752 | 13745.9955 | 13570.2494 | 13374.0678 | 13260.6503 | 13337.2838 | 13794.0191 | 14600.2029 | 14474.524 | 13900.2841 | 13060.3816 | 11889.4227 | 10675.549 | 14600.2029
2016-01-31 | 9768.2091 | 9241.9928 | 9026.3974 | 8934.4372 | 9076.4646 | 9844.8425 | 11406.1211 | 12340.0273 | 12712.9767 | 13190.1476 | 13537.5525 | 13729.647 | 13769.4964 | 13718.4074 | 13623.382 | 13678.558 | 13599.881 | 13725.5599 | 14315.1265 | 14087.2697 | 13463.9844 | 12671.0838 | 11748.4171 | 10678.6143 | 14315.1265
2016-02-01 | 9682.3796 | 9005.9618 | 8580.9016 | 8357.132 | 8316.2608 | 8513.4642 | 9034.5716 | 9788.6447 | 11140.4585 | 12408.4865 | 13252.4761 | 13714.3203 | 14054.5728 | 14258.9286 | 14386.651 | 14431.6093 | 14321.2571 | 14049.4639 | 14366.2154 | 14083.1826 | 13344.4362 | 12510.6644 | 11608.4334 | 10573.3711 | 14431.6093
2016-02-02 | 9553.6354 | 8864.9563 | 8424.5694 | 8177.2989 | 8090.4476 | 8171.1682 | 8512.4424 | 9106.0962 | 10607.0898 | 11985.4699 | 12835.5902 | 13372.0243 | 14038.2243 | 14508.2427 | 14839.2992 | 14991.5443 | 14973.1523 | 14678.8799 | 14673.771 | 13987.1354 | 13341.3709 | 12946.9641 | 12412.5736 | 11108.7834 | 14991.5443
2016-02-03 | 9928.6284 | 8947.7204 | 8565.575 | 8403.1121 | 8507.3335 | 9185.7949 | 10552.9355 | 11387.7291 | 12146.911 | 13111.4706 | 14075.0084 | 14742.2302 | 15260.2722 | 15661.8314 | 15954.0603 | 16072.5867 | 15871.2962 | 15598.4811 | 16022.5195 | 15814.0765 | 14922.0633 | 13893.1317 | 12611.8206 | 11225.2662 | 16072.5867
2016-02-04 | 10042.0459 | 9344.1707 | 8924.2195 | 8719.8636 | 8764.8219 | 9363.5845 | 10731.7468 | 11539.9742 | 12248.0672 | 13267.8028 | 14182.2952 | 14853.6041 | 15377.7768 | 15706.7897 | 15927.494 | 16054.1947 | 15936.69 | 15606.6554 | 16037.8462 | 15957.1256 | 15177.5081 | 14091.3568 | 12884.6356 | 11507.2773 | 16054.1947
2016-02-05 | 10342.449 | 9574.071 | 9160.2505 | 8941.5897 | 8979.3955 | 9644.5738 | 11080.1736 | 11893.5098 | 12608.7552 | 13677.5363 | 14609.3989 | 15304.2087 | 15739.4867 | 16043.9769 | 16230.9625 | 16145.133 | 15803.8588 | 15517.7606 | 15909.102 | 15695.5502 | 14913.8891 | 13853.2823 | 12567.8841 | 11188.4821 | 16230.9625
2016-02-06 | 10016.5014 | 9221.5572 | 8805.6931 | 8592.1412 | 8653.448 | 9266.5155 | 10687.8103 | 11506.2555 | 12249.0889 | 13103.2964 | 13846.1298 | 14387.6728 | 14827.0378 | 15235.7495 | 15406.3866 | 15509.5863 | 15411.4955 | 15286.8385 | 15723.1382 | 15613.8078 | 14846.4517 | 13804.2369 | 12545.4049 | 11122.0665 | 15723.1382
2016-02-07 | 9920.4542 | 9185.7949 | 8682.0578 | 8450.1139 | 8485.8762 | 9114.2704 | 10520.2386 | 11382.6202 | 11930.2938 | 12636.3433 | 13304.5869 | 13924.8068 | 14291.6256 | 14351.9105 | 14823.9725 | 14956.8038 | 14918.998 | 14821.929 | 14869.9526 | 14478.6111 | 13906.4148 | 12947.9859 | 12054.9509 | 10946.3205 | 14956.8038
2016-02-08 | 9930.672 | 9163.3158 | 8705.5587 | 8474.6366 | 8457.2664 | 8647.3173 | 9173.5336 | 9909.2146 | 11274.3116 | 12671.0838 | 13713.2985 | 14350.8887 | 14775.9489 | 14982.3483 | 15113.136 | 15031.3937 | 14848.4952 | 14578.7455 | 14748.3608 | 14401.9777 | 13681.6234 | 12865.2218 | 11969.1214 | 10997.4094 | 15113.136
2016-02-09 | 9973.5867 | 9220.5354 | 8763.8001 | 8525.7256 | 8472.5931 | 8634.0342 | 9014.136 | 9598.5937 | 10667.3748 | 11643.1739 | 12287.9166 | 12621.0166 | 12928.5721 | 13114.5359 | 13196.2783 | 13127.8191 | 12964.3344 | 12914.2672 | 13507.9209 | 13597.8375 | 12930.6157 | 12036.5589 | 11076.0864 | 9865.2781 | 13597.8375
2016-02-10 | 8861.8909 | 8294.8035 | 8059.7943 | 8021.9884 | 8213.0611 | 9009.0271 | 10574.3929 | 11482.7546 | 11872.0524 | 12356.3758 | 12891.7881 | 13240.2148 | 13563.097 | 13814.4547 | 13918.6761 | 14026.9847 | 14046.3985 | 13968.7433 | 14521.5259 | 14658.4443 | 13932.9811 | 12898.9405 | 11675.8708 | 10345.5143 | 14658.4443
2016-02-11 | 9278.7768 | 8612.5768 | 8289.6946 | 8183.4295 | 8321.3697 | 9071.3557 | 10635.6996 | 11537.9306 | 11995.6877 | 12607.7334 | 13157.4506 | 13662.2096 | 14086.2479 | 14460.2191 | 14686.0323 | 14918.998 | 14986.4354 | 14854.6259 | 15254.1415 | 15304.2087 | 14658.4443 | 13409.8301 | 12085.6043 | 10660.2223 | 15304.2087
2016-02-12 | 9424.8913 | 8739.2774 | 8319.3262 | 8143.5802 | 8236.5621 | 8899.6968 | 10373.1024 | 11181.3297 | 11805.6368 | 12603.6463 | 13298.4562 | 13858.3912 | 14274.2553 | 14613.486 | 14700.3372 | 14565.4624 | 14383.5857 | 14417.3044 | 15083.5044 | 14917.9762 | 14216.0139 | 13172.7773 | 11712.6549 | 10230.0533 | 15083.5044
2016-02-13 | 9152.0762 | 8470.5495 | 8152.7762 | 8029.1409 | 8172.19 | 8898.675 | 10438.4962 | 11387.7291 | 11886.3573 | 12204.1307 | 12488.1853 | 12588.3196 | 12643.4957 | 12627.1472 | 12570.9494 | 12483.0764 | 12395.2034 | 12397.2469 | 13117.6013 | 13396.547 | 12970.4651 | 12234.784 | 11247.7453 | 10118.6793 | 13396.547
2016-02-14 | 9228.7097 | 8788.3228 | 8640.1648 | 8690.232 | 9011.0707 | 10041.0241 | 12012.0362 | 13264.7375 | 13240.2148 | 12929.5939 | 12678.2362 | 12255.2196 | 11918.0325 | 11687.1104 | 11540.996 | 11535.8871 | 11531.8 | 11640.1085 | 12367.6153 | 12509.6426 | 12063.1251 | 11457.2101 | 10774.6616 | 9959.2818 | 13264.7375
2016-02-15 | 9251.1888 | 8800.5842 | 8561.4878 | 8473.6148 | 8511.4207 | 8807.7366 | 9387.0854 | 10203.487 | 11088.3478 | 11653.3917 | 11973.2086 | 12005.9055 | 11858.7693 | 11709.5895 | 11577.78 | 11528.7346 | 11501.1466 | 11574.7147 | 12141.8021 | 12274.6334 | 11847.5297 | 11281.4641 | 10620.3729 | 9764.122 | 12274.6334
2016-02-16 | 9041.7241 | 8631.9906 | 8577.8363 | 8626.8817 | 8725.9943 | 9158.2069 | 9919.4324 | 10950.4076 | 11782.1359 | 12024.2975 | 11908.8365 | 11640.1085 | 11487.8634 | 11376.4895 | 11325.4006 | 11343.7926 | 11406.1211 | 11522.6039 | 12168.3684 | 12393.1598 | 11894.5316 | 11223.2226 | 10511.0425 | 9558.7443 | 12393.1598
2016-02-17 | 8801.606 | 8391.8725 | 8256.9976 | 8299.9124 | 8566.5967 | 9297.1689 | 10502.8683 | 11598.2156 | 12205.1524 | 12437.0963 | 12541.3178 | 12565.8405 | 12603.6463 | 12673.1273 | 12745.6736 | 12850.9169 | 12906.093 | 12936.7463 | 13446.6142 | 13615.2077 | 12937.7681 | 11986.4917 | 10808.3803 | 9643.552 | 13615.2077
2016-02-18 | 8635.0559 | 8051.62 | 7847.2642 | 7794.1317 | 8005.64 | 8800.5842 | 10408.8646 | 11407.1429 | 11787.2448 | 12158.1506 | 12503.512 | 12786.5448 | 13032.7936 | 13294.3691 | 13538.5743 | 13770.5182 | 13853.2823 | 13727.6034 | 14062.747 | 14225.2099 | 13508.9427 | 12407.4647 | 11240.5929 | 9877.5394 | 14225.2099
2016-02-19 | 8803.6495 | 8158.9068 | 7867.6998 | 7749.1734 | 7891.2007 | 8615.6421 | 10137.0714 | 11006.6055 | 11520.5604 | 12106.0399 | 12696.6282 | 13200.3654 | 13594.7721 | 13973.8522 | 14335.5621 | 14679.9016 | 14763.6875 | 14558.3099 | 14747.3391 | 14832.1467 | 14131.2062 | 13057.3163 | 11812.7892 | 10440.5398 | 14832.1467
2016-02-20 | 9258.3413 | 8573.7492 | 8192.6256 | 7989.2915 | 8046.5111 | 8737.2339 | 10203.487 | 11097.5438 | 11840.3773 | 12707.8678 | 13523.2476 | 14077.0519 | 14584.8762 | 14980.3047 | 15258.2287 | 15498.3468 | 15531.0437 | 15303.187 | 15565.7842 | 15699.6373 | 15045.6986 | 14083.1826 | 12836.612 | 11544.0613 | 15699.6373
2016-02-21 | 10350.6232 | 9504.59 | 9060.1161 | 8838.39 | 8851.6731 | 9437.1526 | 10852.3168 | 11749.4389 | 12830.4813 | 13962.6127 | 14920.0198 | 15618.9167 | 16098.1312 | 16407.7303 | 16445.5361 | 16358.6849 | 15848.817 | 15427.844 | 15611.7643 | 15377.7768 | 14630.8562 | 13661.1878 | 12709.9114 | 11530.7782 | 16445.5361
2016-02-22 | 10400.6904 | 9512.7643 | 9031.5063 | 8722.929 | 8642.2084 | 8745.4081 | 9207.2523 | 9997.0876 | 11652.3699 | 13150.2982 | 14222.1446 | 15003.8056 | 15612.786 | 15943.8425 | 16072.5867 | 16129.8063 | 15921.3634 | 15382.8857 | 15291.9474 | 15077.3737 | 14243.6019 | 13350.5669 | 12378.8549 | 11244.68 | 16129.8063
2016-02-23 | 10156.4852 | 9364.6063 | 8855.7603 | 8558.4225 | 8423.5477 | 8472.5931 | 8770.9526 | 9455.5446 | 11049.5202 | 12611.8206 | 13819.5636 | 14725.8817 | 15770.14 | 15937.7118 | 16080.7609 | 16209.5051 | 16087.9134 | 15750.7262 | 15746.6391 | 15772.1836 | 15023.2195 | 13796.0626 | 12648.6046 | 11244.68 | 16209.5051
2016-02-24 | 9973.5867 | 9288.9946 | 8839.4118 | 8580.9016 | 8612.5768 | 9227.6879 | 10464.0407 | 11378.5331 | 12265.4374 | 13336.262 | 14318.1918 | 15009.9363 | 15685.3324 | 16146.1548 | 16429.1876 | 16646.8266 | 16452.6885 | 16146.1548 | 16440.4272 | 16499.6904 | 15531.0437 | 14298.778 | 12867.2654 | 11379.5549 | 16646.8266
2016-02-25 | 10081.8953 | 9278.7768 | 8795.4753 | 8528.7909 | 8549.2265 | 9171.49 | 10562.1315 | 11345.8361 | 12155.0853 | 13075.7083 | 13898.2406 | 14581.8108 | 15230.6406 | 15795.6845 | 16236.0714 | 16492.5379 | 16416.9263 | 15970.4088 | 16060.3253 | 16063.3907 | 15196.9219 | 13959.5473 | 12632.2561 | 11121.0447 | 16492.5379
2016-02-26 | 9837.6901 | 9027.4192 | 8527.7691 | 8294.8035 | 8312.1737 | 8856.782 | 10198.3781 | 11050.542 | 11755.5696 | 12539.2742 | 13573.3148 | 14259.9504 | 14871.9961 | 15288.882 | 15554.5446 | 15608.6989 | 15372.6679 | 15209.1833 | 15635.2652 | 15621.9821 | 14891.4099 | 13863.5001 | 12590.3632 | 11237.5275 | 15635.2652
2016-02-27 | 10060.4379 | 9377.8894 | 9012.0925 | 8840.4336 | 8894.5879 | 9491.3069 | 10885.0137 | 11647.261 | 12099.9092 | 12660.866 | 13271.8899 | 13143.1457 | 13749.0608 | 13831.8249 | 13801.1715 | 13725.5599 | 13561.0534 | 13829.7814 | 14325.3443 | 14413.2173 | 13807.3022 | 12759.9785 | 11527.7128 | 10290.3382 | 14413.2173
2016-02-28 | 9237.9057 | 8634.0342 | 8354.0667 | 8266.1937 | 8395.9596 | 9129.5971 | 10682.7014 | 11568.584 | 11845.4862 | 12015.1015 | 12148.9546 | 12189.8258 | 12198 | 12264.4156 | 12336.962 | 12438.1181 | 12501.4684 | 12418.7043 | 12707.8678 | 12879.5267 | 12326.7442 | 11599.2374 | 10733.7904 | 9747.7735 | 12879.5267
2016-02-29 | 9237.9057 | 8634.0342 | 8354.0667 | 8266.1937 | 8395.9596 | 9129.5971 | 10682.7014 | 11568.584 | 11845.4862 | 12015.1015 | 12148.9546 | 12189.8258 | 12198 | 12264.4156 | 12336.962 | 12438.1181 | 12501.4684 | 12418.7043 | 12707.8678 | 12879.5267 | 12326.7442 | 11599.2374 | 10733.7904 | 9747.7735 | 12879.5267
2016-03-01 | 8864.9563 | 8308.0866 | 8003.5964 | 7870.7651 | 7922.8759 | 8242.6927 | 8858.8256 | 9689.5321 | 10731.7468 | 11416.3389 | 11847.5297 | 12070.2776 | 12282.8077 | 12492.2724 | 12647.5828 | 12846.8298 | 12871.3525 | 12703.7807 | 12718.0856 | 12952.073 | 12317.5482 | 11605.3681 | 10786.9229 | 9794.7753 | 12952.073
2016-03-02 | 8918.0888 | 8363.2627 | 8048.5547 | 7766.5436 | 7724.6507 | 7883.0265 | 8270.2808 | 8942.6115 | 10248.4453 | 11332.553 | 12013.058 | 12504.5337 | 12880.5485 | 13248.389 | 13504.8556 | 13729.647 | 13802.1933 | 13630.5344 | 13700.0154 | 13949.3295 | 13238.1712 | 12275.6552 | 11172.1337 | 9954.1729 | 13949.3295
2016-03-03 | 9046.833 | 8295.8253 | 7886.0918 | 7732.8249 | 7820.6979 | 8487.9197 | 9840.7554 | 10691.8975 | 11455.1665 | 12302.2215 | 13086.9479 | 13660.166 | 14221.1228 | 14763.6875 | 15108.0271 | 15416.6044 | 15508.5646 | 15278.6642 | 15275.5989 | 15419.6698 | 14528.6783 | 13308.674 | 11967.0779 | 10472.2149 | 15508.5646
2016-03-04 | 9259.363 | 8483.8326 | 8059.7943 | 7845.2206 | 7892.2225 | 8506.3118 | 9863.2345 | 10745.03 | 11466.4061 | 12303.2432 | 13054.2509 | 13666.2967 | 14218.0574 | 14727.9253 | 15161.1596 | 15481.9983 | 15559.6535 | 15318.5136 | 15343.0363 | 15436.0182 | 14658.4443 | 13586.5979 | 12262.3721 | 10842.099 | 15559.6535
2016-03-05 | 9609.8333 | 8900.7185 | 8488.9415 | 8318.3044 | 8387.7854 | 9005.9618 | 10450.7576 | 11325.4006 | 12002.8402 | 12947.9859 | 13761.3222 | 14457.1538 | 15035.4808 | 15407.4084 | 15555.5664 | 15603.59 | 15413.5391 | 15165.2468 | 15336.9057 | 15422.7351 | 14749.3826 | 13709.2114 | 12443.227 | 11026.0193 | 15603.59
2016-03-06 | 9838.7118 | 9142.8802 | 8706.5805 | 8522.6602 | 8552.2918 | 9145.9455 | 10504.9119 | 11372.4024 | 12312.4393 | 13268.8246 | 13972.8304 | 14553.201 | 14938.4118 | 14859.7348 | 14680.9234 | 13606.0117 | 13080.8172 | 13167.6684 | 13762.3439 | 13882.9139 | 13324.0007 | 12428.9221 | 11383.642 | 10192.2474 | 14938.4118
2016-03-07 | 9157.1851 | 8515.5078 | 8247.8016 | 8124.1664 | 8238.6056 | 8903.7839 | 10323.0352 | 11190.5257 | 11971.165 | 12612.8423 | 13137.0151 | 13373.0461 | 13495.6596 | 13506.8991 | 13496.6813 | 13505.8774 | 13416.9826 | 13177.8862 | 13299.478 | 13386.3292 | 12882.592 | 12011.0144 | 11083.2389 | 9888.779 | 13506.8991
2016-03-08 | 9079.5299 | 8477.702 | 8199.778 | 8097.6001 | 8175.2553 | 8437.8526 | 9100.9873 | 10024.6756 | 10983.1045 | 11529.7564 | 11686.0886 | 11673.8273 | 11648.2828 | 11638.065 | 11716.742 | 11833.2248 | 11895.5533 | 11838.3337 | 12013.058 | 12321.6353 | 11790.3101 | 11148.6328 | 10358.7974 | 9560.7879 | 12321.6353
2016-03-09 | 8656.5133 | 0 | 8145.6237 | 7868.7216 | 7770.6308 | 7898.3531 | 8258.0194 | 8778.105 | 9535.2434 | 10465.0625 | 11220.1573 | 11551.2138 | 11998.753 | 12246.0236 | 12426.8785 | 12689.4758 | 12960.2473 | 13090.0132 | 12895.8752 | 12952.073 | 13258.6068 | 12496.3595 | 11501.1466 | 10078.8299 | 13258.6068
2016-03-10 | 8898.675 | 8114.9703 | 7734.8685 | 7616.3421 | 7755.3041 | 8380.6329 | 9738.5775 | 10738.8993 | 11037.2588 | 11621.7165 | 12323.6788 | 12744.6519 | 13218.7574 | 13533.4654 | 14002.462 | 14456.132 | 14830.1032 | 14855.6477 | 14546.0486 | 14463.2845 | 14587.9415 | 13521.204 | 12332.8748 | 10838.0119 | 14855.6477
2016-03-11 | 9450.4357 | 8589.0759 | 8111.905 | 7874.8522 | 7873.8304 | 8475.6584 | 9820.3198 | 10780.7922 | 11039.3024 | 11724.9162 | 12333.8966 | 12898.9405 | 13389.3945 | 13838.9774 | 14260.9722 | 14733.0342 | 15130.5063 | 15246.9891 | 14976.2176 | 14841.3428 | 14978.2612 | 14057.6381 | 12808.0022 | 11184.395 | 15246.9891
2016-03-12 | 9912.2799 | 9039.6805 | 8587.0323 | 8386.7636 | 8431.7219 | 9038.6587 | 10440.5398 | 10383.3201 | 11610.477 | 12433.0092 | 13434.3528 | 14234.4059 | 14853.6041 | 15273.5554 | 15499.3686 | 15934.6465 | 16196.222 | 16074.6302 | 15640.3741 | 15459.5192 | 15537.1744 | 14586.9197 | 13386.3292 | 11912.9236 | 16196.222
2016-03-13 | 10547.8266 | 9634.356 | 9089.7477 | 8799.5624 | 8723.9507 | 9179.6643 | 10379.233 | 11132.2843 | 11351.9668 | 11999.7748 | 12482.0546 | 12764.0657 | 12920.3979 | 13018.4887 | 13085.9261 | 13156.4289 | 13293.3473 | 13260.6503 | 12884.6356 | 12838.6555 | 13093.0786 | 12299.1561 | 11233.4404 | 9947.0204 | 13293.3473
2016-03-14 | 8865.978 | 8254.9541 | 7914.7016 | 7829.8939 | 8000.5311 | 8732.125 | 10366.9717 | 11537.9306 | 11799.5061 | 12031.45 | 12208.2178 | 12251.1325 | 12232.7405 | 12278.7205 | 12337.9837 | 12446.2923 | 12601.6028 | 12592.4068 | 12352.2886 | 12331.8531 | 12554.6009 | 11930.2938 | 11061.7815 | 10061.4597 | 12601.6028
2016-03-15 | 8955.8946 | 8294.8035 | 7891.2007 | 7709.324 | 7744.0645 | 7992.3568 | 8511.4207 | 9380.9548 | 10357.7757 | 11250.8107 | 11930.2938 | 12318.5699 | 12597.5157 | 12830.4813 | 13103.2964 | 13383.2638 | 13685.7105 | 13737.8212 | 13401.6559 | 13075.7083 | 13150.2982 | 12436.0745 | 11618.6512 | 10466.0843 | 13737.8212
2016-03-16 | 9443.2833 | 8732.125 | 8276.4115 | 8020.9667 | 7917.767 | 7984.1826 | 8321.3697 | 8847.586 | 9903.0839 | 11267.1591 | 12225.588 | 12925.5068 | 13479.3111 | 13902.3277 | 14312.0611 | 14592.0286 | 14721.7946 | 14676.8363 | 14314.1047 | 14176.1645 | 14421.3915 | 13654.0353 | 12685.3887 | 11319.2699 | 14721.7946
2016-03-17 | 10118.6793 | 9324.7569 | 8879.2612 | 8717.8201 | 8805.6931 | 9439.1962 | 10742.9864 | 11716.742 | 12239.8929 | 13269.8464 | 14385.6292 | 15146.8547 | 15694.5284 | 15972.4523 | 16117.545 | 16219.7229 | 16250.3763 | 16024.5631 | 15767.0747 | 15920.3416 | 15909.102 | 15051.8293 | 14035.159 | 12636.3433 | 16250.3763
2016-03-18 | 11393.8598 | 10579.5017 | 10164.6594 | 9964.3907 | 9932.7155 | 10382.2984 | 11524.6475 | 12198 | 12083.5607 | 12453.4448 | 12814.1328 | 13010.3144 | 13177.8862 | 13409.8301 | 13712.2767 | 14033.1154 | 14370.3025 | 14474.524 | 14186.3823 | 14043.3332 | 14216.0139 | 13335.2402 | 12126.4754 | 10629.5689 | 14474.524
2016-03-19 | 9312.4956 | 8524.7038 | 8102.709 | 7914.7016 | 7964.7688 | 8577.8363 | 9925.5631 | 10834.9465 | 11208.9177 | 11938.4681 | 12656.7788 | 13185.0387 | 13533.4654 | 13957.5038 | 14374.3897 | 14774.9271 | 15025.263 | 15040.5897 | 14635.9651 | 14361.1065 | 14552.1792 | 13695.9283 | 12544.3831 | 11082.2171 | 15040.5897
2016-03-20 | 9832.5812 | 9004.94 | 8566.5967 | 8318.3044 | 8333.6311 | 8892.5443 | 10193.2692 | 11116.9576 | 11516.4733 | 12217.4138 | 12949.0077 | 13494.6378 | 13920.7197 | 14364.1719 | 14765.7311 | 15084.5262 | 15292.9692 | 15219.4011 | 14858.713 | 14562.397 | 14718.7293 | 13728.6252 | 12505.5555 | 11087.326 | 15292.9692
2016-03-21 | 9722.229 | 8840.4336 | 8295.8253 | 7995.4222 | 7988.2697 | 8449.0921 | 9537.287 | 10490.607 | 11087.326 | 11978.3175 | 12875.4396 | 13578.4237 | 14136.3151 | 14691.1412 | 15217.3575 | 15644.4612 | 15811.0112 | 15647.5265 | 15064.0906 | 14631.878 | 14667.6403 | 13811.3893 | 12878.5049 | 11715.7202 | 15811.0112
2016-03-22 | 10532.4999 | 9737.5557 | 9191.9256 | 8864.9563 | 8733.1467 | 8873.1305 | 9303.2995 | 9862.2128 | 10804.2932 | 12257.2632 | 13337.2838 | 13906.4148 | 14402.9995 | 14779.0142 | 15036.5026 | 15315.4483 | 15673.071 | 15665.9186 | 15210.205 | 14657.4225 | 14593.0504 | 13716.3639 | 12660.866 | 11386.7073 | 15673.071
2016-03-23 | 10189.1821 | 9280.8204 | 8733.1467 | 8412.3081 | 8259.0412 | 8324.4351 | 8620.751 | 9076.4646 | 10079.8517 | 11561.4316 | 12841.7209 | 13803.2151 | 14714.6421 | 15502.4339 | 16035.8026 | 16480.2766 | 16672.3711 | 16650.9137 | 16268.7683 | 15802.837 | 15878.4486 | 14859.7348 | 13673.4491 | 12185.7386 | 16672.3711
2016-03-24 | 10862.5346 | 9913.3017 | 9277.7551 | 9012.0925 | 8977.352 | 9425.913 | 10390.4726 | 11227.3098 | 11814.8328 | 12642.4739 | 13291.3037 | 13738.843 | 13910.5019 | 13891.0881 | 13709.2114 | 13589.6632 | 13601.9246 | 13675.4927 | 13663.2313 | 13736.7994 | 13628.4909 | 12775.3052 | 11789.2883 | 10502.8683 | 13910.5019
2016-03-25 | 9413.6517 | 8607.4679 | 8097.6001 | 7910.6145 | 7964.7688 | 8456.2446 | 9593.4848 | 10493.6723 | 11034.1935 | 11829.1377 | 12384.9856 | 12938.7899 | 13371.0025 | 13670.3838 | 13947.286 | 14166.9685 | 14355.9976 | 14371.3243 | 14083.1826 | 13736.7994 | 13864.5218 | 12929.5939 | 11664.6312 | 10198.3781 | 14371.3243
2016-03-26 | 8899.6968 | 8145.6237 | 7720.5636 | 7573.4274 | 7688.8884 | 8294.8035 | 9620.0511 | 10741.9646 | 11386.7073 | 11714.6984 | 11974.2303 | 11976.2739 | 11852.6386 | 11701.4153 | 11603.3245 | 11548.1484 | 11647.261 | 11715.7202 | 11680.9797 | 12011.0144 | 12497.3813 | 11880.2267 | 10906.4711 | 9837.6901 | 12497.3813
2016-03-27 | 8866.9998 | 8291.7381 | 7994.4004 | 7924.9194 | 8060.816 | 8656.5133 | 9913.3017 | 10799.1843 | 11237.5275 | 11852.6386 | 12154.0635 | 12302.2215 | 12370.6807 | 12426.8785 | 12419.7261 | 12406.4429 | 12428.9221 | 12413.5954 | 12335.9402 | 12613.8641 | 12870.3307 | 12231.7187 | 11299.8561 | 10165.6812 | 12870.3307
2016-03-28 | 9134.706 | 8435.809 | 8070.0121 | 7874.8522 | 7952.5074 | 8467.4842 | 9564.875 | 10471.1932 | 11117.9794 | 11993.6441 | 12866.2436 | 13380.1985 | 13733.7341 | 13940.1335 | 14107.7053 | 14211.9268 | 14193.5347 | 13972.8304 | 13647.9047 | 13650.97 | 13785.8449 | 13177.8862 | 12395.2034 | 11348.9015 | 14211.9268
2016-03-29 | 10335.2965 | 9631.2907 | 9172.5118 | 8934.4372 | 8884.3701 | 9051.9419 | 9494.3722 | 10137.0714 | 11093.4567 | 12393.1598 | 13502.812 | 14263.0157 | 14595.094 | 14771.8618 | 14735.0777 | 14556.2664 | 14321.2571 | 14075.0084 | 13688.7758 | 13578.4237 | 13303.5651 | 12459.5755 | 11665.653 | 10638.7649 | 14771.8618
2016-03-30 | 9602.6808 | 8866.9998 | 8349.9796 | 8093.513 | 7999.5093 | 8097.6001 | 8488.9415 | 8975.3084 | 9865.2781 | 11017.845 | 11812.7892 | 12211.2831 | 12392.138 | 12528.0347 | 12656.7788 | 12765.0874 | 12874.4178 | 12849.8951 | 12589.3414 | 12405.4212 | 12748.739 | 11958.9037 | 10899.3186 | 9592.463 | 12874.4178
2016-03-31 | 8486.898 | 7894.266 | 7512.1206 | 7388.4853 | 7531.5344 | 8336.6964 | 9778.4269 | 10690.8757 | 10998.4312 | 11424.5131 | 11863.8782 | 12214.3485 | 12464.6844 | 12762.0221 | 13023.5976 | 13241.2365 | 13343.4145 | 13233.0623 | 13105.3399 | 13262.6939 | 13549.8139 | 12669.0402 | 11513.4079 | 10097.222 | 13549.8139
2016-04-01 | 8892.5443 | 8177.2989 | 7812.5237 | 7663.3439 | 7765.5219 | 8433.7654 | 10002.1965 | 10954.4947 | 11294.7472 | 11756.5914 | 12204.1307 | 12589.3414 | 12897.9187 | 13296.4126 | 13775.6271 | 14313.0829 | 14801.4934 | 14976.2176 | 14710.555 | 14237.4713 | 14348.8452 | 13406.7648 | 12011.0144 | 10483.4545 | 14976.2176
2016-04-02 | 9191.9256 | 8393.9161 | 7959.6599 | 7735.8903 | 7794.1317 | 8464.4188 | 9903.0839 | 10706.2024 | 11077.1082 | 11768.8527 | 12349.2233 | 12873.396 | 13229.997 | 13668.3402 | 14332.4967 | 14926.1504 | 15371.6462 | 15557.61 | 15207.1397 | 14728.947 | 14827.0378 | 13880.8703 | 12468.7715 | 10927.9285 | 15557.61
2016-04-03 | 9579.1799 | 8724.9725 | 8240.6492 | 8040.3805 | 8084.317 | 8759.713 | 10076.7864 | 10859.4692 | 11382.6202 | 12168.3684 | 12907.1147 | 13517.1169 | 14062.747 | 14582.8326 | 15293.9909 | 15760.944 | 16088.9351 | 15958.1474 | 15592.3505 | 15056.9382 | 15336.9057 | 14357.0194 | 12919.3761 | 11349.9233 | 16088.9351
2016-04-04 | 9969.4996 | 9110.1833 | 8577.8363 | 8316.2608 | 8286.6292 | 8871.0869 | 10285.2293 | 11030.1064 | 11603.3245 | 12507.5991 | 13372.0243 | 14079.0955 | 14620.6385 | 15174.4428 | 15705.768 | 16167.6121 | 16539.5398 | 16504.7993 | 16050.1075 | 15258.2287 | 15089.6351 | 14237.4713 | 13114.5359 | 11795.419 | 16539.5398
2016-04-05 | 10517.1732 | 9600.6373 | 9003.9182 | 8633.0124 | 8482.8108 | 8535.9434 | 8972.2431 | 9520.9385 | 10822.6852 | 12303.2432 | 13434.3528 | 14335.5621 | 15067.156 | 15807.9459 | 16315.7701 | 16689.7413 | 16830.7468 | 16738.7867 | 16118.5667 | 15297.0563 | 15206.1179 | 14315.1265 | 13242.2583 | 11999.7748 | 16830.7468
2016-04-06 | 10709.2677 | 9757.9913 | 9071.3557 | 8659.5786 | 8487.9197 | 8513.4642 | 8807.7366 | 9220.5354 | 10585.6324 | 12171.4337 | 13428.2221 | 14328.4096 | 15142.7676 | 15852.9042 | 16503.7775 | 16918.6199 | 17119.9104 | 17105.6054 | 16617.195 | 15955.0821 | 15978.583 | 14942.4989 | 13647.9047 | 12027.3629 | 17119.9104
2016-04-07 | 10769.5527 | 9894.9097 | 9413.6517 | 9179.6643 | 9244.0363 | 9890.8226 | 11232.4187 | 11992.6224 | 12666.9966 | 13909.4801 | 15133.5716 | 16192.1348 | 17062.6907 | 17833.1122 | 18438.0055 | 18893.719 | 19172.6647 | 19061.2908 | 18510.5518 | 18027.2503 | 17882.1576 | 16696.8938 | 15225.5317 | 13692.8629 | 19172.6647
2016-04-08 | 12391.1163 | 11410.2082 | 10687.8103 | 10308.7303 | 10314.8609 | 10859.4692 | 12239.8929 | 12970.4651 | 13568.2059 | 14409.1302 | 15382.8857 | 16188.0477 | 16659.0879 | 16904.3149 | 16855.2695 | 16595.7376 | 16735.7214 | 16174.7646 | 15096.7876 | 14573.6366 | 14644.1394 | 13658.1225 | 12277.6988 | 10799.1843 | 16904.3149
2016-04-09 | 9653.7698 | 8886.4136 | 8440.9179 | 8216.1265 | 8200.7998 | 8764.8219 | 10107.4398 | 10738.8993 | 11060.7597 | 11707.546 | 12209.2396 | 12475.9239 | 12634.2997 | 12766.1092 | 12979.6611 | 13240.2148 | 13488.5071 | 13646.8829 | 13476.2458 | 13235.1059 | 13602.9464 | 12787.5666 | 11471.515 | 10077.8082 | 13646.8829
2016-04-10 | 8914.0017 | 8227.366 | 7827.8504 | 7679.6924 | 7751.2169 | 8389.8289 | 9820.3198 | 10574.3929 | 10930.9938 | 11519.5386 | 12061.0816 | 12452.423 | 12717.0638 | 13020.5322 | 13348.5234 | 13704.1025 | 13949.3295 | 13943.1988 | 13702.059 | 13532.4436 | 13888.0228 | 13016.4451 | 11793.3754 | 10370.037 | 13949.3295
2016-04-11 | 9201.1216 | 8410.2645 | 7997.4657 | 7821.7197 | 7879.9611 | 8458.2881 | 9841.7772 | 10617.3076 | 11151.6981 | 12016.1233 | 12791.6537 | 13318.8918 | 13682.6452 | 14044.355 | 14373.3679 | 14493.9378 | 14531.7437 | 14346.8016 | 14004.5056 | 13740.8866 | 13923.785 | 13281.0859 | 12386.0074 | 11244.68 | 14531.7437
2016-04-12 | 10119.7011 | 9323.7351 | 8757.6694 | 8432.7437 | 8295.8253 | 8401.0685 | 8878.2394 | 9470.8713 | 10778.7487 | 12204.1307 | 13287.2166 | 14117.9231 | 14675.8145 | 15171.3774 | 15467.6934 | 15737.4431 | 15837.5775 | 15726.2035 | 15132.5498 | 14443.8707 | 14438.7618 | 13754.1697 | 12682.3233 | 11576.7582 | 15837.5775
2016-04-13 | 10483.4545 | 9628.2253 | 9090.7695 | 8728.0379 | 8575.7928 | 8631.9906 | 8948.7422 | 9397.3032 | 10570.3057 | 11984.4481 | 13046.0767 | 13801.1715 | 14458.1756 | 14891.4099 | 15072.2649 | 15217.3575 | 15255.1633 | 15183.6388 | 14840.321 | 14737.1213 | 15049.7857 | 14273.2335 | 13160.516 | 11759.6567 | 15255.1633
2016-04-14 | 10528.4128 | 9724.2726 | 9276.7333 | 9020.2667 | 9043.7676 | 9609.8333 | 10955.5165 | 11717.7638 | 12537.2307 | 13777.6706 | 14915.9326 | 15896.8407 | 16682.5889 | 17449.945 | 18056.8819 | 18569.815 | 18837.5212 | 18749.6482 | 18185.626 | 17473.446 | 17374.3334 | 16294.3128 | 14794.3409 | 13092.0568 | 18837.5212
2016-04-15 | 11632.9561 | 10692.9192 | 10107.4398 | 9702.8152 | 9625.16 | 10126.8536 | 11453.123 | 12152.0199 | 13137.0151 | 14512.3299 | 15653.6572 | 16688.7195 | 17436.6619 | 17969.0089 | 18178.4736 | 18339.9147 | 18222.4101 | 17509.2082 | 17143.4113 | 16634.5652 | 16672.3711 | 15692.4848 | 14200.6872 | 12570.9494 | 18339.9147
2016-04-16 | 11217.092 | 10291.36 | 9708.9459 | 9407.521 | 9344.1707 | 9822.3634 | 11048.4984 | 11651.3481 | 12082.5389 | 12745.6736 | 13299.478 | 13678.558 | 14071.943 | 14524.5912 | 14851.5605 | 15095.7658 | 15243.9238 | 15189.7695 | 14935.3464 | 14875.0615 | 15155.029 | 14516.417 | 13299.478 | 11820.9635 | 15243.9238
2016-04-17 | 10630.5907 | 9849.9514 | 9393.2161 | 9154.1198 | 9187.8385 | 9765.1437 | 11078.13 | 11825.0506 | 12480.011 | 13455.8102 | 14311.0394 | 14860.7566 | 15043.655 | 15184.6606 | 15237.7931 | 15157.0725 | 15034.459 | 14777.9924 | 14538.8961 | 14393.8035 | 14575.6802 | 14029.0283 | 13047.0985 | 11781.1141 | 15237.7931
2016-04-18 | 10636.7214 | 9832.5812 | 9310.452 | 9023.332 | 8978.3738 | 9433.0655 | 10363.9063 | 11144.5456 | 12175.5208 | 13457.8537 | 14498.0249 | 15187.7259 | 15612.786 | 16073.6085 | 16297.3781 | 16257.5287 | 16168.6339 | 16063.3907 | 15618.9167 | 15092.7004 | 15121.3103 | 14491.8943 | 13590.685 | 12528.0347 | 16297.3781
2016-04-19 | 11369.3371 | 10598.9156 | 10060.4379 | 9708.9459 | 9589.3977 | 9700.7716 | 9914.3235 | 10237.2057 | 11163.9594 | 12695.6065 | 13941.1553 | 14794.3409 | 15480.9765 | 15982.6701 | 16256.5069 | 16441.449 | 16411.8174 | 16038.868 | 15312.383 | 14421.3915 | 14263.0157 | 13453.7666 | 12496.3595 | 11156.807 | 16441.449
2016-04-20 | 9941.9115 | 9033.5498 | 8414.3516 | 8091.4694 | 7955.5728 | 8027.0973 | 8354.0667 | 8740.2992 | 9830.5376 | 10960.6254 | 11585.9543 | 12096.8438 | 12439.1399 | 12685.3887 | 12850.9169 | 12980.6828 | 13064.4687 | 12976.5957 | 12754.8696 | 12628.169 | 13071.6212 | 12576.0583 | 11580.8454 | 10266.8373 | 13071.6212
2016-04-21 | 9110.1833 | 8352.0231 | 7947.3986 | 7750.1952 | 7811.5019 | 8418.4388 | 9697.7063 | 10383.3201 | 10946.3205 | 11665.653 | 12336.962 | 12846.8298 | 13361.8065 | 13776.6488 | 14245.6455 | 14616.5513 | 14914.9109 | 14888.3446 | 14659.4661 | 14341.6927 | 14585.898 | 13720.451 | 12418.7043 | 10999.453 | 14914.9109
2016-04-22 | 9670.1183 | 8781.1704 | 8349.9796 | 8085.3387 | 8090.4476 | 8748.4734 | 10087.0042 | 10669.4183 | 11263.072 | 11990.5788 | 12745.6736 | 13491.5724 | 14051.5074 | 14506.1992 | 14975.1958 | 15542.2833 | 15933.6247 | 16007.1928 | 15707.8115 | 15252.098 | 15457.4756 | 14545.0268 | 13082.8608 | 11461.2972 | 16007.1928
2016-04-23 | 10121.7447 | 9270.6026 | 8734.1685 | 8409.2427 | 8357.132 | 8897.6532 | 10131.9625 | 9439.1962 | 11485.8199 | 12317.5482 | 13110.4488 | 13697.9718 | 14396.8688 | 15235.7495 | 16124.6974 | 16789.8757 | 17269.0901 | 17389.6601 | 17017.7324 | 16305.5523 | 16230.9625 | 15449.3014 | 14013.7016 | 12078.4518 | 17389.6601
2016-04-24 | 10747.0735 | 9853.0167 | 9021.2885 | 8664.6875 | 8675.9271 | 9005.9618 | 10207.5741 | 10915.6671 | 11693.2411 | 12796.7626 | 13897.2188 | 14817.8418 | 15656.7226 | 16400.5778 | 17023.8631 | 17631.8217 | 17983.3138 | 17937.3337 | 17420.3134 | 16610.0425 | 16542.6051 | 15599.5029 | 14093.4004 | 12477.9675 | 17983.3138
2016-04-25 | 11033.1717 | 9987.8916 | 9330.8876 | 8949.7639 | 8860.8691 | 9350.3014 | 10540.6741 | 11211.9831 | 12046.7767 | 13186.0605 | 14389.7164 | 15437.04 | 16346.4235 | 17181.2171 | 17899.5279 | 18505.4429 | 18836.4994 | 18746.5828 | 18051.773 | 17031.0156 | 16746.9609 | 15822.2508 | 14502.1121 | 13047.0985 | 18836.4994
2016-04-26 | 11577.78 | 10471.1932 | 9745.7299 | 9274.6897 | 9003.9182 | 9022.3103 | 9324.7569 | 9916.3671 | 11386.7073 | 13009.2927 | 14470.4369 | 15719.0511 | 16692.8067 | 17427.4659 | 17867.8527 | 18259.1942 | 18460.4847 | 18340.9365 | 17668.6058 | 16637.6306 | 16348.4671 | 15496.3032 | 14339.6492 | 13061.4034 | 18460.4847
2016-04-27 | 11812.7892 | 10828.8159 | 10088.026 | 9643.552 | 9357.4538 | 9307.3867 | 9470.8713 | 9931.6937 | 11550.192 | 13378.155 | 14894.4753 | 16113.4578 | 17055.5383 | 17816.7638 | 18321.5227 | 18751.6917 | 18922.3288 | 18807.8896 | 18207.0834 | 17348.7889 | 17224.1318 | 16292.2692 | 14822.9507 | 13339.3273 | 18922.3288
2016-04-28 | 12038.6024 | 11144.5456 | 10573.3711 | 10215.7484 | 10185.095 | 10749.1171 | 11942.5552 | 12641.4522 | 13568.2059 | 14844.4081 | 16271.8336 | 17459.141 | 18349.1107 | 19106.2491 | 19731.578 | 20210.7924 | 20337.493 | 20287.4258 | 19722.382 | 18865.1092 | 18618.8604 | 17480.5984 | 15835.5339 | 14174.1209 | 20337.493
2016-04-29 | 12812.0893 | 11848.5515 | 11219.1355 | 10854.3604 | 10793.0536 | 11293.7254 | 12416.6607 | 13101.2528 | 14200.6872 | 15570.8931 | 16919.6416 | 18050.7512 | 18878.3923 | 19541.527 | 20001.3277 | 20327.2752 | 20259.8378 | 20023.8068 | 19554.8102 | 18784.3887 | 18490.1162 | 17416.2263 | 15826.3379 | 14166.9685 | 20327.2752
2016-04-30 | 12767.131 | 11886.3573 | 11311.0956 | 10989.2352 | 10968.7996 | 11462.319 | 12610.7988 | 13289.2602 | 14349.867 | 15718.0293 | 17047.364 | 18090.6006 | 18858.9785 | 19523.135 | 19927.7596 | 20205.6835 | 20061.6126 | 19270.7556 | 18680.1672 | 18043.5987 | 17999.6622 | 17036.1245 | 15516.7388 | 13930.9375 | 20205.6835
2016-05-01 | 12542.3396 | 11629.8908 | 11018.8668 | 10690.8757 | 10597.8938 | 11140.4585 | 12357.3975 | 13069.5776 | 14035.159 | 15416.6044 | 16818.4855 | 17867.8527 | 18695.4939 | 19398.4779 | 19843.9737 | 20066.7215 | 19955.3476 | 19363.7375 | 18456.3975 | 17752.3917 | 17686.9978 | 16638.6524 | 15215.3139 | 13701.0372 | 20066.7215
2016-05-02 | 12407.4647 | 11499.103 | 10913.6235 | 10554.979 | 10460.9754 | 10974.9303 | 12150.9981 | 12882.592 | 13745.9955 | 14991.5443 | 16049.0858 | 16838.9211 | 17295.6564 | 17821.8727 | 18198.9092 | 18396.1126 | 18273.4991 | 17902.5932 | 17331.4186 | 16553.8447 | 16538.518 | 15427.844 | 14305.9305 | 13093.0786 | 18396.1126
2016-05-03 | 11892.488 | 10976.9739 | 10361.8628 | 9987.8916 | 9796.8189 | 9902.0621 | 10260.7066 | 10820.6416 | 11915.9889 | 13252.4761 | 14330.4532 | 15062.0471 | 15397.1906 | 15557.61 | 15467.6934 | 15055.9164 | 14103.6182 | 13733.7341 | 13392.4599 | 13298.4562 | 13531.4218 | 13102.2746 | 12375.7896 | 11454.1447 | 15557.61
2016-05-04 | 10504.9119 | 9756.9695 | 9291.0382 | 8975.3084 | 8876.1958 | 8878.2394 | 8997.7876 | 9142.8802 | 10203.487 | 11399.9904 | 12331.8531 | 12994.9878 | 13666.2967 | 14240.5366 | 14736.0995 | 15287.8603 | 15715.9857 | 15932.6029 | 15745.6173 | 15074.3084 | 14846.4517 | 13969.7651 | 12829.4595 | 11234.4622 | 15932.6029
2016-05-05 | 9967.456 | 8973.2649 | 8587.0323 | 8309.1084 | 8317.2826 | 8893.5661 | 10025.6974 | 10722.5508 | 11538.9524 | 12604.6681 | 13691.8412 | 14597.1375 | 15450.3232 | 16229.9407 | 16945.1861 | 17543.9487 | 18067.0997 | 18140.6678 | 17720.7165 | 16349.4888 | 16388.3165 | 15354.2759 | 13384.2856 | 12071.2994 | 18140.6678
2016-05-06 | 10624.46 | 9714.0548 | 9102.009 | 8738.2556 | 8652.4262 | 9149.0109 | 10296.4689 | 10995.3659 | 11833.2248 | 12998.0531 | 14153.6854 | 15269.4682 | 16312.7048 | 17098.453 | 17840.2647 | 18478.8767 | 18884.523 | 18857.9568 | 18355.2414 | 17010.58 | 17176.1082 | 16170.6775 | 14638.0087 | 12897.9187 | 18884.523
2016-05-07 | 11513.4079 | 10564.1751 | 10012.4143 | 9645.5956 | 9565.8968 | 10037.9588 | 11170.0901 | 11858.7693 | 12838.6555 | 14011.6581 | 15282.7514 | 16325.9879 | 17247.6328 | 18086.5135 | 18841.6083 | 19213.5359 | 19487.3727 | 19410.7393 | 18807.8896 | 17928.1377 | 17714.5858 | 16849.1389 | 15280.7078 | 13650.97 | 19487.3727
2016-05-08 | 12195.9564 | 11278.3987 | 10693.941 | 10267.8591 | 10167.7247 | 10608.1116 | 11705.5024 | 12342.0709 | 13376.1114 | 14595.094 | 15813.0548 | 16806.2241 | 17643.0613 | 18427.7877 | 19031.6592 | 19564.0062 | 19885.8666 | 19796.9718 | 19280.9733 | 18340.9365 | 17980.2484 | 17024.8849 | 15563.7406 | 14013.7016 | 19885.8666
2016-05-09 | 12405.4212 | 11390.7944 | 10816.5545 | 10377.1895 | 10268.8809 | 10725.6162 | 11817.8981 | 12467.7497 | 13447.6359 | 14677.8581 | 15855.9695 | 16810.3113 | 17627.7346 | 18353.1978 | 19002.0276 | 19480.2203 | 19719.3166 | 19482.2638 | 18743.5175 | 17701.3027 | 17263.9812 | 16378.0987 | 15222.4664 | 13938.09 | 19719.3166
2016-05-10 | 12652.6917 | 11737.1776 | 11121.0447 | 10679.6361 | 10467.106 | 10521.2603 | 10742.9864 | 11321.3134 | 12865.2218 | 14436.7182 | 15578.0456 | 16444.5143 | 17319.1573 | 17887.2665 | 18254.0853 | 18523.835 | 18508.5083 | 18310.2831 | 17744.2174 | 16739.8085 | 16836.8775 | 16084.848 | 15092.7004 | 13889.0445 | 18523.835
2016-05-11 | 12687.4322 | 11803.5932 | 11151.6981 | 10731.7468 | 10526.3692 | 10473.2367 | 10556.0008 | 10915.6671 | 12164.2813 | 13670.3838 | 14856.6694 | 15766.0529 | 16560.9971 | 17231.2843 | 17722.7601 | 17965.9435 | 18056.8819 | 17806.546 | 17283.395 | 16526.2566 | 16540.5616 | 16022.5195 | 14850.5388 | 13360.7847 | 18056.8819
2016-05-12 | 11973.2086 | 11066.8904 | 10502.8683 | 10206.5523 | 10181.0079 | 10698.0281 | 11811.7675 | 12465.7061 | 13372.0243 | 14658.4443 | 15945.8861 | 16969.7088 | 17802.4589 | 18451.2886 | 18923.3506 | 19334.1059 | 19486.351 | 19359.6503 | 18932.5466 | 18286.7822 | 18106.9491 | 17075.9738 | 15554.5446 | 14007.5709 | 19486.351
2016-05-13 | 12644.5175 | 11771.9181 | 11152.7199 | 10772.618 | 10689.8539 | 11180.3079 | 12271.5681 | 12893.8316 | 13755.1915 | 15021.1759 | 16201.3309 | 17089.257 | 17891.3536 | 18418.5917 | 18806.8678 | 19128.7282 | 19294.2565 | 19110.3362 | 18570.8368 | 17835.1558 | 17720.7165 | 16916.5763 | 15478.933 | 13871.6743 | 19294.2565
2016-05-14 | 12632.2561 | 11764.7656 | 11113.8923 | 10734.8122 | 10662.2659 | 10862.5346 | 12360.4629 | 12861.1347 | 13814.4547 | 15203.0526 | 16383.2076 | 17471.4024 | 18241.8239 | 18727.169 | 19068.4433 | 19058.2255 | 18959.1129 | 18744.5393 | 18161.1033 | 17468.3371 | 17518.4042 | 16680.5453 | 15338.9492 | 13761.3222 | 19068.4433
2016-05-15 | 12394.1816 | 11492.9723 | 10885.0137 | 10550.8919 | 10538.6306 | 11022.9539 | 12131.5843 | 12742.6083 | 13544.705 | 14863.8219 | 16016.3888 | 16615.1514 | 16836.8775 | 16792.941 | 16437.3619 | 16022.5195 | 15909.102 | 15892.7535 | 15675.1146 | 15317.4919 | 15317.4919 | 14746.3173 | 13554.9228 | 12227.6316 | 16836.8775
2016-05-16 | 11011.7143 | 10237.2057 | 9737.5557 | 9420.8041 | 9372.7805 | 9927.6066 | 11073.0211 | 11574.7147 | 11947.6641 | 12619.9948 | 13192.1911 | 13595.7939 | 13775.6271 | 13898.2406 | 14151.6418 | 14296.7344 | 14459.1973 | 14289.582 | 13845.108 | 13266.781 | 13025.6411 | 12502.4902 | 11613.5423 | 10477.3238 | 14459.1973
2016-05-17 | 9388.1072 | 8667.7529 | 8170.1464 | 7889.1571 | 7804.3495 | 7900.3967 | 8203.8651 | 8779.1268 | 9991.9787 | 11248.7671 | 12266.4592 | 13040.9678 | 13603.9682 | 14117.9231 | 14610.4207 | 14997.675 | 15240.8584 | 15194.8784 | 14745.2955 | 13972.8304 | 13740.8866 | 13289.2602 | 12325.7224 | 11248.7671 | 15240.8584
2016-05-18 | 10198.3781 | 9403.4339 | 8850.6514 | 8474.6366 | 8305.0213 | 8339.7618 | 8442.9615 | 8908.8928 | 10203.487 | 11685.0668 | 12861.1347 | 13745.9955 | 14476.5676 | 15066.1342 | 15597.4594 | 15981.6483 | 16257.5287 | 16195.2002 | 15676.1364 | 14937.39 | 14852.5823 | 14302.8651 | 13118.623 | 11702.4371 | 16257.5287
2016-05-19 | 10455.8665 | 9594.5066 | 9053.9854 | 8787.301 | 8799.5624 | 9320.6698 | 10429.3002 | 11077.1082 | 12036.5589 | 13166.6467 | 14210.905 | 15092.7004 | 15838.5992 | 16575.302 | 17066.7778 | 17539.8616 | 17795.3064 | 17754.4352 | 17330.3969 | 16504.7993 | 16213.5922 | 15450.3232 | 14085.2262 | 12455.4883 | 17795.3064
2016-05-20 | 11088.3478 | 10150.3545 | 9607.7897 | 9276.7333 | 9181.7078 | 9622.0946 | 10661.2441 | 11426.5567 | 12373.746 | 13526.3129 | 14650.27 | 15564.7624 | 16290.2256 | 16891.0318 | 17316.092 | 17656.3444 | 17854.5696 | 17766.6966 | 17406.0085 | 16557.9318 | 16297.3781 | 15452.3667 | 14048.4421 | 12480.011 | 17854.5696
2016-05-21 | 11111.8487 | 10161.5941 | 9556.7008 | 9168.4247 | 9062.1596 | 9503.5683 | 10576.4364 | 11319.2699 | 12156.107 | 13208.5396 | 14239.5148 | 15138.6805 | 15884.5793 | 16678.5017 | 17427.4659 | 17934.2684 | 18239.7803 | 18114.1015 | 17587.8852 | 16705.068 | 16296.3563 | 15551.4793 | 14167.9903 | 12549.492 | 18239.7803
2016-05-22 | 11043.3895 | 10060.4379 | 9367.6716 | 9010.0489 | 8946.6986 | 9419.7824 | 10503.8901 | 11199.7217 | 12173.4773 | 13324.0007 | 14536.8526 | 15680.2235 | 16726.5254 | 17727.869 | 18470.7024 | 19093.9878 | 19483.2856 | 19363.7375 | 18807.8896 | 17822.8944 | 17258.8723 | 16520.126 | 14933.3029 | 13218.7574 | 19483.2856
2016-05-23 | 11669.7401 | 10623.4383 | 9903.0839 | 9478.0238 | 9306.3649 | 9696.6845 | 10650.0045 | 11533.8435 | 12689.4758 | 14065.8123 | 15473.8241 | 16847.0953 | 18000.684 | 19152.2292 | 19983.9574 | 20526.5222 | 20700.2246 | 20465.2154 | 19735.6651 | 18464.5718 | 17927.1159 | 17161.8033 | 15812.033 | 14337.6056 | 20700.2246
2016-05-24 | 12923.4632 | 11854.6822 | 11014.7797 | 10436.4527 | 10121.7447 | 10035.9152 | 10117.6576 | 10746.0518 | 12406.4429 | 14220.101 | 15836.5557 | 17309.9613 | 18541.2052 | 19386.2166 | 19898.128 | 20169.9212 | 20157.6599 | 19926.7378 | 19132.8154 | 18097.753 | 17655.3226 | 16866.5091 | 15661.8314 | 14334.5403 | 20169.9212
2016-05-25 | 13085.9261 | 12026.3411 | 11222.2009 | 10688.8321 | 10362.8846 | 10239.2493 | 10291.36 | 10688.8321 | 12026.3411 | 13675.4927 | 15424.7787 | 16794.9846 | 17995.5751 | 18786.4322 | 19253.3853 | 19520.0697 | 19608.9645 | 19241.124 | 18464.5718 | 17565.4061 | 17282.3732 | 16571.2149 | 15325.6661 | 14065.8123 | 19608.9645
2016-05-26 | 12750.7825 | 11817.8981 | 11127.1754 | 10673.5054 | 10424.1913 | 10428.2784 | 10538.6306 | 11055.6509 | 12665.9749 | 14558.3099 | 16239.1367 | 17436.6619 | 18438.0055 | 19124.6411 | 19506.7865 | 19705.0117 | 19711.1424 | 19404.6086 | 18647.4702 | 17744.2174 | 17553.1447 | 16735.7214 | 15373.6897 | 13802.1933 | 19711.1424
2016-05-27 | 12484.0982 | 11529.7564 | 10902.384 | 10518.195 | 10389.4508 | 10868.6653 | 11859.7911 | 12723.1945 | 13876.7832 | 15287.8603 | 16636.6088 | 17832.0904 | 18706.7334 | 19374.977 | 19762.2313 | 19944.108 | 19653.9227 | 18892.6972 | 18172.3429 | 17467.3153 | 17385.5729 | 16631.4999 | 15282.7514 | 13630.5344 | 19944.108
2016-05-28 | 12289.9601 | 11366.2717 | 10781.814 | 10414.9953 | 10326.1005 | 10797.1407 | 11829.1377 | 12586.2761 | 13663.2313 | 14946.586 | 16256.5069 | 17577.6674 | 18506.4647 | 19264.6249 | 19675.3801 | 19791.8629 | 19780.6234 | 19385.1948 | 18762.9313 | 18070.165 | 17847.4171 | 17039.1898 | 15651.6137 | 14096.4657 | 19791.8629
2016-05-29 | 12685.3887 | 11668.7184 | 11059.738 | 10686.7886 | 10554.979 | 10983.1045 | 11984.4481 | 12733.4123 | 13644.8393 | 14777.9924 | 15946.9078 | 16769.4401 | 17262.9594 | 17585.8417 | 17361.0502 | 17112.7579 | 16954.3821 | 16754.1134 | 16570.1931 | 16012.3017 | 15958.1474 | 15418.648 | 14298.778 | 12912.2236 | 17585.8417
2016-05-30 | 11530.7782 | 10534.5435 | 10044.0895 | 9739.5993 | 9683.4014 | 10125.8318 | 11100.6091 | 11871.0306 | 12935.7246 | 14460.2191 | 15797.7281 | 16879.7922 | 17724.8036 | 18374.6552 | 18755.7788 | 18999.9841 | 18931.5249 | 18415.5264 | 17488.7726 | 16723.46 | 16494.5815 | 15809.9894 | 14741.2084 | 13579.4455 | 18999.9841
2016-05-31 | 12422.7914 | 11427.5785 | 10733.7904 | 10280.1204 | 10105.3962 | 10074.7428 | 10280.1204 | 10941.2116 | 12574.0147 | 14376.4332 | 15954.0603 | 17162.8251 | 17935.2901 | 18426.7659 | 18508.5083 | 18433.9184 | 18161.1033 | 17563.3625 | 16869.5745 | 16134.9152 | 16035.8026 | 15540.2397 | 14642.0958 | 13478.2893 | 18508.5083
2016-06-01 | 12415.639 | 11460.2754 | 10832.903 | 10392.5162 | 10151.3763 | 10139.1149 | 10233.1186 | 10702.1153 | 12092.7567 | 13774.6053 | 15290.9256 | 16416.9263 | 17337.5493 | 17964.9217 | 18285.7604 | 18206.0616 | 17818.8073 | 17149.5419 | 16403.6431 | 15890.71 | 15880.4922 | 15524.913 | 14548.0921 | 13247.3672 | 18285.7604
2016-06-02 | 12067.2123 | 11247.7453 | 10774.6616 | 10510.0208 | 10542.7177 | 11113.8923 | 12126.4754 | 12801.8715 | 13425.1568 | 14143.4676 | 14828.0596 | 15214.2922 | 15591.3287 | 15842.6864 | 16011.2799 | 16003.1057 | 15964.2781 | 15771.1618 | 15572.9367 | 15354.2759 | 15423.7569 | 14992.5661 | 13876.7832 | 12550.5138 | 16011.2799
2016-06-03 | 11332.553 | 10504.9119 | 9991.9787 | 9683.4014 | 9665.0094 | 10188.1603 | 11236.5058 | 11899.6405 | 12530.0782 | 13418.0043 | 14303.8869 | 15049.7857 | 15589.2851 | 15978.583 | 16141.0459 | 16194.1784 | 15995.9532 | 15781.3796 | 15413.5391 | 15092.7004 | 15197.9437 | 14642.0958 | 13553.901 | 12175.5208 | 16194.1784
2016-06-04 | 10912.6018 | 10063.5033 | 9531.1563 | 9253.2324 | 9249.1452 | 9759.0131 | 10775.6834 | 10926.9067 | 12259.3067 | 13459.8973 | 14447.9578 | 15221.4446 | 15748.6827 | 16376.0551 | 16825.6379 | 17128.0846 | 17357.9849 | 17403.965 | 17106.6272 | 16411.8174 | 16066.456 | 15481.9983 | 14326.366 | 12839.6773 | 17403.965
2016-06-05 | 11490.9288 | 10579.5017 | 9960.3036 | 9577.1364 | 9454.5229 | 9877.5394 | 10764.4438 | 11693.2411 | 12951.0513 | 14320.2354 | 15712.9204 | 16939.0554 | 17870.9181 | 18722.0601 | 19305.496 | 19722.382 | 19896.0844 | 19819.451 | 19331.0405 | 18330.7187 | 17763.6312 | 16862.422 | 15430.9093 | 13731.6906 | 19896.0844
2016-06-06 | 12355.354 | 11277.3769 | 10541.6959 | 10074.7428 | 9857.1039 | 10187.1385 | 10893.188 | 11831.1813 | 13306.6304 | 14905.7148 | 16531.3655 | 18001.7058 | 19168.5776 | 20042.1988 | 20650.1575 | 20987.3446 | 21097.6967 | 20895.3845 | 20240.424 | 19187.9914 | 18492.1598 | 17706.4116 | 16381.164 | 14997.675 | 21097.6967
2016-06-07 | 13630.5344 | 12555.6227 | 11781.1141 | 11290.6601 | 10951.4294 | 10831.8812 | 10932.0156 | 11600.2592 | 13287.2166 | 15065.1124 | 16840.9646 | 18369.5463 | 19357.6068 | 20041.1771 | 20441.7145 | 20549.0013 | 20178.0955 | 19608.9645 | 18845.6954 | 18058.9254 | 17517.3825 | 16778.6361 | 15607.6771 | 14314.1047 | 20549.0013
2016-06-08 | 13087.9697 | 12075.3865 | 11340.7272 | 10698.0281 | 10493.6723 | 10414.9953 | 10429.3002 | 10867.6435 | 12345.1362 | 14294.6909 | 16113.4578 | 17632.8435 | 18518.7261 | 18720.0166 | 18493.1816 | 18351.1543 | 18081.4046 | 17792.2411 | 17234.3496 | 16555.8882 | 16170.6775 | 15569.8713 | 14284.4731 | 13020.5322 | 18720.0166
2016-06-09 | 11700.3935 | 10771.5962 | 10120.7229 | 9784.5575 | 9737.5557 | 10163.6376 | 10948.364 | 11802.5714 | 13032.7936 | 14517.4388 | 16115.5014 | 17710.4987 | 18910.0675 | 19890.9755 | 20410.0393 | 20254.7289 | 19977.8268 | 19270.7556 | 18430.8531 | 17677.8018 | 17251.7199 | 16512.9735 | 15140.7241 | 13622.3602 | 20410.0393
2016-06-10 | 12240.9147 | 11268.1809 | 10665.3312 | 10283.1858 | 10184.0732 | 10599.9373 | 11388.7509 | 12393.1598 | 13783.8013 | 15237.7931 | 16576.3238 | 17772.8273 | 18686.2979 | 19186.9697 | 19160.4034 | 18501.3558 | 17903.615 | 17620.5822 | 17545.9923 | 17008.5364 | 16829.7251 | 16023.5413 | 14663.5532 | 13199.3436 | 19186.9697
2016-06-11 | 11955.8383 | 11042.3677 | 10393.5379 | 10041.0241 | 9960.3036 | 10327.1223 | 11153.7417 | 12049.842 | 13322.9789 | 14924.1069 | 16339.2711 | 17508.1864 | 18230.5843 | 18671.9929 | 18230.5843 | 17450.9668 | 17052.4729 | 16927.8159 | 16750.0263 | 16210.5269 | 15950.995 | 15409.452 | 14207.8397 | 12839.6773 | 18671.9929
2016-06-12 | 11597.1938 | 10680.6579 | 10091.0913 | 9724.2726 | 9641.5085 | 9993.0005 | 10801.2278 | 11500.1248 | 12238.8712 | 13205.4743 | 14416.2826 | 15708.8333 | 17071.8867 | 18269.4119 | 19055.1601 | 19226.819 | 18741.4739 | 17970.0306 | 17378.4205 | 16765.353 | 16437.3619 | 15728.2471 | 14328.4096 | 12893.8316 | 19226.819
2016-06-13 | 11609.4552 | 10685.7668 | 10078.8299 | 9683.4014 | 9608.8115 | 9955.1947 | 10664.3094 | 11614.5641 | 12982.7264 | 14388.6946 | 15729.2689 | 17004.4493 | 17982.292 | 18474.7896 | 18463.55 | 17925.0724 | 17370.2463 | 16775.5708 | 16242.202 | 15460.5409 | 14984.3918 | 14503.1338 | 13577.4019 | 12405.4212 | 18474.7896
2016-06-14 | 11299.8561 | 10443.6051 | 9838.7118 | 9474.9584 | 9312.4956 | 9377.8894 | 9603.7026 | 10243.3364 | 11670.7619 | 13352.6105 | 14928.194 | 16313.7266 | 17361.0502 | 18206.0616 | 18592.2942 | 18562.6626 | 18066.0779 | 17565.4061 | 16776.5925 | 15911.1456 | 15579.0673 | 15008.9145 | 14037.2025 | 12910.1801 | 18592.2942
2016-06-15 | 11824.0288 | 11016.8232 | 10370.037 | 9977.6738 | 9864.2563 | 9965.4125 | 10147.2892 | 10742.9864 | 12263.3939 | 14049.4639 | 15613.8078 | 17007.5146 | 18120.2322 | 18822.1945 | 19224.7755 | 19073.5522 | 18539.1616 | 17864.7874 | 17143.4113 | 16386.2729 | 16235.0496 | 15874.3615 | 14800.4716 | 13590.685 | 19224.7755
2016-06-16 | 12293.0255 | 11427.5785 | 10871.7306 | 10522.2821 | 10402.7339 | 10780.7922 | 11513.4079 | 12267.481 | 13234.0841 | 14424.4568 | 15953.0385 | 17394.769 | 18369.5463 | 19221.7101 | 19808.2114 | 20152.551 | 20357.9286 | 20212.836 | 19478.1767 | 18207.0834 | 17602.1901 | 16831.7686 | 15437.04 | 13931.9593 | 20357.9286
2016-06-17 | 12543.3614 | 11591.0631 | 10874.7959 | 10453.8229 | 10304.6431 | 10629.5689 | 11385.6855 | 12208.2178 | 13214.6703 | 14286.5167 | 15309.3176 | 16234.0278 | 17021.8195 | 17706.4116 | 17937.3337 | 17933.2466 | 17756.4788 | 17596.0595 | 17268.0683 | 16723.46 | 16397.5125 | 15966.3216 | 14567.5059 | 13106.3617 | 17937.3337
2016-06-18 | 11749.4389 | 10858.4475 | 10283.1858 | 9916.3671 | 9856.0821 | 10236.1839 | 11069.9558 | 11914.9672 | 13055.2727 | 14312.0611 | 15658.7661 | 16908.4021 | 17579.711 | 17816.7638 | 17662.4751 | 17242.5239 | 16764.3312 | 16354.5977 | 15950.995 | 15546.3704 | 15389.0164 | 14984.3918 | 13834.8903 | 12494.316 | 17816.7638
2016-06-19 | 11244.68 | 10428.2784 | 9923.5195 | 9624.1382 | 9546.483 | 9933.7373 | 10745.03 | 11575.7365 | 12805.9586 | 14205.7961 | 15672.0492 | 16816.4419 | 17748.3046 | 18418.5917 | 18472.746 | 17892.3754 | 17346.7453 | 16785.7886 | 16217.6793 | 15676.1364 | 15387.9946 | 14772.8835 | 13690.8194 | 12335.9402 | 18472.746
2016-06-20 | 11099.5874 | 10249.4671 | 9693.6192 | 9385.0419 | 9306.3649 | 9643.552 | 10393.5379 | 11279.4205 | 12575.0365 | 14136.3151 | 15587.2416 | 16892.0536 | 17878.0705 | 18433.9184 | 18273.4991 | 17466.2935 | 16952.3386 | 16491.5161 | 16099.1529 | 15582.1327 | 15274.5771 | 14892.4317 | 13960.5691 | 12792.6755 | 18433.9184
2016-06-21 | 11589.0196 | 10742.9864 | 10137.0714 | 9780.4704 | 9623.1164 | 9685.445 | 9839.7336 | 10589.7195 | 12364.55 | 14273.2335 | 15798.7499 | 17180.1953 | 18258.1724 | 18879.4141 | 18693.4503 | 18025.2067 | 17445.8579 | 16971.7524 | 16394.4471 | 15787.5103 | 15483.0201 | 15119.2667 | 14218.0574 | 13024.6194 | 18879.4141
2016-06-22 | 11840.3773 | 11058.7162 | 10426.2349 | 10028.7628 | 9801.9278 | 9788.6447 | 9848.9296 | 10591.7631 | 12282.8077 | 14243.6019 | 15858.0131 | 17067.7996 | 18181.5389 | 18989.7663 | 19502.6994 | 19581.3764 | 19248.2764 | 18494.2034 | 17533.7309 | 16694.8502 | 16352.5542 | 15842.6864 | 14763.6875 | 13349.5451 | 19581.3764
2016-06-23 | 12023.2757 | 11214.0266 | 10637.7432 | 10289.3165 | 10213.7048 | 10613.2205 | 11386.7073 | 12321.6353 | 13670.3838 | 15150.9419 | 16711.1987 | 18079.361 | 19268.712 | 20211.8142 | 20745.1829 | 20865.7529 | 20655.2664 | 20196.4875 | 19524.1568 | 18586.1635 | 17962.8782 | 17128.0846 | 15788.5321 | 14152.6636 | 20865.7529
2016-06-24 | 12757.935 | 11766.8092 | 11109.8051 | 10680.6579 | 10537.6088 | 10878.8831 | 11630.9125 | 12546.4267 | 13962.6127 | 15487.1072 | 17136.2588 | 18524.8567 | 19707.0553 | 20740.074 | 21345.9891 | 21676.0238 | 21735.287 | 21328.6188 | 20791.163 | 19861.3439 | 19349.4325 | 18459.4629 | 16994.2315 | 15342.0146 | 21735.287
2016-06-25 | 13888.0228 | 12798.8062 | 11995.6877 | 11492.9723 | 11302.9214 | 11602.3027 | 12312.4393 | 13209.5614 | 14622.682 | 16299.4217 | 18019.076 | 19308.5614 | 20452.9541 | 21340.8802 | 21887.5321 | 21941.6864 | 21486.9946 | 20892.3191 | 20140.2896 | 19150.1856 | 18538.1399 | 17740.1303 | 16480.2766 | 14878.1268 | 21941.6864
2016-06-26 | 13474.2022 | 12365.5718 | 11612.5205 | 11127.1754 | 10938.1462 | 11197.6782 | 11932.3374 | 12820.2635 | 14275.2771 | 16041.9333 | 17728.8908 | 19031.6592 | 20024.8286 | 20672.6366 | 21306.1397 | 21512.5391 | 21517.648 | 21192.7222 | 20602.1338 | 19634.5089 | 18938.6773 | 18086.5135 | 16686.676 | 15045.6986 | 21517.648
2016-06-27 | 13582.5108 | 12563.7969 | 11828.1159 | 11361.1628 | 11206.8742 | 11528.7346 | 12135.6715 | 12999.0749 | 14432.6311 | 16085.8698 | 17567.4496 | 18866.131 | 19672.3148 | 20348.7326 | 20927.0596 | 20989.3882 | 20768.6838 | 20226.1191 | 19241.124 | 18200.9527 | 17619.5604 | 16800.0935 | 15755.8351 | 14399.9341 | 20989.3882
2016-06-28 | 12974.5522 | 11938.4681 | 11236.5058 | 10706.2024 | 10383.3201 | 10120.7229 | 10838.0119 | 11268.1809 | 13002.1402 | 14981.3265 | 16533.4091 | 18090.6006 | 19323.8881 | 20083.07 | 20544.9142 | 20888.232 | 20847.3608 | 20607.2427 | 19893.0191 | 18896.7844 | 18330.7187 | 17632.8435 | 16469.037 | 15056.9382 | 20888.232
2016-06-29 | 13735.7777 | 12725.2381 | 11971.165 | 11435.7527 | 11126.1536 | 11005.5837 | 10966.7561 | 11452.1012 | 13225.9099 | 15323.6225 | 17207.7834 | 18857.9568 | 20107.5927 | 20708.3989 | 20734.9651 | 20335.4495 | 20020.7415 | 19513.939 | 18502.3776 | 17557.2318 | 16989.1226 | 16405.6867 | 15274.5771 | 13868.609 | 20734.9651
2016-06-30 | 12626.1255 | 11688.1322 | 11051.5637 | 10674.5272 | 10627.5254 | 11037.2588 | 11785.2012 | 12548.4702 | 13808.324 | 15438.0618 | 16933.9465 | 18213.2141 | 19228.8626 | 20088.1789 | 20609.2863 | 20863.7093 | 20637.8961 | 19772.4491 | 18918.2417 | 18124.3193 | 17682.9107 | 17015.6889 | 15884.5793 | 14413.2173 | 20863.7093
2016-07-01 | 13071.6212 | 12124.4319 | 11536.9089 | 11180.3079 | 11095.5002 | 11504.2119 | 12320.6135 | 12987.8353 | 13826.716 | 14991.5443 | 16169.6557 | 17343.68 | 18072.2086 | 18397.1343 | 18712.8641 | 18847.739 | 19081.7264 | 18936.6338 | 18546.3141 | 18182.5607 | 17989.4444 | 17211.8705 | 15882.5358 | 14418.3262 | 19081.7264
2016-07-02 | 12984.77 | 12081.5172 | 11480.711 | 11152.7199 | 11047.4766 | 11382.6202 | 12134.6497 | 12899.9623 | 14153.6854 | 15723.1382 | 17382.5076 | 18519.7478 | 19197.1874 | 19279.9516 | 18886.5666 | 18512.5954 | 18412.461 | 18267.3684 | 17984.3355 | 17465.2717 | 17274.199 | 16845.0517 | 15782.4014 | 14310.0176 | 19279.9516
2016-07-03 | 13145.1893 | 12211.2831 | 11658.5006 | 11286.5729 | 11226.288 | 11553.2573 | 12296.0908 | 13077.7519 | 14341.6927 | 16041.9333 | 17809.6113 | 19165.5123 | 20111.6798 | 20772.771 | 21310.2268 | 21605.521 | 21486.9946 | 20705.3335 | 19849.0826 | 19002.0276 | 18476.8331 | 17868.8745 | 16727.5471 | 15301.1434 | 21605.521
2016-07-04 | 13999.3967 | 12929.5939 | 12134.6497 | 11595.1503 | 11308.0303 | 11300.8779 | 11419.4042 | 11796.4408 | 13304.5869 | 15436.0182 | 17352.876 | 18825.2598 | 19702.9681 | 20127.0065 | 20271.0774 | 20234.2933 | 19203.3181 | 17934.2684 | 17015.6889 | 16187.026 | 15659.7879 | 14988.479 | 14614.5078 | 13825.6942 | 20271.0774
2016-07-05 | 12737.4994 | 11796.4408 | 11164.9812 | 10746.0518 | 10542.7177 | 10550.8919 | 10677.5926 | 11040.3242 | 12310.3957 | 13732.7123 | 15358.363 | 16489.4726 | 17415.2045 | 18289.8475 | 18398.1561 | 17757.5006 | 17163.8469 | 16750.0263 | 16340.2928 | 15909.102 | 15636.287 | 15212.2486 | 14393.8035 | 13297.4344 | 18398.1561
2016-07-06 | 12268.5028 | 11427.5785 | 10842.099 | 10439.518 | 10310.7738 | 10332.2312 | 10422.1478 | 10820.6416 | 12277.6988 | 13730.6688 | 15022.1977 | 15520.8259 | 16021.4977 | 16472.1023 | 16880.814 | 16945.1861 | 16827.6815 | 16513.9953 | 16009.2364 | 15226.5535 | 15074.3084 | 14753.4697 | 13831.8249 | 12625.1037 | 16945.1861
2016-07-07 | 11610.477 | 10867.6435 | 10410.9082 | 10183.0514 | 10171.8119 | 10601.9809 | 11365.2499 | 12182.6733 | 13377.1332 | 14595.094 | 15807.9459 | 16595.7376 | 16959.491 | 17239.4585 | 17337.5493 | 17619.5604 | 17619.5604 | 17573.5803 | 17369.2245 | 17102.5401 | 16897.1625 | 16408.752 | 15266.4029 | 13881.8921 | 17619.5604
2016-07-08 | 12590.3632 | 11643.1739 | 10999.453 | 10625.4818 | 10519.2168 | 10846.1861 | 11600.2592 | 12460.5972 | 13701.0372 | 15363.4719 | 16965.6217 | 18374.6552 | 19466.9372 | 19965.5654 | 19868.4964 | 19285.0605 | 18677.1018 | 18141.6895 | 17579.711 | 16831.7686 | 16208.4833 | 15509.5863 | 14378.4768 | 13090.0132 | 19965.5654
2016-07-09 | 11873.0742 | 11064.8469 | 10537.6088 | 10019.5668 | 10063.5033 | 10552.9355 | 11357.0757 | 12159.1724 | 13468.0715 | 15172.3992 | 16676.4582 | 18123.2975 | 19046.9859 | 19310.6049 | 18501.3558 | 17848.4389 | 17532.7091 | 17066.7778 | 16500.7122 | 16168.6339 | 15875.3833 | 16130.8281 | 14287.5384 | 13024.6194 | 19310.6049
2016-07-10 | 11749.4389 | 10903.4058 | 10390.4726 | 10098.2437 | 10011.3925 | 10383.3201 | 11191.5475 | 12082.5389 | 13388.3727 | 14940.4553 | 16125.7192 | 16922.707 | 17648.1702 | 18159.0598 | 18138.6242 | 17800.4153 | 17286.4604 | 16724.4818 | 16255.4852 | 15762.9876 | 15626.0692 | 15195.9001 | 14202.7308 | 12958.2037 | 18159.0598
2016-07-11 | 11725.938 | 10898.2969 | 10367.9935 | 10088.026 | 10021.6103 | 10361.8628 | 11061.7815 | 11976.2739 | 13477.2675 | 15099.8529 | 16645.8048 | 18013.9671 | 19032.681 | 19846.0172 | 20320.1228 | 20434.562 | 20335.4495 | 19982.9356 | 19405.6304 | 18518.7261 | 17992.5098 | 17415.2045 | 16302.487 | 14986.4354 | 20434.562
2016-07-12 | 13724.5381 | 12769.1746 | 12038.6024 | 11574.7147 | 11210.9613 | 11214.0266 | 11309.0521 | 11766.8092 | 13206.496 | 15155.029 | 16705.068 | 18076.2957 | 19165.5123 | 19758.1442 | 19930.8249 | 19896.0844 | 19738.7304 | 19213.5359 | 18479.8985 | 17467.3153 | 16952.3386 | 16235.0496 | 15202.0308 | 14016.7669 | 19930.8249
2016-07-13 | 13044.0332 | 12276.677 | 11718.7855 | 11280.4423 | 10990.257 | 10875.8177 | 10899.3186 | 11410.2082 | 13049.1421 | 14856.6694 | 16354.5977 | 17681.8889 | 18637.2525 | 19114.4233 | 19503.7212 | 19774.4927 | 19724.4255 | 19354.5414 | 18746.5828 | 17957.7693 | 17523.5131 | 17054.5165 | 15954.0603 | 14630.8562 | 19774.4927
2016-07-14 | 13397.5688 | 12470.815 | 11771.9181 | 11385.6855 | 11282.4858 | 11589.0196 | 12300.1779 | 13073.6648 | 14448.9795 | 16053.1729 | 17616.495 | 18899.8497 | 19819.451 | 20065.6998 | 19880.7577 | 19781.6451 | 19740.774 | 19721.3602 | 19464.8936 | 18612.7298 | 17842.3082 | 17002.4057 | 15713.9422 | 14256.8851 | 20065.6998
2016-07-15 | 12949.0077 | 12027.3629 | 11394.8815 | 10987.1916 | 10891.1444 | 11215.0484 | 11989.557 | 12735.4558 | 13862.4783 | 15418.648 | 16718.3511 | 17813.6984 | 18471.7242 | 18476.8331 | 18195.8438 | 17684.9542 | 17329.3751 | 17079.0392 | 16970.7306 | 16560.9971 | 16422.0352 | 15978.583 | 14867.909 | 13540.6178 | 18476.8331
2016-07-16 | 12363.5282 | 11446.9923 | 10815.5327 | 10501.8465 | 10456.8882 | 10893.188 | 11873.0742 | 12675.1709 | 14042.3114 | 15594.394 | 16865.4873 | 17811.6549 | 18393.0472 | 17955.7257 | 17447.9015 | 17028.972 | 16652.9573 | 16299.4217 | 16065.4342 | 15667.9621 | 15723.1382 | 15432.9529 | 14457.1538 | 13216.7138 | 18393.0472
2016-07-17 | 12061.0816 | 11273.2898 | 10655.1134 | 10349.6014 | 10319.9698 | 10723.5726 | 11554.2791 | 12258.285 | 13771.5399 | 15225.5317 | 16628.4346 | 17820.8509 | 17849.4607 | 17658.388 | 17420.3134 | 17807.5677 | 18326.6316 | 18386.9165 | 18271.4555 | 17793.2628 | 17401.9214 | 16831.7686 | 15511.6299 | 14164.9249 | 18386.9165
2016-07-18 | 12745.6736 | 11802.5714 | 11173.1555 | 10757.2913 | 10598.9156 | 10907.4929 | 11583.9107 | 12384.9856 | 13846.1298 | 15613.8078 | 17219.0229 | 18649.5138 | 19809.2332 | 20659.3535 | 21177.3955 | 21460.4284 | 21461.4501 | 20920.9289 | 19899.1498 | 18818.1074 | 18133.5153 | 17392.7254 | 16193.1566 | 14896.5188 | 21461.4501
2016-07-19 | 13584.5544 | 12545.4049 | 11807.6803 | 11334.5966 | 11031.1282 | 11011.7143 | 11115.9358 | 11627.8472 | 13391.4381 | 15368.5808 | 17068.8214 | 18502.3776 | 19575.2457 | 20343.6237 | 20661.397 | 20769.7056 | 21025.1504 | 20828.9688 | 20035.0464 | 19173.6865 | 18660.7534 | 17860.7003 | 16649.8919 | 15385.9511 | 21025.1504
2016-07-20 | 14102.5964 | 13104.3181 | 12327.7659 | 11780.0923 | 11460.2754 | 11323.357 | 11338.6837 | 11662.5877 | 13292.3255 | 15353.2541 | 17044.2987 | 18671.9929 | 19884.8448 | 20683.8762 | 21066.0216 | 20846.3391 | 20649.1357 | 20334.4277 | 19644.7267 | 18784.3887 | 18421.657 | 17775.8926 | 16642.7395 | 15176.4863 | 21066.0216
2016-07-21 | 13829.7814 | 12855.004 | 12143.8457 | 11703.4589 | 11594.1285 | 11899.6405 | 12649.6264 | 13338.3056 | 14533.7872 | 16103.2401 | 17716.6294 | 19046.9859 | 19877.6924 | 20019.7197 | 19545.6142 | 19063.3344 | 18545.2923 | 18077.3175 | 17597.0812 | 17061.6689 | 16956.4257 | 16196.222 | 15080.4391 | 13771.5399 | 20019.7197
2016-07-22 | 12487.1635 | 11590.0414 | 11074.0429 | 10704.1588 | 10648.9827 | 11111.8487 | 11884.3138 | 12654.7353 | 13968.7433 | 15445.2143 | 16767.3965 | 17754.4352 | 18346.0454 | 18676.0801 | 19128.7282 | 19392.3473 | 19192.0786 | 18594.3377 | 18065.0561 | 17472.4242 | 17303.8306 | 16664.1968 | 15472.8023 | 14164.9249 | 19392.3473
2016-07-23 | 12978.6393 | 12091.735 | 11472.5368 | 11080.1736 | 10980.0392 | 11309.0521 | 12190.8475 | 12879.5267 | 14175.1427 | 15499.3686 | 16659.0879 | 17580.7328 | 18281.6733 | 18943.7862 | 19583.42 | 19910.3893 | 20033.0028 | 19929.8031 | 19850.1044 | 19129.75 | 18689.3632 | 18021.1196 | 16642.7395 | 15211.2268 | 20033.0028
2016-07-24 | 13847.1516 | 12783.4795 | 12059.038 | 11609.4552 | 11450.0576 | 11739.2211 | 12386.0074 | 13123.7319 | 14477.5894 | 16181.9171 | 17707.4334 | 16386.2729 | 19843.9737 | 20345.6673 | 20639.9397 | 20919.9072 | 21304.0961 | 21082.3701 | 20735.9869 | 19889.9537 | 19115.4451 | 18352.1761 | 16834.834 | 15275.5989 | 21304.0961
2016-07-25 | 13955.4602 | 12852.9604 | 12131.5843 | 11636.0214 | 11396.9251 | 11683.0233 | 12327.7659 | 13103.2964 | 14663.5532 | 16388.3165 | 17922.007 | 19304.4743 | 20132.1154 | 20579.6547 | 20988.3664 | 21370.5118 | 21422.6225 | 21037.4118 | 20236.3369 | 19247.2546 | 18722.0601 | 17910.7674 | 16721.4165 | 15415.5827 | 21422.6225
2016-07-26 | 14250.7544 | 13269.8464 | 12624.0819 | 12074.3647 | 11737.1776 | 11680.9797 | 11826.0724 | 12214.3485 | 13656.0789 | 15568.8495 | 17295.6564 | 18430.8531 | 18909.0457 | 19171.643 | 19093.9878 | 18804.8242 | 18807.8896 | 18592.2942 | 18113.0797 | 17444.8361 | 17269.0901 | 16572.2367 | 15484.0419 | 14458.1756 | 19171.643
2016-07-27 | 13339.3273 | 12451.4012 | 11834.2466 | 11380.5766 | 11138.415 | 11068.934 | 11125.1318 | 11478.6674 | 13269.8464 | 15295.0127 | 16962.5564 | 18432.8966 | 19594.6596 | 20482.5857 | 21051.7167 | 21429.775 | 21556.4756 | 21412.4047 | 20765.6185 | 19806.1678 | 19363.7375 | 18621.9258 | 17313.0266 | 15892.7535 | 21556.4756
2016-07-28 | 14477.5894 | 13516.0951 | 12789.6101 | 12333.8966 | 12205.1524 | 12532.1218 | 13217.7356 | 13891.0881 | 15279.686 | 17037.1462 | 18567.7715 | 19981.9139 | 20932.1685 | 21804.7679 | 22584.3855 | 23017.6198 | 23173.9521 | 23000.2496 | 22558.841 | 21685.2198 | 21147.7639 | 20269.0338 | 18648.492 | 16929.8594 | 23173.9521
2016-07-29 | 15404.3431 | 14323.3007 | 13543.6832 | 13064.4687 | 12851.9387 | 13088.9914 | 13714.3203 | 14310.0176 | 15693.5066 | 17280.3297 | 18777.2362 | 20099.4185 | 20963.8437 | 21548.3014 | 21836.4431 | 21611.6517 | 21390.9474 | 20637.8961 | 19713.1859 | 18889.6319 | 18542.227 | 17819.8291 | 16490.4944 | 15192.8348 | 21836.4431
2016-07-30 | 13888.0228 | 13014.4016 | 12344.1144 | 11953.7948 | 11798.4843 | 12115.2359 | 12914.2672 | 13540.6178 | 14881.1921 | 16364.8155 | 17579.711 | 18978.5267 | 20150.5074 | 21169.2213 | 21701.5682 | 21744.483 | 21113.0234 | 20068.7651 | 19315.7138 | 18573.9021 | 18106.9491 | 17406.0085 | 16060.3253 | 14696.2501 | 21744.483
2016-07-31 | 13367.9372 | 12421.7696 | 11774.9834 | 11389.7726 | 11255.9196 | 11548.1484 | 12323.6788 | 12916.3108 | 14102.5964 | 15798.7499 | 17561.319 | 19116.4669 | 20124.963 | 20787.0759 | 21013.9109 | 20758.4661 | 19958.4129 | 19204.3399 | 18565.7279 | 17846.3954 | 17628.7564 | 17000.3622 | 15818.1637 | 14459.1973 | 21013.9109
2016-08-01 | 13287.2166 | 12402.3558 | 11686.0886 | 11365.2499 | 11188.4821 | 11512.3861 | 12177.5644 | 13002.1402 | 14406.0648 | 16174.7646 | 17731.9561 | 19078.6611 | 20086.1353 | 20791.163 | 21375.6207 | 21688.2851 | 21643.3268 | 21030.2593 | 20119.8541 | 19226.819 | 18856.935 | 18094.6877 | 16765.353 | 15452.3667 | 21688.2851
2016-08-02 | 14196.6001 | 13159.4942 | 12430.9656 | 11924.1632 | 11641.1303 | 11615.5858 | 11782.1359 | 12149.9764 | 13722.4945 | 15629.1345 | 17284.4168 | 18537.1181 | 19499.6341 | 20041.1771 | 20524.4786 | 20503.0213 | 20337.493 | 19911.4111 | 19148.142 | 18368.5245 | 18068.1214 | 17464.2499 | 16313.7266 | 15145.833 | 20524.4786
2016-08-03 | 13957.5038 | 13034.8371 | 12344.1144 | 11883.292 | 11607.4116 | 11573.6929 | 11696.3064 | 11879.2049 | 13123.7319 | 14687.0541 | 15851.8824 | 17086.1916 | 17675.7582 | 17850.4825 | 17913.8328 | 18070.165 | 18199.931 | 18038.4898 | 17611.3861 | 17192.4567 | 16821.5508 | 16123.6756 | 14933.3029 | 13612.1424 | 18199.931
2016-08-04 | 12361.4847 | 11518.5168 | 10969.8214 | 10644.8956 | 10622.4165 | 11058.7162 | 11898.6187 | 12520.8822 | 13713.2985 | 15202.0308 | 16659.0879 | 17896.4625 | 18233.6497 | 18080.3828 | 17538.8398 | 16987.0791 | 16438.3836 | 15826.3379 | 15436.0182 | 15139.7023 | 15338.9492 | 14854.6259 | 13916.6326 | 12850.9169 | 18233.6497
2016-08-05 | 11803.5932 | 11086.3042 | 10665.3312 | 10433.3873 | 10421.126 | 10809.4021 | 11712.6549 | 12445.2706 | 13757.235 | 15394.1253 | 16773.5272 | 18054.8383 | 19064.3562 | 19666.1841 | 19544.5924 | 19451.6105 | 19543.5706 | 19628.3783 | 19296.3 | 18555.5101 | 18217.3012 | 17348.7889 | 15935.6683 | 14523.5694 | 19666.1841
2016-08-06 | 13103.2964 | 12169.3902 | 11496.0377 | 11070.9775 | 10990.257 | 11298.8343 | 12070.2776 | 12810.0457 | 14256.8851 | 16005.1493 | 17564.3843 | 19194.1221 | 20305.8179 | 21230.528 | 21800.6808 | 21846.6609 | 21358.2504 | 20823.8599 | 20096.3531 | 19369.8681 | 19038.8117 | 18236.715 | 16682.5889 | 15241.8802 | 21846.6609
2016-08-07 | 13813.4329 | 12820.2635 | 12156.107 | 11714.6984 | 11552.2355 | 11859.7911 | 12624.0819 | 13289.2602 | 14818.8636 | 16611.0643 | 18200.9527 | 19696.8375 | 20850.4262 | 21639.2397 | 21801.7026 | 21706.6771 | 21550.3449 | 21277.5299 | 20550.0231 | 19713.1859 | 18943.7862 | 17870.9181 | 16230.9625 | 14717.7075 | 21801.7026
2016-08-08 | 13351.5887 | 12314.4828 | 11690.1757 | 11312.1174 | 11142.5021 | 11754.5478 | 12236.8276 | 12888.7227 | 13938.09 | 15474.8459 | 16883.8794 | 18380.7859 | 19715.2295 | 20810.5768 | 21371.5336 | 21405.2523 | 21221.332 | 20429.4532 | 19451.6105 | 18536.0963 | 18206.0616 | 17432.5748 | 16244.2456 | 15136.6369 | 21405.2523
2016-08-09 | 13741.9083 | 12776.327 | 12051.8856 | 11584.9325 | 11356.0539 | 11356.0539 | 11509.3208 | 11973.2086 | 13716.3639 | 15764.0094 | 17481.6202 | 18964.2218 | 20060.5909 | 20784.0105 | 21281.617 | 21574.8676 | 21533.9965 | 20908.6676 | 19874.6271 | 18865.1092 | 18479.8985 | 17653.2791 | 16446.5579 | 15323.6225 | 21574.8676
2016-08-10 | 14090.335 | 13149.2764 | 12378.8549 | 11883.292 | 11582.8889 | 11475.6021 | 11524.6475 | 11802.5714 | 13469.0933 | 15519.8041 | 17281.3515 | 18973.4178 | 20139.2679 | 21009.8237 | 21425.6879 | 21507.4302 | 21434.8839 | 21147.7639 | 20372.2335 | 19371.9117 | 18908.0239 | 17923.0288 | 16479.2548 | 14990.5225 | 21507.4302
2016-08-11 | 13600.9028 | 12586.2761 | 11886.3573 | 11459.2536 | 11321.3134 | 11693.2411 | 12461.619 | 13031.7718 | 14352.9323 | 16188.0477 | 17879.0923 | 19552.7666 | 20812.6204 | 21607.5646 | 21809.8768 | 21753.679 | 21783.3106 | 21591.2161 | 21011.8673 | 20115.7669 | 19754.0571 | 18601.4902 | 17181.2171 | 15531.0437 | 21809.8768
2016-08-12 | 14086.2479 | 13093.0786 | 12299.1561 | 11811.7675 | 11651.3481 | 11961.969 | 12729.3252 | 13349.5451 | 14688.0759 | 16418.9698 | 17966.9653 | 19361.6939 | 20360.9939 | 21129.3719 | 21409.3394 | 21387.882 | 21554.432 | 21443.0581 | 21052.7385 | 20197.5093 | 19666.1841 | 18596.3813 | 17099.4748 | 15613.8078 | 21554.432
2016-08-13 | 14148.5765 | 13225.9099 | 12507.5991 | 11912.9236 | 11757.6132 | 12084.5825 | 12883.6138 | 13522.2258 | 14978.2612 | 16733.6778 | 18320.5009 | 19953.3041 | 21122.2194 | 21928.4032 | 22334.0496 | 22543.5143 | 22542.4925 | 22051.0167 | 21291.8348 | 20301.7308 | 19887.9102 | 18920.2853 | 17401.9214 | 15891.7318 | 22543.5143
2016-08-14 | 14533.7872 | 13597.8375 | 12936.7463 | 12505.5555 | 12312.4393 | 12559.7098 | 13329.1096 | 13910.5019 | 15308.2958 | 17105.6054 | 18731.2561 | 20000.3059 | 21085.4354 | 21657.6317 | 21737.3305 | 21004.7148 | 19914.4764 | 19075.5957 | 18371.5899 | 17771.8055 | 17649.192 | 16827.6815 | 15705.768 | 14288.5602 | 21737.3305
2016-08-15 | 13061.4034 | 12225.588 | 11575.7365 | 11277.3769 | 11198.6999 | 11598.2156 | 12480.011 | 13216.7138 | 14652.3136 | 16200.3091 | 17674.7365 | 18732.2779 | 19530.2875 | 19362.7157 | 17950.6168 | 17045.3205 | 16438.3836 | 16018.4324 | 15492.2161 | 14987.4572 | 15055.9164 | 14525.613 | 13777.6706 | 12818.22 | 19530.2875
2016-08-16 | 11824.0288 | 11162.9377 | 10712.333 | 10410.9082 | 10256.6195 | 10312.8174 | 10595.8502 | 11057.6944 | 12663.9313 | 14899.5842 | 16739.8085 | 18075.2739 | 19313.6703 | 19532.331 | 20144.3768 | 19681.5108 | 18840.5865 | 17963.9 | 17129.1064 | 16415.9045 | 16218.7011 | 15642.4176 | 14787.1885 | 13622.3602 | 20144.3768
2016-08-17 | 12559.7098 | 11769.8745 | 11178.2644 | 10763.422 | 10588.6978 | 10596.872 | 10785.9011 | 11146.5892 | 12665.9749 | 14796.3845 | 16709.1551 | 18233.6497 | 19485.3292 | 20525.5004 | 20697.1593 | 20503.0213 | 20602.1338 | 20564.328 | 20109.6363 | 19360.6721 | 19123.6193 | 18265.3248 | 16801.1152 | 15085.548 | 20697.1593
2016-08-18 | 13791.9755 | 12764.0657 | 12071.2994 | 11654.4135 | 11563.4751 | 12138.7368 | 13121.6884 | 13557.9881 | 14603.2682 | 16414.8827 | 18125.3411 | 19661.0752 | 20802.4026 | 21715.8732 | 22126.6284 | 22459.7284 | 22512.8609 | 22295.222 | 21823.16 | 20976.105 | 20639.9397 | 19393.3691 | 17604.2337 | 16030.6937 | 22512.8609
2016-08-19 | 14503.1338 | 13477.2675 | 12738.5212 | 12266.4592 | 12123.4101 | 12593.4285 | 13600.9028 | 13994.2878 | 15095.7658 | 16839.9429 | 18386.9165 | 19894.0409 | 21084.4136 | 21886.5103 | 22355.5069 | 22916.4637 | 23202.5619 | 22910.333 | 22359.594 | 21396.0563 | 21004.7148 | 19835.7994 | 18063.0125 | 16408.752 | 23202.5619
2016-08-20 | 14908.7802 | 13868.609 | 13145.1893 | 12600.581 | 12423.8132 | 12837.6338 | 13791.9755 | 12713.9985 | 15201.009 | 16956.4257 | 18487.0509 | 20082.0482 | 21096.675 | 22070.4305 | 22464.8373 | 22542.4925 | 22511.8391 | 22208.3707 | 21550.3449 | 20734.9651 | 20367.1246 | 19338.193 | 17733.9996 | 16076.6738 | 22542.4925
2016-08-21 | 14776.9707 | 13750.0826 | 13022.5758 | 12554.6009 | 12364.55 | 12804.9368 | 13815.4764 | 14265.0593 | 15385.9511 | 16990.1444 | 18603.5337 | 20137.2243 | 21219.2885 | 22150.1293 | 22670.2149 | 23196.4312 | 23214.8232 | 22445.4235 | 21634.1308 | 20513.239 | 20256.7725 | 19120.554 | 17599.1248 | 15948.9514 | 23214.8232
2016-08-22 | 14450.0013 | 13474.2022 | 12769.1746 | 12322.657 | 12140.7804 | 12556.6445 | 13572.293 | 14006.5492 | 15109.0489 | 16867.5309 | 18416.5481 | 19882.8013 | 21029.2375 | 21846.6609 | 22149.1075 | 22795.8938 | 22962.4438 | 22503.6649 | 21757.7661 | 20634.8308 | 20024.8286 | 18837.5212 | 17458.1193 | 16067.4778 | 22962.4438
2016-08-23 | 14670.7056 | 13682.6452 | 12882.592 | 12330.8313 | 11988.5353 | 11957.8819 | 12116.2577 | 12455.4883 | 14028.0065 | 16200.3091 | 18011.9236 | 19595.6813 | 20784.0105 | 21578.9547 | 21934.5339 | 22221.6539 | 22385.1385 | 22156.26 | 21428.7532 | 20353.8415 | 19838.8648 | 18883.5012 | 17704.368 | 16301.4652 | 22385.1385
2016-08-24 | 14879.1486 | 13818.5418 | 12989.8789 | 12415.639 | 12065.1687 | 11930.2938 | 11946.6423 | 12161.2159 | 13845.108 | 15987.779 | 17710.4987 | 19454.6758 | 20808.5332 | 21764.9186 | 22338.1367 | 22636.4962 | 22667.1496 | 22499.5778 | 21825.2035 | 20900.4934 | 20496.8906 | 19269.7338 | 17688.0196 | 16121.6321 | 22667.1496
2016-08-25 | 14883.2357 | 13820.5853 | 13203.4307 | 12833.5466 | 12812.0893 | 13377.1332 | 14424.4568 | 14834.1903 | 15595.4158 | 17113.7797 | 18574.9239 | 19821.4945 | 20593.9596 | 20895.3845 | 20961.8001 | 20943.4081 | 21003.6931 | 20767.6621 | 20063.6562 | 19409.7175 | 19243.1675 | 18102.8619 | 16694.8502 | 15091.6787 | 21003.6931
2016-08-26 | 13931.9593 | 13097.1657 | 12509.6426 | 12160.1942 | 12096.8438 | 12627.1472 | 13695.9283 | 14084.2044 | 14930.2375 | 16489.4726 | 17846.3954 | 19072.5304 | 19926.7378 | 20680.8108 | 21185.5698 | 21589.1725 | 21795.5719 | 21618.8041 | 21012.8891 | 20090.2225 | 19753.0353 | 18608.6426 | 16862.422 | 15304.2087 | 21795.5719
2016-08-27 | 13794.0191 | 12783.4795 | 12046.7767 | 11601.2809 | 11435.7527 | 11897.5969 | 12943.8988 | 13299.478 | 14280.386 | 15987.779 | 17457.0975 | 18850.8043 | 19956.3694 | 20847.3608 | 21528.8876 | 22013.2109 | 22297.2655 | 22120.4977 | 21525.8222 | 20538.7835 | 20215.9013 | 19062.3126 | 17388.6383 | 15866.1873 | 22297.2655
2016-08-28 | 14455.1102 | 13476.2458 | 12746.6954 | 12258.285 | 12055.9727 | 12518.8387 | 13607.0335 | 14004.5056 | 14951.6949 | 16314.7483 | 17377.3987 | 18277.5862 | 19301.4089 | 20331.3624 | 21256.0725 | 21830.3124 | 22080.6483 | 21652.5228 | 20772.771 | 20051.3949 | 19608.9645 | 18381.8077 | 16882.8576 | 15414.5609 | 22080.6483
2016-08-29 | 13978.9611 | 13057.3163 | 12427.9003 | 11992.6224 | 11876.1395 | 12350.2451 | 13444.5706 | 13974.874 | 15056.9382 | 16823.5944 | 18440.0491 | 19638.5961 | 20500.9777 | 21313.2922 | 21883.4449 | 22204.2836 | 22096.9968 | 21388.9038 | 20479.5203 | 19569.1151 | 19220.6884 | 18152.9291 | 16899.206 | 15718.0293 | 22204.2836
2016-08-30 | 14535.8308 | 13612.1424 | 12935.7246 | 12442.2052 | 12226.6098 | 12431.9874 | 12505.5555 | 12762.0221 | 14081.139 | 16107.3272 | 17806.546 | 19381.1077 | 20421.2789 | 21218.2667 | 21805.7897 | 22058.1692 | 22023.4287 | 21416.4919 | 20342.6019 | 19415.8482 | 19070.4868 | 18052.7948 | 16906.3585 | 15794.6627 | 22058.1692
2016-08-31 | 14576.7019 | 13578.4237 | 12821.2853 | 12360.4629 | 12033.4935 | 11890.4445 | 11977.2957 | 12215.3702 | 13763.3657 | 15956.1039 | 17570.515 | 18983.6356 | 20136.2025 | 20914.7983 | 21260.1596 | 21371.5336 | 21138.5679 | 20681.8326 | 19713.1859 | 18794.6064 | 18520.7696 | 17560.2972 | 16386.2729 | 15141.7458 | 21371.5336
2016-09-01 | 13960.5691 | 13142.124 | 12512.708 | 12041.6678 | 11887.3791 | 11979.3392 | 12259.3067 | 12386.0074 | 13839.9991 | 16005.1493 | 17786.1104 | 19463.8718 | 20382.4513 | 21079.3047 | 21676.0238 | 21879.3578 | 21715.8732 | 21304.0961 | 20599.0685 | 19725.4473 | 19454.6758 | 18315.392 | 16778.6361 | 15343.0363 | 21879.3578
2016-09-02 | 13988.1571 | 13032.7936 | 12356.3758 | 11955.8383 | 11819.9417 | 12293.0255 | 13324.0007 | 13732.7123 | 14624.7256 | 16255.4852 | 17689.0414 | 19143.0332 | 20165.8341 | 20790.1412 | 21458.3848 | 21843.5956 | 21924.3161 | 21572.8241 | 20785.0323 | 19907.324 | 19388.2602 | 17959.8128 | 16278.9861 | 14630.8562 | 21924.3161
2016-09-03 | 13248.389 | 12307.3304 | 11695.2846 | 11293.7254 | 11186.4386 | 11665.653 | 12779.3923 | 13187.0822 | 14017.7887 | 15446.236 | 16438.3836 | 17472.4242 | 18446.1797 | 19462.85 | 20189.335 | 20431.4967 | 20577.6111 | 20236.3369 | 19627.3565 | 18830.3687 | 18585.1417 | 17494.9033 | 16007.1928 | 14388.6946 | 20577.6111
2016-09-04 | 13061.4034 | 12128.519 | 11519.5386 | 11143.5239 | 11040.3242 | 11515.4515 | 12670.062 | 13061.4034 | 13665.2749 | 14930.2375 | 16252.4198 | 17336.5275 | 18234.6715 | 19073.5522 | 19424.0224 | 19571.1586 | 19746.9047 | 19481.2421 | 18998.9623 | 18555.5101 | 18428.8095 | 17334.484 | 15828.3815 | 14395.847 | 19746.9047
2016-09-05 | 13087.9697 | 12199.0218 | 11632.9561 | 11278.3987 | 11222.2009 | 11716.742 | 12922.4414 | 13343.4145 | 14229.297 | 15845.7517 | 17389.6601 | 18757.8224 | 19902.2151 | 20761.5314 | 21245.8547 | 21275.4863 | 20807.5115 | 19863.3875 | 18861.0221 | 18177.4518 | 17775.8926 | 16761.2659 | 15642.4176 | 14537.8743 | 21275.4863
2016-09-06 | 13374.0678 | 12605.6899 | 12007.9491 | 11595.1503 | 11395.9033 | 11392.838 | 11641.1303 | 12045.7549 | 13320.9353 | 14985.4136 | 16259.5723 | 17220.0447 | 17777.9362 | 17705.3898 | 17529.6438 | 17298.7217 | 16850.1606 | 16489.4726 | 16067.4778 | 15848.817 | 15850.8606 | 15234.7277 | 14473.5022 | 13609.0771 | 17777.9362
2016-09-07 | 12642.4739 | 11776.0052 | 11183.3733 | 10771.5962 | 10615.264 | 10642.8521 | 10856.4039 | 11132.2843 | 12349.2233 | 13919.6979 | 15321.579 | 16705.068 | 17824.938 | 18587.1853 | 18940.7209 | 18699.581 | 18274.5208 | 17684.9542 | 16802.137 | 16512.9735 | 16499.6904 | 15646.5048 | 14439.7835 | 13160.516 | 18940.7209
2016-09-08 | 12107.0616 | 11389.7726 | 10831.8812 | 10495.7159 | 10474.2585 | 11075.0647 | 12224.5662 | 12650.6482 | 13341.3709 | 14959.8691 | 16582.4545 | 17989.4444 | 19093.9878 | 19925.716 | 20531.6311 | 20785.0323 | 20757.4443 | 20529.5875 | 19689.685 | 19210.4706 | 18876.3488 | 17661.4533 | 16152.2855 | 14640.0523 | 20785.0323
2016-09-09 | 13320.9353 | 12367.6153 | 11765.7874 | 11381.5984 | 11223.2226 | 11684.0451 | 12802.8933 | 13203.4307 | 13899.2623 | 15354.2759 | 16859.3567 | 18193.8003 | 19303.4525 | 20261.8814 | 20696.1375 | 21153.8946 | 21042.5207 | 20557.1756 | 19764.2749 | 19119.5322 | 18668.9276 | 17322.2226 | 15754.8134 | 14259.9504 | 21153.8946
2016-09-10 | 13029.7282 | 12217.4138 | 11670.7619 | 11281.4641 | 11197.6782 | 11726.9598 | 12867.2654 | 13239.193 | 13923.785 | 15213.2704 | 16680.5453 | 17859.6785 | 18889.6319 | 19771.4274 | 20280.2734 | 20515.2826 | 20423.3225 | 20001.3277 | 19296.3 | 18762.9313 | 18442.0926 | 17114.8015 | 15615.8514 | 14095.4439 | 20515.2826
2016-09-11 | 12818.22 | 11982.4046 | 11383.642 | 11006.6055 | 10920.776 | 11422.4696 | 12582.189 | 12997.0313 | 13625.4255 | 15019.1323 | 16281.0296 | 17352.876 | 18134.5371 | 18687.3196 | 18876.3488 | 18934.5902 | 18580.0328 | 17878.0705 | 17232.3061 | 16866.5091 | 16682.5889 | 15709.8551 | 14604.29 | 13271.8899 | 18934.5902
2016-09-12 | 11919.0543 | 11231.3969 | 10738.8993 | 10487.5416 | 10487.5416 | 11054.6291 | 12315.5046 | 12677.2144 | 13418.0043 | 14639.0305 | 15749.7045 | 16675.4364 | 17579.711 | 18430.8531 | 18641.3396 | 18560.619 | 18618.8604 | 18688.3414 | 18045.6423 | 17318.1355 | 17023.8631 | 16147.1766 | 15162.1814 | 13956.482 | 18688.3414
2016-09-13 | 12636.3433 | 11754.5478 | 11129.219 | 10623.4383 | 10417.0389 | 10397.6251 | 10677.5926 | 11057.6944 | 12196.9782 | 13821.6071 | 15511.6299 | 17005.4711 | 18137.6024 | 18833.4341 | 19112.3798 | 19080.7046 | 18684.2543 | 18117.1668 | 17154.6508 | 16661.1315 | 16350.5106 | 15370.6244 | 14199.6654 | 12982.7264 | 19112.3798
2016-09-14 | 11997.7313 | 11195.6346 | 10617.3076 | 10225.9661 | 9993.0005 | 9954.1729 | 10112.5487 | 10332.2312 | 11712.6549 | 13542.6614 | 15233.706 | 16782.7232 | 17923.0288 | 18676.0801 | 19055.1601 | 19181.8608 | 19201.2746 | 18708.777 | 17829.0251 | 17309.9613 | 17031.0156 | 15990.8443 | 14729.9688 | 13279.0424 | 19201.2746
2016-09-15 | 12173.4773 | 11357.0757 | 10849.2515 | 10563.1533 | 10551.9137 | 11102.6527 | 12246.0236 | 12697.65 | 13462.9626 | 15024.2412 | 16875.7051 | 18248.9764 | 19373.9552 | 20342.6019 | 21016.9762 | 21464.5155 | 21544.2143 | 21249.9418 | 20499.9559 | 19926.7378 | 19499.6341 | 18146.7984 | 16629.4563 | 14821.929 | 21544.2143
2016-09-16 | 13403.6994 | 12506.5773 | 11810.7457 | 11367.2935 | 11242.6364 | 11691.1975 | 12818.22 | 13221.8227 | 13944.2206 | 15377.7768 | 16927.8159 | 18328.6751 | 19379.0641 | 20152.551 | 20015.6326 | 19592.616 | 19245.2111 | 18837.5212 | 18374.6552 | 18191.7567 | 17830.0469 | 16632.5217 | 15256.1851 | 13804.2369 | 20152.551
2016-09-17 | 12453.4448 | 11616.6076 | 11023.9757 | 10650.0045 | 10619.3511 | 11184.395 | 12404.3994 | 12813.1111 | 13425.1568 | 14567.5059 | 15995.9532 | 17071.8867 | 17844.3518 | 18253.0635 | 18700.6028 | 18674.0365 | 18039.5116 | 17305.8742 | 16798.0499 | 16883.8794 | 16738.7867 | 15814.0765 | 14482.6983 | 13024.6194 | 18700.6028
2016-09-18 | 11899.6405 | 11049.5202 | 10600.9591 | 10291.36 | 10264.7938 | 10822.6852 | 12055.9727 | 12470.815 | 13106.3617 | 14338.6274 | 15512.6517 | 16716.3076 | 17854.5696 | 18885.5448 | 19608.9645 | 20013.589 | 19877.6924 | 19938.9991 | 19063.3344 | 18541.2052 | 18077.3175 | 16879.7922 | 15417.6262 | 13876.7832 | 20013.589
2016-09-19 | 12605.6899 | 11690.1757 | 11132.2843 | 10773.6398 | 10708.2459 | 11224.2444 | 12430.9656 | 12936.7463 | 13574.3366 | 14911.8455 | 16016.3888 | 16698.9373 | 16901.2496 | 16568.1496 | 16001.0621 | 15735.3995 | 15492.2161 | 15252.098 | 14965.9998 | 15074.3084 | 14950.6731 | 14316.1483 | 13405.743 | 12388.0509 | 16901.2496
2016-09-20 | 11358.0975 | 10654.0916 | 10187.1385 | 9928.6284 | 9796.8189 | 9927.6066 | 10324.057 | 10836.9901 | 11795.419 | 13247.3672 | 14528.6783 | 15534.109 | 16272.8554 | 16755.1352 | 16810.3113 | 16063.3907 | 15439.0836 | 15126.4191 | 14632.8998 | 14741.2084 | 14632.8998 | 13887.001 | 12978.6393 | 12013.058 | 16810.3113
2016-09-21 | 11093.4567 | 10330.1876 | 9829.5158 | 9504.59 | 9364.6063 | 9400.3686 | 9659.9005 | 9955.1947 | 11083.2389 | 12806.9804 | 14374.3897 | 15819.1854 | 16972.7741 | 17775.8926 | 18315.392 | 18518.7261 | 18490.1162 | 18111.0362 | 17257.8505 | 16863.4438 | 16429.1876 | 15266.4029 | 14011.6581 | 12584.2325 | 18518.7261
2016-09-22 | 11434.7309 | 10639.7867 | 10112.5487 | 9892.8661 | 9947.0204 | 10619.3511 | 11824.0288 | 12369.6589 | 13070.5994 | 14326.366 | 15580.0891 | 16678.5017 | 17500.0122 | 17670.6493 | 17455.0539 | 17180.1953 | 17023.8631 | 16717.3294 | 16526.2566 | 16641.7177 | 16249.3545 | 15162.1814 | 13823.6507 | 12458.5537 | 17670.6493
2016-09-23 | 11304.965 | 10513.0861 | 9981.7609 | 9704.8588 | 9734.4904 | 10444.6269 | 11797.4625 | 12377.8331 | 12669.0402 | 13501.7902 | 14100.5528 | 14811.7112 | 15325.6661 | 15436.0182 | 15492.2161 | 15616.8732 | 15785.4667 | 16058.2818 | 15879.4704 | 16116.5232 | 15909.102 | 14926.1504 | 13697.9718 | 12315.5046 | 16116.5232
2016-09-24 | 11146.5892 | 10380.2548 | 10001.1747 | 9703.837 | 9673.1836 | 10366.9717 | 11692.2193 | 12261.3503 | 12719.1074 | 13562.0752 | 14365.1937 | 15160.1379 | 15691.463 | 16337.2275 | 17065.7561 | 17638.9742 | 17692.1067 | 17460.1628 | 17052.4729 | 17045.3205 | 16813.3766 | 15852.9042 | 14462.2627 | 13149.2764 | 17692.1067
2016-09-25 | 12014.0797 | 11182.3515 | 10639.7867 | 10298.5125 | 10278.0769 | 10736.8557 | 11744.33 | 12370.6807 | 13114.5359 | 14441.8271 | 15739.4867 | 16590.6287 | 17045.3205 | 17446.8797 | 17981.2702 | 18416.5481 | 18103.8837 | 17265.003 | 16691.7849 | 16600.8465 | 16286.1385 | 15286.8385 | 14022.8976 | 12820.2635 | 18416.5481
2016-09-26 | 11714.6984 | 10971.865 | 10487.5416 | 10199.3999 | 10193.2692 | 10812.4674 | 12047.7984 | 12646.5611 | 13139.0586 | 14067.8559 | 15256.1851 | 16590.6287 | 17591.9723 | 18571.8586 | 18911.0893 | 18942.7644 | 18598.4248 | 17927.1159 | 17228.2189 | 17119.9104 | 16714.264 | 15854.9477 | 14730.9906 | 14369.2808 | 18942.7644
2016-09-27 | 13031.7718 | 11797.4625 | 11298.8343 | 10939.168 | 10799.1843 | 10860.491 | 11172.1337 | 11559.388 | 12804.9368 | 14608.3771 | 16122.6539 | 17528.622 | 18627.0347 | 19370.8899 | 19887.9102 | 19913.4547 | 19264.6249 | 18580.0328 | 17653.2791 | 17420.3134 | 16869.5745 | 16018.4324 | 14913.8891 | 13679.5798 | 19913.4547
2016-09-28 | 12582.189 | 11784.1794 | 11196.6564 | 10788.9665 | 10599.9373 | 10625.4818 | 10836.9901 | 11198.6999 | 12328.7877 | 14117.9231 | 15723.1382 | 17174.0646 | 18387.9383 | 19244.1893 | 19777.558 | 19942.0645 | 19715.2295 | 19053.1166 | 18050.7512 | 18030.3156 | 17637.9524 | 16546.6922 | 15141.7458 | 13658.1225 | 19942.0645
2016-09-29 | 12538.2525 | 11639.0868 | 11119.0012 | 10788.9665 | 10789.9883 | 11343.7926 | 12535.1871 | 13041.9896 | 13674.4709 | 15113.136 | 16638.6524 | 18122.2757 | 19027.5721 | 19782.6669 | 20159.7034 | 20156.6381 | 19900.1715 | 19206.3835 | 18430.8531 | 18112.0579 | 17154.6508 | 15992.8879 | 14541.9615 | 13143.1457 | 20159.7034
2016-09-30 | 11928.2503 | 11126.1536 | 10628.5471 | 10331.2094 | 10328.1441 | 10925.8849 | 12280.7641 | 12735.4558 | 13476.2458 | 14886.301 | 16267.7465 | 17436.6619 | 18366.481 | 18674.0365 | 18954.004 | 18514.6389 | 18454.354 | 18320.5009 | 17816.7638 | 17878.0705 | 17479.5766 | 16431.2312 | 15018.1106 | 13540.6178 | 18954.004
2016-10-01 | 12348.2015 | 11504.2119 | 11020.9104 | 10725.6162 | 10676.5708 | 11296.7907 | 12612.8423 | 13064.4687 | 13824.6725 | 15231.6624 | 16527.2784 | 17789.1757 | 18792.5629 | 19531.3092 | 19848.0608 | 20387.5602 | 20704.3118 | 20384.4949 | 19614.0734 | 19228.8626 | 18705.7117 | 17485.7073 | 15856.9913 | 15014.0234 | 20704.3118
2016-10-02 | 13271.8899 | 12168.3684 | 11576.7582 | 11199.7217 | 11102.6527 | 11612.5205 | 12817.1982 | 13242.2583 | 14025.963 | 15538.1962 | 17056.56 | 18304.1524 | 19315.7138 | 20345.6673 | 20901.5151 | 21291.8348 | 21519.6916 | 21134.4808 | 20252.6854 | 19803.1025 | 19214.5577 | 17866.8309 | 16360.7284 | 14703.4026 | 21519.6916
2016-10-03 | 13384.2856 | 12470.815 | 11765.7874 | 11360.1411 | 11201.7653 | 11657.4788 | 12817.1982 | 13318.8918 | 14190.4694 | 15793.641 | 17352.876 | 18772.1273 | 19730.5562 | 20764.5967 | 21287.7477 | 21568.737 | 21555.4538 | 20679.7891 | 19416.87 | 18717.973 | 17799.3935 | 16677.48 | 15407.4084 | 14133.2498 | 21568.737
2016-10-04 | 12932.6592 | 11984.4481 | 11379.5549 | 10957.56 | 10752.1824 | 10823.707 | 11141.4803 | 11539.9742 | 12870.3307 | 14612.4642 | 15935.6683 | 17089.257 | 18061.9908 | 18643.3831 | 18855.9132 | 18729.2126 | 18285.7604 | 17617.5168 | 16749.0045 | 16598.803 | 16107.3272 | 15171.3774 | 14024.9412 | 12828.4377 | 18855.9132
2016-10-05 | 11594.1285 | 10567.2404 | 9796.8189 | 9191.9256 | 8857.8038 | 8768.909 | 8921.1541 | 9067.2685 | 9828.494 | 10958.5818 | 12063.1251 | 12842.7427 | 13681.6234 | 14421.3915 | 15036.5026 | 15486.0854 | 15921.3634 | 15750.7262 | 15083.5044 | 15028.3283 | 14650.27 | 13629.5126 | 12393.1598 | 11078.13 | 15921.3634
2016-10-06 | 10020.5885 | 9271.6244 | 8814.8891 | 8577.8363 | 8634.0342 | 9347.236 | 10584.6106 | 11122.0665 | 11646.2392 | 12612.8423 | 13590.685 | 14458.1756 | 15363.4719 | 16028.6502 | 16695.872 | 16903.2932 | 17132.1717 | 16811.333 | 16485.3855 | 16824.6162 | 16298.3999 | 15183.6388 | 13934.0028 | 12542.3396 | 17132.1717
2016-10-07 | 11316.2045 | 10580.5235 | 10104.3744 | 9798.8624 | 9730.4032 | 10301.5778 | 11600.2592 | 12189.8258 | 12457.5319 | 13415.9608 | 14445.9142 | 15170.3557 | 15760.944 | 16255.4852 | 16502.7557 | 16390.36 | 16376.0551 | 16179.8735 | 16029.672 | 16416.9263 | 15976.5394 | 15189.7695 | 13820.5853 | 12274.6334 | 16502.7557
2016-10-08 | 11131.2625 | 10389.4508 | 9858.1256 | 9593.4848 | 9624.1382 | 10277.0551 | 11590.0414 | 12090.7132 | 12604.6681 | 13783.8013 | 15100.8747 | 16197.2437 | 17215.9576 | 17998.6405 | 18635.2089 | 18922.3288 | 18897.8061 | 18591.2724 | 18033.3809 | 18038.4898 | 17518.4042 | 16371.968 | 14963.9563 | 13542.6614 | 18922.3288
2016-10-09 | 12243.9801 | 11420.426 | 10847.2079 | 10425.2131 | 10358.7974 | 10240.2711 | 12037.5807 | 12515.7733 | 13123.7319 | 14537.8743 | 15881.514 | 17067.7996 | 17954.704 | 18804.8242 | 19384.173 | 19767.3402 | 19834.7777 | 19466.9372 | 18640.3178 | 18458.4411 | 17844.3518 | 16642.7395 | 15293.9909 | 13723.5163 | 19834.7777
2016-10-10 | 12391.1163 | 11430.6438 | 10855.3821 | 10441.5616 | 10366.9717 | 10871.7306 | 12068.234 | 12604.6681 | 13264.7375 | 14694.2066 | 16098.1312 | 17182.2389 | 18136.5806 | 18925.3942 | 19460.8065 | 19822.5163 | 19894.0409 | 19390.3037 | 18362.3938 | 17999.6622 | 17312.0048 | 16270.8118 | 15101.8964 | 13853.2823 | 19894.0409
2016-10-11 | 12627.1472 | 11730.0251 | 11156.807 | 10726.638 | 10485.4981 | 10497.7594 | 10782.8358 | 11080.1736 | 12293.0255 | 14195.5783 | 15767.0747 | 17085.1699 | 18098.7748 | 18866.131 | 19387.2384 | 19718.2948 | 19781.6451 | 19348.4108 | 18252.0417 | 17758.5223 | 17065.7561 | 16008.2146 | 14956.8038 | 13701.0372 | 19781.6451
2016-10-12 | 12560.7316 | 11637.0432 | 10937.1245 | 10497.7594 | 10286.2511 | 10246.4017 | 10450.7576 | 10605.0462 | 11926.2067 | 13957.5038 | 15597.4594 | 16967.6653 | 18122.2757 | 18867.1528 | 19360.6721 | 19626.3347 | 19655.9663 | 19272.7991 | 18352.1761 | 18272.4773 | 17609.3426 | 16461.8846 | 15265.3811 | 13878.8268 | 19655.9663
2016-10-13 | 12716.042 | 11880.2267 | 11352.9886 | 11040.3242 | 11047.4766 | 11617.6294 | 12742.6083 | 13211.6049 | 13832.8467 | 15147.8765 | 16620.2603 | 17788.1539 | 18602.512 | 19257.4724 | 19699.9028 | 19989.0663 | 19950.2387 | 19539.4835 | 18751.6917 | 18715.9294 | 18023.1632 | 16893.0754 | 15522.8695 | 14050.4857 | 19989.0663
2016-10-14 | 12809.0239 | 12022.254 | 11538.9524 | 11213.0048 | 11135.3496 | 11723.8944 | 12998.0531 | 13485.4418 | 14106.6835 | 15463.6063 | 16766.3748 | 17852.526 | 18612.7298 | 19425.0442 | 19863.3875 | 19981.9139 | 19745.8829 | 19134.8589 | 18586.1635 | 18723.0819 | 17951.6386 | 16752.0698 | 15319.5354 | 13788.9102 | 19981.9139
2016-10-15 | 12381.9202 | 11472.5368 | 10932.0156 | 10593.8067 | 10600.9591 | 11164.9812 | 12399.2905 | 12959.2255 | 13527.3347 | 14714.6421 | 15825.3161 | 16875.7051 | 15787.5103 | 18194.8221 | 18354.2196 | 18469.6807 | 18190.7349 | 17745.2392 | 17202.6745 | 17333.4622 | 16612.0861 | 15515.717 | 14062.747 | 12631.2344 | 18469.6807
2016-10-16 | 11365.2499 | 10523.3039 | 10002.1965 | 9646.6173 | 9488.2416 | 9925.5631 | 11008.649 | 11384.6638 | 11760.6785 | 12680.2798 | 13548.7921 | 14223.1663 | 14920.0198 | 15627.091 | 16259.5723 | 16884.9011 | 17238.4367 | 17059.6254 | 16343.3582 | 16275.9207 | 15596.4376 | 14409.1302 | 12997.0313 | 11499.103 | 17238.4367
2016-10-17 | 10199.3999 | 9312.4956 | 8812.8455 | 8520.6167 | 8448.0704 | 8970.1995 | 10084.9606 | 10579.5017 | 11074.0429 | 11993.6441 | 12844.7862 | 13613.1642 | 14248.7108 | 14979.2829 | 15685.3324 | 16318.8355 | 16624.3474 | 16346.4235 | 15467.6934 | 15165.2468 | 14384.6075 | 13304.5869 | 12273.6116 | 11093.4567 | 16624.3474
2016-10-18 | 10093.1349 | 9200.0998 | 8642.2084 | 8324.4351 | 8180.3642 | 8310.1302 | 8706.5805 | 9117.3357 | 10148.3109 | 11488.8852 | 12603.6463 | 13519.1605 | 14422.4133 | 15208.1615 | 15918.298 | 16461.8846 | 16660.1097 | 16350.5106 | 15463.6063 | 15222.4664 | 14478.6111 | 13444.5706 | 12469.7933 | 11305.9868 | 16660.1097
2016-10-19 | 10277.0551 | 9470.8713 | 8886.4136 | 8533.8998 | 8386.7636 | 8392.8943 | 8660.6004 | 8919.1106 | 10002.1965 | 11451.0794 | 12709.9114 | 13772.5617 | 14861.7783 | 15691.463 | 16356.6413 | 16751.0481 | 16885.9229 | 16581.4327 | 15901.9496 | 15959.1692 | 15313.4047 | 14155.7289 | 12954.1166 | 11648.2828 | 16885.9229
2016-10-20 | 10500.8248 | 9668.0747 | 9174.5554 | 8917.067 | 8932.3937 | 9513.7861 | 10659.2005 | 11247.7453 | 11906.7929 | 13186.0605 | 14422.4133 | 15461.5627 | 16336.2057 | 17016.7107 | 17629.7782 | 17808.5895 | 17684.9542 | 17266.0248 | 16852.2042 | 17001.384 | 16250.3763 | 15077.3737 | 13737.8212 | 12340.0273 | 17808.5895
2016-10-21 | 11109.8051 | 10364.9281 | 9932.7155 | 9660.9223 | 9681.3578 | 10285.2293 | 11563.4751 | 12203.1089 | 12447.3141 | 13242.2583 | 14123.032 | 14654.3572 | 15015.0452 | 15189.7695 | 15231.6624 | 15268.4465 | 15190.7912 | 15039.5679 | 15034.459 | 15472.8023 | 14916.9544 | 14028.0065 | 12811.0675 | 11395.9033 | 15472.8023
2016-10-22 | 10329.1658 | 9606.768 | 9187.8385 | 8981.4391 | 9030.4845 | 9591.4413 | 10993.3223 | 11668.7184 | 11948.6859 | 12686.4104 | 13616.2295 | 14535.8308 | 15210.205 | 15786.4885 | 16206.4398 | 16444.5143 | 16305.5523 | 15957.1256 | 15794.6627 | 16064.4124 | 15481.9983 | 14495.9814 | 13185.0387 | 11784.1794 | 16444.5143
2016-10-23 | 10625.4818 | 9952.1293 | 9499.4811 | 9225.6443 | 9194.9909 | 9779.4486 | 11123.0883 | 11788.2665 | 11948.6859 | 12578.1018 | 13298.4562 | 13896.197 | 14391.7599 | 14707.4897 | 14998.6968 | 15132.5498 | 15054.8946 | 14838.2774 | 14675.8145 | 14969.0652 | 14700.3372 | 13841.0209 | 12673.1273 | 11424.5131 | 15132.5498
2016-10-24 | 10362.8846 | 9644.5738 | 9227.6879 | 9043.7676 | 9102.009 | 9653.7698 | 10800.2061 | 11506.2555 | 11932.3374 | 12742.6083 | 13411.8737 | 13885.9792 | 14120.9884 | 14373.3679 | 14566.4842 | 14740.1866 | 14721.7946 | 14490.8725 | 14294.6909 | 14402.9995 | 13861.4565 | 13159.4942 | 12349.2233 | 11242.6364 | 14740.1866
2016-10-25 | 10082.9171 | 9247.1017 | 8696.3627 | 8349.9796 | 8226.3443 | 8320.348 | 8699.428 | 9171.49 | 10091.0913 | 11338.6837 | 12362.5064 | 13113.5141 | 13757.235 | 14349.867 | 14791.2756 | 15110.0707 | 15117.2231 | 14734.0559 | 14036.1808 | 13941.1553 | 13302.5433 | 12523.9475 | 11679.9579 | 10605.0462 | 15117.2231
2016-10-26 | 9636.3996 | 8918.0888 | 8478.7237 | 8171.1682 | 8044.4676 | 8070.0121 | 8323.4133 | 8712.7112 | 9573.0492 | 10857.4257 | 11962.9908 | 12782.4577 | 13475.224 | 14149.5982 | 14689.0977 | 15099.8529 | 15282.7514 | 15019.1323 | 14410.1519 | 14597.1375 | 13940.1335 | 12870.3307 | 11623.7601 | 10259.6849 | 15282.7514
2016-10-27 | 9135.7278 | 8417.417 | 7999.5093 | 7810.4801 | 7876.8958 | 8515.5078 | 9773.318 | 10481.4109 | 10848.2297 | 11776.0052 | 12703.7807 | 13534.4872 | 14219.0792 | 14940.4553 | 15559.6535 | 16123.6756 | 16414.8827 | 16196.222 | 15744.5956 | 15935.6683 | 15143.7894 | 13921.7415 | 12540.296 | 11050.542 | 16414.8827
2016-10-28 | 9879.583 | 9115.2922 | 8629.9471 | 8382.6765 | 8395.9596 | 9037.6369 | 10331.2094 | 10972.8867 | 11372.4024 | 12442.2052 | 13426.1786 | 14362.1283 | 15126.4191 | 16061.3471 | 16732.656 | 17212.8923 | 17442.7926 | 17173.0429 | 16603.9119 | 16758.2005 | 15937.7118 | 14829.0814 | 13421.0697 | 11964.0126 | 17442.7926
2016-10-29 | 10787.9447 | 9965.4125 | 9415.6952 | 9111.205 | 9110.1833 | 9677.2707 | 11014.7797 | 11577.78 | 11945.6205 | 13211.6049 | 14244.6237 | 15199.9873 | 16095.0658 | 16841.9864 | 17430.5312 | 17935.2901 | 18034.4027 | 17572.5585 | 16843.0082 | 16845.0517 | 16074.6302 | 14943.5207 | 13535.5089 | 12027.3629 | 18034.4027
2016-10-30 | 10667.3748 | 9830.5376 | 9267.5373 | 8949.7639 | 8911.9581 | 9472.9149 | 10740.9429 | 11358.0975 | 11720.8291 | 12859.0911 | 14055.5946 | 15027.3066 | 15845.7517 | 16504.7993 | 16884.9011 | 17177.13 | 17377.3987 | 16993.2097 | 16470.0588 | 16577.3456 | 15820.2072 | 14817.8418 | 13503.8338 | 12084.5825 | 17377.3987
2016-10-31 | 10789.9883 | 9931.6937 | 9331.9094 | 9025.3756 | 8959.9817 | 9512.7643 | 10784.8794 | 11429.622 | 11832.203 | 12935.7246 | 13942.1771 | 14845.4299 | 15507.5428 | 15966.3216 | 16305.5523 | 16559.9754 | 16615.1514 | 16085.8698 | 15124.3756 | 14597.1375 | 13597.8375 | 12731.3687 | 11692.2193 | 10528.4128 | 16615.1514
2016-11-01 | 9363.5845 | 8567.6185 | 8108.8397 | 7853.3949 | 7759.3912 | 7865.6562 | 8313.1955 | 8768.909 | 9683.4014 | 10787.9447 | 11587.9978 | 11953.7948 | 12092.7567 | 12088.6696 | 12130.5626 | 12158.1506 | 12070.2776 | 11743.3082 | 11514.4297 | 11842.4208 | 11325.4006 | 10674.5272 | 9886.7355 | 9063.1814 | 12158.1506
2016-11-02 | 16143.0894 | 7574.4491 | 7485.5544 | 7478.4019 | 7596.9283 | 7948.4203 | 8564.5532 | 9693.6192 | 10675.549 | 11069.9558 | 11125.1318 | 11017.845 | 10918.7324 | 10762.4002 | 10691.8975 | 10616.2858 | 10645.9174 | 11087.326 | 11955.8383 | 11710.6113 | 11277.3769 | 10537.6088 | 9592.463 | 8742.3428 | 16143.0894
2016-11-03 | 8035.2716 | 7811.5019 | 7685.8231 | 7733.8467 | 8007.6835 | 8936.4808 | 10454.8447 | 11053.6073 | 11207.896 | 11404.0776 | 11640.1085 | 11816.8763 | 11837.3119 | 11868.9871 | 11802.5714 | 11700.3935 | 11791.3319 | 12185.7386 | 13013.3798 | 12741.5865 | 12210.2613 | 11298.8343 | 10218.8137 | 9168.4247 | 13013.3798
2016-11-04 | 8428.6566 | 7953.5292 | 7686.8449 | 7634.7341 | 7762.4565 | 8503.2464 | 9704.8588 | 10552.9355 | 11217.092 | 11727.9816 | 12220.4791 | 12648.6046 | 12851.9387 | 13035.8589 | 13133.9497 | 13212.6267 | 13086.9479 | 13292.3255 | 14086.2479 | 13839.9991 | 13263.7157 | 12225.588 | 11174.1772 | 10100.2873 | 14086.2479
2016-11-05 | 9218.4919 | 8610.5332 | 8294.8035 | 8141.5366 | 8243.7145 | 8926.263 | 10142.1803 | 10550.8919 | 11573.6929 | 12551.5356 | 13289.2602 | 13858.3912 | 14233.3841 | 14417.3044 | 14486.7854 | 14349.867 | 14119.9666 | 14298.778 | 14986.4354 | 14643.1176 | 14054.5728 | 13126.7973 | 11899.6405 | 10645.9174 | 14986.4354
2016-11-06 | 9640.4867 | 8965.0906 | 8527.7691 | 8295.8253 | 8331.5875 | 9020.2667 | 10188.1603 | 11039.3024 | 11912.9236 | 12880.5485 | 13824.6725 | 14604.29 | 15199.9873 | 15639.3523 | 15848.817 | 15833.4904 | 15478.933 | 15139.7023 | 15501.4121 | 14957.8256 | 14082.1608 | 12936.7463 | 11616.6076 | 10372.0806 | 15848.817
2016-11-07 | 9311.4738 | 8619.7293 | 8184.4513 | 8014.836 | 8055.7071 | 8667.7529 | 9901.0404 | 10678.6143 | 11518.5168 | 12450.3794 | 13275.977 | 14006.5492 | 14588.9633 | 15060.0035 | 15261.294 | 15218.3793 | 14805.5805 | 14470.4369 | 14693.1848 | 13970.7869 | 13215.6921 | 12320.6135 | 11394.8815 | 10411.93 | 15261.294
2016-11-08 | 9462.6971 | 8766.8655 | 8285.6075 | 8076.1427 | 8033.228 | 8214.0829 | 8651.4044 | 9503.5683 | 10988.2134 | 12171.4337 | 12978.6393 | 13615.2077 | 14150.62 | 14373.3679 | 14340.671 | 14099.5311 | 13754.1697 | 13866.5654 | 14113.836 | 13486.4635 | 12839.6773 | 12074.3647 | 11252.8542 | 10293.4036 | 14373.3679
2016-11-09 | 9464.7407 | 8763.8001 | 8351.0013 | 8134.3841 | 8045.4894 | 8170.1464 | 8475.6584 | 9115.2922 | 10332.2312 | 11270.2245 | 11793.3754 | 12099.9092 | 12137.715 | 11985.4699 | 11827.0941 | 11576.7582 | 11519.5386 | 12089.6914 | 12588.3196 | 12224.5662 | 11687.1104 | 10904.4275 | 10070.6557 | 9075.4428 | 12588.3196
2016-11-10 | 8275.3897 | 7829.8939 | 7591.8194 | 7491.685 | 7615.3203 | 8158.9068 | 9468.8278 | 10497.7594 | 10958.5818 | 11517.495 | 11944.5987 | 12319.5917 | 12592.4068 | 12831.5031 | 12949.0077 | 13043.0114 | 12936.7463 | 13105.3399 | 13729.647 | 13274.9553 | 12562.7752 | 11585.9543 | 10549.8702 | 9451.4575 | 13729.647
2016-11-11 | 8464.4188 | 7886.0918 | 7572.4056 | 7455.9228 | 7538.6869 | 8003.5964 | 8923.1977 | 9860.1692 | 10679.6361 | 11405.0993 | 11946.6423 | 12334.9184 | 12693.5629 | 13024.6194 | 13178.908 | 13320.9353 | 13197.3 | 13263.7157 | 13865.5436 | 13443.5488 | 12730.3469 | 11758.6349 | 10664.3094 | 9466.7842 | 13865.5436
2016-11-12 | 8449.0921 | 7856.4602 | 7583.6452 | 7468.1841 | 7609.1896 | 8265.1719 | 9595.5284 | 10351.645 | 10874.7959 | 11540.996 | 12219.4574 | 12822.3071 | 13350.5669 | 13890.0663 | 14251.7762 | 14381.5421 | 14186.3823 | 14053.551 | 14547.0703 | 14058.6599 | 13317.87 | 12341.0491 | 11173.1555 | 9950.0858 | 14547.0703
2016-11-13 | 8949.7639 | 8349.9796 | 7983.1608 | 7869.7433 | 7960.6817 | 8597.2501 | 9884.6919 | 10675.549 | 11376.4895 | 12252.1543 | 13028.7065 | 13599.881 | 14153.6854 | 14640.0523 | 14856.6694 | 14886.301 | 14616.5513 | 14468.3934 | 14890.3882 | 14393.8035 | 13628.4909 | 12598.5374 | 11348.9015 | 10145.2456 | 14890.3882
2016-11-14 | 9120.4011 | 8438.8743 | 8061.8378 | 7864.6344 | 7911.6363 | 8488.9415 | 9774.3397 | 10598.9156 | 11312.1174 | 12071.2994 | 12731.3687 | 13165.6249 | 13572.293 | 13867.5872 | 14040.2679 | 14038.2243 | 13736.7994 | 13639.7304 | 13960.5691 | 13380.1985 | 12701.7371 | 11859.7911 | 11015.8015 | 10056.3508 | 14040.2679
2016-11-15 | 9185.7949 | 8549.2265 | 8188.5384 | 7992.3568 | 7974.9866 | 8180.3642 | 8677.9707 | 9456.5664 | 10658.1787 | 11657.4788 | 12304.265 | 12796.7626 | 13122.7102 | 13407.7865 | 13513.0298 | 13453.7666 | 13195.2565 | 13143.1457 | 13514.0516 | 12940.8335 | 12319.5917 | 11639.0868 | 10916.6889 | 10114.5922 | 13514.0516
2016-11-16 | 9283.8857 | 8728.0379 | 8365.3062 | 8162.994 | 8102.709 | 8267.2154 | 8565.575 | 9216.4483 | 10697.0064 | 12030.4282 | 12985.7917 | 13680.6016 | 14259.9504 | 14622.682 | 14775.9489 | 14766.7529 | 14478.6111 | 14424.4568 | 14867.909 | 14382.5639 | 13641.774 | 12762.0221 | 11820.9635 | 10744.0082 | 14867.909
2016-11-17 | 9842.799 | 9293.0817 | 8979.3955 | 8842.4771 | 9020.2667 | 9737.5557 | 11050.542 | 11820.9635 | 12716.042 | 13911.5237 | 15040.5897 | 15892.7535 | 16499.6904 | 16832.7904 | 16876.7269 | 16733.6778 | 16431.2312 | 16440.4272 | 16745.9392 | 16111.4143 | 15165.2468 | 13929.9157 | 12669.0402 | 11288.6165 | 16876.7269
2016-11-18 | 10200.4217 | 9495.394 | 9008.0054 | 8756.6477 | 8817.9544 | 9378.9112 | 10757.2913 | 11540.996 | 12173.4773 | 12881.5703 | 13354.654 | 13443.5488 | 13216.7138 | 12969.4433 | 12636.3433 | 12303.2432 | 12318.5699 | 12982.7264 | 13649.9482 | 13442.527 | 12935.7246 | 12149.9764 | 11103.6745 | 10109.4833 | 13649.9482
2016-11-19 | 9400.3686 | 9081.5735 | 8951.8075 | 8970.1995 | 9273.6679 | 10178.9643 | 11939.4899 | 12703.7807 | 13011.3362 | 13160.516 | 13079.7954 | 12769.1746 | 12392.138 | 12111.1488 | 11890.4445 | 11807.6803 | 11946.6423 | 12741.5865 | 13533.4654 | 13406.7648 | 13015.4233 | 12247.0454 | 11250.8107 | 10223.9226 | 13533.4654
2016-11-20 | 9481.0891 | 9108.1397 | 9016.1796 | 9055.0072 | 9372.7805 | 10266.8373 | 11841.399 | 12472.8586 | 12328.7877 | 12326.7442 | 12273.6116 | 12208.2178 | 12105.0181 | 11999.7748 | 11828.1159 | 11744.33 | 11782.1359 | 12517.8169 | 13314.8046 | 13195.2565 | 12756.9132 | 12004.8837 | 11031.1282 | 10002.1965 | 13314.8046
2016-11-21 | 9197.0345 | 8696.3627 | 8522.6602 | 8418.4388 | 8565.575 | 9511.7425 | 10820.6416 | 11570.6276 | 11832.203 | 12084.5825 | 12296.0908 | 12344.1144 | 12172.4555 | 12051.8856 | 11904.7494 | 11770.8963 | 11849.5733 | 12438.1181 | 12804.9368 | 12476.9457 | 12037.5807 | 11427.5785 | 10713.3548 | 9885.7137 | 12804.9368
2016-11-22 | 9077.4863 | 8555.3572 | 8264.1501 | 8160.9504 | 8198.7562 | 8434.7872 | 8978.3738 | 9707.9241 | 10928.9502 | 11986.4917 | 12592.4068 | 12918.3543 | 12935.7246 | 12915.289 | 12813.1111 | 12638.3868 | 12606.7117 | 13105.3399 | 13488.5071 | 13231.0187 | 12853.9822 | 12292.0037 | 11650.3263 | 10768.5309 | 13488.5071
2016-11-23 | 9920.4542 | 9367.6716 | 8934.4372 | 8687.1667 | 8641.1866 | 8789.3446 | 9099.9655 | 9809.0802 | 11427.5785 | 13018.4887 | 14050.4857 | 14715.6639 | 15135.6152 | 15440.1054 | 15495.2814 | 15392.0817 | 14999.7185 | 15157.0725 | 15646.5048 | 15317.4919 | 14736.0995 | 13873.7179 | 12914.2672 | 11953.7948 | 15646.5048
2016-11-24 | 10734.8122 | 9991.9787 | 9571.0057 | 9408.5428 | 9538.3088 | 10191.2257 | 11383.642 | 12215.3702 | 13293.3473 | 14481.6765 | 15553.5229 | 16658.0662 | 17504.0993 | 17932.2248 | 18133.5153 | 18057.9037 | 17580.7328 | 17404.9867 | 17757.5006 | 17159.7597 | 16367.8809 | 15177.5081 | 14090.335 | 12723.1945 | 18133.5153
2016-11-25 | 11529.7564 | 10704.1588 | 10240.2711 | 10058.3944 | 10103.3526 | 10745.03 | 11929.2721 | 12728.3034 | 13788.9102 | 14894.4753 | 15854.9477 | 16490.4944 | 16850.1606 | 17109.6926 | 17078.0174 | 16903.2932 | 16525.2349 | 16648.8701 | 16993.2097 | 16535.4527 | 15779.3361 | 14882.2139 | 13794.0191 | 12713.9985 | 17109.6926
2016-11-26 | 11653.3917 | 10930.9938 | 10457.91 | 10210.6395 | 10212.683 | 10582.5671 | 11379.5549 | 12135.6715 | 13034.8371 | 13669.362 | 13712.2767 | 13564.1188 | 13333.1967 | 12971.4868 | 12535.1871 | 12108.0834 | 11876.1395 | 12352.2886 | 12875.4396 | 12575.0365 | 12077.43 | 11557.3444 | 10865.5999 | 9984.8263 | 13712.2767
2016-11-27 | 9175.5771 | 8639.1431 | 8366.328 | 8296.847 | 8369.3934 | 8698.4063 | 9315.5609 | 10215.7484 | 11246.7236 | 11921.0978 | 12320.6135 | 12476.9457 | 12466.7279 | 12253.1761 | 12008.9708 | 11626.8254 | 11125.1318 | 10917.7107 | 11066.8904 | 10672.4837 | 10401.7122 | 10157.5069 | 9772.2962 | 9211.3394 | 12476.9457
2016-11-28 | 8674.9053 | 8355.0884 | 8226.3443 | 8270.2808 | 8501.2029 | 8985.5262 | 9757.9913 | 10571.3275 | 11341.749 | 11776.0052 | 11834.2466 | 11641.1303 | 11402.034 | 11185.4168 | 10984.1263 | 10853.3386 | 10863.5564 | 11528.7346 | 12285.873 | 12071.2994 | 11740.2429 | 11536.9089 | 10851.295 | 10072.6993 | 12285.873
2016-11-29 | 9371.7587 | 8991.6569 | 8789.3446 | 8763.8001 | 8883.3483 | 9133.6842 | 9680.3361 | 10374.1241 | 11111.8487 | 11449.0358 | 11491.9506 | 11464.3625 | 11365.2499 | 11254.8978 | 11120.0229 | 10986.1699 | 10867.6435 | 11328.4659 | 11922.1196 | 11655.4352 | 11240.5929 | 10767.5091 | 10128.8971 | 9350.3014 | 11922.1196
2016-11-30 | 8579.8799 | 8079.2081 | 7826.8286 | 7730.7814 | 7777.7832 | 7978.0519 | 8363.2627 | 8972.2431 | 10002.1965 | 10784.8794 | 11268.1809 | 11583.9107 | 11813.811 | 11931.3156 | 11954.8165 | 11876.1395 | 11760.6785 | 12221.5009 | 13031.7718 | 12750.7825 | 12281.7859 | 11567.5622 | 10704.1588 | 9610.8551 | 13031.7718
2016-12-01 | 8760.7348 | 8204.8869 | 7927.9847 | 7840.1117 | 7989.2915 | 8717.8201 | 10059.4161 | 10800.2061 | 11432.6874 | 12126.4754 | 12850.9169 | 13412.8954 | 13673.4491 | 13771.5399 | 13648.9264 | 13426.1786 | 13217.7356 | 13692.8629 | 14466.3498 | 14228.2752 | 13668.3402 | 12763.0439 | 11687.1104 | 10431.3438 | 14466.3498
2016-12-02 | 9363.5845 | 8696.3627 | 8271.3026 | 8103.7308 | 8219.1918 | 8881.3047 | 10262.7502 | 10969.8214 | 11476.6239 | 12205.1524 | 12900.9841 | 13325.0224 | 13569.2277 | 13721.4728 | 13669.362 | 13491.5724 | 13249.4108 | 13768.4746 | 14524.5912 | 14250.7544 | 13697.9718 | 12831.5031 | 11705.5024 | 10442.5833 | 14524.5912
2016-12-03 | 9349.2796 | 8637.0995 | 8256.9976 | 8076.1427 | 8153.7979 | 8824.0851 | 10326.1005 | 10970.8432 | 11597.1938 | 12481.0328 | 13154.3853 | 13697.9718 | 14104.64 | 14294.6909 | 14441.8271 | 14510.2863 | 14175.1427 | 14332.4967 | 14997.675 | 14642.0958 | 14004.5056 | 13066.5123 | 11918.0325 | 10579.5017 | 14997.675
2016-12-04 | 9469.8495 | 8788.3228 | 8395.9596 | 8227.366 | 8325.4569 | 9015.1578 | 10360.841 | 11096.522 | 11703.4589 | 12564.8187 | 13249.4108 | 13818.5418 | 14257.9068 | 14452.0449 | 14580.7891 | 14628.8127 | 14267.1028 | 14439.7835 | 15140.7241 | 14842.3645 | 14254.8415 | 13391.4381 | 12196.9782 | 10894.2097 | 15140.7241
2016-12-05 | 9767.1873 | 8992.6787 | 8571.7056 | 8399.025 | 8466.4624 | 9132.6624 | 10482.4327 | 11224.2444 | 11958.9037 | 12977.6175 | 13731.6906 | 14237.4713 | 14514.3734 | 14488.8289 | 14461.2409 | 14562.397 | 14426.5004 | 14605.3118 | 14985.4136 | 14520.5041 | 13916.6326 | 13159.4942 | 12284.8512 | 11193.591 | 14985.4136
2016-12-06 | 10105.3962 | 9334.9747 | 8851.6731 | 8549.2265 | 8426.613 | 8562.5096 | 8989.6133 | 9670.1183 | 11068.934 | 12429.9439 | 13422.0915 | 14073.9866 | 14512.3299 | 14782.0796 | 14902.6495 | 14805.5805 | 14365.1937 | 14176.1645 | 14475.5458 | 13781.7577 | 13104.3181 | 12394.1816 | 11501.1466 | 10446.6705 | 14902.6495
2016-12-07 | 9359.4974 | 8675.9271 | 8225.3225 | 7932.0719 | 7850.3295 | 7965.7906 | 8266.1937 | 8812.8455 | 10108.4615 | 11389.7726 | 12206.1742 | 12734.4341 | 13010.3144 | 13161.5378 | 13206.496 | 13010.3144 | 12741.5865 | 13057.3163 | 13864.5218 | 13335.2402 | 12765.0874 | 11936.4245 | 10856.4039 | 9662.9658 | 13864.5218
2016-12-08 | 8645.2737 | 8026.0755 | 7715.4547 | 7607.1461 | 7731.8031 | 8419.4605 | 9745.7299 | 10477.3238 | 10958.5818 | 11521.5822 | 12007.9491 | 12324.7006 | 12530.0782 | 12695.6065 | 12772.2399 | 12864.2 | 12828.4377 | 13275.977 | 14139.3805 | 13895.1752 | 13213.6485 | 12257.2632 | 11122.0665 | 9786.6011 | 14139.3805
2016-12-09 | 8714.7547 | 8143.5802 | 7855.4384 | 7774.7179 | 7906.5274 | 8664.6875 | 10222.9008 | 10945.2987 | 11314.161 | 11612.5205 | 11789.2883 | 11827.0941 | 11811.7675 | 11744.33 | 11637.0432 | 11479.6892 | 11557.3444 | 12368.6371 | 13402.6777 | 13290.2819 | 12852.9604 | 12116.2577 | 11053.6073 | 9937.8244 | 13402.6777
2016-12-10 | 9076.4646 | 8699.428 | 8522.6602 | 8626.8817 | 8924.2195 | 10046.133 | 11937.4463 | 12980.6828 | 12886.6792 | 12565.8405 | 12312.4393 | 12002.8402 | 11738.1994 | 11556.3227 | 11332.553 | 11246.7236 | 11368.3153 | 12318.5699 | 13595.7939 | 13594.7721 | 13411.8737 | 12777.3488 | 11797.4625 | 10709.2677 | 13595.7939
2016-12-11 | 9989.9352 | 9648.6609 | 9568.9621 | 9595.5284 | 9950.0858 | 11053.6073 | 13018.4887 | 13926.8504 | 13542.6614 | 13150.2982 | 12662.9095 | 12336.962 | 12013.058 | 11767.8309 | 11536.9089 | 11439.8398 | 11568.584 | 12466.7279 | 13530.4001 | 13447.6359 | 13191.1694 | 12549.492 | 11478.6674 | 10404.7775 | 13926.8504
2016-12-12 | 9620.0511 | 9213.383 | 9070.3339 | 9052.9636 | 9408.5428 | 10470.1714 | 12222.5227 | 13066.5123 | 13125.7755 | 13114.5359 | 12910.1801 | 12647.5828 | 12329.8095 | 12060.0598 | 11782.1359 | 11684.0451 | 11838.3337 | 12806.9804 | 13711.255 | 13545.7267 | 13344.4362 | 12849.8951 | 12120.3448 | 11237.5275 | 13711.255
2016-12-13 | 10432.3655 | 10080.8735 | 9914.3235 | 9934.7591 | 10125.8318 | 10641.8303 | 11434.7309 | 12374.7678 | 12928.5721 | 12895.8752 | 12505.5555 | 12144.8675 | 11876.1395 | 11609.4552 | 11372.4024 | 11247.7453 | 11213.0048 | 11839.3555 | 12597.5157 | 12355.354 | 12095.8221 | 11711.6331 | 11129.219 | 10484.4763 | 12928.5721
2016-12-14 | 9822.3634 | 9407.521 | 9264.4719 | 9276.7333 | 9420.8041 | 9833.6029 | 10584.6106 | 11514.4297 | 12358.4193 | 12453.4448 | 12115.2359 | 11857.7475 | 11657.4788 | 11491.9506 | 11380.5766 | 11281.4641 | 11285.5512 | 11942.5552 | 13022.5758 | 12889.7445 | 12583.2107 | 12016.1233 | 11051.5637 | 10105.3962 | 13022.5758
2016-12-15 | 9392.1943 | 9030.4845 | 9002.8965 | 9080.5517 | 9499.4811 | 10567.2404 | 12467.7497 | 13442.527 | 13360.7847 | 12883.6138 | 12532.1218 | 12251.1325 | 12184.7169 | 12078.4518 | 11950.7294 | 11931.3156 | 11961.969 | 12674.1491 | 13775.6271 | 13665.2749 | 13237.1494 | 12455.4883 | 11380.5766 | 10244.3582 | 13775.6271
2016-12-16 | 9379.933 | 8969.1777 | 8818.9762 | 8873.1305 | 9172.5118 | 10174.8772 | 12009.9926 | 12851.9387 | 12764.0657 | 12433.0092 | 12213.3267 | 12100.931 | 12063.1251 | 12080.4954 | 12060.0598 | 12086.6261 | 12101.9527 | 12644.5175 | 13630.5344 | 13449.6795 | 12919.3761 | 12021.2322 | 10951.4294 | 9774.3397 | 13630.5344
2016-12-17 | 8793.4317 | 8277.4332 | 8073.0774 | 8049.5765 | 8314.2173 | 9201.1216 | 10786.9229 | 11637.0432 | 11721.8509 | 11820.9635 | 11909.8583 | 11961.969 | 12066.1905 | 12193.9129 | 12327.7659 | 12462.6408 | 12396.2252 | 12882.592 | 13740.8866 | 13470.1151 | 12894.8534 | 12128.519 | 11038.2806 | 9806.0149 | 13740.8866
2016-12-18 | 8840.4336 | 8310.1302 | 8092.4912 | 8081.2516 | 8328.5222 | 9162.294 | 10768.5309 | 11651.3481 | 11957.8819 | 12138.7368 | 12214.3485 | 12152.0199 | 12141.8021 | 12333.8966 | 12451.4012 | 12481.0328 | 12420.7479 | 12868.2871 | 13730.6688 | 13462.9626 | 13027.6847 | 12238.8712 | 11207.896 | 10041.0241 | 13730.6688
2016-12-19 | 9106.0962 | 8597.2501 | 8349.9796 | 8311.1519 | 8532.878 | 9338.04 | 10789.9883 | 11729.0033 | 12052.9073 | 12236.8276 | 12398.2687 | 12461.619 | 12454.4666 | 12512.708 | 12511.6862 | 12488.1853 | 12370.6807 | 12720.1292 | 13453.7666 | 13069.5776 | 12547.4485 | 11892.488 | 11138.415 | 10142.1803 | 13453.7666
2016-12-20 | 9245.0581 | 8647.3173 | 8339.7618 | 8198.7562 | 8184.4513 | 8486.898 | 9066.2468 | 9835.6465 | 10838.0119 | 11604.3463 | 12026.3411 | 12101.9527 | 12405.4212 | 12441.1834 | 12476.9457 | 12487.1635 | 12372.7242 | 12682.3233 | 13335.2402 | 12850.9169 | 12312.4393 | 11698.35 | 10929.972 | 9980.7391 | 13335.2402
2016-12-21 | 9019.2449 | 8342.8271 | 7927.9847 | 7735.8903 | 7709.324 | 7849.3077 | 8217.1483 | 8831.2376 | 10033.8717 | 11224.2444 | 11949.7076 | 12325.7224 | 12713.9985 | 12829.4595 | 12742.6083 | 12581.1672 | 12449.3577 | 12952.073 | 13725.5599 | 13413.9172 | 12974.5522 | 12327.7659 | 11424.5131 | 10262.7502 | 13725.5599
2016-12-22 | 9201.1216 | 8497.1158 | 8074.0992 | 7864.6344 | 7927.9847 | 8433.7654 | 9317.6044 | 10198.3781 | 11368.3153 | 12485.1199 | 13407.7865 | 13991.2225 | 14382.5639 | 14671.7274 | 14873.0179 | 14772.8835 | 14425.4786 | 14628.8127 | 15397.1906 | 14981.3265 | 14359.063 | 13610.0988 | 12592.4068 | 11207.896 | 15397.1906
2016-12-23 | 10006.2836 | 9163.3158 | 8625.8599 | 8356.1102 | 8392.8943 | 8894.5879 | 9749.817 | 10614.2422 | 11853.6604 | 13104.3181 | 14025.963 | 14677.8581 | 15147.8765 | 15333.8403 | 14915.9326 | 14466.3498 | 14066.8341 | 14223.1663 | 14937.39 | 14532.7654 | 13950.3513 | 13501.7902 | 12843.7644 | 11988.5353 | 15333.8403
2016-12-24 | 10945.2987 | 10137.0714 | 9610.8551 | 9378.9112 | 9325.7787 | 9640.4867 | 10226.9879 | 10969.8214 | 12378.8549 | 13948.3077 | 15158.0943 | 15964.2781 | 16382.1858 | 16454.7321 | 16508.8864 | 16312.7048 | 16100.1747 | 16293.291 | 16473.1241 | 15541.2615 | 14664.575 | 13923.785 | 13202.4089 | 12170.4119 | 16508.8864
2016-12-25 | 11120.0229 | 10307.7085 | 9581.2235 | 9022.3103 | 8638.1213 | 8569.6621 | 8729.0596 | 9172.5118 | 10222.9008 | 11292.7036 | 11964.0126 | 12301.1997 | 12418.7043 | 12333.8966 | 12153.0417 | 11771.9181 | 11365.2499 | 11539.9742 | 12022.254 | 11771.9181 | 11568.584 | 11249.7889 | 10669.4183 | 9843.8207 | 12418.7043
2016-12-26 | 8986.548 | 8389.8289 | 8117.0139 | 7972.943 | 8040.3805 | 8405.1556 | 9028.4409 | 9751.8606 | 10660.2223 | 11505.2337 | 12153.0417 | 12419.7261 | 12412.5736 | 12256.2414 | 12160.1942 | 12091.735 | 12152.0199 | 12840.6991 | 13573.3148 | 13309.6957 | 12817.1982 | 12207.196 | 11470.4932 | 10482.4327 | 13573.3148
2016-12-27 | 9485.1762 | 8760.7348 | 8283.5639 | 8064.9032 | 8065.9249 | 8227.366 | 8651.4044 | 9123.4664 | 10229.0315 | 11552.2355 | 12575.0365 | 13233.0623 | 13641.774 | 13774.6053 | 13779.7142 | 13564.1188 | 13301.5215 | 13604.9899 | 14282.4295 | 13856.3476 | 13242.2583 | 12582.189 | 11713.6767 | 10615.264 | 14282.4295
2016-12-28 | 9577.1364 | 8804.6713 | 8315.2391 | 8035.2716 | 7897.3314 | 7960.6817 | 8275.3897 | 8685.1231 | 10053.2855 | 11532.8217 | 12615.9077 | 13423.1132 | 13983.0482 | 14374.3897 | 14580.7891 | 14573.6366 | 14349.867 | 14284.4731 | 14920.0198 | 14424.4568 | 13743.9519 | 12961.269 | 11956.8601 | 10699.0499 | 14920.0198
2016-12-29 | 9621.0729 | 8881.3047 | 8434.7872 | 8238.6056 | 8260.063 | 8651.4044 | 9464.7407 | 10230.0533 | 11469.4714 | 12868.2871 | 13975.8958 | 14692.163 | 15065.1124 | 15231.6624 | 15354.2759 | 15416.6044 | 15171.3774 | 15101.8964 | 15805.9023 | 15271.5118 | 14546.0486 | 13562.0752 | 12486.1417 | 11142.5021 | 15805.9023
2016-12-30 | 9925.5631 | 9128.5753 | 8644.252 | 8380.6329 | 8355.0884 | 8747.4517 | 9505.6118 | 10247.4235 | 11326.4223 | 12525.9911 | 13598.8593 | 14470.4369 | 15013.0017 | 15393.1035 | 15496.3032 | 15369.6026 | 15072.2649 | 15069.1995 | 15764.0094 | 15236.7713 | 14582.8326 | 13646.8829 | 12638.3868 | 11399.9904 | 15764.0094
2016-12-31 | 10248.4453 | 9419.7824 | 8914.0017 | 8641.1866 | 8617.6857 | 8961.0035 | 9662.9658 | 10452.8011 | 11491.9506 | 12555.6227 | 13401.6559 | 13892.1099 | 14008.5927 | 14084.2044 | 14060.7035 | 13913.5672 | 13955.4602 | 14680.9234 | 15303.187 | 14570.5713 | 13692.8629 | 12732.3905 | 11753.526 | 10948.364 | 15303.187
Max | 16143.0894 | 14323.3007 | 13543.6832 | 13064.4687 | 13194.2347 | 14525.613 | 16781.7014 | 17871.9398 | 17252.7416 | 17280.3297 | 18777.2362 | 20137.2243 | 21219.2885 | 22150.1293 | 22670.2149 | 23196.4312 | 23214.8232 | 23000.2496 | 22558.841 | 21685.2198 | 21147.7639 | 20269.0338 | 18648.492 | 16929.8594 | 6274035.878
Note on C80: Jessica Shrader: Blank due to Daylight Savings Time. No "HR-2" occurred.
Note on B320: Jessica Shrader: Hour 1 and 2 combined due to the end of DST.

## Hourly Loads p.u of Peak
OPC 012918
FPL RC-16
Hourly Loads p.u. of Peak
(hourly load/peak)
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | Max
2016-01-01 | 0.41084 | 0.39589 | 0.3754 | 0.36142 | 0.35533 | 0.35831 | 0.36763 | 0.37532 | 0.40937 | 0.46315 | 0.51349 | 0.54796 | 0.56837 | 0.57639 | 0.57399 | 0.56665 | 0.55905 | 0.56555 | 0.59301 | 0.57668 | 0.55195 | 0.52441 | 0.4878 | 0.4417 | 0.59301
2016-01-02 | 0.39853 | 0.37086 | 0.35226 | 0.34336 | 0.34084 | 0.35117 | 0.39068 | 0.42276 | 0.47041 | 0.52647 | 0.57156 | 0.60246 | 0.62455 | 0.63991 | 0.6468 | 0.64331 | 0.63034 | 0.62484 | 0.64806 | 0.62337 | 0.59016 | 0.55313 | 0.51164 | 0.46307 | 0.64806
2016-01-03 | 0.4165 | 0.38321 | 0.36255 | 0.35252 | 0.35168 | 0.36331 | 0.39744 | 0.42952 | 0.46693 | 0.49867 | 0.51681 | 0.52269 | 0.52273 | 0.5179 | 0.51303 | 0.51001 | 0.50845 | 0.53276 | 0.56938 | 0.55942 | 0.53902 | 0.51433 | 0.48087 | 0.4422 | 0.56938
2016-01-04 | 0.40764 | 0.38451 | 0.37065 | 0.36465 | 0.36541 | 0.37448 | 0.39383 | 0.41936 | 0.4587 | 0.49346 | 0.51379 | 0.51824 | 0.51404 | 0.50732 | 0.49871 | 0.49069 | 0.49237 | 0.51719 | 0.53889 | 0.52424 | 0.50556 | 0.48263 | 0.45387 | 0.4199 | 0.53889
2016-01-05 | 0.38518 | 0.36028 | 0.34458 | 0.33555 | 0.33371 | 0.34152 | 0.35999 | 0.38132 | 0.4228 | 0.46319 | 0.50698 | 0.53402 | 0.54805 | 0.55246 | 0.55208 | 0.54691 | 0.53978 | 0.54578 | 0.5792 | 0.5622 | 0.53839 | 0.50237 | 0.46021 | 0.41495 | 0.5792
2016-01-06 | 0.36952 | 0.3445 | 0.32959 | 0.32426 | 0.3285 | 0.35306 | 0.40387 | 0.43594 | 0.46504 | 0.50413 | 0.54439 | 0.56992 | 0.58999 | 0.6007 | 0.59738 | 0.58466 | 0.57261 | 0.59066 | 0.62089 | 0.60351 | 0.56476 | 0.51706 | 0.47696 | 0.43267 | 0.62089
2016-01-07 | 0.39879 | 0.38002 | 0.37523 | 0.37905 | 0.39694 | 0.43737 | 0.5129 | 0.56648 | 0.59016 | 0.60418 | 0.59864 | 0.58306 | 0.56812 | 0.55329 | 0.54162 | 0.54087 | 0.55682 | 0.60784 | 0.66557 | 0.66951 | 0.65499 | 0.61749 | 0.57064 | 0.52432 | 0.66951
2016-01-08 | 0.48872 | 0.47008 | 0.4634 | 0.46042 | 0.46756 | 0.49955 | 0.55942 | 0.58835 | 0.58546 | 0.58546 | 0.58185 | 0.56715 | 0.54704 | 0.52798 | 0.51156 | 0.50509 | 0.50984 | 0.5381 | 0.57101 | 0.5606 | 0.53637 | 0.49712 | 0.45156 | 0.40349 | 0.58835
2016-01-09 | 0.3644 | 0.3442 | 0.33467 | 0.33119 | 0.33807 | 0.36662 | 0.42477 | 0.4629 | 0.47486 | 0.49636 | 0.5111 | 0.51908 | 0.51979 | 0.51597 | 0.5111 | 0.50938 | 0.51244 | 0.53667 | 0.57311 | 0.56623 | 0.54397 | 0.50862 | 0.46626 | 0.41743 | 0.57311
2016-01-10 | 0.37418 | 0.34685 | 0.33115 | 0.32523 | 0.32875 | 0.35323 | 0.4084 | 0.44526 | 0.47314 | 0.50686 | 0.53356 | 0.55057 | 0.56001 | 0.56711 | 0.56736 | 0.56581 | 0.56362 | 0.56698 | 0.59683 | 0.58017 | 0.55367 | 0.52059 | 0.4862 | 0.44686 | 0.59683
2016-01-11 | 0.40088 | 0.37208 | 0.3526 | 0.34315 | 0.34118 | 0.35042 | 0.37112 | 0.39732 | 0.45593 | 0.51828 | 0.56152 | 0.5884 | 0.60834 | 0.62043 | 0.62534 | 0.62266 | 0.60926 | 0.59835 | 0.61619 | 0.59314 | 0.56316 | 0.52768 | 0.4909 | 0.44967 | 0.62534
2016-01-12 | 0.40529 | 0.37385 | 0.3542 | 0.34278 | 0.33707 | 0.34055 | 0.35436 | 0.37267 | 0.41739 | 0.46332 | 0.4959 | 0.51454 | 0.53096 | 0.54133 | 0.54423 | 0.54082 | 0.53289 | 0.52735 | 0.55825 | 0.54742 | 0.5226 | 0.48784 | 0.44833 | 0.4024 | 0.55825
2016-01-13 | 0.3644 | 0.34332 | 0.3335 | 0.33249 | 0.3416 | 0.37594 | 0.44052 | 0.47915 | 0.49443 | 0.51484 | 0.53285 | 0.54628 | 0.55854 | 0.56799 | 0.57404 | 0.57836 | 0.57584 | 0.58092 | 0.61695 | 0.60897 | 0.57739 | 0.5336 | 0.48566 | 0.43149 | 0.61695
2016-01-14 | 0.38455 | 0.35596 | 0.34072 | 0.33291 | 0.33602 | 0.36289 | 0.42108 | 0.45572 | 0.48347 | 0.52134 | 0.55283 | 0.57114 | 0.5805 | 0.58096 | 0.57698 | 0.56623 | 0.56329 | 0.57639 | 0.61098 | 0.60191 | 0.57374 | 0.53335 | 0.48314 | 0.42893 | 0.61098
2016-01-15 | 0.38241 | 0.35642 | 0.34181 | 0.33686 | 0.34026 | 0.37007 | 0.43208 | 0.46815 | 0.48091 | 0.49783 | 0.50661 | 0.50724 | 0.50027 | 0.49338 | 0.4857 | 0.48204 | 0.48586 | 0.51282 | 0.54805 | 0.54011 | 0.51882 | 0.48557 | 0.44312 | 0.39631 | 0.54805
2016-01-16 | 0.3615 | 0.34294 | 0.33744 | 0.3395 | 0.35155 | 0.39194 | 0.46714 | 0.51576 | 0.52403 | 0.52701 | 0.52693 | 0.51903 | 0.50694 | 0.49414 | 0.48297 | 0.47747 | 0.48309 | 0.51719 | 0.58965 | 0.60359 | 0.6004 | 0.58096 | 0.5496 | 0.51467 | 0.60359
2016-01-17 | 0.48998 | 0.48024 | 0.48167 | 0.48998 | 0.5085 | 0.55544 | 0.63844 | 0.68862 | 0.68148 | 0.64592 | 0.60674 | 0.56656 | 0.53318 | 0.50619 | 0.48729 | 0.47688 | 0.47877 | 0.50824 | 0.55565 | 0.5522 | 0.54103 | 0.51895 | 0.49346 | 0.4626 | 0.68862
2016-01-18 | 0.43296 | 0.41978 | 0.41587 | 0.41755 | 0.42671 | 0.44762 | 0.48297 | 0.5281 | 0.55846 | 0.56182 | 0.55128 | 0.52966 | 0.5069 | 0.48645 | 0.46831 | 0.45845 | 0.45857 | 0.48465 | 0.54208 | 0.55216 | 0.55212 | 0.54758 | 0.53558 | 0.5184 | 0.56182
2016-01-19 | 0.5061 | 0.5019 | 0.50514 | 0.51475 | 0.5302 | 0.55518 | 0.5939 | 0.64058 | 0.66725 | 0.64646 | 0.60108 | 0.55682 | 0.52147 | 0.49544 | 0.47449 | 0.45761 | 0.45257 | 0.46714 | 0.51761 | 0.51442 | 0.5022 | 0.47743 | 0.45219 | 0.41667 | 0.66725
2016-01-20 | 0.39068 | 0.37838 | 0.37557 | 0.37914 | 0.39404 | 0.42364 | 0.47222 | 0.51798 | 0.53461 | 0.52714 | 0.51698 | 0.50719 | 0.49565 | 0.48675 | 0.47994 | 0.47617 | 0.47684 | 0.49292 | 0.53818 | 0.53457 | 0.51085 | 0.47608 | 0.43326 | 0.38732 | 0.53818
2016-01-21 | 0.35273 | 0.33459 | 0.32711 | 0.32707 | 0.33555 | 0.36977 | 0.43594 | 0.47465 | 0.48301 | 0.48557 | 0.48817 | 0.48809 | 0.48708 | 0.48259 | 0.47864 | 0.47461 | 0.47617 | 0.4972 | 0.5386 | 0.53709 | 0.51475 | 0.47902 | 0.4367 | 0.39341 | 0.5386
2016-01-22 | 0.35923 | 0.34639 | 0.34429 | 0.35084 | 0.37032 | 0.41835 | 0.50375 | 0.55716 | 0.54922 | 0.55905 | 0.55212 | 0.53822 | 0.52235 | 0.50388 | 0.49086 | 0.48381 | 0.48864 | 0.52122 | 0.5931 | 0.61279 | 0.6122 | 0.59335 | 0.56388 | 0.52865 | 0.61279
2016-01-23 | 0.50749 | 0.50237 | 0.50778 | 0.51983 | 0.54217 | 0.59688 | 0.68958 | 0.73438 | 0.70894 | 0.66649 | 0.6261 | 0.58134 | 0.54393 | 0.51274 | 0.49178 | 0.48104 | 0.48192 | 0.50719 | 0.56761 | 0.57861 | 0.56946 | 0.54376 | 0.50346 | 0.46328 | 0.73438
2016-01-24 | 0.43389 | 0.42352 | 0.42284 | 0.42855 | 0.44543 | 0.49183 | 0.57328 | 0.61594 | 0.61552 | 0.60175 | 0.58407 | 0.55842 | 0.53562 | 0.51601 | 0.49989 | 0.49057 | 0.493 | 0.51513 | 0.56446 | 0.56564 | 0.55287 | 0.53134 | 0.50425 | 0.4705 | 0.61594
2016-01-25 | 0.44237 | 0.42818 | 0.42247 | 0.4241 | 0.43179 | 0.44963 | 0.48091 | 0.52013 | 0.55674 | 0.55464 | 0.53352 | 0.51043 | 0.49195 | 0.47734 | 0.46609 | 0.45757 | 0.45383 | 0.46491 | 0.50266 | 0.49875 | 0.48179 | 0.46101 | 0.43263 | 0.40021 | 0.55674
2016-01-26 | 0.37229 | 0.35386 | 0.34597 | 0.34261 | 0.34517 | 0.35709 | 0.37972 | 0.41084 | 0.45442 | 0.4768 | 0.48683 | 0.48578 | 0.48519 | 0.48465 | 0.48141 | 0.47797 | 0.4773 | 0.48935 | 0.52747 | 0.52621 | 0.50279 | 0.46953 | 0.43082 | 0.3856 | 0.52747
2016-01-27 | 0.34832 | 0.32619 | 0.31649 | 0.31389 | 0.32266 | 0.35369 | 0.41823 | 0.45412 | 0.46903 | 0.48645 | 0.50623 | 0.5192 | 0.52978 | 0.53847 | 0.54246 | 0.5475 | 0.54977 | 0.55392 | 0.58709 | 0.58327 | 0.55271 | 0.50711 | 0.45643 | 0.40109 | 0.58709
2016-01-28 | 0.35462 | 0.32909 | 0.31662 | 0.31166 | 0.31779 | 0.3476 | 0.40853 | 0.44682 | 0.46382 | 0.4867 | 0.51026 | 0.52684 | 0.54221 | 0.55497 | 0.56434 | 0.57143 | 0.57387 | 0.575 | 0.60347 | 0.59843 | 0.57064 | 0.52437 | 0.47612 | 0.42255 | 0.60347
2016-01-29 | 0.37565 | 0.3492 | 0.33631 | 0.33169 | 0.33799 | 0.36944 | 0.43074 | 0.47167 | 0.48931 | 0.51332 | 0.53108 | 0.54578 | 0.47827 | 0.5433 | 0.53755 | 0.53986 | 0.54834 | 0.57055 | 0.59847 | 0.59159 | 0.57248 | 0.53663 | 0.49267 | 0.44241 | 0.59847
2016-01-30 | 0.40542 | 0.38321 | 0.37208 | 0.36965 | 0.37825 | 0.41163 | 0.48007 | 0.52151 | 0.54213 | 0.56165 | 0.57236 | 0.57097 | 0.56484 | 0.55762 | 0.54956 | 0.5449 | 0.54805 | 0.56681 | 0.59994 | 0.59478 | 0.57118 | 0.53667 | 0.48855 | 0.43867 | 0.59994
2016-01-31 | 0.40139 | 0.37977 | 0.37091 | 0.36713 | 0.37296 | 0.40454 | 0.46869 | 0.50707 | 0.52239 | 0.542 | 0.55628 | 0.56417 | 0.56581 | 0.56371 | 0.5598 | 0.56207 | 0.55884 | 0.564 | 0.58823 | 0.57886 | 0.55325 | 0.52067 | 0.48276 | 0.4388 | 0.58823
2016-02-01 | 0.39786 | 0.37007 | 0.3526 | 0.34341 | 0.34173 | 0.34983 | 0.37124 | 0.40223 | 0.45778 | 0.50988 | 0.54456 | 0.56354 | 0.57752 | 0.58592 | 0.59117 | 0.59301 | 0.58848 | 0.57731 | 0.59033 | 0.5787 | 0.54834 | 0.51408 | 0.47701 | 0.43447 | 0.59301
2016-02-02 | 0.39257 | 0.36427 | 0.34618 | 0.33602 | 0.33245 | 0.33576 | 0.34979 | 0.37418 | 0.43586 | 0.4925 | 0.52743 | 0.54947 | 0.57685 | 0.59616 | 0.60977 | 0.61602 | 0.61527 | 0.60317 | 0.60296 | 0.57475 | 0.54821 | 0.53201 | 0.51005 | 0.45647 | 0.61602
2016-02-03 | 0.40798 | 0.36767 | 0.35197 | 0.34529 | 0.34958 | 0.37746 | 0.43363 | 0.46794 | 0.49913 | 0.53877 | 0.57836 | 0.60578 | 0.62706 | 0.64357 | 0.65557 | 0.66044 | 0.65217 | 0.64096 | 0.65839 | 0.64982 | 0.61317 | 0.57089 | 0.51824 | 0.46126 | 0.66044
2016-02-04 | 0.41264 | 0.38396 | 0.36671 | 0.35831 | 0.36016 | 0.38476 | 0.44098 | 0.47419 | 0.50329 | 0.54519 | 0.58277 | 0.61035 | 0.63189 | 0.64541 | 0.65448 | 0.65969 | 0.65486 | 0.6413 | 0.65902 | 0.6557 | 0.62366 | 0.57903 | 0.52945 | 0.47285 | 0.65969
2016-02-05 | 0.42498 | 0.39341 | 0.37641 | 0.36742 | 0.36898 | 0.39631 | 0.4553 | 0.48872 | 0.51811 | 0.56203 | 0.60032 | 0.62887 | 0.64676 | 0.65927 | 0.66695 | 0.66342 | 0.6494 | 0.63765 | 0.65373 | 0.64495 | 0.61283 | 0.56925 | 0.51643 | 0.45975 | 0.66695
2016-02-06 | 0.41159 | 0.37893 | 0.36184 | 0.35306 | 0.35558 | 0.38077 | 0.43918 | 0.47281 | 0.50333 | 0.53843 | 0.56896 | 0.59121 | 0.60926 | 0.62606 | 0.63307 | 0.63731 | 0.63328 | 0.62816 | 0.64608 | 0.64159 | 0.61006 | 0.56723 | 0.51551 | 0.45702 | 0.64608
2016-02-07 | 0.40764 | 0.37746 | 0.35676 | 0.34723 | 0.3487 | 0.37452 | 0.43229 | 0.46773 | 0.49023 | 0.51924 | 0.5467 | 0.57219 | 0.58726 | 0.58974 | 0.60914 | 0.61459 | 0.61304 | 0.60905 | 0.61103 | 0.59495 | 0.57143 | 0.53205 | 0.49535 | 0.4498 | 0.61459
2016-02-08 | 0.40806 | 0.37653 | 0.35772 | 0.34823 | 0.34752 | 0.35533 | 0.37695 | 0.40718 | 0.46328 | 0.52067 | 0.5635 | 0.5897 | 0.60716 | 0.61564 | 0.62102 | 0.61766 | 0.61014 | 0.59906 | 0.60603 | 0.5918 | 0.5622 | 0.52865 | 0.49183 | 0.4519 | 0.62102
2016-02-09 | 0.40983 | 0.37888 | 0.36012 | 0.35033 | 0.34815 | 0.35478 | 0.3704 | 0.39442 | 0.43834 | 0.47843 | 0.50493 | 0.51861 | 0.53125 | 0.53889 | 0.54225 | 0.53944 | 0.53272 | 0.53066 | 0.55506 | 0.55875 | 0.53134 | 0.4946 | 0.45513 | 0.40538 | 0.55875
2016-02-10 | 0.36415 | 0.34084 | 0.33119 | 0.32963 | 0.33749 | 0.37019 | 0.43452 | 0.47184 | 0.48784 | 0.50774 | 0.52974 | 0.54406 | 0.55733 | 0.56765 | 0.57194 | 0.57639 | 0.57719 | 0.57399 | 0.59671 | 0.60233 | 0.57252 | 0.53003 | 0.47978 | 0.42511 | 0.60233
2016-02-11 | 0.38128 | 0.3539 | 0.34063 | 0.33627 | 0.34194 | 0.37275 | 0.43703 | 0.47411 | 0.49292 | 0.51807 | 0.54066 | 0.5614 | 0.57882 | 0.59419 | 0.60347 | 0.61304 | 0.61581 | 0.6104 | 0.62681 | 0.62887 | 0.60233 | 0.55103 | 0.49661 | 0.43804 | 0.62887
2016-02-12 | 0.38728 | 0.35911 | 0.34185 | 0.33463 | 0.33845 | 0.3657 | 0.42624 | 0.45946 | 0.48511 | 0.5179 | 0.54645 | 0.56946 | 0.58655 | 0.60049 | 0.60406 | 0.59851 | 0.59104 | 0.59243 | 0.6198 | 0.613 | 0.58415 | 0.54129 | 0.48129 | 0.42037 | 0.6198
2016-02-13 | 0.37607 | 0.34807 | 0.33501 | 0.32993 | 0.33581 | 0.36566 | 0.42893 | 0.46794 | 0.48843 | 0.50148 | 0.51316 | 0.51727 | 0.51954 | 0.51887 | 0.51656 | 0.51295 | 0.50934 | 0.50942 | 0.53902 | 0.55048 | 0.53297 | 0.50274 | 0.46218 | 0.41579 | 0.55048
2016-02-14 | 0.37922 | 0.36112 | 0.35504 | 0.35709 | 0.37028 | 0.4126 | 0.49359 | 0.54507 | 0.54406 | 0.53129 | 0.52097 | 0.50358 | 0.48973 | 0.48024 | 0.47423 | 0.47402 | 0.47386 | 0.47831 | 0.5082 | 0.51404 | 0.49569 | 0.47079 | 0.44275 | 0.40924 | 0.54507
2016-02-15 | 0.38014 | 0.36163 | 0.3518 | 0.34819 | 0.34975 | 0.36192 | 0.38573 | 0.41927 | 0.45563 | 0.47885 | 0.49199 | 0.49334 | 0.48729 | 0.48116 | 0.47575 | 0.47373 | 0.4726 | 0.47562 | 0.49892 | 0.50438 | 0.48683 | 0.46357 | 0.43641 | 0.40122 | 0.50438
2016-02-16 | 0.37154 | 0.3547 | 0.35247 | 0.35449 | 0.35856 | 0.37632 | 0.4076 | 0.44997 | 0.48414 | 0.49409 | 0.48935 | 0.47831 | 0.47205 | 0.46747 | 0.46538 | 0.46613 | 0.46869 | 0.47348 | 0.50001 | 0.50925 | 0.48876 | 0.46118 | 0.43191 | 0.39278 | 0.50925
2016-02-17 | 0.36167 | 0.34483 | 0.33929 | 0.34105 | 0.35201 | 0.38203 | 0.43158 | 0.47659 | 0.50153 | 0.51106 | 0.51534 | 0.51635 | 0.5179 | 0.52076 | 0.52374 | 0.52806 | 0.53033 | 0.53159 | 0.55254 | 0.55947 | 0.53163 | 0.49254 | 0.44413 | 0.39627 | 0.55947
2016-02-18 | 0.35483 | 0.33085 | 0.32245 | 0.32027 | 0.32896 | 0.36163 | 0.42771 | 0.46873 | 0.48435 | 0.49959 | 0.51379 | 0.52542 | 0.53553 | 0.54628 | 0.55632 | 0.56585 | 0.56925 | 0.56409 | 0.57786 | 0.58453 | 0.5551 | 0.50984 | 0.46189 | 0.40588 | 0.58453
2016-02-19 | 0.36175 | 0.33526 | 0.32329 | 0.31842 | 0.32426 | 0.35403 | 0.41655 | 0.45228 | 0.4734 | 0.49745 | 0.52172 | 0.54242 | 0.55863 | 0.5742 | 0.58907 | 0.60322 | 0.60666 | 0.59822 | 0.60599 | 0.60947 | 0.58067 | 0.53654 | 0.4854 | 0.42902 | 0.60947
2016-02-20 | 0.38044 | 0.35231 | 0.33665 | 0.32829 | 0.33064 | 0.35902 | 0.41927 | 0.45601 | 0.48654 | 0.52218 | 0.55569 | 0.57844 | 0.59931 | 0.61556 | 0.62698 | 0.63685 | 0.63819 | 0.62883 | 0.63962 | 0.64512 | 0.61825 | 0.5787 | 0.52747 | 0.47436 | 0.64512
2016-02-21 | 0.42532 | 0.39056 | 0.37229 | 0.36318 | 0.36373 | 0.38779 | 0.44594 | 0.4828 | 0.52722 | 0.57374 | 0.61308 | 0.6418 | 0.66149 | 0.67422 | 0.67577 | 0.6722 | 0.65125 | 0.63395 | 0.64151 | 0.63189 | 0.6012 | 0.56136 | 0.52227 | 0.47381 | 0.67577
2016-02-22 | 0.42738 | 0.39089 | 0.37112 | 0.35844 | 0.35512 | 0.35936 | 0.37834 | 0.41079 | 0.47881 | 0.54036 | 0.58441 | 0.61653 | 0.64155 | 0.65515 | 0.66044 | 0.6628 | 0.65423 | 0.6321 | 0.62837 | 0.61955 | 0.58529 | 0.54859 | 0.50866 | 0.46206 | 0.6628
2016-02-23 | 0.41734 | 0.3848 | 0.36389 | 0.35168 | 0.34613 | 0.34815 | 0.36041 | 0.38854 | 0.45404 | 0.51824 | 0.56786 | 0.60511 | 0.64802 | 0.6549 | 0.66078 | 0.66607 | 0.66107 | 0.64722 | 0.64705 | 0.6481 | 0.61732 | 0.5669 | 0.51975 | 0.46206 | 0.66607
2016-02-24 | 0.40983 | 0.3817 | 0.36322 | 0.3526 | 0.3539 | 0.37918 | 0.42998 | 0.46756 | 0.504 | 0.548 | 0.58835 | 0.61678 | 0.64453 | 0.66347 | 0.6751 | 0.68404 | 0.67606 | 0.66347 | 0.67556 | 0.67799 | 0.63819 | 0.58756 | 0.52873 | 0.4676 | 0.68404
2016-02-25 | 0.41428 | 0.38128 | 0.36142 | 0.35046 | 0.3513 | 0.37687 | 0.43401 | 0.46622 | 0.49947 | 0.5373 | 0.5711 | 0.59919 | 0.62585 | 0.64907 | 0.66716 | 0.6777 | 0.67459 | 0.65625 | 0.65994 | 0.66007 | 0.62446 | 0.57362 | 0.51908 | 0.45698 | 0.6777
2016-02-26 | 0.40424 | 0.37095 | 0.35042 | 0.34084 | 0.34156 | 0.36394 | 0.41906 | 0.45408 | 0.48305 | 0.51526 | 0.55775 | 0.58596 | 0.61111 | 0.62824 | 0.63916 | 0.64138 | 0.63168 | 0.62497 | 0.64247 | 0.64193 | 0.61191 | 0.56967 | 0.51735 | 0.46176 | 0.64247
2016-02-27 | 0.4134 | 0.38535 | 0.37032 | 0.36327 | 0.36549 | 0.39001 | 0.44728 | 0.4786 | 0.4972 | 0.52025 | 0.54536 | 0.54007 | 0.56497 | 0.56837 | 0.56711 | 0.564 | 0.55724 | 0.56828 | 0.58865 | 0.59226 | 0.56736 | 0.52432 | 0.47369 | 0.42284 | 0.59226
2016-02-28 | 0.3796 | 0.35478 | 0.34328 | 0.33967 | 0.345 | 0.37515 | 0.43897 | 0.47537 | 0.48675 | 0.49372 | 0.49922 | 0.5009 | 0.50123 | 0.50396 | 0.50694 | 0.5111 | 0.5137 | 0.5103 | 0.52218 | 0.52924 | 0.50652 | 0.47663 | 0.44107 | 0.40055 | 0.52924
2016-02-29 | 0.3796 | 0.35478 | 0.34328 | 0.33967 | 0.345 | 0.37515 | 0.43897 | 0.47537 | 0.48675 | 0.49372 | 0.49922 | 0.5009 | 0.50123 | 0.50396 | 0.50694 | 0.5111 | 0.5137 | 0.5103 | 0.52218 | 0.52924 | 0.50652 | 0.47663 | 0.44107 | 0.40055 | 0.52924
2016-03-01 | 0.36427 | 0.34139 | 0.32888 | 0.32342 | 0.32556 | 0.3387 | 0.36402 | 0.39816 | 0.44098 | 0.46911 | 0.48683 | 0.49598 | 0.50472 | 0.51332 | 0.51971 | 0.52789 | 0.5289 | 0.52202 | 0.5226 | 0.53222 | 0.50614 | 0.47688 | 0.44325 | 0.40248 | 0.53222
2016-03-02 | 0.36646 | 0.34366 | 0.33073 | 0.31914 | 0.31742 | 0.32392 | 0.33984 | 0.36746 | 0.42112 | 0.46567 | 0.49363 | 0.51383 | 0.52928 | 0.54439 | 0.55493 | 0.56417 | 0.56715 | 0.5601 | 0.56295 | 0.5732 | 0.54397 | 0.50442 | 0.45908 | 0.40903 | 0.5732
2016-03-03 | 0.37175 | 0.34089 | 0.32405 | 0.31775 | 0.32136 | 0.34878 | 0.40437 | 0.43934 | 0.47071 | 0.50551 | 0.53776 | 0.56131 | 0.58436 | 0.60666 | 0.62081 | 0.63349 | 0.63727 | 0.62782 | 0.62769 | 0.63361 | 0.597 | 0.54687 | 0.49174 | 0.43032 | 0.63727
2016-03-04 | 0.38048 | 0.34861 | 0.33119 | 0.32237 | 0.3243 | 0.34954 | 0.40529 | 0.44153 | 0.47117 | 0.50556 | 0.53642 | 0.56157 | 0.58424 | 0.60519 | 0.62299 | 0.63618 | 0.63937 | 0.62946 | 0.63047 | 0.63429 | 0.60233 | 0.55829 | 0.50388 | 0.44552 | 0.63937
2016-03-05 | 0.39488 | 0.36574 | 0.34882 | 0.34181 | 0.34467 | 0.37007 | 0.42944 | 0.46538 | 0.49321 | 0.53205 | 0.56547 | 0.59406 | 0.61783 | 0.63311 | 0.6392 | 0.64117 | 0.63336 | 0.62316 | 0.63021 | 0.63374 | 0.60607 | 0.56333 | 0.51131 | 0.45307 | 0.64117
2016-03-06 | 0.40429 | 0.37569 | 0.35776 | 0.35021 | 0.35142 | 0.37582 | 0.43166 | 0.46731 | 0.50593 | 0.54523 | 0.57416 | 0.59801 | 0.61384 | 0.61061 | 0.60326 | 0.55909 | 0.53751 | 0.54108 | 0.56551 | 0.57047 | 0.5475 | 0.51072 | 0.46777 | 0.41881 | 0.61384
2016-03-07 | 0.37628 | 0.34991 | 0.33891 | 0.33383 | 0.33854 | 0.36587 | 0.42419 | 0.45983 | 0.49191 | 0.51828 | 0.53982 | 0.54952 | 0.55455 | 0.55502 | 0.5546 | 0.55497 | 0.55132 | 0.5415 | 0.54649 | 0.55006 | 0.52936 | 0.49355 | 0.45542 | 0.40634 | 0.55502
2016-03-08 | 0.37309 | 0.34836 | 0.33694 | 0.33274 | 0.33593 | 0.34672 | 0.37397 | 0.41193 | 0.45131 | 0.47377 | 0.4802 | 0.47969 | 0.47864 | 0.47822 | 0.48146 | 0.48624 | 0.4888 | 0.48645 | 0.49363 | 0.50631 | 0.48448 | 0.45811 | 0.42566 | 0.39287 | 0.50631
2016-03-09 | 0.35571 | 0 | 0.33471 | 0.32334 | 0.31931 | 0.32455 | 0.33933 | 0.3607 | 0.39182 | 0.43002 | 0.46105 | 0.47465 | 0.49304 | 0.50321 | 0.51064 | 0.52143 | 0.53255 | 0.53789 | 0.52991 | 0.53222 | 0.54481 | 0.51349 | 0.4726 | 0.41415 | 0.54481
2016-03-10 | 0.36566 | 0.33345 | 0.31784 | 0.31297 | 0.31868 | 0.34437 | 0.40017 | 0.44128 | 0.45354 | 0.47755 | 0.5064 | 0.52369 | 0.54318 | 0.55611 | 0.57538 | 0.59402 | 0.60939 | 0.61044 | 0.59772 | 0.59432 | 0.59944 | 0.5556 | 0.50677 | 0.44535 | 0.61044
2016-03-11 | 0.38833 | 0.35294 | 0.33333 | 0.32359 | 0.32355 | 0.34828 | 0.40353 | 0.443 | 0.45362 | 0.48179 | 0.50682 | 0.53003 | 0.55019 | 0.56866 | 0.586 | 0.6054 | 0.62173 | 0.62652 | 0.61539 | 0.60985 | 0.61548 | 0.57765 | 0.5263 | 0.45958 | 0.62652
2016-03-12 | 0.40731 | 0.37145 | 0.35285 | 0.34462 | 0.34647 | 0.37141 | 0.42902 | 0.42666 | 0.47709 | 0.51089 | 0.55204 | 0.58491 | 0.61035 | 0.62761 | 0.63689 | 0.65478 | 0.66552 | 0.66053 | 0.64268 | 0.63525 | 0.63844 | 0.5994 | 0.55006 | 0.48952 | 0.66552
2016-03-13 | 0.43342 | 0.39589 | 0.37351 | 0.36159 | 0.35848 | 0.3772 | 0.4265 | 0.45744 | 0.46647 | 0.49309 | 0.5129 | 0.52449 | 0.53092 | 0.53495 | 0.53772 | 0.54062 | 0.54624 | 0.5449 | 0.52945 | 0.52756 | 0.53801 | 0.50539 | 0.4616 | 0.40874 | 0.54624
2016-03-14 | 0.36431 | 0.33921 | 0.32523 | 0.32174 | 0.32875 | 0.35881 | 0.42599 | 0.47411 | 0.48486 | 0.49439 | 0.50165 | 0.50342 | 0.50266 | 0.50455 | 0.50698 | 0.51143 | 0.51782 | 0.51744 | 0.50757 | 0.50673 | 0.51589 | 0.49023 | 0.45454 | 0.41344 | 0.51782
2016-03-15 | 0.36801 | 0.34084 | 0.32426 | 0.31679 | 0.31821 | 0.32842 | 0.34975 | 0.38548 | 0.42561 | 0.46231 | 0.49023 | 0.50619 | 0.51765 | 0.52722 | 0.53843 | 0.54994 | 0.56236 | 0.56451 | 0.55069 | 0.5373 | 0.54036 | 0.51101 | 0.47743 | 0.43007 | 0.56451
2016-03-16 | 0.38804 | 0.35881 | 0.34009 | 0.32959 | 0.32535 | 0.32808 | 0.34194 | 0.36356 | 0.40693 | 0.46298 | 0.50237 | 0.53113 | 0.55388 | 0.57126 | 0.5881 | 0.59961 | 0.60494 | 0.60309 | 0.58819 | 0.58252 | 0.59259 | 0.56106 | 0.52126 | 0.46512 | 0.60494
2016-03-17 | 0.41579 | 0.38317 | 0.36486 | 0.35823 | 0.36184 | 0.38787 | 0.44144 | 0.48146 | 0.50295 | 0.54528 | 0.59112 | 0.6224 | 0.64491 | 0.65633 | 0.66229 | 0.66649 | 0.66775 | 0.65847 | 0.64789 | 0.65419 | 0.65373 | 0.6185 | 0.57672 | 0.51924 | 0.66775
2016-03-18 | 0.46819 | 0.43473 | 0.41768 | 0.40945 | 0.40815 | 0.42662 | 0.47356 | 0.50123 | 0.49653 | 0.51173 | 0.52655 | 0.53461 | 0.5415 | 0.55103 | 0.56346 | 0.57664 | 0.59049 | 0.59478 | 0.58294 | 0.57706 | 0.58415 | 0.54796 | 0.49829 | 0.43678 | 0.59478
2016-03-19 | 0.38266 | 0.35029 | 0.33295 | 0.32523 | 0.32728 | 0.35247 | 0.40785 | 0.44522 | 0.46059 | 0.49057 | 0.52008 | 0.54179 | 0.55611 | 0.57353 | 0.59066 | 0.60712 | 0.61741 | 0.61804 | 0.60141 | 0.59012 | 0.59797 | 0.56278 | 0.51547 | 0.45538 | 0.61804
2016-03-20 | 0.40403 | 0.37002 | 0.35201 | 0.34181 | 0.34244 | 0.36541 | 0.41885 | 0.45681 | 0.47323 | 0.50203 | 0.53209 | 0.55451 | 0.57202 | 0.59024 | 0.60674 | 0.61984 | 0.62841 | 0.62539 | 0.61056 | 0.59839 | 0.60481 | 0.56413 | 0.51387 | 0.45559 | 0.62841
2016-03-21 | 0.3995 | 0.36327 | 0.34089 | 0.32854 | 0.32825 | 0.34718 | 0.3919 | 0.43107 | 0.45559 | 0.4922 | 0.52907 | 0.55796 | 0.58088 | 0.60368 | 0.6253 | 0.64285 | 0.6497 | 0.64298 | 0.619 | 0.60124 | 0.60271 | 0.56753 | 0.52919 | 0.48141 | 0.6497
2016-03-22 | 0.43279 | 0.40013 | 0.37771 | 0.36427 | 0.35886 | 0.36461 | 0.38228 | 0.40525 | 0.44396 | 0.50367 | 0.54805 | 0.57143 | 0.59184 | 0.60729 | 0.61787 | 0.62933 | 0.64403 | 0.64373 | 0.62501 | 0.60229 | 0.59965 | 0.56362 | 0.52025 | 0.46789 | 0.64403
2016-03-23 | 0.41869 | 0.38136 | 0.35886 | 0.34567 | 0.33937 | 0.34206 | 0.35424 | 0.37296 | 0.41419 | 0.47507 | 0.52768 | 0.56719 | 0.60464 | 0.63702 | 0.65893 | 0.6772 | 0.68509 | 0.68421 | 0.66851 | 0.64936 | 0.65247 | 0.61061 | 0.56186 | 0.50073 | 0.68509
2016-03-24 | 0.44636 | 0.40735 | 0.38124 | 0.37032 | 0.36889 | 0.38732 | 0.42696 | 0.46134 | 0.48549 | 0.5195 | 0.54616 | 0.56455 | 0.5716 | 0.5708 | 0.56333 | 0.55842 | 0.55892 | 0.56194 | 0.56144 | 0.56446 | 0.56001 | 0.52495 | 0.48444 | 0.43158 | 0.5716
2016-03-25 | 0.38682 | 0.35369 | 0.33274 | 0.32506 | 0.32728 | 0.34748 | 0.39421 | 0.4312 | 0.45341 | 0.48607 | 0.50892 | 0.53167 | 0.54943 | 0.56173 | 0.57311 | 0.58214 | 0.58991 | 0.59054 | 0.5787 | 0.56446 | 0.56971 | 0.53129 | 0.47932 | 0.41906 | 0.59054
2016-03-26 | 0.3657 | 0.33471 | 0.31725 | 0.3112 | 0.31595 | 0.34084 | 0.3953 | 0.4414 | 0.46789 | 0.48137 | 0.49204 | 0.49212 | 0.48704 | 0.48083 | 0.4768 | 0.47453 | 0.4786 | 0.48141 | 0.47999 | 0.49355 | 0.51353 | 0.48817 | 0.44816 | 0.40424 | 0.51353
2016-03-27 | 0.36436 | 0.34072 | 0.3285 | 0.32565 | 0.33123 | 0.35571 | 0.40735 | 0.44375 | 0.46176 | 0.48704 | 0.49943 | 0.50551 | 0.50833 | 0.51064 | 0.51034 | 0.5098 | 0.51072 | 0.51009 | 0.5069 | 0.51832 | 0.52886 | 0.50262 | 0.46433 | 0.41772 | 0.52886
2016-03-28 | 0.37536 | 0.34664 | 0.33161 | 0.32359 | 0.32678 | 0.34794 | 0.39303 | 0.43028 | 0.45685 | 0.49283 | 0.52869 | 0.54981 | 0.56434 | 0.57282 | 0.5797 | 0.58399 | 0.58323 | 0.57416 | 0.56081 | 0.56094 | 0.56648 | 0.5415 | 0.50934 | 0.46634 | 0.58399
2016-03-29 | 0.42469 | 0.39576 | 0.37691 | 0.36713 | 0.36507 | 0.37196 | 0.39014 | 0.41655 | 0.45584 | 0.50925 | 0.55485 | 0.58609 | 0.59973 | 0.607 | 0.60548 | 0.59814 | 0.58848 | 0.57836 | 0.56249 | 0.55796 | 0.54666 | 0.51198 | 0.47936 | 0.43716 | 0.607
2016-03-30 | 0.39459 | 0.36436 | 0.34311 | 0.33257 | 0.32871 | 0.33274 | 0.34882 | 0.36881 | 0.40538 | 0.45274 | 0.4854 | 0.50178 | 0.50921 | 0.51479 | 0.52008 | 0.52453 | 0.52903 | 0.52802 | 0.51731 | 0.50976 | 0.52386 | 0.49141 | 0.44787 | 0.39417 | 0.52903
2016-03-31 | 0.34874 | 0.32439 | 0.30868 | 0.3036 | 0.30948 | 0.34257 | 0.40181 | 0.4393 | 0.45194 | 0.46945 | 0.4875 | 0.5019 | 0.51219 | 0.52441 | 0.53516 | 0.5441 | 0.5483 | 0.54376 | 0.53852 | 0.54498 | 0.55678 | 0.52059 | 0.4731 | 0.41491 | 0.55678
2016-04-01 | 0.36541 | 0.33602 | 0.32103 | 0.3149 | 0.3191 | 0.34655 | 0.411 | 0.45013 | 0.46412 | 0.48309 | 0.50148 | 0.51731 | 0.52999 | 0.54637 | 0.56606 | 0.58814 | 0.60821 | 0.61539 | 0.60448 | 0.58504 | 0.58961 | 0.5509 | 0.49355 | 0.43078 | 0.61539
2016-04-02 | 0.37771 | 0.34492 | 0.32707 | 0.31788 | 0.32027 | 0.34781 | 0.40693 | 0.43993 | 0.45517 | 0.4836 | 0.50745 | 0.52898 | 0.54364 | 0.56165 | 0.58894 | 0.61334 | 0.63164 | 0.63928 | 0.62488 | 0.60523 | 0.60926 | 0.57038 | 0.51236 | 0.44904 | 0.63928
2016-04-03 | 0.39362 | 0.35852 | 0.33862 | 0.33039 | 0.3322 | 0.35995 | 0.41407 | 0.44623 | 0.46773 | 0.50001 | 0.53037 | 0.55544 | 0.57786 | 0.59923 | 0.62845 | 0.64764 | 0.66112 | 0.65574 | 0.64071 | 0.61871 | 0.63021 | 0.58995 | 0.53087 | 0.46638 | 0.66112
2016-04-04 | 0.40966 | 0.37435 | 0.35247 | 0.34173 | 0.34051 | 0.36452 | 0.42263 | 0.45324 | 0.4768 | 0.51395 | 0.54947 | 0.57853 | 0.60078 | 0.62354 | 0.64537 | 0.66435 | 0.67963 | 0.6782 | 0.65952 | 0.62698 | 0.62005 | 0.58504 | 0.53889 | 0.48469 | 0.67963
2016-04-05 | 0.43216 | 0.3945 | 0.36998 | 0.35474 | 0.34857 | 0.35075 | 0.36868 | 0.39123 | 0.44472 | 0.50556 | 0.55204 | 0.58907 | 0.61913 | 0.64957 | 0.67044 | 0.6858 | 0.6916 | 0.68782 | 0.66233 | 0.62858 | 0.62484 | 0.58823 | 0.54414 | 0.49309 | 0.6916
2016-04-06 | 0.44006 | 0.40097 | 0.37275 | 0.35583 | 0.34878 | 0.34983 | 0.36192 | 0.37888 | 0.43498 | 0.50014 | 0.55178 | 0.58877 | 0.62224 | 0.65142 | 0.67816 | 0.69521 | 0.70348 | 0.70289 | 0.68282 | 0.65562 | 0.65658 | 0.61401 | 0.56081 | 0.49422 | 0.70348
2016-04-07 | 0.44254 | 0.40659 | 0.38682 | 0.3772 | 0.37985 | 0.40643 | 0.46155 | 0.49279 | 0.5205 | 0.57156 | 0.62186 | 0.66536 | 0.70113 | 0.73279 | 0.75764 | 0.77637 | 0.78783 | 0.78325 | 0.76062 | 0.74076 | 0.7348 | 0.6861 | 0.62564 | 0.56266 | 0.78783
2016-04-08 | 0.50917 | 0.46886 | 0.43918 | 0.4236 | 0.42385 | 0.44623 | 0.50295 | 0.53297 | 0.55754 | 0.59209 | 0.6321 | 0.66519 | 0.68454 | 0.69462 | 0.69261 | 0.68194 | 0.68769 | 0.66464 | 0.62035 | 0.59885 | 0.60175 | 0.56123 | 0.50451 | 0.44375 | 0.69462
2016-04-09 | 0.39669 | 0.36515 | 0.34685 | 0.33761 | 0.33698 | 0.36016 | 0.41533 | 0.44128 | 0.4545 | 0.48108 | 0.50169 | 0.51265 | 0.51916 | 0.52458 | 0.53335 | 0.54406 | 0.55426 | 0.56077 | 0.55376 | 0.54385 | 0.55896 | 0.52546 | 0.47138 | 0.41411 | 0.56077
2016-04-10 | 0.36629 | 0.33807 | 0.32166 | 0.31557 | 0.31851 | 0.34475 | 0.40353 | 0.43452 | 0.44917 | 0.47335 | 0.49561 | 0.51169 | 0.52256 | 0.53503 | 0.54851 | 0.56312 | 0.5732 | 0.57294 | 0.56304 | 0.55607 | 0.57068 | 0.53486 | 0.48461 | 0.42612 | 0.5732
2016-04-11 | 0.37809 | 0.34559 | 0.32863 | 0.3214 | 0.3238 | 0.34756 | 0.40441 | 0.43628 | 0.45824 | 0.49376 | 0.52563 | 0.54729 | 0.56224 | 0.5771 | 0.59062 | 0.59558 | 0.59713 | 0.58953 | 0.57546 | 0.56463 | 0.57215 | 0.54574 | 0.50896 | 0.46206 | 0.59713
2016-04-12 | 0.41583 | 0.38312 | 0.35986 | 0.34651 | 0.34089 | 0.34521 | 0.36482 | 0.38917 | 0.44291 | 0.50148 | 0.54599 | 0.58012 | 0.60305 | 0.62341 | 0.63559 | 0.64667 | 0.65079 | 0.64621 | 0.62182 | 0.59352 | 0.59331 | 0.56518 | 0.52113 | 0.4757 | 0.65079
2016-04-13 | 0.43078 | 0.39564 | 0.37355 | 0.35865 | 0.35239 | 0.3547 | 0.36772 | 0.38615 | 0.43435 | 0.49246 | 0.53608 | 0.56711 | 0.59411 | 0.61191 | 0.61934 | 0.6253 | 0.62685 | 0.62392 | 0.60981 | 0.60557 | 0.61842 | 0.58651 | 0.54078 | 0.48322 | 0.62685
2016-04-14 | 0.43263 | 0.39958 | 0.38119 | 0.37065 | 0.37162 | 0.39488 | 0.45018 | 0.4815 | 0.51517 | 0.56614 | 0.61292 | 0.65322 | 0.68551 | 0.71704 | 0.74198 | 0.76306 | 0.77406 | 0.77045 | 0.74727 | 0.71801 | 0.71393 | 0.66955 | 0.60792 | 0.53797 | 0.77406
2016-04-15 | 0.47801 | 0.43939 | 0.41533 | 0.3987 | 0.39551 | 0.41613 | 0.47062 | 0.49934 | 0.53982 | 0.59633 | 0.64323 | 0.68576 | 0.7165 | 0.73837 | 0.74698 | 0.75361 | 0.74878 | 0.71948 | 0.70445 | 0.68354 | 0.68509 | 0.64482 | 0.58352 | 0.51656 | 0.75361
2016-04-16 | 0.46093 | 0.42289 | 0.39895 | 0.38657 | 0.38396 | 0.40361 | 0.454 | 0.47877 | 0.49649 | 0.52374 | 0.54649 | 0.56207 | 0.57823 | 0.59683 | 0.61027 | 0.6203 | 0.62639 | 0.62417 | 0.61371 | 0.61124 | 0.62274 | 0.5965 | 0.54649 | 0.48574 | 0.62639
2016-04-17 | 0.43682 | 0.40475 | 0.38598 | 0.37615 | 0.37754 | 0.40126 | 0.45521 | 0.48591 | 0.51282 | 0.55292 | 0.58806 | 0.61065 | 0.61816 | 0.62396 | 0.62614 | 0.62282 | 0.61779 | 0.60725 | 0.59742 | 0.59146 | 0.59893 | 0.57647 | 0.53612 | 0.4841 | 0.62614
2016-04-18 | 0.43708 | 0.40403 | 0.38258 | 0.37078 | 0.36893 | 0.38762 | 0.42587 | 0.45794 | 0.50031 | 0.553 | 0.59574 | 0.62408 | 0.64155 | 0.66049 | 0.66968 | 0.66804 | 0.66439 | 0.66007 | 0.6418 | 0.62018 | 0.62135 | 0.59549 | 0.55846 | 0.51479 | 0.66968
2016-04-19 | 0.46718 | 0.43552 | 0.4134 | 0.39895 | 0.39404 | 0.39862 | 0.40739 | 0.42066 | 0.45874 | 0.52168 | 0.57286 | 0.60792 | 0.63613 | 0.65675 | 0.668 | 0.6756 | 0.67438 | 0.65906 | 0.62921 | 0.59259 | 0.58609 | 0.55283 | 0.51349 | 0.45845 | 0.6756
2016-04-20 | 0.40853 | 0.3712 | 0.34576 | 0.33249 | 0.3269 | 0.32984 | 0.34328 | 0.35915 | 0.40395 | 0.45039 | 0.47608 | 0.49708 | 0.51114 | 0.52126 | 0.52806 | 0.53339 | 0.53684 | 0.53323 | 0.52411 | 0.51891 | 0.53713 | 0.51677 | 0.47587 | 0.42188 | 0.53713
2016-04-21 | 0.37435 | 0.3432 | 0.32657 | 0.31847 | 0.32098 | 0.34592 | 0.39849 | 0.42666 | 0.4498 | 0.47936 | 0.50694 | 0.52789 | 0.54905 | 0.5661 | 0.58537 | 0.60061 | 0.61287 | 0.61178 | 0.60238 | 0.58932 | 0.59935 | 0.56379 | 0.5103 | 0.45198 | 0.61287
2016-04-22 | 0.39736 | 0.36083 | 0.34311 | 0.33224 | 0.33245 | 0.35949 | 0.41449 | 0.43842 | 0.46281 | 0.49271 | 0.52374 | 0.55439 | 0.57739 | 0.59608 | 0.61535 | 0.63865 | 0.65473 | 0.65776 | 0.64545 | 0.62673 | 0.63517 | 0.59767 | 0.53759 | 0.47096 | 0.65776
2016-04-23 | 0.41592 | 0.38094 | 0.3589 | 0.34555 | 0.34341 | 0.36562 | 0.41634 | 0.38787 | 0.47197 | 0.50614 | 0.53873 | 0.56287 | 0.59159 | 0.62606 | 0.66259 | 0.68992 | 0.70961 | 0.71456 | 0.69928 | 0.67002 | 0.66695 | 0.63483 | 0.57584 | 0.49632 | 0.71456
2016-04-24 | 0.44161 | 0.40487 | 0.3707 | 0.35604 | 0.35651 | 0.37007 | 0.41944 | 0.44854 | 0.48049 | 0.52584 | 0.57106 | 0.60888 | 0.64336 | 0.67392 | 0.69953 | 0.72451 | 0.73896 | 0.73707 | 0.71582 | 0.68253 | 0.67976 | 0.641 | 0.57912 | 0.51274 | 0.73896
2016-04-25 | 0.45337 | 0.41042 | 0.38342 | 0.36776 | 0.3641 | 0.38422 | 0.43313 | 0.46072 | 0.49502 | 0.54183 | 0.59129 | 0.63433 | 0.6717 | 0.706 | 0.73552 | 0.76041 | 0.77402 | 0.77032 | 0.74177 | 0.69983 | 0.68815 | 0.65016 | 0.59591 | 0.53612 | 0.77402
2016-04-26 | 0.47575 | 0.43028 | 0.40046 | 0.38111 | 0.36998 | 0.37074 | 0.38317 | 0.40748 | 0.46789 | 0.53457 | 0.59461 | 0.64592 | 0.68593 | 0.71612 | 0.73421 | 0.75029 | 0.75857 | 0.75365 | 0.72603 | 0.68366 | 0.67178 | 0.63676 | 0.58924 | 0.53671 | 0.75857
2016-04-27 | 0.4854 | 0.44497 | 0.41453 | 0.39627 | 0.38451 | 0.38245 | 0.38917 | 0.40811 | 0.47461 | 0.54973 | 0.61203 | 0.66212 | 0.70083 | 0.73211 | 0.75286 | 0.77053 | 0.77754 | 0.77284 | 0.74815 | 0.71288 | 0.70776 | 0.66947 | 0.60909 | 0.54813 | 0.77754
2016-04-28 | 0.49468 | 0.45794 | 0.43447 | 0.41978 | 0.41852 | 0.4417 | 0.49074 | 0.51945 | 0.55754 | 0.60998 | 0.66863 | 0.71742 | 0.75399 | 0.7851 | 0.8108 | 0.83049 | 0.83569 | 0.83364 | 0.81042 | 0.77519 | 0.76507 | 0.7183 | 0.6507 | 0.58243 | 0.83569
2016-04-29 | 0.52647 | 0.48687 | 0.46101 | 0.44602 | 0.4435 | 0.46407 | 0.51022 | 0.53835 | 0.58352 | 0.63983 | 0.69525 | 0.74173 | 0.77574 | 0.80299 | 0.82188 | 0.83527 | 0.8325 | 0.8228 | 0.80353 | 0.77188 | 0.75978 | 0.71566 | 0.65033 | 0.58214 | 0.83527
2016-04-30 | 0.52462 | 0.48843 | 0.46479 | 0.45156 | 0.45072 | 0.471 | 0.51819 | 0.54607 | 0.58965 | 0.64587 | 0.7005 | 0.74337 | 0.77494 | 0.80223 | 0.81886 | 0.83028 | 0.82436 | 0.79186 | 0.76759 | 0.74144 | 0.73963 | 0.70004 | 0.6376 | 0.57244 | 0.83028
2016-05-01 | 0.51538 | 0.47789 | 0.45278 | 0.4393 | 0.43548 | 0.45778 | 0.50778 | 0.53705 | 0.57672 | 0.63349 | 0.69109 | 0.73421 | 0.76822 | 0.79711 | 0.81542 | 0.82457 | 0.81999 | 0.79568 | 0.7584 | 0.72947 | 0.72678 | 0.6837 | 0.62522 | 0.56299 | 0.82457
2016-05-02 | 0.50984 | 0.47251 | 0.44846 | 0.43372 | 0.42986 | 0.45097 | 0.4993 | 0.52936 | 0.56484 | 0.61602 | 0.65948 | 0.69193 | 0.7107 | 0.73232 | 0.74782 | 0.75592 | 0.75088 | 0.73564 | 0.71217 | 0.68022 | 0.67959 | 0.63395 | 0.58785 | 0.53801 | 0.75592
2016-05-03 | 0.48868 | 0.45106 | 0.42578 | 0.41042 | 0.40256 | 0.40689 | 0.42163 | 0.44463 | 0.48964 | 0.54456 | 0.58886 | 0.61892 | 0.63269 | 0.63928 | 0.63559 | 0.61867 | 0.57954 | 0.56434 | 0.55031 | 0.54645 | 0.55602 | 0.53839 | 0.50854 | 0.47067 | 0.63928
2016-05-04 | 0.43166 | 0.40093 | 0.38178 | 0.36881 | 0.36473 | 0.36482 | 0.36973 | 0.37569 | 0.41927 | 0.46844 | 0.50673 | 0.53398 | 0.56157 | 0.58516 | 0.60553 | 0.6282 | 0.64579 | 0.65469 | 0.64701 | 0.61942 | 0.61006 | 0.57404 | 0.52718 | 0.46164 | 0.65469
2016-05-05 | 0.40958 | 0.36872 | 0.35285 | 0.34143 | 0.34177 | 0.36545 | 0.41197 | 0.4406 | 0.47415 | 0.51794 | 0.56262 | 0.59982 | 0.63487 | 0.66691 | 0.6963 | 0.7209 | 0.7424 | 0.74542 | 0.72817 | 0.67182 | 0.67342 | 0.63093 | 0.54998 | 0.49603 | 0.74542
2016-05-06 | 0.43657 | 0.39916 | 0.37401 | 0.35907 | 0.35554 | 0.37594 | 0.4231 | 0.45181 | 0.48624 | 0.53411 | 0.58159 | 0.62744 | 0.67031 | 0.7026 | 0.73308 | 0.75932 | 0.77599 | 0.7749 | 0.75424 | 0.69899 | 0.70579 | 0.66447 | 0.6015 | 0.52999 | 0.77599
2016-05-07 | 0.4731 | 0.4341 | 0.41142 | 0.39635 | 0.39308 | 0.41247 | 0.45899 | 0.48729 | 0.52756 | 0.57576 | 0.62799 | 0.67086 | 0.70873 | 0.7432 | 0.77423 | 0.78951 | 0.80076 | 0.79761 | 0.77284 | 0.73669 | 0.72792 | 0.69235 | 0.6279 | 0.56094 | 0.80076
2016-05-08 | 0.50115 | 0.46344 | 0.43943 | 0.42192 | 0.41781 | 0.4359 | 0.48099 | 0.50715 | 0.54964 | 0.59973 | 0.64978 | 0.69059 | 0.72498 | 0.75722 | 0.78204 | 0.80391 | 0.81714 | 0.81348 | 0.79228 | 0.75365 | 0.73883 | 0.69957 | 0.63953 | 0.57584 | 0.81714
2016-05-09 | 0.50976 | 0.46806 | 0.44447 | 0.42641 | 0.42196 | 0.44073 | 0.48561 | 0.51232 | 0.55258 | 0.60313 | 0.65154 | 0.69076 | 0.72435 | 0.75416 | 0.78082 | 0.80047 | 0.81029 | 0.80055 | 0.7702 | 0.72737 | 0.7094 | 0.673 | 0.62551 | 0.57273 | 0.81029
2016-05-10 | 0.51992 | 0.4823 | 0.45698 | 0.43884 | 0.43011 | 0.43233 | 0.44144 | 0.46521 | 0.52865 | 0.59322 | 0.64012 | 0.67573 | 0.71167 | 0.73501 | 0.75008 | 0.76117 | 0.76054 | 0.75239 | 0.72913 | 0.68786 | 0.69185 | 0.66095 | 0.62018 | 0.57072 | 0.76117
2016-05-11 | 0.52134 | 0.48503 | 0.45824 | 0.44098 | 0.43254 | 0.43036 | 0.43376 | 0.44854 | 0.49985 | 0.56173 | 0.61048 | 0.64785 | 0.68051 | 0.70806 | 0.72825 | 0.73824 | 0.74198 | 0.73169 | 0.7102 | 0.67909 | 0.67967 | 0.65839 | 0.61023 | 0.54901 | 0.74198
2016-05-12 | 0.49199 | 0.45475 | 0.43158 | 0.4194 | 0.41835 | 0.4396 | 0.48536 | 0.51223 | 0.54947 | 0.60233 | 0.65524 | 0.69731 | 0.73153 | 0.75819 | 0.77759 | 0.79446 | 0.80072 | 0.79551 | 0.77796 | 0.75143 | 0.74404 | 0.70167 | 0.63916 | 0.57559 | 0.80072
2016-05-13 | 0.51958 | 0.48372 | 0.45828 | 0.44266 | 0.43926 | 0.45941 | 0.50425 | 0.52982 | 0.56522 | 0.61724 | 0.66573 | 0.70222 | 0.73518 | 0.75684 | 0.7728 | 0.78602 | 0.79283 | 0.78527 | 0.7631 | 0.73287 | 0.72817 | 0.69512 | 0.63605 | 0.57001 | 0.79283
2016-05-14 | 0.51908 | 0.48343 | 0.45668 | 0.44111 | 0.43813 | 0.44636 | 0.50791 | 0.52848 | 0.56765 | 0.62471 | 0.67321 | 0.71792 | 0.74958 | 0.76952 | 0.78355 | 0.78313 | 0.77905 | 0.77024 | 0.74626 | 0.7178 | 0.71985 | 0.68543 | 0.6303 | 0.56547 | 0.78355
2016-05-15 | 0.50929 | 0.47226 | 0.44728 | 0.43355 | 0.43305 | 0.45295 | 0.4985 | 0.52361 | 0.55657 | 0.61077 | 0.65813 | 0.68274 | 0.69185 | 0.69004 | 0.67543 | 0.65839 | 0.65373 | 0.65305 | 0.64411 | 0.62942 | 0.62942 | 0.60595 | 0.55699 | 0.50245 | 0.69185
2016-05-16 | 0.45249 | 0.42066 | 0.40013 | 0.38711 | 0.38514 | 0.40794 | 0.45501 | 0.47562 | 0.49095 | 0.51857 | 0.54208 | 0.55867 | 0.56606 | 0.5711 | 0.58151 | 0.58747 | 0.59415 | 0.58718 | 0.56891 | 0.54515 | 0.53524 | 0.51374 | 0.47722 | 0.43053 | 0.59415
2016-05-17 | 0.38577 | 0.35617 | 0.33572 | 0.32418 | 0.32069 | 0.32464 | 0.33711 | 0.36075 | 0.41058 | 0.46223 | 0.50404 | 0.53587 | 0.559 | 0.58012 | 0.60036 | 0.61627 | 0.62627 | 0.62438 | 0.6059 | 0.57416 | 0.56463 | 0.54607 | 0.50648 | 0.46223 | 0.62627
2016-05-18 | 0.41906 | 0.3864 | 0.36368 | 0.34823 | 0.34126 | 0.34269 | 0.34693 | 0.36608 | 0.41927 | 0.48015 | 0.52848 | 0.56484 | 0.59486 | 0.61909 | 0.64092 | 0.65671 | 0.66804 | 0.66548 | 0.64415 | 0.6138 | 0.61031 | 0.58772 | 0.53906 | 0.48087 | 0.66804
2016-05-19 | 0.42965 | 0.39425 | 0.37204 | 0.36108 | 0.36159 | 0.383 | 0.42855 | 0.45517 | 0.4946 | 0.54103 | 0.58394 | 0.62018 | 0.65083 | 0.6811 | 0.7013 | 0.72074 | 0.73123 | 0.72955 | 0.71213 | 0.6782 | 0.66624 | 0.63487 | 0.57878 | 0.51181 | 0.73123
2016-05-20 | 0.45563 | 0.41709 | 0.3948 | 0.38119 | 0.37729 | 0.39538 | 0.43808 | 0.46953 | 0.50845 | 0.55581 | 0.602 | 0.63958 | 0.66939 | 0.69407 | 0.71154 | 0.72552 | 0.73367 | 0.73006 | 0.71524 | 0.68039 | 0.66968 | 0.63496 | 0.57727 | 0.51282 | 0.73367
2016-05-21 | 0.4566 | 0.41755 | 0.3927 | 0.37674 | 0.37238 | 0.39051 | 0.4346 | 0.46512 | 0.49951 | 0.54276 | 0.58512 | 0.62207 | 0.65272 | 0.68534 | 0.71612 | 0.73694 | 0.7495 | 0.74433 | 0.72271 | 0.68643 | 0.66964 | 0.63903 | 0.58218 | 0.51568 | 0.7495
2016-05-22 | 0.45379 | 0.4134 | 0.38493 | 0.37023 | 0.36763 | 0.38707 | 0.43162 | 0.46021 | 0.50022 | 0.5475 | 0.59734 | 0.64432 | 0.68731 | 0.72846 | 0.75899 | 0.7846 | 0.80059 | 0.79568 | 0.77284 | 0.73237 | 0.70919 | 0.67883 | 0.61363 | 0.54318 | 0.80059
2016-05-23 | 0.47953 | 0.43653 | 0.40693 | 0.38946 | 0.38241 | 0.39845 | 0.43762 | 0.47394 | 0.52143 | 0.57798 | 0.63584 | 0.69227 | 0.73967 | 0.78699 | 0.82117 | 0.84346 | 0.8506 | 0.84094 | 0.81096 | 0.75873 | 0.73665 | 0.7052 | 0.64974 | 0.58915 | 0.8506
2016-05-24 | 0.53104 | 0.48712 | 0.45261 | 0.42885 | 0.41592 | 0.41239 | 0.41575 | 0.44157 | 0.5098 | 0.58432 | 0.65074 | 0.71129 | 0.76188 | 0.79661 | 0.81764 | 0.82881 | 0.8283 | 0.81882 | 0.78619 | 0.74366 | 0.72548 | 0.69307 | 0.64357 | 0.58903 | 0.82881
2016-05-25 | 0.53772 | 0.49418 | 0.46114 | 0.43922 | 0.42582 | 0.42074 | 0.42289 | 0.43922 | 0.49418 | 0.56194 | 0.63382 | 0.69013 | 0.73946 | 0.77196 | 0.79115 | 0.80211 | 0.80576 | 0.79064 | 0.75873 | 0.72179 | 0.71016 | 0.68093 | 0.62975 | 0.57798 | 0.80576
2016-05-26 | 0.52395 | 0.48561 | 0.45723 | 0.43859 | 0.42834 | 0.42851 | 0.43305 | 0.45429 | 0.52046 | 0.59822 | 0.66729 | 0.7165 | 0.75764 | 0.78586 | 0.80156 | 0.8097 | 0.80996 | 0.79736 | 0.76625 | 0.72913 | 0.72128 | 0.68769 | 0.63173 | 0.56715 | 0.80996
2016-05-27 | 0.51299 | 0.47377 | 0.44799 | 0.43221 | 0.42692 | 0.44661 | 0.48733 | 0.52281 | 0.57022 | 0.6282 | 0.68362 | 0.73274 | 0.76868 | 0.79614 | 0.81206 | 0.81953 | 0.80761 | 0.77633 | 0.74673 | 0.71776 | 0.7144 | 0.68341 | 0.62799 | 0.5601 | 0.81953
2016-05-28 | 0.50501 | 0.46706 | 0.44304 | 0.42797 | 0.42431 | 0.44367 | 0.48607 | 0.51719 | 0.56144 | 0.61417 | 0.668 | 0.72229 | 0.76046 | 0.79161 | 0.80849 | 0.81327 | 0.81281 | 0.79656 | 0.77099 | 0.74253 | 0.73337 | 0.70016 | 0.64315 | 0.57924 | 0.81327
2016-05-29 | 0.52126 | 0.47948 | 0.45446 | 0.43913 | 0.43372 | 0.45131 | 0.49246 | 0.52323 | 0.56068 | 0.60725 | 0.65528 | 0.68908 | 0.70936 | 0.72263 | 0.71339 | 0.70319 | 0.69668 | 0.68845 | 0.68089 | 0.65797 | 0.65574 | 0.63357 | 0.58756 | 0.53058 | 0.72263
2016-05-30 | 0.47381 | 0.43288 | 0.41272 | 0.40021 | 0.3979 | 0.41608 | 0.45614 | 0.4878 | 0.53155 | 0.59419 | 0.64915 | 0.69361 | 0.72834 | 0.75504 | 0.7707 | 0.78073 | 0.77792 | 0.75672 | 0.71864 | 0.68719 | 0.67778 | 0.64965 | 0.60574 | 0.558 | 0.78073
2016-05-31 | 0.51047 | 0.46957 | 0.44107 | 0.42242 | 0.41524 | 0.41398 | 0.42242 | 0.44959 | 0.51668 | 0.59075 | 0.65557 | 0.70524 | 0.73698 | 0.75718 | 0.76054 | 0.75747 | 0.74626 | 0.7217 | 0.69319 | 0.663 | 0.65893 | 0.63857 | 0.60166 | 0.55384 | 0.76054
2016-06-01 | 0.51017 | 0.47092 | 0.44514 | 0.42704 | 0.41713 | 0.41663 | 0.42049 | 0.43976 | 0.49691 | 0.56602 | 0.62832 | 0.67459 | 0.71242 | 0.7382 | 0.75139 | 0.74811 | 0.7322 | 0.7047 | 0.67405 | 0.65297 | 0.65255 | 0.63794 | 0.5978 | 0.54435 | 0.75139
2016-06-02 | 0.49586 | 0.46218 | 0.44275 | 0.43187 | 0.43321 | 0.45668 | 0.49829 | 0.52605 | 0.55166 | 0.58117 | 0.6093 | 0.62518 | 0.64067 | 0.651 | 0.65792 | 0.65759 | 0.65599 | 0.64806 | 0.63991 | 0.63093 | 0.63378 | 0.61606 | 0.57022 | 0.51572 | 0.65792
2016-06-03 | 0.46567 | 0.43166 | 0.41058 | 0.3979 | 0.39715 | 0.41864 | 0.46172 | 0.48897 | 0.51488 | 0.55136 | 0.58777 | 0.61842 | 0.64058 | 0.65658 | 0.66326 | 0.66544 | 0.65729 | 0.64848 | 0.63336 | 0.62018 | 0.6245 | 0.60166 | 0.55695 | 0.50031 | 0.66544
2016-06-04 | 0.44841 | 0.41352 | 0.39165 | 0.38023 | 0.38006 | 0.40101 | 0.44279 | 0.449 | 0.50375 | 0.55308 | 0.59369 | 0.62547 | 0.64713 | 0.67291 | 0.69139 | 0.70382 | 0.71326 | 0.71515 | 0.70293 | 0.67438 | 0.66019 | 0.63618 | 0.58869 | 0.5276 | 0.71515
2016-06-05 | 0.47218 | 0.43473 | 0.40928 | 0.39354 | 0.3885 | 0.40588 | 0.44233 | 0.48049 | 0.53218 | 0.58844 | 0.64566 | 0.69605 | 0.73434 | 0.76931 | 0.79329 | 0.81042 | 0.81756 | 0.81441 | 0.79434 | 0.75323 | 0.72993 | 0.6929 | 0.63408 | 0.56425 | 0.81756
2016-06-06 | 0.5077 | 0.4634 | 0.43317 | 0.41398 | 0.40504 | 0.4186 | 0.44762 | 0.48616 | 0.54679 | 0.6125 | 0.6793 | 0.73971 | 0.78766 | 0.82356 | 0.84854 | 0.8624 | 0.86693 | 0.85862 | 0.83171 | 0.78846 | 0.75987 | 0.72758 | 0.67312 | 0.61627 | 0.86693
2016-06-07 | 0.5601 | 0.51593 | 0.4841 | 0.46395 | 0.45001 | 0.4451 | 0.44921 | 0.47667 | 0.54599 | 0.61905 | 0.69202 | 0.75483 | 0.79543 | 0.82352 | 0.83998 | 0.84439 | 0.82914 | 0.80576 | 0.77439 | 0.74207 | 0.71981 | 0.68946 | 0.64134 | 0.58819 | 0.84439
2016-06-08 | 0.5378 | 0.49619 | 0.46601 | 0.4396 | 0.4312 | 0.42797 | 0.42855 | 0.44657 | 0.50728 | 0.58739 | 0.66212 | 0.72456 | 0.76096 | 0.76923 | 0.75991 | 0.75407 | 0.74299 | 0.73111 | 0.70818 | 0.6803 | 0.66447 | 0.63979 | 0.58697 | 0.53503 | 0.76923
2016-06-09 | 0.48078 | 0.44262 | 0.41587 | 0.40206 | 0.40013 | 0.41764 | 0.44988 | 0.48498 | 0.53553 | 0.59654 | 0.66221 | 0.72775 | 0.77704 | 0.81735 | 0.83868 | 0.83229 | 0.82092 | 0.79186 | 0.75735 | 0.7264 | 0.7089 | 0.67854 | 0.62215 | 0.55976 | 0.83868
2016-06-10 | 0.503 | 0.46302 | 0.43825 | 0.42255 | 0.41848 | 0.43557 | 0.46798 | 0.50925 | 0.56639 | 0.62614 | 0.68114 | 0.73031 | 0.76784 | 0.78842 | 0.78733 | 0.76025 | 0.73568 | 0.72405 | 0.72099 | 0.6989 | 0.69156 | 0.65843 | 0.60254 | 0.54238 | 0.78842
2016-06-11 | 0.49128 | 0.45375 | 0.42708 | 0.4126 | 0.40928 | 0.42436 | 0.45832 | 0.49514 | 0.54746 | 0.61325 | 0.6714 | 0.71943 | 0.74912 | 0.76726 | 0.74912 | 0.71708 | 0.70071 | 0.69559 | 0.68828 | 0.66611 | 0.65545 | 0.63319 | 0.58382 | 0.5276 | 0.76726
2016-06-12 | 0.47654 | 0.43888 | 0.41466 | 0.39958 | 0.39618 | 0.41063 | 0.44384 | 0.47256 | 0.50291 | 0.54263 | 0.59238 | 0.6455 | 0.70151 | 0.75071 | 0.783 | 0.79006 | 0.77011 | 0.73841 | 0.7141 | 0.68891 | 0.67543 | 0.64629 | 0.58877 | 0.52982 | 0.79006
2016-06-13 | 0.47705 | 0.43909 | 0.41415 | 0.3979 | 0.39484 | 0.40907 | 0.43821 | 0.47726 | 0.53348 | 0.59125 | 0.64634 | 0.69874 | 0.73892 | 0.75915 | 0.75869 | 0.73656 | 0.71377 | 0.68933 | 0.66741 | 0.63529 | 0.61573 | 0.59595 | 0.55791 | 0.50976 | 0.75915
2016-06-14 | 0.46433 | 0.42914 | 0.40429 | 0.38934 | 0.38266 | 0.38535 | 0.39463 | 0.42091 | 0.47957 | 0.54868 | 0.61342 | 0.67035 | 0.71339 | 0.74811 | 0.76398 | 0.76276 | 0.74236 | 0.72179 | 0.68937 | 0.65381 | 0.64016 | 0.61674 | 0.57681 | 0.5305 | 0.76398
2016-06-15 | 0.48586 | 0.4527 | 0.42612 | 0.41 | 0.40534 | 0.40949 | 0.41697 | 0.44144 | 0.50392 | 0.57731 | 0.64159 | 0.69886 | 0.74458 | 0.77343 | 0.78997 | 0.78376 | 0.7618 | 0.73409 | 0.70445 | 0.67333 | 0.66712 | 0.6523 | 0.60817 | 0.55846 | 0.78997
2016-06-16 | 0.50514 | 0.46957 | 0.44673 | 0.43237 | 0.42746 | 0.443 | 0.4731 | 0.50409 | 0.54381 | 0.59272 | 0.65553 | 0.71477 | 0.75483 | 0.78985 | 0.81395 | 0.82809 | 0.83653 | 0.83057 | 0.80038 | 0.74815 | 0.7233 | 0.69164 | 0.63433 | 0.57248 | 0.83653
2016-06-17 | 0.51542 | 0.47629 | 0.44686 | 0.42956 | 0.42343 | 0.43678 | 0.46785 | 0.50165 | 0.54301 | 0.58705 | 0.62908 | 0.66708 | 0.69945 | 0.72758 | 0.73707 | 0.7369 | 0.72964 | 0.72305 | 0.70957 | 0.68719 | 0.6738 | 0.65608 | 0.5986 | 0.53856 | 0.73707
2016-06-18 | 0.4828 | 0.44619 | 0.42255 | 0.40748 | 0.405 | 0.42062 | 0.45488 | 0.4896 | 0.53646 | 0.5881 | 0.64344 | 0.69479 | 0.72237 | 0.73211 | 0.72577 | 0.70852 | 0.68887 | 0.67203 | 0.65545 | 0.63882 | 0.63235 | 0.61573 | 0.56849 | 0.51341 | 0.73211
2016-06-19 | 0.46206 | 0.42851 | 0.40777 | 0.39547 | 0.39228 | 0.40819 | 0.44153 | 0.47566 | 0.52621 | 0.58373 | 0.64399 | 0.69101 | 0.7293 | 0.75684 | 0.75907 | 0.73522 | 0.7128 | 0.68975 | 0.66641 | 0.64415 | 0.63231 | 0.60704 | 0.56257 | 0.5069 | 0.75907
2016-06-20 | 0.4561 | 0.42116 | 0.39832 | 0.38564 | 0.38241 | 0.39627 | 0.42708 | 0.46349 | 0.51672 | 0.58088 | 0.6405 | 0.69412 | 0.73463 | 0.75747 | 0.75088 | 0.71771 | 0.69659 | 0.67766 | 0.66154 | 0.64029 | 0.62765 | 0.61195 | 0.57366 | 0.52567 | 0.75747
2016-06-21 | 0.47621 | 0.44144 | 0.41655 | 0.40189 | 0.39543 | 0.39799 | 0.40433 | 0.43515 | 0.50808 | 0.58651 | 0.64919 | 0.70596 | 0.75025 | 0.77578 | 0.76814 | 0.74068 | 0.71687 | 0.69739 | 0.67367 | 0.64873 | 0.63622 | 0.62127 | 0.58424 | 0.5352 | 0.77578
2016-06-22 | 0.48654 | 0.45442 | 0.42843 | 0.4121 | 0.40277 | 0.40223 | 0.40471 | 0.43523 | 0.50472 | 0.58529 | 0.65163 | 0.70134 | 0.7471 | 0.78031 | 0.80139 | 0.80462 | 0.79094 | 0.75995 | 0.72048 | 0.68601 | 0.67195 | 0.651 | 0.60666 | 0.54855 | 0.80462
2016-06-23 | 0.49405 | 0.4608 | 0.43712 | 0.4228 | 0.41969 | 0.43611 | 0.46789 | 0.50631 | 0.56173 | 0.62257 | 0.68669 | 0.7429 | 0.79178 | 0.83053 | 0.85245 | 0.8574 | 0.84875 | 0.8299 | 0.80227 | 0.76373 | 0.73812 | 0.70382 | 0.64877 | 0.58155 | 0.8574
2016-06-24 | 0.52424 | 0.48351 | 0.45652 | 0.43888 | 0.433 | 0.44703 | 0.47793 | 0.51555 | 0.57374 | 0.63639 | 0.70415 | 0.76121 | 0.80979 | 0.85224 | 0.87713 | 0.8907 | 0.89313 | 0.87642 | 0.85434 | 0.81613 | 0.79509 | 0.75852 | 0.69832 | 0.63042 | 0.89313
2016-06-25 | 0.57068 | 0.52592 | 0.49292 | 0.47226 | 0.46445 | 0.47675 | 0.50593 | 0.5428 | 0.60087 | 0.66976 | 0.74043 | 0.79341 | 0.84044 | 0.87692 | 0.89939 | 0.90161 | 0.88293 | 0.85849 | 0.82759 | 0.78691 | 0.76176 | 0.72897 | 0.6772 | 0.61136 | 0.90161
2016-06-26 | 0.55367 | 0.50812 | 0.47717 | 0.45723 | 0.44946 | 0.46013 | 0.49032 | 0.5268 | 0.58659 | 0.65918 | 0.7285 | 0.78204 | 0.82285 | 0.84947 | 0.8755 | 0.88398 | 0.88419 | 0.87084 | 0.84657 | 0.80681 | 0.77822 | 0.7432 | 0.68568 | 0.61825 | 0.88419
2016-06-27 | 0.55812 | 0.51626 | 0.48603 | 0.46685 | 0.46051 | 0.47373 | 0.49867 | 0.53415 | 0.59306 | 0.66099 | 0.72187 | 0.77523 | 0.80836 | 0.83616 | 0.85992 | 0.86248 | 0.85341 | 0.83112 | 0.79064 | 0.7479 | 0.72401 | 0.69034 | 0.64743 | 0.59171 | 0.86248
2016-06-28 | 0.53314 | 0.49057 | 0.46172 | 0.43993 | 0.42666 | 0.41587 | 0.44535 | 0.46302 | 0.53428 | 0.6156 | 0.67938 | 0.74337 | 0.79404 | 0.82524 | 0.84422 | 0.85832 | 0.85665 | 0.84678 | 0.81743 | 0.77649 | 0.75323 | 0.72456 | 0.67673 | 0.61871 | 0.85832
2016-06-29 | 0.56442 | 0.5229 | 0.49191 | 0.46991 | 0.45719 | 0.45223 | 0.45064 | 0.47058 | 0.54347 | 0.62967 | 0.70709 | 0.7749 | 0.82625 | 0.85094 | 0.85203 | 0.83561 | 0.82268 | 0.80185 | 0.76029 | 0.72145 | 0.69811 | 0.67413 | 0.62765 | 0.56988 | 0.85203
2016-06-30 | 0.51882 | 0.48028 | 0.45412 | 0.43863 | 0.4367 | 0.45354 | 0.48427 | 0.51563 | 0.5674 | 0.63437 | 0.69584 | 0.7484 | 0.79014 | 0.82545 | 0.84686 | 0.85732 | 0.84804 | 0.81248 | 0.77738 | 0.74475 | 0.72661 | 0.6992 | 0.65272 | 0.59226 | 0.85732
2016-07-01 | 0.53713 | 0.49821 | 0.47407 | 0.45941 | 0.45593 | 0.47272 | 0.50627 | 0.53369 | 0.56816 | 0.61602 | 0.66443 | 0.71267 | 0.74261 | 0.75596 | 0.76894 | 0.77448 | 0.78409 | 0.77813 | 0.76209 | 0.74715 | 0.73921 | 0.70726 | 0.65263 | 0.59247 | 0.78409
2016-07-02 | 0.53356 | 0.49645 | 0.47176 | 0.45828 | 0.45396 | 0.46773 | 0.49863 | 0.53008 | 0.58159 | 0.64608 | 0.71427 | 0.761 | 0.78884 | 0.79224 | 0.77607 | 0.76071 | 0.75659 | 0.75063 | 0.739 | 0.71767 | 0.70982 | 0.69219 | 0.64852 | 0.58802 | 0.79224
2016-07-03 | 0.54015 | 0.50178 | 0.47906 | 0.46378 | 0.4613 | 0.47474 | 0.50526 | 0.53738 | 0.58932 | 0.65918 | 0.73182 | 0.78754 | 0.82642 | 0.85358 | 0.87567 | 0.8878 | 0.88293 | 0.85081 | 0.81562 | 0.78082 | 0.75924 | 0.73426 | 0.68736 | 0.62874 | 0.8878
2016-07-04 | 0.57525 | 0.53129 | 0.49863 | 0.47646 | 0.46466 | 0.46437 | 0.46924 | 0.48473 | 0.5467 | 0.63429 | 0.71305 | 0.77355 | 0.80962 | 0.82705 | 0.83297 | 0.83145 | 0.78909 | 0.73694 | 0.6992 | 0.66515 | 0.64348 | 0.6159 | 0.60053 | 0.56812 | 0.83297
2016-07-05 | 0.5234 | 0.48473 | 0.45878 | 0.44157 | 0.43321 | 0.43355 | 0.43876 | 0.45366 | 0.50585 | 0.5643 | 0.6311 | 0.67757 | 0.71561 | 0.75155 | 0.756 | 0.72968 | 0.70529 | 0.68828 | 0.67144 | 0.65373 | 0.64252 | 0.62509 | 0.59146 | 0.54641 | 0.756
2016-07-06 | 0.50413 | 0.46957 | 0.44552 | 0.42897 | 0.42368 | 0.42457 | 0.42826 | 0.44463 | 0.50451 | 0.56421 | 0.61728 | 0.63777 | 0.65834 | 0.67686 | 0.69365 | 0.6963 | 0.69147 | 0.67858 | 0.65784 | 0.62568 | 0.61942 | 0.60624 | 0.56837 | 0.51878 | 0.6963
2016-07-07 | 0.47709 | 0.44657 | 0.4278 | 0.41844 | 0.41797 | 0.43565 | 0.46701 | 0.5006 | 0.54968 | 0.59973 | 0.64957 | 0.68194 | 0.69689 | 0.70839 | 0.71242 | 0.72401 | 0.72401 | 0.72212 | 0.71372 | 0.70277 | 0.69433 | 0.67426 | 0.62732 | 0.57043 | 0.72401
2016-07-08 | 0.51735 | 0.47843 | 0.45198 | 0.43662 | 0.43225 | 0.44568 | 0.47667 | 0.51202 | 0.56299 | 0.63131 | 0.69714 | 0.75504 | 0.79992 | 0.82041 | 0.81642 | 0.79245 | 0.76747 | 0.74547 | 0.72237 | 0.69164 | 0.66603 | 0.63731 | 0.59083 | 0.53789 | 0.82041
2016-07-09 | 0.48788 | 0.45467 | 0.433 | 0.41172 | 0.41352 | 0.43363 | 0.46668 | 0.49964 | 0.55342 | 0.62345 | 0.68526 | 0.74471 | 0.78267 | 0.7935 | 0.76025 | 0.73342 | 0.72044 | 0.7013 | 0.67804 | 0.66439 | 0.65234 | 0.66284 | 0.58709 | 0.5352 | 0.7935
2016-07-10 | 0.4828 | 0.44804 | 0.42696 | 0.41495 | 0.41138 | 0.42666 | 0.45988 | 0.49649 | 0.55015 | 0.61392 | 0.66263 | 0.69538 | 0.72519 | 0.74618 | 0.74534 | 0.73144 | 0.71032 | 0.68723 | 0.66796 | 0.64772 | 0.6421 | 0.62442 | 0.58361 | 0.53247 | 0.74618
2016-07-11 | 0.48183 | 0.44783 | 0.42603 | 0.41453 | 0.4118 | 0.42578 | 0.45454 | 0.49212 | 0.5538 | 0.62047 | 0.684 | 0.74022 | 0.78208 | 0.8155 | 0.83498 | 0.83968 | 0.83561 | 0.82113 | 0.7974 | 0.76096 | 0.73934 | 0.71561 | 0.66989 | 0.61581 | 0.83968
2016-07-12 | 0.56396 | 0.5247 | 0.49468 | 0.47562 | 0.46067 | 0.4608 | 0.4647 | 0.48351 | 0.54267 | 0.62274 | 0.68643 | 0.74278 | 0.78754 | 0.81189 | 0.81898 | 0.81756 | 0.81109 | 0.78951 | 0.75936 | 0.71776 | 0.69659 | 0.66712 | 0.62467 | 0.57597 | 0.81898
2016-07-13 | 0.536 | 0.50446 | 0.48154 | 0.46353 | 0.4516 | 0.4469 | 0.44787 | 0.46886 | 0.53621 | 0.61048 | 0.67203 | 0.72657 | 0.76583 | 0.78544 | 0.80143 | 0.81256 | 0.8105 | 0.7953 | 0.77032 | 0.73791 | 0.72006 | 0.70079 | 0.65557 | 0.6012 | 0.81256
2016-07-14 | 0.55052 | 0.51244 | 0.48372 | 0.46785 | 0.46361 | 0.47621 | 0.50543 | 0.53721 | 0.59373 | 0.65965 | 0.72389 | 0.77662 | 0.81441 | 0.82453 | 0.81693 | 0.81285 | 0.81117 | 0.81038 | 0.79984 | 0.76482 | 0.73316 | 0.69865 | 0.64571 | 0.58583 | 0.82453
2016-07-15 | 0.53209 | 0.49422 | 0.46823 | 0.45148 | 0.44753 | 0.46084 | 0.49267 | 0.52332 | 0.56963 | 0.63357 | 0.68698 | 0.73199 | 0.75903 | 0.75924 | 0.74769 | 0.7267 | 0.71209 | 0.7018 | 0.69735 | 0.68051 | 0.6748 | 0.65658 | 0.61094 | 0.5564 | 0.75924
2016-07-16 | 0.50803 | 0.47037 | 0.44442 | 0.43153 | 0.42969 | 0.44762 | 0.48788 | 0.52084 | 0.57702 | 0.64079 | 0.69303 | 0.7319 | 0.75579 | 0.73782 | 0.71696 | 0.69974 | 0.68429 | 0.66976 | 0.66015 | 0.64382 | 0.64608 | 0.63416 | 0.59406 | 0.54309 | 0.75579
2016-07-17 | 0.49561 | 0.46323 | 0.43783 | 0.42528 | 0.42406 | 0.44065 | 0.47478 | 0.50371 | 0.56589 | 0.62564 | 0.68328 | 0.73228 | 0.73346 | 0.72561 | 0.71582 | 0.73174 | 0.75307 | 0.75554 | 0.7508 | 0.73115 | 0.71507 | 0.69164 | 0.63739 | 0.58206 | 0.75554
2016-07-18 | 0.52374 | 0.48498 | 0.45912 | 0.44203 | 0.43552 | 0.4482 | 0.476 | 0.50892 | 0.56896 | 0.64159 | 0.70755 | 0.76633 | 0.81399 | 0.84892 | 0.87021 | 0.88184 | 0.88188 | 0.85967 | 0.81768 | 0.77326 | 0.74513 | 0.71469 | 0.6654 | 0.61212 | 0.88188
2016-07-19 | 0.55821 | 0.51551 | 0.48519 | 0.46575 | 0.45328 | 0.45249 | 0.45677 | 0.4778 | 0.55027 | 0.63152 | 0.70138 | 0.76029 | 0.80437 | 0.83595 | 0.849 | 0.85345 | 0.86395 | 0.85589 | 0.82327 | 0.78787 | 0.76679 | 0.73392 | 0.68417 | 0.63223 | 0.86395
2016-07-20 | 0.57949 | 0.53847 | 0.50656 | 0.48406 | 0.47092 | 0.46529 | 0.46592 | 0.47923 | 0.5462 | 0.63089 | 0.70037 | 0.76726 | 0.81709 | 0.84993 | 0.86563 | 0.8566 | 0.8485 | 0.83557 | 0.80723 | 0.77188 | 0.75697 | 0.73043 | 0.68387 | 0.62362 | 0.86563
2016-07-21 | 0.56828 | 0.52823 | 0.49901 | 0.48091 | 0.47642 | 0.48897 | 0.51979 | 0.54809 | 0.59721 | 0.6617 | 0.728 | 0.78267 | 0.8168 | 0.82264 | 0.80316 | 0.78334 | 0.76205 | 0.74282 | 0.72309 | 0.70109 | 0.69676 | 0.66552 | 0.61968 | 0.56589 | 0.82264
2016-07-22 | 0.51311 | 0.47625 | 0.45505 | 0.43985 | 0.43758 | 0.4566 | 0.48834 | 0.52 | 0.57399 | 0.63466 | 0.68899 | 0.72955 | 0.75386 | 0.76742 | 0.78602 | 0.79686 | 0.78863 | 0.76407 | 0.74232 | 0.71796 | 0.71104 | 0.68475 | 0.6358 | 0.58206 | 0.79686
2016-07-23 | 0.53331 | 0.49687 | 0.47142 | 0.4553 | 0.45118 | 0.4647 | 0.50094 | 0.52924 | 0.58248 | 0.63689 | 0.68454 | 0.72242 | 0.75122 | 0.77843 | 0.80471 | 0.81814 | 0.82318 | 0.81894 | 0.81567 | 0.78607 | 0.76797 | 0.74051 | 0.68387 | 0.62505 | 0.82318
2016-07-24 | 0.569 | 0.52529 | 0.49552 | 0.47705 | 0.4705 | 0.48238 | 0.50896 | 0.53927 | 0.5949 | 0.66494 | 0.72762 | 0.67333 | 0.81542 | 0.83603 | 0.84812 | 0.85963 | 0.87541 | 0.8663 | 0.85207 | 0.8173 | 0.78548 | 0.75412 | 0.69177 | 0.62769 | 0.87541
2016-07-25 | 0.57345 | 0.52815 | 0.4985 | 0.47814 | 0.46831 | 0.48007 | 0.50656 | 0.53843 | 0.60254 | 0.67342 | 0.73644 | 0.79325 | 0.82726 | 0.84565 | 0.86244 | 0.87814 | 0.88028 | 0.86445 | 0.83154 | 0.7909 | 0.76931 | 0.73598 | 0.68711 | 0.63345 | 0.88028
2016-07-26 | 0.58558 | 0.54528 | 0.51874 | 0.49615 | 0.4823 | 0.47999 | 0.48595 | 0.5019 | 0.56115 | 0.63974 | 0.7107 | 0.75735 | 0.777 | 0.78779 | 0.7846 | 0.77272 | 0.77284 | 0.76398 | 0.74429 | 0.71683 | 0.70961 | 0.68098 | 0.63626 | 0.59411 | 0.78779
2016-07-27 | 0.54813 | 0.51164 | 0.48628 | 0.46764 | 0.45769 | 0.45484 | 0.45715 | 0.47167 | 0.54528 | 0.62849 | 0.69701 | 0.75743 | 0.80517 | 0.84166 | 0.86504 | 0.88058 | 0.88578 | 0.87986 | 0.85329 | 0.81386 | 0.79568 | 0.7652 | 0.71142 | 0.65305 | 0.88578
2016-07-28 | 0.5949 | 0.55539 | 0.52554 | 0.50682 | 0.50153 | 0.51496 | 0.54313 | 0.5708 | 0.62786 | 0.70008 | 0.76297 | 0.82108 | 0.86013 | 0.89599 | 0.92802 | 0.94582 | 0.95225 | 0.94511 | 0.92697 | 0.89107 | 0.86899 | 0.83288 | 0.76629 | 0.69567 | 0.95225
2016-07-29 | 0.63298 | 0.58856 | 0.55653 | 0.53684 | 0.5281 | 0.53784 | 0.56354 | 0.58802 | 0.64487 | 0.71007 | 0.77158 | 0.82591 | 0.86143 | 0.88545 | 0.89729 | 0.88805 | 0.87898 | 0.84804 | 0.81004 | 0.7762 | 0.76192 | 0.73224 | 0.67762 | 0.62429 | 0.89729
2016-07-30 | 0.57068 | 0.53478 | 0.50724 | 0.4912 | 0.48482 | 0.49783 | 0.53066 | 0.5564 | 0.61149 | 0.67245 | 0.72237 | 0.77985 | 0.82801 | 0.86987 | 0.89175 | 0.89351 | 0.86756 | 0.82465 | 0.79371 | 0.76323 | 0.74404 | 0.71524 | 0.65994 | 0.60389 | 0.89351
2016-07-31 | 0.54931 | 0.51043 | 0.48385 | 0.46802 | 0.46252 | 0.47453 | 0.5064 | 0.53075 | 0.57949 | 0.64919 | 0.72162 | 0.78552 | 0.82696 | 0.85417 | 0.86349 | 0.85299 | 0.82012 | 0.78913 | 0.76289 | 0.73333 | 0.72439 | 0.69857 | 0.64999 | 0.59415 | 0.86349
2016-08-01 | 0.54599 | 0.50963 | 0.4802 | 0.46701 | 0.45975 | 0.47306 | 0.50039 | 0.53428 | 0.59196 | 0.66464 | 0.72863 | 0.78397 | 0.82537 | 0.85434 | 0.87835 | 0.8912 | 0.88935 | 0.86416 | 0.82675 | 0.79006 | 0.77486 | 0.74353 | 0.68891 | 0.63496 | 0.8912
2016-08-02 | 0.58336 | 0.54074 | 0.5108 | 0.48998 | 0.47835 | 0.4773 | 0.48414 | 0.49926 | 0.56388 | 0.64222 | 0.71024 | 0.76171 | 0.80127 | 0.82352 | 0.84338 | 0.8425 | 0.83569 | 0.81819 | 0.78682 | 0.75479 | 0.74244 | 0.71763 | 0.67035 | 0.62236 | 0.84338
2016-08-03 | 0.57353 | 0.53562 | 0.50724 | 0.4883 | 0.47696 | 0.47558 | 0.48062 | 0.48813 | 0.53927 | 0.60351 | 0.65137 | 0.70209 | 0.72632 | 0.7335 | 0.7361 | 0.74253 | 0.74786 | 0.74123 | 0.72368 | 0.70646 | 0.69122 | 0.66254 | 0.61363 | 0.55934 | 0.74786
2016-08-04 | 0.50795 | 0.47331 | 0.45076 | 0.43741 | 0.43649 | 0.45442 | 0.48893 | 0.5145 | 0.5635 | 0.62467 | 0.68454 | 0.73539 | 0.74924 | 0.74295 | 0.72069 | 0.69802 | 0.67547 | 0.65033 | 0.63429 | 0.62211 | 0.6303 | 0.6104 | 0.57185 | 0.52806 | 0.74924
2016-08-05 | 0.48503 | 0.45555 | 0.43825 | 0.42872 | 0.42822 | 0.44417 | 0.48129 | 0.51139 | 0.5653 | 0.63256 | 0.68925 | 0.7419 | 0.78338 | 0.80811 | 0.80311 | 0.79929 | 0.80307 | 0.80656 | 0.79291 | 0.76247 | 0.74857 | 0.71288 | 0.65482 | 0.59679 | 0.80811
2016-08-06 | 0.53843 | 0.50006 | 0.47239 | 0.45492 | 0.4516 | 0.46428 | 0.49598 | 0.52638 | 0.58583 | 0.65767 | 0.72174 | 0.78871 | 0.83439 | 0.87239 | 0.89582 | 0.89771 | 0.87764 | 0.85568 | 0.82579 | 0.79593 | 0.78233 | 0.74937 | 0.68551 | 0.62631 | 0.89771
2016-08-07 | 0.56761 | 0.5268 | 0.49951 | 0.48137 | 0.4747 | 0.48733 | 0.51874 | 0.54607 | 0.60893 | 0.68257 | 0.7479 | 0.80937 | 0.85677 | 0.88918 | 0.89586 | 0.89196 | 0.88553 | 0.87432 | 0.84443 | 0.81004 | 0.77843 | 0.73434 | 0.66695 | 0.60477 | 0.89586
2016-08-08 | 0.54863 | 0.50602 | 0.48036 | 0.46483 | 0.45786 | 0.48301 | 0.50283 | 0.52961 | 0.57273 | 0.63588 | 0.69378 | 0.75529 | 0.81012 | 0.85513 | 0.87818 | 0.87957 | 0.87201 | 0.83947 | 0.79929 | 0.76167 | 0.74811 | 0.71633 | 0.6675 | 0.62198 | 0.87957
2016-08-09 | 0.56467 | 0.525 | 0.49523 | 0.47604 | 0.46664 | 0.46664 | 0.47293 | 0.49199 | 0.56362 | 0.64776 | 0.71834 | 0.77926 | 0.82432 | 0.85404 | 0.87449 | 0.88654 | 0.88486 | 0.85916 | 0.81667 | 0.77519 | 0.75936 | 0.7254 | 0.67581 | 0.62967 | 0.88654
2016-08-10 | 0.57899 | 0.54032 | 0.50866 | 0.4883 | 0.47596 | 0.47155 | 0.47356 | 0.48498 | 0.55346 | 0.63773 | 0.71011 | 0.77964 | 0.82755 | 0.86332 | 0.88041 | 0.88377 | 0.88079 | 0.86899 | 0.83712 | 0.79602 | 0.77696 | 0.73648 | 0.67715 | 0.61598 | 0.88377
2016-08-11 | 0.55888 | 0.51719 | 0.48843 | 0.47088 | 0.46521 | 0.48049 | 0.51206 | 0.53549 | 0.58978 | 0.66519 | 0.73468 | 0.80345 | 0.85522 | 0.88788 | 0.8962 | 0.89389 | 0.8951 | 0.88721 | 0.86341 | 0.82658 | 0.81172 | 0.76436 | 0.706 | 0.63819 | 0.8962
2016-08-12 | 0.57882 | 0.53801 | 0.50539 | 0.48536 | 0.47877 | 0.49153 | 0.52306 | 0.54855 | 0.60355 | 0.67468 | 0.73829 | 0.7956 | 0.83666 | 0.86823 | 0.87974 | 0.87886 | 0.8857 | 0.88112 | 0.86508 | 0.82994 | 0.80811 | 0.76415 | 0.70264 | 0.64159 | 0.8857
2016-08-13 | 0.58138 | 0.54347 | 0.51395 | 0.48952 | 0.48314 | 0.49657 | 0.5294 | 0.55565 | 0.61548 | 0.68761 | 0.75281 | 0.81991 | 0.86794 | 0.90107 | 0.91774 | 0.92634 | 0.9263 | 0.90611 | 0.87491 | 0.83422 | 0.81722 | 0.77746 | 0.71507 | 0.65301 | 0.92634
2016-08-14 | 0.59721 | 0.55875 | 0.53159 | 0.51387 | 0.50593 | 0.5161 | 0.54771 | 0.5716 | 0.62904 | 0.70289 | 0.76969 | 0.82184 | 0.86643 | 0.88994 | 0.89322 | 0.86311 | 0.81831 | 0.78384 | 0.75491 | 0.73027 | 0.72523 | 0.69147 | 0.64537 | 0.58714 | 0.89322
2016-08-15 | 0.53671 | 0.50237 | 0.47566 | 0.4634 | 0.46017 | 0.47659 | 0.51282 | 0.54309 | 0.60208 | 0.66569 | 0.72628 | 0.76973 | 0.80253 | 0.79564 | 0.73761 | 0.70041 | 0.67547 | 0.65822 | 0.6366 | 0.61585 | 0.61867 | 0.59688 | 0.56614 | 0.52672 | 0.80253
2016-08-16 | 0.48586 | 0.4587 | 0.44018 | 0.4278 | 0.42146 | 0.42377 | 0.4354 | 0.45438 | 0.52038 | 0.61224 | 0.68786 | 0.74274 | 0.79362 | 0.80261 | 0.82776 | 0.80874 | 0.77418 | 0.73816 | 0.70386 | 0.67455 | 0.66645 | 0.64277 | 0.60763 | 0.55976 | 0.82776
2016-08-17 | 0.5161 | 0.48364 | 0.45933 | 0.44228 | 0.4351 | 0.43544 | 0.44321 | 0.45803 | 0.52046 | 0.608 | 0.6866 | 0.74924 | 0.80068 | 0.84342 | 0.85047 | 0.8425 | 0.84657 | 0.84502 | 0.82633 | 0.79556 | 0.78581 | 0.75055 | 0.69038 | 0.61989 | 0.85047
2016-08-18 | 0.56673 | 0.52449 | 0.49603 | 0.4789 | 0.47516 | 0.4988 | 0.53919 | 0.55712 | 0.60007 | 0.67451 | 0.74479 | 0.8079 | 0.8548 | 0.89233 | 0.90921 | 0.9229 | 0.92508 | 0.91614 | 0.89674 | 0.86194 | 0.84812 | 0.7969 | 0.72338 | 0.65872 | 0.92508
2016-08-19 | 0.59595 | 0.5538 | 0.52344 | 0.50404 | 0.49817 | 0.51748 | 0.55888 | 0.57504 | 0.6203 | 0.69198 | 0.75554 | 0.81747 | 0.86639 | 0.89935 | 0.91862 | 0.94167 | 0.95342 | 0.94142 | 0.91879 | 0.87919 | 0.86311 | 0.81508 | 0.74223 | 0.67426 | 0.95342
2016-08-20 | 0.61262 | 0.56988 | 0.54015 | 0.51777 | 0.51051 | 0.52752 | 0.56673 | 0.52243 | 0.62463 | 0.69676 | 0.75966 | 0.8252 | 0.86689 | 0.9069 | 0.92311 | 0.9263 | 0.92504 | 0.91257 | 0.88553 | 0.85203 | 0.83691 | 0.79463 | 0.72871 | 0.66061 | 0.9263
2016-08-21 | 0.60721 | 0.56501 | 0.53511 | 0.51589 | 0.50808 | 0.52617 | 0.5677 | 0.58617 | 0.63223 | 0.69815 | 0.76444 | 0.82747 | 0.87193 | 0.91018 | 0.93155 | 0.95317 | 0.95393 | 0.92231 | 0.88897 | 0.84292 | 0.83238 | 0.78569 | 0.72317 | 0.65536 | 0.95393
2016-08-22 | 0.59377 | 0.55367 | 0.5247 | 0.50635 | 0.49888 | 0.51597 | 0.5577 | 0.57555 | 0.62085 | 0.69311 | 0.75676 | 0.81701 | 0.86412 | 0.89771 | 0.91014 | 0.93671 | 0.94356 | 0.92471 | 0.89406 | 0.84791 | 0.82285 | 0.77406 | 0.71738 | 0.66023 | 0.94356
2016-08-23 | 0.60284 | 0.56224 | 0.52936 | 0.50669 | 0.49262 | 0.49137 | 0.49787 | 0.51181 | 0.57643 | 0.66569 | 0.74013 | 0.80521 | 0.85404 | 0.88671 | 0.90132 | 0.91312 | 0.91983 | 0.91043 | 0.88054 | 0.83637 | 0.81521 | 0.77595 | 0.7275 | 0.66985 | 0.91983
2016-08-24 | 0.6114 | 0.56782 | 0.53377 | 0.51017 | 0.49577 | 0.49023 | 0.4909 | 0.49972 | 0.56891 | 0.65696 | 0.72775 | 0.79942 | 0.85505 | 0.89435 | 0.9179 | 0.93016 | 0.93142 | 0.92454 | 0.89683 | 0.85883 | 0.84224 | 0.79182 | 0.72682 | 0.66246 | 0.93142
2016-08-25 | 0.61157 | 0.56791 | 0.54255 | 0.52735 | 0.52647 | 0.54968 | 0.59272 | 0.60956 | 0.64084 | 0.70323 | 0.76327 | 0.81449 | 0.84623 | 0.85862 | 0.86135 | 0.86059 | 0.86307 | 0.85337 | 0.82444 | 0.79757 | 0.79073 | 0.74387 | 0.68601 | 0.62014 | 0.86307
2016-08-26 | 0.57248 | 0.53818 | 0.51404 | 0.49968 | 0.49708 | 0.51887 | 0.56278 | 0.57874 | 0.6135 | 0.67757 | 0.73333 | 0.78372 | 0.81882 | 0.8498 | 0.87054 | 0.88713 | 0.89561 | 0.88835 | 0.86345 | 0.82553 | 0.81168 | 0.76465 | 0.6929 | 0.62887 | 0.89561
2016-08-27 | 0.56681 | 0.52529 | 0.49502 | 0.47671 | 0.46991 | 0.48889 | 0.53188 | 0.54649 | 0.5868 | 0.65696 | 0.71734 | 0.7746 | 0.82003 | 0.85665 | 0.88465 | 0.90455 | 0.91622 | 0.90896 | 0.88452 | 0.84397 | 0.8307 | 0.7833 | 0.71452 | 0.65196 | 0.91622
2016-08-28 | 0.59398 | 0.55376 | 0.52378 | 0.50371 | 0.4954 | 0.51442 | 0.55913 | 0.57546 | 0.61438 | 0.67039 | 0.71406 | 0.75105 | 0.79312 | 0.83544 | 0.87344 | 0.89704 | 0.90732 | 0.88973 | 0.85358 | 0.82394 | 0.80576 | 0.75533 | 0.69374 | 0.6334 | 0.90732
2016-08-29 | 0.57441 | 0.53654 | 0.51068 | 0.49279 | 0.48801 | 0.50749 | 0.55246 | 0.57425 | 0.61871 | 0.6913 | 0.75773 | 0.80698 | 0.84241 | 0.87579 | 0.89922 | 0.9124 | 0.90799 | 0.8789 | 0.84153 | 0.80412 | 0.7898 | 0.74593 | 0.69441 | 0.64587 | 0.9124
2016-08-30 | 0.5973 | 0.55934 | 0.53155 | 0.51127 | 0.50241 | 0.51085 | 0.51387 | 0.52441 | 0.57861 | 0.66187 | 0.73169 | 0.7964 | 0.83914 | 0.87189 | 0.89603 | 0.9064 | 0.90497 | 0.88003 | 0.8359 | 0.79782 | 0.78363 | 0.74181 | 0.6947 | 0.64902 | 0.9064
2016-08-31 | 0.59898 | 0.55796 | 0.52684 | 0.50791 | 0.49447 | 0.48859 | 0.49216 | 0.50195 | 0.56555 | 0.65566 | 0.722 | 0.78006 | 0.82742 | 0.85942 | 0.87361 | 0.87818 | 0.86861 | 0.84984 | 0.81004 | 0.7723 | 0.76104 | 0.72158 | 0.67333 | 0.62219 | 0.87818
2016-09-01 | 0.57366 | 0.54003 | 0.51416 | 0.49481 | 0.48847 | 0.49225 | 0.50375 | 0.50896 | 0.5687 | 0.65767 | 0.73085 | 0.7998 | 0.83754 | 0.86618 | 0.8907 | 0.89905 | 0.89233 | 0.87541 | 0.84644 | 0.81054 | 0.79942 | 0.7526 | 0.68946 | 0.63047 | 0.89905
2016-09-02 | 0.57479 | 0.53553 | 0.50774 | 0.49128 | 0.4857 | 0.50514 | 0.5475 | 0.5643 | 0.60095 | 0.66796 | 0.72687 | 0.78661 | 0.82864 | 0.85429 | 0.88175 | 0.89758 | 0.9009 | 0.88646 | 0.85408 | 0.81802 | 0.79669 | 0.73799 | 0.66893 | 0.6012 | 0.9009
2016-09-03 | 0.54439 | 0.50572 | 0.48057 | 0.46407 | 0.45967 | 0.47936 | 0.52512 | 0.54187 | 0.57601 | 0.63471 | 0.67547 | 0.71796 | 0.75798 | 0.79975 | 0.82961 | 0.83956 | 0.84556 | 0.83154 | 0.80651 | 0.77376 | 0.76369 | 0.71889 | 0.65776 | 0.59125 | 0.84556
2016-09-04 | 0.53671 | 0.49838 | 0.47335 | 0.4579 | 0.45366 | 0.47319 | 0.52063 | 0.53671 | 0.56152 | 0.6135 | 0.66783 | 0.71238 | 0.74929 | 0.78376 | 0.79816 | 0.8042 | 0.81143 | 0.80051 | 0.78069 | 0.76247 | 0.75726 | 0.7123 | 0.65041 | 0.59154 | 0.81143
2016-09-05 | 0.5378 | 0.50127 | 0.47801 | 0.46344 | 0.46114 | 0.48146 | 0.531 | 0.5483 | 0.5847 | 0.65112 | 0.71456 | 0.77078 | 0.81781 | 0.85312 | 0.87302 | 0.87424 | 0.85501 | 0.81621 | 0.77502 | 0.74694 | 0.73043 | 0.68874 | 0.64277 | 0.59738 | 0.87424
2016-09-06 | 0.54956 | 0.51798 | 0.49342 | 0.47646 | 0.46827 | 0.46815 | 0.47835 | 0.49498 | 0.54737 | 0.61577 | 0.66813 | 0.70759 | 0.73052 | 0.72754 | 0.72032 | 0.71083 | 0.6924 | 0.67757 | 0.66023 | 0.65125 | 0.65133 | 0.62602 | 0.59474 | 0.55921 | 0.73052
2016-09-07 | 0.5195 | 0.48389 | 0.45954 | 0.44262 | 0.4362 | 0.43733 | 0.4461 | 0.45744 | 0.50745 | 0.57198 | 0.62958 | 0.68643 | 0.73245 | 0.76377 | 0.7783 | 0.76839 | 0.75092 | 0.7267 | 0.69042 | 0.67854 | 0.67799 | 0.64294 | 0.59335 | 0.54078 | 0.7783
2016-09-08 | 0.4975 | 0.46802 | 0.4451 | 0.43128 | 0.4304 | 0.45509 | 0.50232 | 0.51983 | 0.54821 | 0.61472 | 0.68139 | 0.73921 | 0.7846 | 0.81877 | 0.84367 | 0.85408 | 0.85295 | 0.84359 | 0.80908 | 0.78938 | 0.77565 | 0.72573 | 0.66372 | 0.60158 | 0.85408
2016-09-09 | 0.54737 | 0.5082 | 0.48347 | 0.46768 | 0.46118 | 0.48011 | 0.52609 | 0.54255 | 0.57114 | 0.63093 | 0.69277 | 0.74761 | 0.7932 | 0.83259 | 0.85043 | 0.86924 | 0.86466 | 0.84472 | 0.81214 | 0.78565 | 0.76713 | 0.71179 | 0.64739 | 0.58596 | 0.86924
2016-09-10 | 0.53541 | 0.50203 | 0.47957 | 0.46357 | 0.46013 | 0.48188 | 0.52873 | 0.54402 | 0.57215 | 0.62513 | 0.68543 | 0.73388 | 0.7762 | 0.81243 | 0.83334 | 0.843 | 0.83922 | 0.82188 | 0.79291 | 0.77099 | 0.75781 | 0.70327 | 0.64168 | 0.5792 | 0.843
2016-09-11 | 0.52672 | 0.49237 | 0.46777 | 0.45228 | 0.44875 | 0.46936 | 0.51702 | 0.53407 | 0.55989 | 0.61716 | 0.66901 | 0.71305 | 0.74517 | 0.76789 | 0.77565 | 0.77805 | 0.76348 | 0.73463 | 0.7081 | 0.69307 | 0.68551 | 0.64554 | 0.60011 | 0.54536 | 0.77805
2016-09-12 | 0.48977 | 0.46151 | 0.44128 | 0.43095 | 0.43095 | 0.45425 | 0.50606 | 0.52092 | 0.55136 | 0.60154 | 0.64718 | 0.68522 | 0.72237 | 0.75735 | 0.766 | 0.76268 | 0.76507 | 0.76793 | 0.74152 | 0.71163 | 0.69953 | 0.66351 | 0.62303 | 0.57349 | 0.76793
2016-09-13 | 0.51924 | 0.48301 | 0.45731 | 0.43653 | 0.42805 | 0.42725 | 0.43876 | 0.45438 | 0.50119 | 0.56795 | 0.63739 | 0.69878 | 0.7453 | 0.77389 | 0.78535 | 0.78405 | 0.76776 | 0.74446 | 0.70491 | 0.68463 | 0.67186 | 0.6316 | 0.58348 | 0.53348 | 0.78535
2016-09-14 | 0.493 | 0.46004 | 0.43628 | 0.4202 | 0.41063 | 0.40903 | 0.41554 | 0.42457 | 0.48129 | 0.55649 | 0.62597 | 0.68962 | 0.73648 | 0.76742 | 0.783 | 0.78821 | 0.78901 | 0.76877 | 0.73262 | 0.71129 | 0.69983 | 0.65708 | 0.60527 | 0.54565 | 0.78901
2016-09-15 | 0.50022 | 0.46668 | 0.44581 | 0.43405 | 0.43359 | 0.45622 | 0.50321 | 0.52176 | 0.55321 | 0.61737 | 0.69344 | 0.74987 | 0.7961 | 0.8359 | 0.86362 | 0.88201 | 0.88528 | 0.87319 | 0.84237 | 0.81882 | 0.80127 | 0.74568 | 0.68333 | 0.60905 | 0.88528
2016-09-16 | 0.55078 | 0.51391 | 0.48532 | 0.4671 | 0.46197 | 0.48041 | 0.52672 | 0.5433 | 0.57299 | 0.63189 | 0.69559 | 0.75315 | 0.79631 | 0.82809 | 0.82247 | 0.80509 | 0.79081 | 0.77406 | 0.75504 | 0.74752 | 0.73266 | 0.68345 | 0.6269 | 0.56723 | 0.82809
2016-09-17 | 0.51173 | 0.47734 | 0.45299 | 0.43762 | 0.43636 | 0.45958 | 0.50971 | 0.52651 | 0.55166 | 0.5986 | 0.65729 | 0.70151 | 0.73325 | 0.75004 | 0.76843 | 0.76734 | 0.74127 | 0.71112 | 0.69025 | 0.69378 | 0.68782 | 0.64982 | 0.59511 | 0.5352 | 0.76843
2016-09-18 | 0.48897 | 0.45404 | 0.43561 | 0.42289 | 0.42179 | 0.44472 | 0.4954 | 0.51244 | 0.53856 | 0.58919 | 0.63744 | 0.6869 | 0.73367 | 0.77603 | 0.80576 | 0.82238 | 0.8168 | 0.81932 | 0.78334 | 0.76188 | 0.74282 | 0.69361 | 0.63353 | 0.57022 | 0.82238
2016-09-19 | 0.51798 | 0.48036 | 0.45744 | 0.4427 | 0.44002 | 0.46122 | 0.5108 | 0.53159 | 0.55779 | 0.61275 | 0.65813 | 0.68618 | 0.69449 | 0.68081 | 0.6575 | 0.64659 | 0.6366 | 0.62673 | 0.61497 | 0.61942 | 0.61434 | 0.58827 | 0.55086 | 0.50904 | 0.69449
2016-09-20 | 0.46672 | 0.43779 | 0.4186 | 0.40798 | 0.40256 | 0.40794 | 0.42423 | 0.44531 | 0.48469 | 0.54435 | 0.597 | 0.63832 | 0.66867 | 0.68849 | 0.69076 | 0.66007 | 0.63441 | 0.62156 | 0.60129 | 0.60574 | 0.60129 | 0.57064 | 0.53331 | 0.49363 | 0.69076
2016-09-21 | 0.45584 | 0.42448 | 0.40391 | 0.39056 | 0.3848 | 0.38627 | 0.39694 | 0.40907 | 0.45542 | 0.52626 | 0.59066 | 0.65003 | 0.69743 | 0.73043 | 0.7526 | 0.76096 | 0.75978 | 0.74421 | 0.70915 | 0.69294 | 0.6751 | 0.62732 | 0.57576 | 0.5171 | 0.76096
2016-09-22 | 0.46987 | 0.4372 | 0.41554 | 0.40651 | 0.40874 | 0.43636 | 0.48586 | 0.50829 | 0.53709 | 0.58869 | 0.64021 | 0.68534 | 0.7191 | 0.72611 | 0.71725 | 0.70596 | 0.69953 | 0.68694 | 0.67909 | 0.68383 | 0.66771 | 0.62303 | 0.56803 | 0.51194 | 0.72611
2016-09-23 | 0.46454 | 0.432 | 0.41016 | 0.39879 | 0.4 | 0.42918 | 0.48477 | 0.50862 | 0.52059 | 0.55481 | 0.57941 | 0.60863 | 0.62975 | 0.63429 | 0.6366 | 0.64172 | 0.64865 | 0.65986 | 0.65251 | 0.66225 | 0.65373 | 0.61334 | 0.56287 | 0.50606 | 0.66225
2016-09-24 | 0.45803 | 0.42654 | 0.41096 | 0.39874 | 0.39748 | 0.42599 | 0.48045 | 0.50384 | 0.52264 | 0.55728 | 0.59028 | 0.62295 | 0.64478 | 0.67132 | 0.70125 | 0.72481 | 0.72699 | 0.71746 | 0.70071 | 0.70041 | 0.69088 | 0.65142 | 0.59427 | 0.54032 | 0.72699
2016-09-25 | 0.49367 | 0.4595 | 0.4372 | 0.42318 | 0.42234 | 0.44119 | 0.48259 | 0.50833 | 0.53889 | 0.59343 | 0.64676 | 0.68173 | 0.70041 | 0.71692 | 0.73887 | 0.75676 | 0.74391 | 0.70944 | 0.68589 | 0.68215 | 0.66922 | 0.62816 | 0.57622 | 0.5268 | 0.75676
2016-09-26 | 0.48137 | 0.45085 | 0.43095 | 0.41911 | 0.41885 | 0.4443 | 0.49506 | 0.51966 | 0.5399 | 0.57807 | 0.6269 | 0.68173 | 0.72288 | 0.76314 | 0.77708 | 0.77838 | 0.76423 | 0.73665 | 0.70793 | 0.70348 | 0.68681 | 0.6515 | 0.60532 | 0.59045 | 0.77838
2016-09-27 | 0.53549 | 0.48477 | 0.46428 | 0.4495 | 0.44375 | 0.44627 | 0.45908 | 0.47499 | 0.52617 | 0.60028 | 0.6625 | 0.72027 | 0.76541 | 0.79598 | 0.81722 | 0.81827 | 0.79161 | 0.76348 | 0.7254 | 0.71582 | 0.69319 | 0.65822 | 0.61283 | 0.56211 | 0.81827
2016-09-28 | 0.51702 | 0.48423 | 0.46009 | 0.44333 | 0.43557 | 0.43662 | 0.44531 | 0.46017 | 0.50661 | 0.58012 | 0.64608 | 0.7057 | 0.75558 | 0.79077 | 0.81269 | 0.81945 | 0.81012 | 0.78292 | 0.74173 | 0.74089 | 0.72477 | 0.67993 | 0.62219 | 0.56123 | 0.81945
2016-09-29 | 0.51521 | 0.47827 | 0.45689 | 0.44333 | 0.44337 | 0.46613 | 0.51509 | 0.53591 | 0.5619 | 0.62102 | 0.6837 | 0.74467 | 0.78187 | 0.8129 | 0.82839 | 0.82826 | 0.81772 | 0.78922 | 0.75735 | 0.74425 | 0.70491 | 0.65717 | 0.59755 | 0.54007 | 0.82839
2016-09-30 | 0.49015 | 0.45719 | 0.43674 | 0.42452 | 0.4244 | 0.44896 | 0.50463 | 0.52332 | 0.55376 | 0.6117 | 0.66846 | 0.7165 | 0.7547 | 0.76734 | 0.77885 | 0.76079 | 0.75831 | 0.75281 | 0.73211 | 0.73463 | 0.71826 | 0.67518 | 0.61711 | 0.5564 | 0.77885
2016-10-01 | 0.5074 | 0.47272 | 0.45286 | 0.44073 | 0.43871 | 0.4642 | 0.51828 | 0.53684 | 0.56807 | 0.62589 | 0.67913 | 0.73098 | 0.77221 | 0.80257 | 0.81558 | 0.83775 | 0.85077 | 0.83763 | 0.80597 | 0.79014 | 0.76864 | 0.71851 | 0.65158 | 0.61695 | 0.85077
2016-10-02 | 0.54536 | 0.50001 | 0.4757 | 0.46021 | 0.45622 | 0.47717 | 0.52668 | 0.54414 | 0.57635 | 0.63848 | 0.70088 | 0.75214 | 0.79371 | 0.83603 | 0.85887 | 0.87491 | 0.88427 | 0.86844 | 0.83221 | 0.81374 | 0.78955 | 0.73417 | 0.67228 | 0.60418 | 0.88427
2016-10-03 | 0.54998 | 0.51244 | 0.48347 | 0.4668 | 0.4603 | 0.47902 | 0.52668 | 0.54729 | 0.58311 | 0.64898 | 0.71305 | 0.77137 | 0.81075 | 0.85324 | 0.87474 | 0.88629 | 0.88574 | 0.84976 | 0.79786 | 0.76915 | 0.7314 | 0.6853 | 0.63311 | 0.58075 | 0.88629
2016-10-04 | 0.53142 | 0.49246 | 0.4676 | 0.45026 | 0.44182 | 0.44476 | 0.45782 | 0.47419 | 0.52886 | 0.60045 | 0.65482 | 0.70222 | 0.74219 | 0.76608 | 0.77481 | 0.76961 | 0.75139 | 0.72393 | 0.68824 | 0.68207 | 0.66187 | 0.62341 | 0.5763 | 0.52714 | 0.77481
2016-10-05 | 0.47642 | 0.43422 | 0.40256 | 0.37771 | 0.36398 | 0.36033 | 0.36658 | 0.37259 | 0.40387 | 0.4503 | 0.49569 | 0.52773 | 0.5622 | 0.59259 | 0.61787 | 0.63634 | 0.65423 | 0.64722 | 0.6198 | 0.61753 | 0.602 | 0.56005 | 0.50925 | 0.45521 | 0.65423
2016-10-06 | 0.41176 | 0.38098 | 0.36222 | 0.35247 | 0.35478 | 0.38409 | 0.43494 | 0.45702 | 0.47856 | 0.51828 | 0.55846 | 0.59411 | 0.63131 | 0.65864 | 0.68606 | 0.69458 | 0.70398 | 0.6908 | 0.67741 | 0.69135 | 0.66972 | 0.62392 | 0.57257 | 0.51538 | 0.70398
2016-10-07 | 0.465 | 0.43477 | 0.4152 | 0.40265 | 0.39984 | 0.42331 | 0.47667 | 0.5009 | 0.5119 | 0.55128 | 0.5936 | 0.62337 | 0.64764 | 0.66796 | 0.67812 | 0.6735 | 0.67291 | 0.66485 | 0.65868 | 0.67459 | 0.6565 | 0.62417 | 0.56791 | 0.50438 | 0.67812
2016-10-08 | 0.4574 | 0.42692 | 0.40508 | 0.39421 | 0.39547 | 0.4223 | 0.47625 | 0.49682 | 0.51794 | 0.56639 | 0.62051 | 0.66557 | 0.70743 | 0.73959 | 0.76575 | 0.77754 | 0.77654 | 0.76394 | 0.74102 | 0.74123 | 0.71985 | 0.67275 | 0.61489 | 0.55649 | 0.77754
2016-10-09 | 0.50312 | 0.46928 | 0.44573 | 0.42839 | 0.42566 | 0.42079 | 0.49464 | 0.51429 | 0.53927 | 0.59738 | 0.65259 | 0.70134 | 0.73778 | 0.77272 | 0.79652 | 0.81227 | 0.81504 | 0.79992 | 0.76596 | 0.75848 | 0.73325 | 0.68387 | 0.62845 | 0.56392 | 0.81504
2016-10-10 | 0.50917 | 0.4697 | 0.44606 | 0.42906 | 0.42599 | 0.44673 | 0.4959 | 0.51794 | 0.54507 | 0.6038 | 0.66149 | 0.70604 | 0.74526 | 0.77767 | 0.79967 | 0.81453 | 0.81747 | 0.79677 | 0.75453 | 0.73963 | 0.71137 | 0.66859 | 0.62056 | 0.56925 | 0.81747
2016-10-11 | 0.51887 | 0.482 | 0.45845 | 0.44077 | 0.43086 | 0.43137 | 0.44308 | 0.4553 | 0.50514 | 0.58332 | 0.64789 | 0.70205 | 0.7437 | 0.77523 | 0.79665 | 0.81025 | 0.81285 | 0.79505 | 0.75 | 0.72972 | 0.70125 | 0.6578 | 0.61459 | 0.56299 | 0.81285
2016-10-12 | 0.51614 | 0.47818 | 0.44942 | 0.43137 | 0.42268 | 0.42104 | 0.42944 | 0.43578 | 0.49006 | 0.57353 | 0.64092 | 0.69722 | 0.74467 | 0.77528 | 0.79556 | 0.80647 | 0.80769 | 0.79194 | 0.75412 | 0.75084 | 0.72359 | 0.67644 | 0.62727 | 0.5703 | 0.80769
2016-10-13 | 0.52252 | 0.48817 | 0.46651 | 0.45366 | 0.45396 | 0.47738 | 0.52361 | 0.54288 | 0.56841 | 0.62245 | 0.68295 | 0.73094 | 0.7644 | 0.79131 | 0.80949 | 0.82138 | 0.81978 | 0.8029 | 0.77053 | 0.76906 | 0.7406 | 0.69416 | 0.63786 | 0.57735 | 0.82138
2016-10-14 | 0.52634 | 0.49401 | 0.47415 | 0.46076 | 0.45757 | 0.48175 | 0.53411 | 0.55413 | 0.57966 | 0.63542 | 0.68895 | 0.73358 | 0.76482 | 0.7982 | 0.81621 | 0.82108 | 0.81138 | 0.78628 | 0.76373 | 0.76936 | 0.73766 | 0.68836 | 0.6295 | 0.5666 | 0.82108
2016-10-15 | 0.50879 | 0.47142 | 0.44921 | 0.43531 | 0.43561 | 0.45878 | 0.5095 | 0.53251 | 0.55586 | 0.60464 | 0.65028 | 0.69344 | 0.64873 | 0.74765 | 0.7542 | 0.75894 | 0.74748 | 0.72918 | 0.70688 | 0.71225 | 0.68261 | 0.63756 | 0.57786 | 0.51903 | 0.75894
2016-10-16 | 0.46701 | 0.43242 | 0.411 | 0.39639 | 0.38988 | 0.40785 | 0.45236 | 0.46781 | 0.48326 | 0.52105 | 0.55674 | 0.58445 | 0.61308 | 0.64214 | 0.66813 | 0.69382 | 0.70835 | 0.701 | 0.67157 | 0.6688 | 0.64088 | 0.59209 | 0.53407 | 0.47251 | 0.70835
2016-10-17 | 0.41911 | 0.38266 | 0.36213 | 0.35012 | 0.34714 | 0.3686 | 0.4144 | 0.43473 | 0.45505 | 0.49283 | 0.52781 | 0.55938 | 0.5855 | 0.61552 | 0.64453 | 0.67056 | 0.68312 | 0.6717 | 0.63559 | 0.62316 | 0.59108 | 0.5467 | 0.50434 | 0.45584 | 0.68312
2016-10-18 | 0.41474 | 0.37804 | 0.35512 | 0.34206 | 0.33614 | 0.34147 | 0.35776 | 0.37464 | 0.41701 | 0.47209 | 0.5179 | 0.55552 | 0.59264 | 0.62492 | 0.6541 | 0.67644 | 0.68459 | 0.67186 | 0.63542 | 0.62551 | 0.59495 | 0.55246 | 0.5124 | 0.46458 | 0.68459
2016-10-19 | 0.4223 | 0.38917 | 0.36515 | 0.35067 | 0.34462 | 0.34488 | 0.35588 | 0.3665 | 0.411 | 0.47054 | 0.52227 | 0.56593 | 0.61069 | 0.64478 | 0.67212 | 0.68832 | 0.69386 | 0.68135 | 0.65343 | 0.65578 | 0.62925 | 0.58168 | 0.5323 | 0.47864 | 0.69386
2016-10-20 | 0.43149 | 0.39727 | 0.37699 | 0.36641 | 0.36704 | 0.39093 | 0.438 | 0.46218 | 0.48927 | 0.54183 | 0.59264 | 0.63534 | 0.67128 | 0.69924 | 0.72443 | 0.73178 | 0.7267 | 0.70948 | 0.69248 | 0.69861 | 0.66775 | 0.61955 | 0.56451 | 0.50707 | 0.73178
2016-10-21 | 0.45652 | 0.42591 | 0.40815 | 0.39698 | 0.39782 | 0.42263 | 0.47516 | 0.50144 | 0.51148 | 0.54414 | 0.58033 | 0.60217 | 0.61699 | 0.62417 | 0.62589 | 0.6274 | 0.62421 | 0.618 | 0.61779 | 0.6358 | 0.61296 | 0.57643 | 0.52642 | 0.46827 | 0.6358
2016-10-22 | 0.42444 | 0.39475 | 0.37754 | 0.36906 | 0.37107 | 0.39412 | 0.45173 | 0.47948 | 0.49099 | 0.5213 | 0.55951 | 0.5973 | 0.62501 | 0.64869 | 0.66594 | 0.67573 | 0.67002 | 0.6557 | 0.64902 | 0.66011 | 0.63618 | 0.59566 | 0.54179 | 0.48423 | 0.67573
2016-10-23 | 0.43662 | 0.40895 | 0.39035 | 0.37909 | 0.37783 | 0.40185 | 0.45706 | 0.4844 | 0.49099 | 0.51685 | 0.54645 | 0.57101 | 0.59138 | 0.60435 | 0.61632 | 0.62182 | 0.61863 | 0.60972 | 0.60305 | 0.6151 | 0.60406 | 0.56875 | 0.52076 | 0.46945 | 0.62182
2016-10-24 | 0.42582 | 0.39631 | 0.37918 | 0.37162 | 0.37401 | 0.39669 | 0.44379 | 0.47281 | 0.49032 | 0.52361 | 0.55111 | 0.57059 | 0.58025 | 0.59062 | 0.59856 | 0.60569 | 0.60494 | 0.59545 | 0.58739 | 0.59184 | 0.56959 | 0.54074 | 0.50745 | 0.46197 | 0.60569
2016-10-25 | 0.41432 | 0.37998 | 0.35735 | 0.34311 | 0.33803 | 0.34189 | 0.35747 | 0.37687 | 0.41466 | 0.46592 | 0.50799 | 0.53885 | 0.5653 | 0.58965 | 0.60779 | 0.62089 | 0.62119 | 0.60544 | 0.57677 | 0.57286 | 0.54662 | 0.51463 | 0.47994 | 0.43578 | 0.62119
2016-10-26 | 0.39597 | 0.36646 | 0.3484 | 0.33576 | 0.33056 | 0.33161 | 0.34202 | 0.35802 | 0.39337 | 0.44615 | 0.49158 | 0.52525 | 0.55371 | 0.58143 | 0.60359 | 0.62047 | 0.62799 | 0.61716 | 0.59213 | 0.59982 | 0.57282 | 0.52886 | 0.47764 | 0.42158 | 0.62799
2016-10-27 | 0.3754 | 0.34588 | 0.32871 | 0.32094 | 0.32367 | 0.34991 | 0.4016 | 0.43069 | 0.44577 | 0.48389 | 0.52202 | 0.55615 | 0.58428 | 0.61392 | 0.63937 | 0.66254 | 0.67451 | 0.66552 | 0.64697 | 0.65482 | 0.62228 | 0.57206 | 0.5153 | 0.45408 | 0.67451
2016-10-28 | 0.40597 | 0.37456 | 0.35462 | 0.34446 | 0.345 | 0.37137 | 0.42452 | 0.45089 | 0.46731 | 0.51127 | 0.5517 | 0.59016 | 0.62156 | 0.65998 | 0.68757 | 0.7073 | 0.71675 | 0.70566 | 0.68228 | 0.68862 | 0.6549 | 0.60935 | 0.55149 | 0.49162 | 0.71675
2016-10-29 | 0.44329 | 0.40949 | 0.3869 | 0.37439 | 0.37435 | 0.39765 | 0.45261 | 0.47575 | 0.49086 | 0.54288 | 0.58533 | 0.62459 | 0.66137 | 0.69206 | 0.71624 | 0.73698 | 0.74106 | 0.72208 | 0.6921 | 0.69219 | 0.66053 | 0.61405 | 0.55619 | 0.49422 | 0.74106
2016-10-30 | 0.43834 | 0.40395 | 0.38082 | 0.36776 | 0.3662 | 0.38925 | 0.44136 | 0.46672 | 0.48162 | 0.5284 | 0.57756 | 0.61749 | 0.65112 | 0.6782 | 0.69382 | 0.70583 | 0.71406 | 0.69827 | 0.67678 | 0.68118 | 0.65007 | 0.60888 | 0.55489 | 0.49657 | 0.71406
2016-10-31 | 0.44337 | 0.40811 | 0.38346 | 0.37086 | 0.36818 | 0.39089 | 0.44316 | 0.46966 | 0.4862 | 0.53155 | 0.5729 | 0.61002 | 0.63723 | 0.65608 | 0.67002 | 0.68047 | 0.68274 | 0.66099 | 0.62148 | 0.59982 | 0.55875 | 0.52315 | 0.48045 | 0.43263 | 0.68274
2016-11-01 | 0.38476 | 0.35205 | 0.3332 | 0.32271 | 0.31884 | 0.32321 | 0.3416 | 0.36033 | 0.3979 | 0.44329 | 0.47617 | 0.4912 | 0.49691 | 0.49674 | 0.49846 | 0.49959 | 0.49598 | 0.48255 | 0.47314 | 0.48662 | 0.46538 | 0.43863 | 0.40626 | 0.37242 | 0.49959
2016-11-02 | 0.66334 | 0.31124 | 0.30759 | 0.3073 | 0.31217 | 0.32661 | 0.35193 | 0.39832 | 0.43867 | 0.45488 | 0.45715 | 0.45274 | 0.44867 | 0.44224 | 0.43934 | 0.43624 | 0.43745 | 0.45559 | 0.49128 | 0.4812 | 0.4634 | 0.433 | 0.39417 | 0.35923 | 0.66334
2016-11-03 | 0.33018 | 0.32098 | 0.31582 | 0.31779 | 0.32905 | 0.36721 | 0.4296 | 0.45421 | 0.46055 | 0.46861 | 0.47831 | 0.48557 | 0.48641 | 0.48771 | 0.48498 | 0.48078 | 0.48452 | 0.50073 | 0.53474 | 0.52357 | 0.50174 | 0.46428 | 0.4199 | 0.37674 | 0.53474
2016-11-04 | 0.34634 | 0.32682 | 0.31586 | 0.31372 | 0.31897 | 0.34941 | 0.39879 | 0.43363 | 0.46093 | 0.48192 | 0.50216 | 0.51975 | 0.5281 | 0.53566 | 0.53969 | 0.54292 | 0.53776 | 0.5462 | 0.57882 | 0.5687 | 0.54502 | 0.50237 | 0.45916 | 0.41503 | 0.57882
2016-11-05 | 0.3788 | 0.35382 | 0.34084 | 0.33455 | 0.33875 | 0.36679 | 0.41676 | 0.43355 | 0.47558 | 0.51576 | 0.54607 | 0.56946 | 0.58487 | 0.59243 | 0.59528 | 0.58965 | 0.58021 | 0.58756 | 0.61581 | 0.60171 | 0.57752 | 0.5394 | 0.48897 | 0.43745 | 0.61581
2016-11-06 | 0.39614 | 0.36839 | 0.35042 | 0.34089 | 0.34236 | 0.37065 | 0.41864 | 0.45362 | 0.48952 | 0.52928 | 0.56807 | 0.60011 | 0.62459 | 0.64264 | 0.65125 | 0.65062 | 0.63605 | 0.62211 | 0.63697 | 0.61464 | 0.57865 | 0.53159 | 0.47734 | 0.4262 | 0.65125
2016-11-07 | 0.38262 | 0.3542 | 0.33631 | 0.32934 | 0.33102 | 0.35617 | 0.40685 | 0.4388 | 0.47331 | 0.5116 | 0.54553 | 0.57555 | 0.59948 | 0.61884 | 0.62711 | 0.62534 | 0.60838 | 0.59461 | 0.60376 | 0.57408 | 0.54305 | 0.50627 | 0.46823 | 0.42784 | 0.62711
2016-11-08 | 0.38883 | 0.36024 | 0.34047 | 0.33186 | 0.3301 | 0.33753 | 0.3555 | 0.39051 | 0.45152 | 0.50014 | 0.53331 | 0.55947 | 0.58147 | 0.59062 | 0.58928 | 0.57937 | 0.56518 | 0.5698 | 0.57996 | 0.55418 | 0.5276 | 0.49615 | 0.46239 | 0.42297 | 0.59062
2016-11-09 | 0.38892 | 0.36012 | 0.34315 | 0.33425 | 0.3306 | 0.33572 | 0.34828 | 0.37456 | 0.42457 | 0.46311 | 0.48461 | 0.4972 | 0.49875 | 0.4925 | 0.48599 | 0.4757 | 0.47335 | 0.49678 | 0.51727 | 0.50232 | 0.48024 | 0.44808 | 0.41382 | 0.37292 | 0.51727
2016-11-10 | 0.34005 | 0.32174 | 0.31196 | 0.30784 | 0.31292 | 0.33526 | 0.38909 | 0.43137 | 0.4503 | 0.47327 | 0.49082 | 0.50623 | 0.51744 | 0.52726 | 0.53209 | 0.53595 | 0.53159 | 0.53852 | 0.56417 | 0.54549 | 0.51622 | 0.47608 | 0.43351 | 0.38837 | 0.56417
2016-11-11 | 0.34781 | 0.32405 | 0.31116 | 0.30637 | 0.30977 | 0.32888 | 0.36667 | 0.40517 | 0.43884 | 0.46865 | 0.4909 | 0.50686 | 0.5216 | 0.5352 | 0.54154 | 0.54737 | 0.54229 | 0.54502 | 0.56975 | 0.55241 | 0.52311 | 0.48318 | 0.43821 | 0.389 | 0.56975
2016-11-12 | 0.34718 | 0.32283 | 0.31162 | 0.30688 | 0.31267 | 0.33963 | 0.39429 | 0.42536 | 0.44686 | 0.47423 | 0.50211 | 0.52689 | 0.54859 | 0.57076 | 0.58562 | 0.59096 | 0.58294 | 0.57748 | 0.59776 | 0.57769 | 0.54725 | 0.50711 | 0.45912 | 0.40886 | 0.59776
2016-11-13 | 0.36776 | 0.34311 | 0.32804 | 0.32338 | 0.32711 | 0.35327 | 0.40618 | 0.43867 | 0.46747 | 0.50346 | 0.53537 | 0.55884 | 0.58159 | 0.60158 | 0.61048 | 0.6117 | 0.60061 | 0.59453 | 0.61187 | 0.59146 | 0.56001 | 0.51769 | 0.46634 | 0.41688 | 0.61187
2016-11-14 | 0.37477 | 0.34676 | 0.33127 | 0.32317 | 0.3251 | 0.34882 | 0.40164 | 0.43552 | 0.46483 | 0.49603 | 0.52315 | 0.54099 | 0.5577 | 0.56984 | 0.57693 | 0.57685 | 0.56446 | 0.56047 | 0.57366 | 0.54981 | 0.52193 | 0.48733 | 0.45265 | 0.41323 | 0.57693
2016-11-15 | 0.37746 | 0.3513 | 0.33648 | 0.32842 | 0.3277 | 0.33614 | 0.35659 | 0.38858 | 0.43796 | 0.47902 | 0.5056 | 0.52584 | 0.53923 | 0.55094 | 0.55527 | 0.55283 | 0.54221 | 0.54007 | 0.55531 | 0.53176 | 0.50623 | 0.47827 | 0.44858 | 0.41562 | 0.55531
2016-11-16 | 0.38149 | 0.35865 | 0.34374 | 0.33543 | 0.33295 | 0.33971 | 0.35197 | 0.37872 | 0.43955 | 0.49435 | 0.5336 | 0.56215 | 0.58596 | 0.60087 | 0.60716 | 0.60679 | 0.59495 | 0.59272 | 0.61094 | 0.591 | 0.56056 | 0.52441 | 0.48574 | 0.44149 | 0.61094
2016-11-17 | 0.40445 | 0.38186 | 0.36898 | 0.36335 | 0.37065 | 0.40013 | 0.45408 | 0.48574 | 0.52252 | 0.57164 | 0.61804 | 0.65305 | 0.67799 | 0.69168 | 0.69349 | 0.68761 | 0.67518 | 0.67556 | 0.68811 | 0.66204 | 0.62316 | 0.5724 | 0.52059 | 0.46386 | 0.69349
2016-11-18 | 0.41915 | 0.39018 | 0.37015 | 0.35982 | 0.36234 | 0.38539 | 0.44203 | 0.47423 | 0.50022 | 0.52932 | 0.54876 | 0.55241 | 0.54309 | 0.53293 | 0.51924 | 0.50556 | 0.50619 | 0.53348 | 0.56089 | 0.55237 | 0.53155 | 0.49926 | 0.45626 | 0.41541 | 0.56089
2016-11-19 | 0.38627 | 0.37317 | 0.36784 | 0.3686 | 0.38107 | 0.41827 | 0.49061 | 0.52202 | 0.53465 | 0.54078 | 0.53747 | 0.5247 | 0.50921 | 0.49766 | 0.48859 | 0.48519 | 0.4909 | 0.52357 | 0.55611 | 0.5509 | 0.53482 | 0.50325 | 0.46231 | 0.42011 | 0.55611
2016-11-20 | 0.38959 | 0.37427 | 0.37049 | 0.37208 | 0.38514 | 0.42188 | 0.48658 | 0.51253 | 0.50661 | 0.50652 | 0.50434 | 0.50165 | 0.49741 | 0.49309 | 0.48603 | 0.48259 | 0.48414 | 0.51437 | 0.54712 | 0.54221 | 0.5242 | 0.4933 | 0.45328 | 0.411 | 0.54712
2016-11-21 | 0.37792 | 0.35735 | 0.35021 | 0.34592 | 0.35197 | 0.39085 | 0.44463 | 0.47545 | 0.4862 | 0.49657 | 0.50526 | 0.50724 | 0.50018 | 0.49523 | 0.48918 | 0.48368 | 0.48691 | 0.5111 | 0.52617 | 0.51269 | 0.49464 | 0.46957 | 0.44023 | 0.40622 | 0.52617
2016-11-22 | 0.37301 | 0.35155 | 0.33958 | 0.33534 | 0.3369 | 0.3466 | 0.36893 | 0.39891 | 0.44908 | 0.49254 | 0.51744 | 0.53083 | 0.53155 | 0.53071 | 0.52651 | 0.51933 | 0.51803 | 0.53852 | 0.55426 | 0.54368 | 0.52819 | 0.50509 | 0.47873 | 0.44249 | 0.55426
2016-11-23 | 0.40764 | 0.38493 | 0.36713 | 0.35697 | 0.35508 | 0.36117 | 0.37393 | 0.40307 | 0.46957 | 0.53495 | 0.57735 | 0.60469 | 0.62194 | 0.63445 | 0.63672 | 0.63248 | 0.61636 | 0.62282 | 0.64294 | 0.62942 | 0.60553 | 0.57009 | 0.53066 | 0.4912 | 0.64294
2016-11-24 | 0.44111 | 0.41058 | 0.39329 | 0.38661 | 0.39194 | 0.41877 | 0.46777 | 0.50195 | 0.54624 | 0.59507 | 0.63911 | 0.6845 | 0.71927 | 0.73686 | 0.74513 | 0.74202 | 0.72242 | 0.71519 | 0.72968 | 0.70512 | 0.67258 | 0.62366 | 0.57899 | 0.52281 | 0.74513
2016-11-25 | 0.47377 | 0.43985 | 0.42079 | 0.41331 | 0.41516 | 0.44153 | 0.49019 | 0.52302 | 0.5666 | 0.61203 | 0.6515 | 0.67762 | 0.6924 | 0.70306 | 0.70176 | 0.69458 | 0.67904 | 0.68412 | 0.69827 | 0.67946 | 0.64839 | 0.61153 | 0.56681 | 0.52243 | 0.70306
2016-11-26 | 0.47885 | 0.44917 | 0.42973 | 0.41957 | 0.41965 | 0.43485 | 0.4676 | 0.49867 | 0.53562 | 0.56169 | 0.56346 | 0.55737 | 0.54788 | 0.53302 | 0.51509 | 0.49754 | 0.48801 | 0.50757 | 0.52907 | 0.51672 | 0.49628 | 0.47491 | 0.44648 | 0.41029 | 0.56346
2016-11-27 | 0.37704 | 0.35499 | 0.34378 | 0.34093 | 0.34391 | 0.35743 | 0.38279 | 0.41978 | 0.46214 | 0.48985 | 0.50627 | 0.51269 | 0.51227 | 0.5035 | 0.49346 | 0.47776 | 0.45715 | 0.44862 | 0.45475 | 0.43855 | 0.42742 | 0.41739 | 0.40156 | 0.37851 | 0.51269
2016-11-28 | 0.35646 | 0.34332 | 0.33803 | 0.33984 | 0.34933 | 0.36923 | 0.40097 | 0.43439 | 0.46605 | 0.48389 | 0.48628 | 0.47835 | 0.46852 | 0.45962 | 0.45135 | 0.44598 | 0.4464 | 0.47373 | 0.50484 | 0.49603 | 0.48242 | 0.47407 | 0.44589 | 0.4139 | 0.50484
2016-11-29 | 0.3851 | 0.36948 | 0.36117 | 0.36012 | 0.36503 | 0.37532 | 0.39778 | 0.42629 | 0.4566 | 0.47046 | 0.47222 | 0.47109 | 0.46701 | 0.46248 | 0.45694 | 0.45144 | 0.44657 | 0.4655 | 0.4899 | 0.47894 | 0.46189 | 0.44245 | 0.41621 | 0.38422 | 0.4899
2016-11-30 | 0.35256 | 0.33199 | 0.32161 | 0.31767 | 0.3196 | 0.32783 | 0.34366 | 0.36868 | 0.411 | 0.44316 | 0.46302 | 0.476 | 0.48545 | 0.49027 | 0.49124 | 0.48801 | 0.48326 | 0.5022 | 0.53549 | 0.52395 | 0.50467 | 0.47533 | 0.43985 | 0.39492 | 0.53549
2016-12-01 | 0.35999 | 0.33715 | 0.32577 | 0.32216 | 0.32829 | 0.35823 | 0.41335 | 0.44379 | 0.46978 | 0.49829 | 0.52806 | 0.55115 | 0.56186 | 0.56589 | 0.56085 | 0.5517 | 0.54313 | 0.56266 | 0.59444 | 0.58466 | 0.56165 | 0.52445 | 0.48024 | 0.42864 | 0.59444
2016-12-02 | 0.38476 | 0.35735 | 0.33988 | 0.33299 | 0.33774 | 0.36494 | 0.42171 | 0.45076 | 0.47159 | 0.50153 | 0.53012 | 0.54754 | 0.55758 | 0.56383 | 0.56169 | 0.55439 | 0.54444 | 0.56576 | 0.59683 | 0.58558 | 0.56287 | 0.52726 | 0.48099 | 0.4291 | 0.59683
2016-12-03 | 0.38417 | 0.35491 | 0.33929 | 0.33186 | 0.33505 | 0.36259 | 0.42431 | 0.45081 | 0.47654 | 0.51286 | 0.54053 | 0.56287 | 0.57958 | 0.58739 | 0.59343 | 0.59625 | 0.58248 | 0.58894 | 0.61627 | 0.60166 | 0.57546 | 0.53692 | 0.48973 | 0.43473 | 0.61627
2016-12-04 | 0.38913 | 0.36112 | 0.345 | 0.33807 | 0.3421 | 0.37044 | 0.42574 | 0.45597 | 0.48091 | 0.5163 | 0.54444 | 0.56782 | 0.58588 | 0.59385 | 0.59914 | 0.60112 | 0.58625 | 0.59335 | 0.62215 | 0.60989 | 0.58575 | 0.55027 | 0.50119 | 0.44766 | 0.62215
2016-12-05 | 0.40135 | 0.36952 | 0.35222 | 0.34513 | 0.3479 | 0.37527 | 0.43074 | 0.46122 | 0.49141 | 0.53327 | 0.56425 | 0.58504 | 0.59641 | 0.59537 | 0.59423 | 0.59839 | 0.5928 | 0.60015 | 0.61577 | 0.59667 | 0.57185 | 0.54074 | 0.5048 | 0.45996 | 0.61577
2016-12-06 | 0.41524 | 0.38359 | 0.36373 | 0.3513 | 0.34626 | 0.35184 | 0.3694 | 0.39736 | 0.45484 | 0.51076 | 0.55153 | 0.57832 | 0.59633 | 0.60742 | 0.61237 | 0.60838 | 0.59028 | 0.58252 | 0.59482 | 0.56631 | 0.53847 | 0.50929 | 0.4726 | 0.42927 | 0.61237
2016-12-07 | 0.38459 | 0.35651 | 0.33799 | 0.32594 | 0.32258 | 0.32732 | 0.33967 | 0.36213 | 0.41537 | 0.46802 | 0.50157 | 0.52327 | 0.53461 | 0.54082 | 0.54267 | 0.53461 | 0.52357 | 0.53654 | 0.56971 | 0.54796 | 0.52453 | 0.49048 | 0.4461 | 0.39706 | 0.56971
2016-12-08 | 0.35525 | 0.3298 | 0.31704 | 0.31259 | 0.31771 | 0.34597 | 0.40046 | 0.43053 | 0.4503 | 0.47344 | 0.49342 | 0.50644 | 0.51488 | 0.52168 | 0.52483 | 0.52861 | 0.52714 | 0.54553 | 0.58101 | 0.57097 | 0.54297 | 0.50367 | 0.45702 | 0.40214 | 0.58101
2016-12-09 | 0.3581 | 0.33463 | 0.32279 | 0.31947 | 0.32489 | 0.35604 | 0.42007 | 0.44976 | 0.46491 | 0.47717 | 0.48444 | 0.48599 | 0.48536 | 0.48259 | 0.47818 | 0.47172 | 0.47491 | 0.50824 | 0.55073 | 0.54612 | 0.52815 | 0.49787 | 0.45421 | 0.40836 | 0.55073
2016-12-10 | 0.37296 | 0.35747 | 0.35021 | 0.35449 | 0.36671 | 0.41281 | 0.49053 | 0.53339 | 0.52953 | 0.51635 | 0.50593 | 0.49321 | 0.48234 | 0.47486 | 0.46567 | 0.46214 | 0.46714 | 0.50619 | 0.55867 | 0.55863 | 0.55111 | 0.52504 | 0.48477 | 0.44006 | 0.55867
2016-12-11 | 0.4105 | 0.39648 | 0.3932 | 0.39429 | 0.40886 | 0.45421 | 0.53495 | 0.57227 | 0.55649 | 0.54036 | 0.52034 | 0.50694 | 0.49363 | 0.48356 | 0.47407 | 0.47008 | 0.47537 | 0.51227 | 0.55598 | 0.55258 | 0.54204 | 0.51568 | 0.47167 | 0.42755 | 0.57227
2016-12-12 | 0.3953 | 0.37859 | 0.37271 | 0.372 | 0.38661 | 0.43023 | 0.50224 | 0.53692 | 0.53936 | 0.53889 | 0.5305 | 0.51971 | 0.50665 | 0.49556 | 0.48414 | 0.48011 | 0.48645 | 0.52626 | 0.56341 | 0.55661 | 0.54834 | 0.52802 | 0.49804 | 0.46176 | 0.56341
2016-12-13 | 0.42868 | 0.41424 | 0.40739 | 0.40823 | 0.41608 | 0.43729 | 0.46987 | 0.5085 | 0.53125 | 0.52991 | 0.51387 | 0.49905 | 0.48801 | 0.47705 | 0.46731 | 0.46218 | 0.46076 | 0.48649 | 0.51765 | 0.5077 | 0.49703 | 0.48125 | 0.45731 | 0.43082 | 0.53125
2016-12-14 | 0.40361 | 0.38657 | 0.38069 | 0.38119 | 0.38711 | 0.40408 | 0.43494 | 0.47314 | 0.50782 | 0.51173 | 0.49783 | 0.48725 | 0.47902 | 0.47222 | 0.46764 | 0.46357 | 0.46374 | 0.49074 | 0.53511 | 0.52966 | 0.51706 | 0.49376 | 0.45412 | 0.41524 | 0.53511
2016-12-15 | 0.38594 | 0.37107 | 0.36994 | 0.37313 | 0.39035 | 0.43422 | 0.51232 | 0.55237 | 0.54901 | 0.5294 | 0.51496 | 0.50342 | 0.50069 | 0.49632 | 0.49107 | 0.49027 | 0.49153 | 0.5208 | 0.56606 | 0.56152 | 0.54393 | 0.51181 | 0.46764 | 0.42095 | 0.56606
2016-12-16 | 0.38543 | 0.36856 | 0.36238 | 0.36461 | 0.37691 | 0.4181 | 0.49351 | 0.5281 | 0.52449 | 0.51089 | 0.50186 | 0.49724 | 0.49569 | 0.4964 | 0.49556 | 0.49666 | 0.49729 | 0.51958 | 0.5601 | 0.55267 | 0.53087 | 0.49397 | 0.45001 | 0.40164 | 0.5601
2016-12-17 | 0.36133 | 0.34013 | 0.33173 | 0.33077 | 0.34164 | 0.37809 | 0.44325 | 0.47818 | 0.48167 | 0.48574 | 0.48939 | 0.49153 | 0.49582 | 0.50106 | 0.50656 | 0.51211 | 0.50938 | 0.52936 | 0.56463 | 0.5535 | 0.52987 | 0.49838 | 0.45358 | 0.40294 | 0.56463
2016-12-18 | 0.36327 | 0.34147 | 0.33253 | 0.33207 | 0.34223 | 0.37649 | 0.44249 | 0.47877 | 0.49137 | 0.4988 | 0.5019 | 0.49934 | 0.49892 | 0.50682 | 0.51164 | 0.51286 | 0.51038 | 0.52877 | 0.56421 | 0.55321 | 0.53532 | 0.50291 | 0.46055 | 0.4126 | 0.56421
2016-12-19 | 0.37418 | 0.35327 | 0.34311 | 0.34152 | 0.35063 | 0.38371 | 0.44337 | 0.48196 | 0.49527 | 0.50283 | 0.50946 | 0.51206 | 0.51177 | 0.51416 | 0.51412 | 0.51316 | 0.50833 | 0.52269 | 0.55283 | 0.53705 | 0.51559 | 0.48868 | 0.45769 | 0.41676 | 0.55283
2016-12-20 | 0.37989 | 0.35533 | 0.34269 | 0.3369 | 0.33631 | 0.34874 | 0.37254 | 0.40416 | 0.44535 | 0.47684 | 0.49418 | 0.49729 | 0.50976 | 0.51122 | 0.51269 | 0.51311 | 0.50841 | 0.52113 | 0.54796 | 0.52806 | 0.50593 | 0.4807 | 0.44913 | 0.41012 | 0.54796
2016-12-21 | 0.37061 | 0.34282 | 0.32577 | 0.31788 | 0.31679 | 0.32254 | 0.33765 | 0.36289 | 0.41231 | 0.46122 | 0.49103 | 0.50648 | 0.52243 | 0.52718 | 0.52361 | 0.51698 | 0.51156 | 0.53222 | 0.564 | 0.5512 | 0.53314 | 0.50656 | 0.46945 | 0.42171 | 0.564
2016-12-22 | 0.37809 | 0.34916 | 0.33178 | 0.32317 | 0.32577 | 0.34655 | 0.38287 | 0.41906 | 0.46714 | 0.51303 | 0.55094 | 0.57492 | 0.591 | 0.60288 | 0.61115 | 0.60704 | 0.59276 | 0.60112 | 0.63269 | 0.6156 | 0.59003 | 0.55926 | 0.51744 | 0.46055 | 0.63269
2016-12-23 | 0.41117 | 0.37653 | 0.35445 | 0.34336 | 0.34488 | 0.36549 | 0.40063 | 0.43615 | 0.48708 | 0.53847 | 0.57635 | 0.60313 | 0.62245 | 0.63009 | 0.61292 | 0.59444 | 0.57802 | 0.58445 | 0.6138 | 0.59717 | 0.57324 | 0.55481 | 0.52777 | 0.49262 | 0.63009
2016-12-24 | 0.44976 | 0.41655 | 0.39492 | 0.38539 | 0.38321 | 0.39614 | 0.42024 | 0.45076 | 0.50866 | 0.57315 | 0.62287 | 0.65599 | 0.67317 | 0.67615 | 0.67837 | 0.67031 | 0.66158 | 0.66951 | 0.6769 | 0.63861 | 0.60259 | 0.57215 | 0.5425 | 0.5001 | 0.67837
2016-12-25 | 0.45694 | 0.42356 | 0.39371 | 0.37074 | 0.35495 | 0.35214 | 0.35869 | 0.37691 | 0.42007 | 0.46403 | 0.49162 | 0.50547 | 0.5103 | 0.50682 | 0.49938 | 0.48372 | 0.46701 | 0.47419 | 0.49401 | 0.48372 | 0.47537 | 0.46227 | 0.43842 | 0.4045 | 0.5103
2016-12-26 | 0.36927 | 0.34475 | 0.33354 | 0.32762 | 0.33039 | 0.34538 | 0.37099 | 0.40072 | 0.43804 | 0.47277 | 0.49938 | 0.51034 | 0.51005 | 0.50363 | 0.49968 | 0.49687 | 0.49934 | 0.52764 | 0.55775 | 0.54691 | 0.52668 | 0.50161 | 0.47134 | 0.43074 | 0.55775
2016-12-27 | 0.38976 | 0.35999 | 0.34038 | 0.3314 | 0.33144 | 0.33807 | 0.3555 | 0.3749 | 0.42032 | 0.4747 | 0.51672 | 0.54376 | 0.56056 | 0.56602 | 0.56623 | 0.55737 | 0.54658 | 0.55905 | 0.58688 | 0.56938 | 0.54414 | 0.51702 | 0.48133 | 0.4362 | 0.58688
2016-12-28 | 0.39354 | 0.3618 | 0.34168 | 0.33018 | 0.32451 | 0.32711 | 0.34005 | 0.35688 | 0.4131 | 0.4739 | 0.5184 | 0.55157 | 0.57458 | 0.59066 | 0.59914 | 0.59885 | 0.58965 | 0.58697 | 0.61308 | 0.59272 | 0.56476 | 0.5326 | 0.49132 | 0.43964 | 0.61308
2016-12-29 | 0.39534 | 0.36494 | 0.3466 | 0.33854 | 0.33942 | 0.3555 | 0.38892 | 0.42037 | 0.4713 | 0.52877 | 0.57429 | 0.60372 | 0.61905 | 0.62589 | 0.63093 | 0.63349 | 0.62341 | 0.62056 | 0.64949 | 0.62753 | 0.59772 | 0.55728 | 0.51307 | 0.45786 | 0.64949
2016-12-30 | 0.40785 | 0.37511 | 0.3552 | 0.34437 | 0.34332 | 0.35944 | 0.3906 | 0.42108 | 0.46542 | 0.51471 | 0.5588 | 0.59461 | 0.6169 | 0.63252 | 0.63676 | 0.63156 | 0.61934 | 0.61921 | 0.64776 | 0.6261 | 0.59923 | 0.56077 | 0.51933 | 0.46844 | 0.64776
2016-12-31 | 0.42112 | 0.38707 | 0.36629 | 0.35508 | 0.35411 | 0.36822 | 0.39706 | 0.42952 | 0.47222 | 0.51593 | 0.55069 | 0.57085 | 0.57563 | 0.57874 | 0.57777 | 0.57173 | 0.57345 | 0.60326 | 0.62883 | 0.59872 | 0.56266 | 0.52319 | 0.48297 | 0.44988 | 0.62883
Max | 0.66334 | 0.58856 | 0.55653 | 0.53684 | 0.54217 | 0.59688 | 0.68958 | 0.73438 | 0.70894 | 0.71007 | 0.77158 | 0.82747 | 0.87193 | 0.91018 | 0.93155 | 0.95317 | 0.95393 | 0.94511 | 0.92697 | 0.89107 | 0.86899 | 0.83288 | 0.76629 | 0.69567

## CLEF
OPC 012919
FPL RC-16
CLEF = (Hourly Loads p.u of Peak) **2
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24
2016-01-01 | 0.16879 | 0.15673 | 0.14092 | 0.13062 | 0.12626 | 0.12839 | 0.13515 | 0.14086 | 0.16758 | 0.21451 | 0.26367 | 0.30026 | 0.32304 | 0.33222 | 0.32947 | 0.32109 | 0.31253 | 0.31985 | 0.35167 | 0.33256 | 0.30465 | 0.275 | 0.23795 | 0.19509
2016-01-02 | 0.15883 | 0.13754 | 0.12409 | 0.1179 | 0.11617 | 0.12332 | 0.15263 | 0.17873 | 0.22129 | 0.27717 | 0.32668 | 0.36296 | 0.39006 | 0.40949 | 0.41835 | 0.41385 | 0.39733 | 0.39042 | 0.41998 | 0.38859 | 0.34829 | 0.30595 | 0.26178 | 0.21443
2016-01-03 | 0.17348 | 0.14685 | 0.13144 | 0.12427 | 0.12368 | 0.13199 | 0.15796 | 0.18449 | 0.21802 | 0.24867 | 0.26709 | 0.2732 | 0.27325 | 0.26822 | 0.2632 | 0.26011 | 0.25853 | 0.28384 | 0.32419 | 0.31296 | 0.29054 | 0.26454 | 0.23123 | 0.19554
2016-01-04 | 0.16617 | 0.14785 | 0.13738 | 0.13297 | 0.13352 | 0.14023 | 0.1551 | 0.17586 | 0.21041 | 0.24351 | 0.26398 | 0.26857 | 0.26423 | 0.25737 | 0.24871 | 0.24078 | 0.24243 | 0.26748 | 0.29041 | 0.27483 | 0.25559 | 0.23293 | 0.206 | 0.17632
2016-01-05 | 0.14837 | 0.1298 | 0.11874 | 0.1126 | 0.11136 | 0.11663 | 0.12959 | 0.1454 | 0.17876 | 0.21455 | 0.25703 | 0.28518 | 0.30036 | 0.30521 | 0.30479 | 0.29911 | 0.29136 | 0.29788 | 0.33547 | 0.31606 | 0.28986 | 0.25237 | 0.21179 | 0.17218
2016-01-06 | 0.13655 | 0.11868 | 0.10863 | 0.10514 | 0.10791 | 0.12465 | 0.16311 | 0.19005 | 0.21626 | 0.25415 | 0.29636 | 0.32481 | 0.34809 | 0.36084 | 0.35686 | 0.34183 | 0.32788 | 0.34888 | 0.38551 | 0.36422 | 0.31895 | 0.26735 | 0.22749 | 0.1872
2016-01-07 | 0.15903 | 0.14441 | 0.1408 | 0.14368 | 0.15756 | 0.19129 | 0.26307 | 0.3209 | 0.34829 | 0.36504 | 0.35837 | 0.33996 | 0.32276 | 0.30614 | 0.29336 | 0.29254 | 0.31005 | 0.36946 | 0.44298 | 0.44825 | 0.42901 | 0.3813 | 0.32562 | 0.27492
2016-01-08 | 0.23885 | 0.22097 | 0.21474 | 0.21199 | 0.21861 | 0.24955 | 0.31296 | 0.34616 | 0.34276 | 0.34276 | 0.33854 | 0.32166 | 0.29925 | 0.27876 | 0.26169 | 0.25512 | 0.25994 | 0.28955 | 0.32606 | 0.31427 | 0.2877 | 0.24713 | 0.20391 | 0.1628
2016-01-09 | 0.13279 | 0.11848 | 0.11201 | 0.10969 | 0.11429 | 0.13441 | 0.18043 | 0.21427 | 0.2255 | 0.24637 | 0.26122 | 0.26944 | 0.27018 | 0.26622 | 0.26122 | 0.25947 | 0.2626 | 0.28801 | 0.32846 | 0.32061 | 0.29591 | 0.2587 | 0.2174 | 0.17425
2016-01-10 | 0.14001 | 0.1203 | 0.10966 | 0.10577 | 0.10808 | 0.12477 | 0.16679 | 0.19826 | 0.22386 | 0.25691 | 0.28469 | 0.30312 | 0.31361 | 0.32161 | 0.3219 | 0.32014 | 0.31767 | 0.32147 | 0.35621 | 0.33659 | 0.30655 | 0.27101 | 0.23639 | 0.19968
2016-01-11 | 0.16071 | 0.13845 | 0.12433 | 0.11775 | 0.1164 | 0.12279 | 0.13773 | 0.15786 | 0.20787 | 0.26861 | 0.31531 | 0.34621 | 0.37008 | 0.38493 | 0.39105 | 0.3877 | 0.3712 | 0.35802 | 0.37969 | 0.35181 | 0.31715 | 0.27845 | 0.24099 | 0.20221
2016-01-12 | 0.16426 | 0.13976 | 0.12545 | 0.1175 | 0.11361 | 0.11597 | 0.12557 | 0.13888 | 0.17421 | 0.21466 | 0.24592 | 0.26475 | 0.28192 | 0.29304 | 0.29618 | 0.29249 | 0.28397 | 0.2781 | 0.31164 | 0.29967 | 0.27311 | 0.23799 | 0.201 | 0.16192
2016-01-13 | 0.13279 | 0.11787 | 0.11122 | 0.11055 | 0.11669 | 0.14133 | 0.19406 | 0.22958 | 0.24446 | 0.26506 | 0.28393 | 0.29843 | 0.31197 | 0.32261 | 0.32952 | 0.3345 | 0.33159 | 0.33747 | 0.38062 | 0.37084 | 0.33338 | 0.28473 | 0.23586 | 0.18619
2016-01-14 | 0.14788 | 0.12671 | 0.11609 | 0.11083 | 0.11291 | 0.13169 | 0.17731 | 0.20768 | 0.23374 | 0.2718 | 0.30562 | 0.3262 | 0.33698 | 0.33752 | 0.3329 | 0.32061 | 0.31729 | 0.33222 | 0.3733 | 0.3623 | 0.32918 | 0.28446 | 0.23342 | 0.18398
2016-01-15 | 0.14624 | 0.12704 | 0.11683 | 0.11347 | 0.11577 | 0.13695 | 0.18669 | 0.21916 | 0.23127 | 0.24784 | 0.25665 | 0.25729 | 0.25027 | 0.24342 | 0.2359 | 0.23237 | 0.23606 | 0.26298 | 0.30036 | 0.29172 | 0.26918 | 0.23578 | 0.19636 | 0.15706
2016-01-16 | 0.13068 | 0.11761 | 0.11387 | 0.11526 | 0.12359 | 0.15362 | 0.21822 | 0.26601 | 0.27461 | 0.27774 | 0.27765 | 0.2694 | 0.25699 | 0.24417 | 0.23326 | 0.22798 | 0.23338 | 0.26748 | 0.34769 | 0.36433 | 0.36048 | 0.33752 | 0.30206 | 0.26488
2016-01-17 | 0.24008 | 0.23063 | 0.232 | 0.24008 | 0.25857 | 0.30851 | 0.40761 | 0.47419 | 0.46441 | 0.41721 | 0.36814 | 0.32099 | 0.28428 | 0.25622 | 0.23745 | 0.22741 | 0.22922 | 0.25831 | 0.30874 | 0.30493 | 0.29272 | 0.26931 | 0.24351 | 0.214
2016-01-18 | 0.18746 | 0.17621 | 0.17295 | 0.17435 | 0.18208 | 0.20036 | 0.23326 | 0.27889 | 0.31188 | 0.31564 | 0.30391 | 0.28054 | 0.25695 | 0.23664 | 0.21932 | 0.21017 | 0.21029 | 0.23488 | 0.29386 | 0.30488 | 0.30484 | 0.29985 | 0.28684 | 0.26874
2016-01-19 | 0.25614 | 0.25191 | 0.25516 | 0.26497 | 0.28111 | 0.30823 | 0.35271 | 0.41035 | 0.44522 | 0.41791 | 0.36129 | 0.31005 | 0.27193 | 0.24546 | 0.22514 | 0.20941 | 0.20482 | 0.21822 | 0.26792 | 0.26462 | 0.2522 | 0.22794 | 0.20448 | 0.17362
2016-01-20 | 0.15263 | 0.14317 | 0.14105 | 0.14374 | 0.15527 | 0.17947 | 0.22299 | 0.26831 | 0.28581 | 0.27787 | 0.26726 | 0.25725 | 0.24567 | 0.23692 | 0.23035 | 0.22673 | 0.22737 | 0.24297 | 0.28964 | 0.28576 | 0.26096 | 0.22665 | 0.18771 | 0.15002
2016-01-21 | 0.12442 | 0.11195 | 0.107 | 0.10698 | 0.1126 | 0.13673 | 0.19005 | 0.2253 | 0.2333 | 0.23578 | 0.23831 | 0.23823 | 0.23725 | 0.23289 | 0.2291 | 0.22526 | 0.22673 | 0.24721 | 0.29009 | 0.28846 | 0.26497 | 0.22946 | 0.19071 | 0.15477
2016-01-22 | 0.12905 | 0.11998 | 0.11853 | 0.12309 | 0.13714 | 0.17502 | 0.25377 | 0.31042 | 0.30165 | 0.31253 | 0.30484 | 0.28968 | 0.27285 | 0.25389 | 0.24094 | 0.23407 | 0.23877 | 0.27167 | 0.35177 | 0.37551 | 0.37479 | 0.35206 | 0.31796 | 0.27947
2016-01-23 | 0.25754 | 0.25237 | 0.25784 | 0.27023 | 0.29395 | 0.35626 | 0.47552 | 0.53932 | 0.50259 | 0.44421 | 0.392 | 0.33796 | 0.29586 | 0.2629 | 0.24185 | 0.2314 | 0.23225 | 0.25725 | 0.32218 | 0.33479 | 0.32428 | 0.29568 | 0.25347 | 0.21462
2016-01-24 | 0.18826 | 0.17937 | 0.1788 | 0.18366 | 0.19841 | 0.24189 | 0.32865 | 0.37938 | 0.37886 | 0.3621 | 0.34114 | 0.31183 | 0.28689 | 0.26627 | 0.24989 | 0.24066 | 0.24305 | 0.26536 | 0.31862 | 0.31995 | 0.30567 | 0.28232 | 0.25427 | 0.22137
2016-01-25 | 0.19569 | 0.18333 | 0.17848 | 0.17986 | 0.18644 | 0.20217 | 0.23127 | 0.27053 | 0.30996 | 0.30762 | 0.28464 | 0.26054 | 0.24202 | 0.22786 | 0.21724 | 0.20937 | 0.20596 | 0.21614 | 0.25267 | 0.24876 | 0.23212 | 0.21253 | 0.18717 | 0.16017
2016-01-26 | 0.1386 | 0.12522 | 0.11969 | 0.11738 | 0.11914 | 0.12752 | 0.14419 | 0.16879 | 0.2065 | 0.22733 | 0.237 | 0.23598 | 0.23541 | 0.23488 | 0.23176 | 0.22846 | 0.22782 | 0.23946 | 0.27823 | 0.2769 | 0.25279 | 0.22046 | 0.18561 | 0.14869
2016-01-27 | 0.12133 | 0.1064 | 0.10017 | 0.098526 | 0.10411 | 0.1251 | 0.17491 | 0.20623 | 0.21999 | 0.23664 | 0.25627 | 0.26957 | 0.28067 | 0.28995 | 0.29427 | 0.29976 | 0.30224 | 0.30683 | 0.34468 | 0.34021 | 0.30549 | 0.25716 | 0.20833 | 0.16088
2016-01-28 | 0.12575 | 0.1083 | 0.10025 | 0.097134 | 0.10099 | 0.12083 | 0.16689 | 0.19965 | 0.21513 | 0.23688 | 0.26036 | 0.27756 | 0.29399 | 0.308 | 0.31848 | 0.32654 | 0.32932 | 0.33063 | 0.36417 | 0.35812 | 0.32562 | 0.27496 | 0.22669 | 0.17855
2016-01-29 | 0.14111 | 0.12194 | 0.1131 | 0.11002 | 0.11424 | 0.13648 | 0.18553 | 0.22248 | 0.23942 | 0.2635 | 0.28205 | 0.29788 | 0.22874 | 0.29518 | 0.28896 | 0.29145 | 0.30068 | 0.32553 | 0.35817 | 0.34997 | 0.32774 | 0.28797 | 0.24272 | 0.19573
2016-01-30 | 0.16436 | 0.14685 | 0.13845 | 0.13664 | 0.14308 | 0.16944 | 0.23047 | 0.27197 | 0.2939 | 0.31545 | 0.32759 | 0.32601 | 0.31905 | 0.31094 | 0.30201 | 0.29691 | 0.30036 | 0.32128 | 0.35993 | 0.35376 | 0.32625 | 0.28801 | 0.23868 | 0.19243
2016-01-31 | 0.16111 | 0.14422 | 0.13757 | 0.13478 | 0.1391 | 0.16365 | 0.21967 | 0.25712 | 0.27289 | 0.29376 | 0.30944 | 0.31829 | 0.32014 | 0.31777 | 0.31338 | 0.31592 | 0.3123 | 0.3181 | 0.34601 | 0.33508 | 0.30609 | 0.2711 | 0.23306 | 0.19254
2016-02-01 | 0.15829 | 0.13695 | 0.12433 | 0.11793 | 0.11678 | 0.12238 | 0.13782 | 0.16179 | 0.20956 | 0.25998 | 0.29655 | 0.31758 | 0.33353 | 0.3433 | 0.34948 | 0.35167 | 0.34631 | 0.33329 | 0.34849 | 0.33489 | 0.30068 | 0.26428 | 0.22753 | 0.18877
2016-02-02 | 0.15411 | 0.13269 | 0.11984 | 0.11291 | 0.11052 | 0.11274 | 0.12235 | 0.14001 | 0.18997 | 0.24256 | 0.27818 | 0.30192 | 0.33275 | 0.35541 | 0.37182 | 0.37948 | 0.37855 | 0.36382 | 0.36357 | 0.33034 | 0.30054 | 0.28303 | 0.26015 | 0.20837
2016-02-03 | 0.16645 | 0.13518 | 0.12388 | 0.11923 | 0.1222 | 0.14247 | 0.18804 | 0.21896 | 0.24913 | 0.29027 | 0.3345 | 0.36697 | 0.39321 | 0.41418 | 0.42978 | 0.43619 | 0.42533 | 0.41083 | 0.43347 | 0.42227 | 0.37597 | 0.32591 | 0.26857 | 0.21276
2016-02-04 | 0.17027 | 0.14743 | 0.13447 | 0.12839 | 0.12971 | 0.14804 | 0.19446 | 0.22486 | 0.2533 | 0.29723 | 0.33962 | 0.37253 | 0.39929 | 0.41656 | 0.42835 | 0.43519 | 0.42884 | 0.41126 | 0.4343 | 0.42994 | 0.38896 | 0.33528 | 0.28031 | 0.22359
2016-02-05 | 0.18061 | 0.15477 | 0.14168 | 0.135 | 0.13614 | 0.15706 | 0.2073 | 0.23885 | 0.26844 | 0.31588 | 0.36038 | 0.39548 | 0.41829 | 0.43463 | 0.44482 | 0.44013 | 0.42172 | 0.40659 | 0.42736 | 0.41596 | 0.37556 | 0.32405 | 0.2667 | 0.21137
2016-02-06 | 0.16941 | 0.14358 | 0.13093 | 0.12465 | 0.12644 | 0.14499 | 0.19288 | 0.22355 | 0.25334 | 0.28991 | 0.32371 | 0.34953 | 0.3712 | 0.39195 | 0.40078 | 0.40616 | 0.40104 | 0.39458 | 0.41743 | 0.41164 | 0.37217 | 0.32175 | 0.26575 | 0.20887
2016-02-07 | 0.16617 | 0.14247 | 0.12728 | 0.12057 | 0.12159 | 0.14026 | 0.18688 | 0.21877 | 0.24033 | 0.26961 | 0.29888 | 0.3274 | 0.34488 | 0.34779 | 0.37105 | 0.37773 | 0.37582 | 0.37095 | 0.37335 | 0.35396 | 0.32654 | 0.28308 | 0.24538 | 0.20232
2016-02-08 | 0.16652 | 0.14178 | 0.12797 | 0.12127 | 0.12077 | 0.12626 | 0.14209 | 0.1658 | 0.21462 | 0.2711 | 0.31753 | 0.34774 | 0.36865 | 0.37902 | 0.38566 | 0.3815 | 0.37228 | 0.35887 | 0.36727 | 0.35022 | 0.31606 | 0.27947 | 0.24189 | 0.20421
2016-02-09 | 0.16796 | 0.14355 | 0.12968 | 0.12273 | 0.12121 | 0.12587 | 0.1372 | 0.15557 | 0.19214 | 0.2289 | 0.25495 | 0.26896 | 0.28223 | 0.29041 | 0.29404 | 0.29099 | 0.28379 | 0.2816 | 0.30809 | 0.3122 | 0.28232 | 0.24463 | 0.20714 | 0.16433
2016-02-10 | 0.1326 | 0.11617 | 0.10969 | 0.10866 | 0.1139 | 0.13704 | 0.1888 | 0.22263 | 0.23799 | 0.2578 | 0.28063 | 0.296 | 0.31061 | 0.32223 | 0.32711 | 0.33222 | 0.33314 | 0.32947 | 0.35606 | 0.36281 | 0.32778 | 0.28094 | 0.23019 | 0.18072
2016-02-11 | 0.14537 | 0.12525 | 0.11603 | 0.11308 | 0.11692 | 0.13895 | 0.191 | 0.22478 | 0.24297 | 0.26839 | 0.29231 | 0.31517 | 0.33504 | 0.35306 | 0.36417 | 0.37582 | 0.37922 | 0.37258 | 0.39289 | 0.39548 | 0.36281 | 0.30363 | 0.24662 | 0.19188
2016-02-12 | 0.14999 | 0.12896 | 0.11686 | 0.11198 | 0.11455 | 0.13374 | 0.18168 | 0.2111 | 0.23533 | 0.26822 | 0.29861 | 0.32428 | 0.34404 | 0.36059 | 0.36488 | 0.35822 | 0.34933 | 0.35097 | 0.38415 | 0.37577 | 0.34124 | 0.29299 | 0.23164 | 0.17671
2016-02-13 | 0.14143 | 0.12115 | 0.11223 | 0.10885 | 0.11277 | 0.13371 | 0.18398 | 0.21896 | 0.23856 | 0.25149 | 0.26333 | 0.26757 | 0.26992 | 0.26922 | 0.26683 | 0.26311 | 0.25942 | 0.25951 | 0.29054 | 0.30303 | 0.28406 | 0.25275 | 0.21361 | 0.17288
2016-02-14 | 0.14381 | 0.13041 | 0.12605 | 0.12752 | 0.1371 | 0.17024 | 0.24363 | 0.2971 | 0.296 | 0.28227 | 0.2714 | 0.2536 | 0.23983 | 0.23063 | 0.2249 | 0.2247 | 0.22454 | 0.22878 | 0.25827 | 0.26423 | 0.24571 | 0.22164 | 0.19602 | 0.16748
2016-02-15 | 0.14451 | 0.13077 | 0.12377 | 0.12124 | 0.12232 | 0.13099 | 0.14879 | 0.17579 | 0.2076 | 0.2293 | 0.24206 | 0.24338 | 0.23745 | 0.23152 | 0.22633 | 0.22442 | 0.22335 | 0.22621 | 0.24892 | 0.2544 | 0.237 | 0.2149 | 0.19045 | 0.16098
2016-02-16 | 0.13804 | 0.12581 | 0.12424 | 0.12566 | 0.12857 | 0.14162 | 0.16614 | 0.20247 | 0.23439 | 0.24413 | 0.23946 | 0.22878 | 0.22283 | 0.21853 | 0.21657 | 0.21728 | 0.21967 | 0.22418 | 0.25001 | 0.25934 | 0.23889 | 0.21268 | 0.18655 | 0.15428
2016-02-17 | 0.1308 | 0.11891 | 0.11512 | 0.11632 | 0.12391 | 0.14595 | 0.18626 | 0.22713 | 0.25153 | 0.26118 | 0.26557 | 0.26661 | 0.26822 | 0.27119 | 0.2743 | 0.27885 | 0.28125 | 0.28259 | 0.3053 | 0.313 | 0.28263 | 0.2426 | 0.19725 | 0.15703
2016-02-18 | 0.1259 | 0.10946 | 0.10398 | 0.10257 | 0.10822 | 0.13077 | 0.18294 | 0.21971 | 0.2346 | 0.24959 | 0.26398 | 0.27606 | 0.2868 | 0.29843 | 0.30949 | 0.32018 | 0.32405 | 0.31819 | 0.33392 | 0.34168 | 0.30814 | 0.25994 | 0.21334 | 0.16474
2016-02-19 | 0.13087 | 0.1124 | 0.10452 | 0.10139 | 0.10514 | 0.12534 | 0.17351 | 0.20455 | 0.2241 | 0.24746 | 0.27219 | 0.29422 | 0.31206 | 0.32971 | 0.347 | 0.36387 | 0.36804 | 0.35787 | 0.36722 | 0.37146 | 0.33718 | 0.28788 | 0.23562 | 0.18405
2016-02-20 | 0.14473 | 0.12412 | 0.11333 | 0.10777 | 0.10932 | 0.1289 | 0.17579 | 0.20795 | 0.23672 | 0.27268 | 0.30879 | 0.3346 | 0.35917 | 0.37891 | 0.3931 | 0.40557 | 0.40729 | 0.39542 | 0.40911 | 0.41618 | 0.38223 | 0.33489 | 0.27823 | 0.22502
2016-02-21 | 0.1809 | 0.15253 | 0.1386 | 0.1319 | 0.1323 | 0.15038 | 0.19886 | 0.2331 | 0.27796 | 0.32918 | 0.37587 | 0.41191 | 0.43757 | 0.45457 | 0.45666 | 0.45185 | 0.42412 | 0.40189 | 0.41153 | 0.39929 | 0.36144 | 0.31512 | 0.27276 | 0.2245
2016-02-22 | 0.18265 | 0.1528 | 0.13773 | 0.12848 | 0.12611 | 0.12914 | 0.14314 | 0.16875 | 0.22926 | 0.29199 | 0.34153 | 0.3801 | 0.41159 | 0.42923 | 0.43619 | 0.4393 | 0.42802 | 0.39955 | 0.39484 | 0.38384 | 0.34256 | 0.30095 | 0.25874 | 0.2135
2016-02-23 | 0.17418 | 0.14807 | 0.13242 | 0.12368 | 0.11981 | 0.12121 | 0.1299 | 0.15096 | 0.20615 | 0.26857 | 0.32247 | 0.36615 | 0.41992 | 0.4289 | 0.43663 | 0.44365 | 0.43702 | 0.41889 | 0.41867 | 0.42003 | 0.38109 | 0.32137 | 0.27014 | 0.2135
2016-02-24 | 0.16796 | 0.14569 | 0.13193 | 0.12433 | 0.12525 | 0.14378 | 0.18488 | 0.21861 | 0.25402 | 0.30031 | 0.34616 | 0.38042 | 0.41542 | 0.44019 | 0.45576 | 0.46791 | 0.45706 | 0.44019 | 0.45638 | 0.45968 | 0.40729 | 0.34522 | 0.27956 | 0.21865
2016-02-25 | 0.17163 | 0.14537 | 0.13062 | 0.12282 | 0.12341 | 0.14203 | 0.18837 | 0.21736 | 0.24947 | 0.28869 | 0.32615 | 0.35902 | 0.39168 | 0.42129 | 0.4451 | 0.45928 | 0.45508 | 0.43066 | 0.43552 | 0.43569 | 0.38995 | 0.32904 | 0.26944 | 0.20883
2016-02-26 | 0.16341 | 0.1376 | 0.12279 | 0.11617 | 0.11666 | 0.13245 | 0.17562 | 0.20619 | 0.23334 | 0.26549 | 0.31108 | 0.34335 | 0.37346 | 0.39469 | 0.40852 | 0.41137 | 0.39902 | 0.39058 | 0.41277 | 0.41207 | 0.37443 | 0.32452 | 0.26766 | 0.21323
2016-02-27 | 0.1709 | 0.14849 | 0.13714 | 0.13196 | 0.13358 | 0.15211 | 0.20006 | 0.22906 | 0.24721 | 0.27066 | 0.29742 | 0.29167 | 0.31919 | 0.32304 | 0.32161 | 0.3181 | 0.31052 | 0.32295 | 0.34651 | 0.35077 | 0.3219 | 0.27492 | 0.22438 | 0.1788
2016-02-28 | 0.14409 | 0.12587 | 0.11784 | 0.11537 | 0.11903 | 0.14074 | 0.19269 | 0.22598 | 0.23692 | 0.24376 | 0.24922 | 0.2509 | 0.25123 | 0.25398 | 0.25699 | 0.26122 | 0.26389 | 0.26041 | 0.27268 | 0.28009 | 0.25656 | 0.22717 | 0.19454 | 0.16044
2016-02-29 | 0.14409 | 0.12587 | 0.11784 | 0.11537 | 0.11903 | 0.14074 | 0.19269 | 0.22598 | 0.23692 | 0.24376 | 0.24922 | 0.2509 | 0.25123 | 0.25398 | 0.25699 | 0.26122 | 0.26389 | 0.26041 | 0.27268 | 0.28009 | 0.25656 | 0.22717 | 0.19454 | 0.16044
2016-03-01 | 0.13269 | 0.11655 | 0.10816 | 0.1046 | 0.10599 | 0.11472 | 0.13251 | 0.15853 | 0.19446 | 0.22007 | 0.237 | 0.246 | 0.25474 | 0.2635 | 0.27009 | 0.27867 | 0.27974 | 0.2725 | 0.27311 | 0.28326 | 0.25618 | 0.22741 | 0.19647 | 0.16199
2016-03-02 | 0.13429 | 0.1181 | 0.10938 | 0.10185 | 0.10075 | 0.10493 | 0.11549 | 0.13503 | 0.17734 | 0.21685 | 0.24367 | 0.26402 | 0.28014 | 0.29636 | 0.30795 | 0.31829 | 0.32166 | 0.31371 | 0.31691 | 0.32855 | 0.29591 | 0.25444 | 0.21075 | 0.16731
2016-03-03 | 0.1382 | 0.1162 | 0.10501 | 0.10097 | 0.10327 | 0.12165 | 0.16351 | 0.19302 | 0.22157 | 0.25554 | 0.28919 | 0.31507 | 0.34148 | 0.36804 | 0.3854 | 0.40131 | 0.40611 | 0.39416 | 0.394 | 0.40147 | 0.35641 | 0.29907 | 0.24181 | 0.18517
2016-03-04 | 0.14476 | 0.12153 | 0.10969 | 0.10392 | 0.10517 | 0.12218 | 0.16426 | 0.19495 | 0.222 | 0.25559 | 0.28774 | 0.31536 | 0.34133 | 0.36625 | 0.38812 | 0.40472 | 0.40879 | 0.39622 | 0.39749 | 0.40232 | 0.36281 | 0.31169 | 0.25389 | 0.19848
2016-03-05 | 0.15593 | 0.13377 | 0.12168 | 0.11683 | 0.11879 | 0.13695 | 0.18441 | 0.21657 | 0.24326 | 0.28308 | 0.31976 | 0.35291 | 0.38171 | 0.40083 | 0.40858 | 0.4111 | 0.40115 | 0.38833 | 0.39717 | 0.40163 | 0.36732 | 0.31734 | 0.26144 | 0.20528
2016-03-06 | 0.16345 | 0.14115 | 0.128 | 0.12265 | 0.1235 | 0.14124 | 0.18633 | 0.21838 | 0.25597 | 0.29728 | 0.32966 | 0.35762 | 0.3768 | 0.37284 | 0.36392 | 0.31258 | 0.28891 | 0.29276 | 0.3198 | 0.32543 | 0.29976 | 0.26084 | 0.21881 | 0.1754
2016-03-07 | 0.14159 | 0.12244 | 0.11486 | 0.11144 | 0.11461 | 0.13386 | 0.17993 | 0.21145 | 0.24198 | 0.26861 | 0.2914 | 0.30197 | 0.30753 | 0.30804 | 0.30758 | 0.308 | 0.30396 | 0.29322 | 0.29865 | 0.30257 | 0.28022 | 0.24359 | 0.20741 | 0.16511
2016-03-08 | 0.1392 | 0.12135 | 0.11353 | 0.11072 | 0.11285 | 0.12022 | 0.13985 | 0.16968 | 0.20368 | 0.22446 | 0.23059 | 0.23011 | 0.2291 | 0.2287 | 0.2318 | 0.23643 | 0.23893 | 0.23664 | 0.24367 | 0.25635 | 0.23472 | 0.20987 | 0.18118 | 0.15434
2016-03-09 | 0.12653 | 0 | 0.11203 | 0.10455 | 0.10196 | 0.10534 | 0.11515 | 0.13011 | 0.15352 | 0.18492 | 0.21257 | 0.2253 | 0.24309 | 0.25322 | 0.26075 | 0.27189 | 0.28361 | 0.28932 | 0.2808 | 0.28326 | 0.29682 | 0.26367 | 0.22335 | 0.17152
2016-03-10 | 0.13371 | 0.11119 | 0.10102 | 0.097947 | 0.10155 | 0.11859 | 0.16014 | 0.19472 | 0.20569 | 0.22806 | 0.25644 | 0.27426 | 0.29504 | 0.30926 | 0.33106 | 0.35286 | 0.37135 | 0.37263 | 0.35726 | 0.35321 | 0.35933 | 0.3087 | 0.25682 | 0.19834
2016-03-11 | 0.1508 | 0.12456 | 0.11111 | 0.10471 | 0.10468 | 0.1213 | 0.16284 | 0.19625 | 0.20577 | 0.23212 | 0.25686 | 0.28094 | 0.30271 | 0.32338 | 0.3434 | 0.36651 | 0.38655 | 0.39253 | 0.37871 | 0.37192 | 0.37881 | 0.33368 | 0.27699 | 0.21122
2016-03-12 | 0.1659 | 0.13798 | 0.1245 | 0.11877 | 0.12004 | 0.13795 | 0.18405 | 0.18204 | 0.22761 | 0.26101 | 0.30474 | 0.34212 | 0.37253 | 0.39389 | 0.40563 | 0.42873 | 0.44292 | 0.4363 | 0.41304 | 0.40355 | 0.40761 | 0.35928 | 0.30257 | 0.23963
2016-03-13 | 0.18786 | 0.15673 | 0.13951 | 0.13074 | 0.12851 | 0.14228 | 0.1819 | 0.20925 | 0.21759 | 0.24313 | 0.26307 | 0.27509 | 0.28187 | 0.28617 | 0.28914 | 0.29226 | 0.29838 | 0.29691 | 0.28031 | 0.27832 | 0.28946 | 0.25542 | 0.21307 | 0.16707
2016-03-14 | 0.13273 | 0.11506 | 0.10577 | 0.10352 | 0.10808 | 0.12875 | 0.18147 | 0.22478 | 0.23509 | 0.24442 | 0.25165 | 0.25343 | 0.25267 | 0.25457 | 0.25703 | 0.26157 | 0.26813 | 0.26774 | 0.25763 | 0.25678 | 0.26614 | 0.24033 | 0.20661 | 0.17093
2016-03-15 | 0.13543 | 0.11617 | 0.10514 | 0.10035 | 0.10126 | 0.10786 | 0.12232 | 0.14859 | 0.18115 | 0.21373 | 0.24033 | 0.25622 | 0.26796 | 0.27796 | 0.28991 | 0.30243 | 0.31625 | 0.31867 | 0.30326 | 0.28869 | 0.29199 | 0.26114 | 0.22794 | 0.18496
2016-03-16 | 0.15057 | 0.12875 | 0.11566 | 0.10863 | 0.10585 | 0.10764 | 0.11692 | 0.13218 | 0.16559 | 0.21435 | 0.25237 | 0.28209 | 0.30679 | 0.32634 | 0.34586 | 0.35953 | 0.36595 | 0.36372 | 0.34596 | 0.33933 | 0.35117 | 0.31479 | 0.27171 | 0.21634
2016-03-17 | 0.17288 | 0.14682 | 0.13312 | 0.12833 | 0.13093 | 0.15044 | 0.19487 | 0.2318 | 0.25296 | 0.29733 | 0.34943 | 0.38739 | 0.41591 | 0.43077 | 0.43863 | 0.44421 | 0.44589 | 0.43358 | 0.41976 | 0.42796 | 0.42736 | 0.38254 | 0.33261 | 0.26961
2016-03-18 | 0.2192 | 0.18899 | 0.17446 | 0.16765 | 0.16659 | 0.18201 | 0.22426 | 0.25123 | 0.24654 | 0.26187 | 0.27725 | 0.28581 | 0.29322 | 0.30363 | 0.31748 | 0.33251 | 0.34868 | 0.35376 | 0.33982 | 0.333 | 0.34124 | 0.30026 | 0.2483 | 0.19078
2016-03-19 | 0.14643 | 0.1227 | 0.11086 | 0.10577 | 0.10711 | 0.12424 | 0.16635 | 0.19822 | 0.21214 | 0.24066 | 0.27049 | 0.29354 | 0.30926 | 0.32894 | 0.34888 | 0.3686 | 0.38119 | 0.38197 | 0.3617 | 0.34824 | 0.35757 | 0.31673 | 0.2657 | 0.20737
2016-03-20 | 0.16324 | 0.13692 | 0.12391 | 0.11683 | 0.11727 | 0.13352 | 0.17544 | 0.20868 | 0.22394 | 0.25203 | 0.28312 | 0.30748 | 0.32721 | 0.34839 | 0.36814 | 0.38421 | 0.3949 | 0.39111 | 0.37279 | 0.35807 | 0.3658 | 0.31824 | 0.26406 | 0.20756
2016-03-21 | 0.1596 | 0.13196 | 0.1162 | 0.10794 | 0.10775 | 0.12054 | 0.15359 | 0.18582 | 0.20756 | 0.24227 | 0.27991 | 0.31131 | 0.33742 | 0.36443 | 0.391 | 0.41326 | 0.4221 | 0.41342 | 0.38317 | 0.36149 | 0.36326 | 0.32209 | 0.28005 | 0.23176
2016-03-22 | 0.18731 | 0.1601 | 0.14266 | 0.13269 | 0.12878 | 0.13294 | 0.14614 | 0.16423 | 0.1971 | 0.25368 | 0.30036 | 0.32654 | 0.35027 | 0.3688 | 0.38176 | 0.39606 | 0.41477 | 0.41439 | 0.39063 | 0.36276 | 0.35958 | 0.31767 | 0.27066 | 0.21893
2016-03-23 | 0.1753 | 0.14544 | 0.12878 | 0.11949 | 0.11518 | 0.11701 | 0.12548 | 0.1391 | 0.17156 | 0.2257 | 0.27845 | 0.32171 | 0.36559 | 0.40579 | 0.43419 | 0.45859 | 0.46935 | 0.46814 | 0.4469 | 0.42167 | 0.42571 | 0.37284 | 0.31569 | 0.25073
2016-03-24 | 0.19923 | 0.16593 | 0.14534 | 0.13714 | 0.13608 | 0.15002 | 0.18229 | 0.21284 | 0.2357 | 0.26988 | 0.29829 | 0.31871 | 0.32673 | 0.32582 | 0.31734 | 0.31183 | 0.31239 | 0.31578 | 0.31522 | 0.31862 | 0.31361 | 0.27558 | 0.23468 | 0.18626
2016-03-25 | 0.14963 | 0.1251 | 0.11072 | 0.10566 | 0.10711 | 0.12074 | 0.1554 | 0.18593 | 0.20558 | 0.23627 | 0.25899 | 0.28268 | 0.30188 | 0.31555 | 0.32846 | 0.33889 | 0.34799 | 0.34873 | 0.33489 | 0.31862 | 0.32457 | 0.28227 | 0.22974 | 0.17562
2016-03-26 | 0.13374 | 0.11203 | 0.10065 | 0.096847 | 0.099822 | 0.11617 | 0.15626 | 0.19484 | 0.21893 | 0.23172 | 0.2421 | 0.24218 | 0.23721 | 0.23119 | 0.22733 | 0.22518 | 0.22906 | 0.23176 | 0.23039 | 0.24359 | 0.26372 | 0.23831 | 0.20085 | 0.16341
2016-03-27 | 0.13276 | 0.11609 | 0.10791 | 0.10604 | 0.10971 | 0.12653 | 0.16593 | 0.19692 | 0.21323 | 0.23721 | 0.24943 | 0.25554 | 0.2584 | 0.26075 | 0.26045 | 0.25989 | 0.26084 | 0.26019 | 0.25695 | 0.26866 | 0.27969 | 0.25262 | 0.2156 | 0.17449
2016-03-28 | 0.14089 | 0.12016 | 0.10996 | 0.10471 | 0.10678 | 0.12106 | 0.15448 | 0.18514 | 0.20871 | 0.24289 | 0.27951 | 0.30229 | 0.31848 | 0.32812 | 0.33606 | 0.34104 | 0.34016 | 0.32966 | 0.31451 | 0.31465 | 0.3209 | 0.29322 | 0.25942 | 0.21747
2016-03-29 | 0.18036 | 0.15663 | 0.14206 | 0.13478 | 0.13328 | 0.13835 | 0.15221 | 0.17351 | 0.20779 | 0.25934 | 0.30786 | 0.3435 | 0.35968 | 0.36844 | 0.36661 | 0.35777 | 0.34631 | 0.3345 | 0.31639 | 0.31131 | 0.29884 | 0.26212 | 0.22978 | 0.19111
2016-03-30 | 0.1557 | 0.13276 | 0.11773 | 0.1106 | 0.10805 | 0.11072 | 0.12168 | 0.13602 | 0.16433 | 0.20497 | 0.23562 | 0.25178 | 0.25929 | 0.26501 | 0.27049 | 0.27514 | 0.27987 | 0.2788 | 0.26761 | 0.25985 | 0.27443 | 0.24148 | 0.20059 | 0.15537
2016-03-31 | 0.12162 | 0.10523 | 0.095285 | 0.092175 | 0.095778 | 0.11735 | 0.16145 | 0.19299 | 0.20425 | 0.22038 | 0.23766 | 0.25191 | 0.26234 | 0.275 | 0.28639 | 0.29604 | 0.30063 | 0.29568 | 0.29 | 0.297 | 0.31 | 0.27101 | 0.22382 | 0.17215
2016-04-01 | 0.13352 | 0.11291 | 0.10306 | 0.09916 | 0.10182 | 0.1201 | 0.16892 | 0.20262 | 0.2154 | 0.23338 | 0.25149 | 0.26761 | 0.28089 | 0.29852 | 0.32042 | 0.34591 | 0.36992 | 0.37871 | 0.36539 | 0.34227 | 0.34764 | 0.30349 | 0.24359 | 0.18557
2016-04-02 | 0.14266 | 0.11897 | 0.10698 | 0.10105 | 0.10257 | 0.12097 | 0.16559 | 0.19354 | 0.20718 | 0.23387 | 0.2575 | 0.27982 | 0.29554 | 0.31545 | 0.34685 | 0.37618 | 0.39897 | 0.40868 | 0.39048 | 0.36631 | 0.3712 | 0.32534 | 0.26251 | 0.20164
2016-04-03 | 0.15494 | 0.12854 | 0.11466 | 0.10916 | 0.11035 | 0.12956 | 0.17145 | 0.19912 | 0.21877 | 0.25001 | 0.28129 | 0.30851 | 0.33392 | 0.35907 | 0.39495 | 0.41943 | 0.43707 | 0.43 | 0.41051 | 0.3828 | 0.39717 | 0.34804 | 0.28183 | 0.21751
2016-04-04 | 0.16782 | 0.14014 | 0.12424 | 0.11678 | 0.11595 | 0.13288 | 0.17862 | 0.20543 | 0.22733 | 0.26415 | 0.30192 | 0.3347 | 0.36094 | 0.3888 | 0.4165 | 0.44136 | 0.4619 | 0.45996 | 0.43497 | 0.3931 | 0.38447 | 0.34227 | 0.29041 | 0.23492
2016-04-05 | 0.18677 | 0.15563 | 0.13689 | 0.12584 | 0.1215 | 0.12303 | 0.13593 | 0.15306 | 0.19777 | 0.25559 | 0.30474 | 0.347 | 0.38332 | 0.42194 | 0.44949 | 0.47033 | 0.47831 | 0.47309 | 0.43869 | 0.39511 | 0.39042 | 0.34601 | 0.29609 | 0.24313
2016-04-06 | 0.19365 | 0.16078 | 0.13895 | 0.12662 | 0.12165 | 0.12238 | 0.13099 | 0.14355 | 0.18921 | 0.25014 | 0.30446 | 0.34665 | 0.38718 | 0.42434 | 0.4599 | 0.48331 | 0.49488 | 0.49406 | 0.46625 | 0.42983 | 0.4311 | 0.377 | 0.31451 | 0.24425
2016-04-07 | 0.19584 | 0.16532 | 0.14963 | 0.14228 | 0.14429 | 0.16518 | 0.21303 | 0.24284 | 0.27092 | 0.32668 | 0.38671 | 0.4427 | 0.49158 | 0.53698 | 0.57402 | 0.60275 | 0.62068 | 0.61349 | 0.57855 | 0.54873 | 0.53993 | 0.47073 | 0.39142 | 0.31658
2016-04-08 | 0.25925 | 0.21983 | 0.19288 | 0.17944 | 0.17965 | 0.19912 | 0.25296 | 0.28406 | 0.31085 | 0.35057 | 0.39955 | 0.44248 | 0.4686 | 0.4825 | 0.4797 | 0.46504 | 0.47292 | 0.44175 | 0.38483 | 0.35862 | 0.3621 | 0.31498 | 0.25453 | 0.19692
2016-04-09 | 0.15736 | 0.13334 | 0.1203 | 0.11398 | 0.11356 | 0.12971 | 0.1725 | 0.19472 | 0.20657 | 0.23144 | 0.2517 | 0.26281 | 0.26953 | 0.27518 | 0.28446 | 0.296 | 0.3072 | 0.31446 | 0.30665 | 0.29577 | 0.31244 | 0.27611 | 0.2222 | 0.17149
2016-04-10 | 0.13417 | 0.11429 | 0.10346 | 0.099584 | 0.10145 | 0.11885 | 0.16284 | 0.1888 | 0.20175 | 0.22406 | 0.24563 | 0.26182 | 0.27307 | 0.28626 | 0.30086 | 0.3171 | 0.32855 | 0.32827 | 0.31701 | 0.30921 | 0.32567 | 0.28608 | 0.23484 | 0.18158
2016-04-11 | 0.14295 | 0.11943 | 0.108 | 0.1033 | 0.10485 | 0.1208 | 0.16355 | 0.19034 | 0.20998 | 0.2438 | 0.27628 | 0.29953 | 0.31611 | 0.33305 | 0.34883 | 0.35471 | 0.35656 | 0.34754 | 0.33116 | 0.31881 | 0.32735 | 0.29783 | 0.25904 | 0.2135
2016-04-12 | 0.17292 | 0.14678 | 0.1295 | 0.12007 | 0.1162 | 0.11917 | 0.13309 | 0.15145 | 0.19617 | 0.25149 | 0.2981 | 0.33654 | 0.36367 | 0.38864 | 0.40397 | 0.41819 | 0.42352 | 0.41759 | 0.38666 | 0.35226 | 0.35201 | 0.31943 | 0.27158 | 0.22629
2016-04-13 | 0.18557 | 0.15653 | 0.13954 | 0.12863 | 0.12418 | 0.12581 | 0.13521 | 0.14911 | 0.18866 | 0.24251 | 0.28738 | 0.32161 | 0.35296 | 0.37443 | 0.38358 | 0.391 | 0.39295 | 0.38927 | 0.37187 | 0.36671 | 0.38244 | 0.34399 | 0.29245 | 0.2335
2016-04-14 | 0.18717 | 0.15967 | 0.14531 | 0.13738 | 0.1381 | 0.15593 | 0.20266 | 0.23184 | 0.2654 | 0.32052 | 0.37567 | 0.4267 | 0.46992 | 0.51415 | 0.55054 | 0.58226 | 0.59917 | 0.59359 | 0.55841 | 0.51553 | 0.5097 | 0.4483 | 0.36957 | 0.28941
2016-04-15 | 0.2285 | 0.19306 | 0.1725 | 0.15896 | 0.15643 | 0.17316 | 0.22149 | 0.24934 | 0.2914 | 0.35561 | 0.41374 | 0.47027 | 0.51337 | 0.54519 | 0.55798 | 0.56793 | 0.56068 | 0.51765 | 0.49624 | 0.46722 | 0.46935 | 0.4158 | 0.3405 | 0.26683
2016-04-16 | 0.21245 | 0.17883 | 0.15916 | 0.14943 | 0.14743 | 0.1629 | 0.20611 | 0.22922 | 0.2465 | 0.2743 | 0.29865 | 0.31592 | 0.33436 | 0.35621 | 0.37243 | 0.38478 | 0.39237 | 0.38959 | 0.37664 | 0.37361 | 0.38781 | 0.35581 | 0.29865 | 0.23594
2016-04-17 | 0.19082 | 0.16382 | 0.14898 | 0.14149 | 0.14254 | 0.16101 | 0.20722 | 0.23611 | 0.26298 | 0.30572 | 0.34581 | 0.37289 | 0.38213 | 0.38932 | 0.39205 | 0.38791 | 0.38166 | 0.36875 | 0.35691 | 0.34983 | 0.35872 | 0.33232 | 0.28743 | 0.23435
2016-04-18 | 0.19104 | 0.16324 | 0.14637 | 0.13748 | 0.13611 | 0.15025 | 0.18136 | 0.20971 | 0.25031 | 0.30581 | 0.35491 | 0.38948 | 0.41159 | 0.43624 | 0.44847 | 0.44628 | 0.44141 | 0.43569 | 0.41191 | 0.38462 | 0.38608 | 0.35461 | 0.31188 | 0.26501
2016-04-19 | 0.21826 | 0.18968 | 0.1709 | 0.15916 | 0.15527 | 0.1589 | 0.16597 | 0.17696 | 0.21044 | 0.27215 | 0.32817 | 0.36957 | 0.40467 | 0.43132 | 0.44623 | 0.45644 | 0.45479 | 0.43436 | 0.3959 | 0.35117 | 0.3435 | 0.30562 | 0.26367 | 0.21017
2016-04-20 | 0.16689 | 0.13779 | 0.11955 | 0.11055 | 0.10687 | 0.1088 | 0.11784 | 0.12899 | 0.16318 | 0.20285 | 0.22665 | 0.24708 | 0.26126 | 0.27171 | 0.27885 | 0.28451 | 0.28819 | 0.28433 | 0.2747 | 0.26927 | 0.28851 | 0.26705 | 0.22645 | 0.17798
2016-04-21 | 0.14014 | 0.11778 | 0.10665 | 0.10142 | 0.10303 | 0.11966 | 0.1588 | 0.18204 | 0.20232 | 0.22978 | 0.25699 | 0.27867 | 0.30146 | 0.32047 | 0.34266 | 0.36074 | 0.37561 | 0.37428 | 0.36286 | 0.3473 | 0.35922 | 0.31786 | 0.26041 | 0.20429
2016-04-22 | 0.15789 | 0.1302 | 0.11773 | 0.11038 | 0.11052 | 0.12923 | 0.1718 | 0.19221 | 0.2142 | 0.24276 | 0.2743 | 0.30734 | 0.33338 | 0.35531 | 0.37866 | 0.40788 | 0.42868 | 0.43264 | 0.41661 | 0.39279 | 0.40344 | 0.35721 | 0.28901 | 0.2218
2016-04-23 | 0.17299 | 0.14512 | 0.12881 | 0.1194 | 0.11793 | 0.13368 | 0.17334 | 0.15044 | 0.22275 | 0.25618 | 0.29023 | 0.31682 | 0.34997 | 0.39195 | 0.43902 | 0.47599 | 0.50355 | 0.5106 | 0.48899 | 0.44892 | 0.44482 | 0.40301 | 0.33159 | 0.24633
2016-04-24 | 0.19502 | 0.16392 | 0.13742 | 0.12677 | 0.1271 | 0.13695 | 0.17593 | 0.20119 | 0.23087 | 0.2765 | 0.3261 | 0.37074 | 0.41391 | 0.45417 | 0.48935 | 0.52492 | 0.54606 | 0.54327 | 0.5124 | 0.46585 | 0.46207 | 0.41089 | 0.33538 | 0.2629
2016-04-25 | 0.20554 | 0.16844 | 0.14701 | 0.13525 | 0.13257 | 0.14762 | 0.1876 | 0.21226 | 0.24504 | 0.29358 | 0.34963 | 0.40237 | 0.45118 | 0.49843 | 0.54098 | 0.57823 | 0.5991 | 0.5934 | 0.55022 | 0.48976 | 0.47356 | 0.4227 | 0.35511 | 0.28743
2016-04-26 | 0.22633 | 0.18514 | 0.16037 | 0.14524 | 0.13689 | 0.13745 | 0.14682 | 0.16604 | 0.21893 | 0.28576 | 0.35356 | 0.41721 | 0.4705 | 0.51282 | 0.53907 | 0.56294 | 0.57542 | 0.56799 | 0.52711 | 0.46739 | 0.45129 | 0.40547 | 0.3472 | 0.28806
2016-04-27 | 0.23562 | 0.198 | 0.17184 | 0.15703 | 0.14785 | 0.14627 | 0.15145 | 0.16655 | 0.22526 | 0.3022 | 0.37459 | 0.43841 | 0.49117 | 0.53599 | 0.56679 | 0.59372 | 0.60457 | 0.59728 | 0.55973 | 0.5082 | 0.50093 | 0.44819 | 0.371 | 0.30045
2016-04-28 | 0.24471 | 0.20971 | 0.18877 | 0.17621 | 0.17516 | 0.19509 | 0.24082 | 0.26983 | 0.31085 | 0.37207 | 0.44707 | 0.51469 | 0.5685 | 0.61638 | 0.65739 | 0.68971 | 0.69839 | 0.69495 | 0.65678 | 0.60092 | 0.58534 | 0.51596 | 0.42341 | 0.33923
2016-04-29 | 0.27717 | 0.23704 | 0.21253 | 0.19893 | 0.19669 | 0.21536 | 0.26032 | 0.28982 | 0.3405 | 0.40938 | 0.48337 | 0.55016 | 0.60177 | 0.64479 | 0.67549 | 0.69768 | 0.69306 | 0.67701 | 0.64567 | 0.59579 | 0.57727 | 0.51216 | 0.42292 | 0.33889
2016-04-30 | 0.27522 | 0.23856 | 0.21603 | 0.20391 | 0.20315 | 0.22184 | 0.26853 | 0.2982 | 0.34769 | 0.41715 | 0.4907 | 0.55259 | 0.60053 | 0.64358 | 0.67053 | 0.68936 | 0.67957 | 0.62704 | 0.5892 | 0.54973 | 0.54705 | 0.49005 | 0.40654 | 0.32769
2016-05-01 | 0.26562 | 0.22838 | 0.20501 | 0.19299 | 0.18964 | 0.20956 | 0.25784 | 0.28842 | 0.33261 | 0.40131 | 0.47761 | 0.53907 | 0.59017 | 0.63538 | 0.6649 | 0.67991 | 0.67239 | 0.63311 | 0.57517 | 0.53213 | 0.52821 | 0.46745 | 0.3909 | 0.31696
2016-05-02 | 0.25994 | 0.22327 | 0.20111 | 0.18811 | 0.18478 | 0.20338 | 0.2493 | 0.28022 | 0.31905 | 0.37948 | 0.43491 | 0.47877 | 0.5051 | 0.5363 | 0.55923 | 0.57142 | 0.56382 | 0.54117 | 0.50719 | 0.4627 | 0.46184 | 0.40189 | 0.34557 | 0.28946
2016-05-03 | 0.23881 | 0.20345 | 0.18129 | 0.16844 | 0.16206 | 0.16556 | 0.17777 | 0.1977 | 0.23975 | 0.29655 | 0.34675 | 0.38306 | 0.4003 | 0.40868 | 0.40397 | 0.38275 | 0.33586 | 0.31848 | 0.30285 | 0.29861 | 0.30916 | 0.28986 | 0.25861 | 0.22153
2016-05-04 | 0.18633 | 0.16074 | 0.14576 | 0.13602 | 0.13303 | 0.13309 | 0.1367 | 0.14115 | 0.17579 | 0.21944 | 0.25678 | 0.28514 | 0.31536 | 0.34242 | 0.36666 | 0.39463 | 0.41705 | 0.42862 | 0.41862 | 0.38369 | 0.37217 | 0.32952 | 0.27792 | 0.21311
2016-05-05 | 0.16775 | 0.13596 | 0.1245 | 0.11658 | 0.11681 | 0.13355 | 0.16972 | 0.19413 | 0.22482 | 0.26826 | 0.31654 | 0.35978 | 0.40307 | 0.44477 | 0.48483 | 0.5197 | 0.55116 | 0.55566 | 0.53023 | 0.45134 | 0.45349 | 0.39807 | 0.30248 | 0.24604
2016-05-06 | 0.1906 | 0.15933 | 0.13989 | 0.12893 | 0.12641 | 0.14133 | 0.17901 | 0.20414 | 0.23643 | 0.28527 | 0.33825 | 0.39368 | 0.44932 | 0.49364 | 0.53741 | 0.57657 | 0.60216 | 0.60047 | 0.56888 | 0.48858 | 0.49814 | 0.44153 | 0.3618 | 0.28089
2016-05-07 | 0.22382 | 0.18844 | 0.16927 | 0.15709 | 0.15451 | 0.17013 | 0.21068 | 0.23745 | 0.27832 | 0.3315 | 0.39437 | 0.45005 | 0.5023 | 0.55234 | 0.59943 | 0.62333 | 0.64122 | 0.63619 | 0.59728 | 0.54271 | 0.52986 | 0.47935 | 0.39426 | 0.31465
2016-05-08 | 0.25115 | 0.21478 | 0.1931 | 0.17802 | 0.17456 | 0.19001 | 0.23136 | 0.2572 | 0.30211 | 0.35968 | 0.42221 | 0.47691 | 0.52559 | 0.57339 | 0.61158 | 0.64627 | 0.66771 | 0.66176 | 0.62771 | 0.56799 | 0.54587 | 0.48941 | 0.409 | 0.33159
2016-05-09 | 0.25985 | 0.21908 | 0.19755 | 0.18183 | 0.17805 | 0.19424 | 0.23582 | 0.26247 | 0.30535 | 0.36377 | 0.42451 | 0.47715 | 0.52468 | 0.56875 | 0.60968 | 0.64075 | 0.65657 | 0.64088 | 0.5932 | 0.52907 | 0.50325 | 0.45293 | 0.39126 | 0.32802
2016-05-10 | 0.27031 | 0.23261 | 0.20883 | 0.19258 | 0.18499 | 0.18691 | 0.19487 | 0.21642 | 0.27947 | 0.35191 | 0.40976 | 0.45661 | 0.50647 | 0.54024 | 0.56263 | 0.57938 | 0.57842 | 0.5661 | 0.53164 | 0.47315 | 0.47866 | 0.43685 | 0.38462 | 0.32572
2016-05-11 | 0.2718 | 0.23525 | 0.20998 | 0.19446 | 0.18709 | 0.18521 | 0.18815 | 0.20119 | 0.24985 | 0.31555 | 0.37269 | 0.41971 | 0.4631 | 0.50134 | 0.53035 | 0.545 | 0.55054 | 0.53538 | 0.50438 | 0.46116 | 0.46196 | 0.43347 | 0.37238 | 0.30141
2016-05-12 | 0.24206 | 0.2068 | 0.18626 | 0.1759 | 0.17502 | 0.19324 | 0.23558 | 0.26238 | 0.30192 | 0.36281 | 0.42934 | 0.48624 | 0.53513 | 0.57485 | 0.60464 | 0.63117 | 0.64115 | 0.63284 | 0.60523 | 0.56464 | 0.55359 | 0.49235 | 0.40852 | 0.3313
2016-05-13 | 0.26996 | 0.23399 | 0.21002 | 0.19595 | 0.19295 | 0.21106 | 0.25427 | 0.28071 | 0.31947 | 0.38099 | 0.4432 | 0.49311 | 0.54049 | 0.57281 | 0.59722 | 0.61783 | 0.62857 | 0.61665 | 0.58232 | 0.5371 | 0.53023 | 0.4832 | 0.40456 | 0.32491
2016-05-14 | 0.26944 | 0.2337 | 0.20856 | 0.19458 | 0.19195 | 0.19923 | 0.25797 | 0.27929 | 0.32223 | 0.39027 | 0.45321 | 0.51541 | 0.56187 | 0.59217 | 0.61395 | 0.61329 | 0.60693 | 0.59327 | 0.55691 | 0.51523 | 0.51819 | 0.46981 | 0.39728 | 0.31976
2016-05-15 | 0.25938 | 0.22303 | 0.20006 | 0.18797 | 0.18753 | 0.20516 | 0.24851 | 0.27417 | 0.30977 | 0.37304 | 0.43314 | 0.46613 | 0.47866 | 0.47616 | 0.45621 | 0.43347 | 0.42736 | 0.42648 | 0.41488 | 0.39616 | 0.39616 | 0.36717 | 0.31024 | 0.25246
2016-05-16 | 0.20474 | 0.17696 | 0.1601 | 0.14986 | 0.14833 | 0.16641 | 0.20703 | 0.22621 | 0.24103 | 0.26892 | 0.29386 | 0.31211 | 0.32042 | 0.32615 | 0.33815 | 0.34512 | 0.35301 | 0.34478 | 0.32366 | 0.29719 | 0.28648 | 0.26393 | 0.22773 | 0.18535
2016-05-17 | 0.14882 | 0.12686 | 0.11271 | 0.10509 | 0.10284 | 0.10539 | 0.11364 | 0.13014 | 0.16858 | 0.21365 | 0.25406 | 0.28716 | 0.31249 | 0.33654 | 0.36043 | 0.37979 | 0.39221 | 0.38985 | 0.36712 | 0.32966 | 0.31881 | 0.2982 | 0.25652 | 0.21365
2016-05-18 | 0.17562 | 0.1493 | 0.13227 | 0.12127 | 0.11646 | 0.11744 | 0.12036 | 0.13401 | 0.17579 | 0.23055 | 0.27929 | 0.31905 | 0.35386 | 0.38327 | 0.41078 | 0.43126 | 0.44628 | 0.44287 | 0.41493 | 0.37675 | 0.37248 | 0.34542 | 0.29059 | 0.23123
2016-05-19 | 0.1846 | 0.15543 | 0.13841 | 0.13038 | 0.13074 | 0.14669 | 0.18366 | 0.20718 | 0.24463 | 0.29272 | 0.34099 | 0.38462 | 0.42358 | 0.4639 | 0.49182 | 0.51946 | 0.5347 | 0.53225 | 0.50713 | 0.45996 | 0.44387 | 0.40307 | 0.33499 | 0.26195
2016-05-20 | 0.2076 | 0.17397 | 0.15586 | 0.14531 | 0.14235 | 0.15633 | 0.19192 | 0.22046 | 0.25853 | 0.30893 | 0.3624 | 0.40906 | 0.44808 | 0.48174 | 0.50629 | 0.52638 | 0.53827 | 0.53298 | 0.51156 | 0.46293 | 0.44847 | 0.40317 | 0.33324 | 0.26298
2016-05-21 | 0.20848 | 0.17435 | 0.15421 | 0.14194 | 0.13866 | 0.1525 | 0.18888 | 0.21634 | 0.24951 | 0.29458 | 0.34237 | 0.38697 | 0.42604 | 0.46969 | 0.51282 | 0.54308 | 0.56175 | 0.55403 | 0.52231 | 0.47119 | 0.44842 | 0.40836 | 0.33894 | 0.26592
2016-05-22 | 0.20592 | 0.1709 | 0.14817 | 0.13707 | 0.13515 | 0.14982 | 0.18629 | 0.21179 | 0.25022 | 0.29976 | 0.35681 | 0.41515 | 0.4724 | 0.53066 | 0.57606 | 0.61559 | 0.64095 | 0.63311 | 0.59728 | 0.53636 | 0.50295 | 0.46082 | 0.37654 | 0.29504
2016-05-23 | 0.22994 | 0.19056 | 0.16559 | 0.15168 | 0.14624 | 0.15876 | 0.19151 | 0.22462 | 0.27189 | 0.33406 | 0.40429 | 0.47924 | 0.54711 | 0.61935 | 0.67432 | 0.71143 | 0.72352 | 0.70718 | 0.65766 | 0.57568 | 0.54265 | 0.49731 | 0.42216 | 0.3471
2016-05-24 | 0.28201 | 0.23729 | 0.20486 | 0.18391 | 0.17299 | 0.17006 | 0.17285 | 0.19498 | 0.25989 | 0.34143 | 0.42347 | 0.50593 | 0.58047 | 0.63458 | 0.66854 | 0.68692 | 0.68609 | 0.67046 | 0.6181 | 0.55303 | 0.52632 | 0.48034 | 0.41418 | 0.34695
2016-05-25 | 0.28914 | 0.24421 | 0.21265 | 0.19291 | 0.18133 | 0.17703 | 0.17883 | 0.19291 | 0.24421 | 0.31578 | 0.40173 | 0.47628 | 0.5468 | 0.59592 | 0.62591 | 0.64337 | 0.64925 | 0.62512 | 0.57568 | 0.52097 | 0.50432 | 0.46367 | 0.39659 | 0.33406
2016-05-26 | 0.27452 | 0.23582 | 0.20906 | 0.19236 | 0.18348 | 0.18362 | 0.18753 | 0.20638 | 0.27088 | 0.35787 | 0.44527 | 0.51337 | 0.57402 | 0.61757 | 0.6425 | 0.65562 | 0.65603 | 0.63578 | 0.58714 | 0.53164 | 0.52025 | 0.47292 | 0.39908 | 0.32166
2016-05-27 | 0.26316 | 0.22446 | 0.2007 | 0.1868 | 0.18226 | 0.19946 | 0.23749 | 0.27333 | 0.32515 | 0.39463 | 0.46734 | 0.53691 | 0.59088 | 0.63384 | 0.65944 | 0.67163 | 0.65223 | 0.60268 | 0.5576 | 0.51517 | 0.51036 | 0.46705 | 0.39437 | 0.31371
2016-05-28 | 0.25504 | 0.21814 | 0.19628 | 0.18315 | 0.18004 | 0.19684 | 0.23627 | 0.26748 | 0.31522 | 0.37721 | 0.44623 | 0.5217 | 0.57829 | 0.62664 | 0.65365 | 0.66141 | 0.66066 | 0.63451 | 0.59443 | 0.55135 | 0.53784 | 0.49023 | 0.41364 | 0.33552
2016-05-29 | 0.27171 | 0.2299 | 0.20653 | 0.19284 | 0.18811 | 0.20368 | 0.24251 | 0.27377 | 0.31437 | 0.36875 | 0.42939 | 0.47483 | 0.50319 | 0.52219 | 0.50892 | 0.49447 | 0.48536 | 0.47396 | 0.46361 | 0.43292 | 0.43 | 0.40141 | 0.34522 | 0.28152
2016-05-30 | 0.2245 | 0.18738 | 0.17034 | 0.16017 | 0.15833 | 0.17313 | 0.20806 | 0.23795 | 0.28254 | 0.35306 | 0.4214 | 0.4811 | 0.53047 | 0.57008 | 0.59398 | 0.60955 | 0.60516 | 0.57262 | 0.51644 | 0.47223 | 0.45939 | 0.42205 | 0.36692 | 0.31136
2016-05-31 | 0.26058 | 0.2205 | 0.19454 | 0.17844 | 0.17243 | 0.17138 | 0.17844 | 0.20213 | 0.26696 | 0.34898 | 0.42978 | 0.49737 | 0.54315 | 0.57332 | 0.57842 | 0.57377 | 0.55691 | 0.52085 | 0.48052 | 0.43958 | 0.43419 | 0.40777 | 0.362 | 0.30674
2016-06-01 | 0.26028 | 0.22176 | 0.19815 | 0.18237 | 0.174 | 0.17358 | 0.17681 | 0.19339 | 0.24692 | 0.32037 | 0.39479 | 0.45508 | 0.50755 | 0.54494 | 0.56458 | 0.55967 | 0.53611 | 0.4966 | 0.45434 | 0.42637 | 0.42582 | 0.40697 | 0.35737 | 0.29632
2016-06-02 | 0.24587 | 0.21361 | 0.19602 | 0.18651 | 0.18767 | 0.20856 | 0.2483 | 0.27672 | 0.30433 | 0.33776 | 0.37125 | 0.39084 | 0.41046 | 0.4238 | 0.43286 | 0.43242 | 0.43033 | 0.41998 | 0.40949 | 0.39807 | 0.40168 | 0.37954 | 0.32515 | 0.26596
2016-06-03 | 0.21685 | 0.18633 | 0.16858 | 0.15833 | 0.15773 | 0.17526 | 0.21319 | 0.23909 | 0.2651 | 0.304 | 0.34547 | 0.38244 | 0.41035 | 0.4311 | 0.43991 | 0.44281 | 0.43204 | 0.42052 | 0.40115 | 0.38462 | 0.39 | 0.362 | 0.31019 | 0.25031
2016-06-04 | 0.20107 | 0.171 | 0.15339 | 0.14457 | 0.14445 | 0.16081 | 0.19606 | 0.2016 | 0.25377 | 0.3059 | 0.35246 | 0.39121 | 0.41878 | 0.45281 | 0.47802 | 0.49536 | 0.50874 | 0.51144 | 0.49412 | 0.45479 | 0.43585 | 0.40472 | 0.34656 | 0.27836
2016-06-05 | 0.22295 | 0.18899 | 0.16751 | 0.15487 | 0.15093 | 0.16474 | 0.19565 | 0.23087 | 0.28321 | 0.34626 | 0.41688 | 0.48448 | 0.53925 | 0.59184 | 0.62931 | 0.65678 | 0.6684 | 0.66326 | 0.63097 | 0.56736 | 0.5328 | 0.48011 | 0.40205 | 0.31838
2016-06-06 | 0.25776 | 0.21474 | 0.18764 | 0.17138 | 0.16406 | 0.17523 | 0.20036 | 0.23635 | 0.29898 | 0.37515 | 0.46144 | 0.54718 | 0.62041 | 0.67825 | 0.72002 | 0.74373 | 0.75157 | 0.73723 | 0.69173 | 0.62167 | 0.5774 | 0.52937 | 0.4531 | 0.37979
2016-06-07 | 0.31371 | 0.26618 | 0.23435 | 0.21525 | 0.20251 | 0.19811 | 0.20179 | 0.22721 | 0.2981 | 0.38322 | 0.47889 | 0.56977 | 0.63271 | 0.67818 | 0.70556 | 0.71299 | 0.68748 | 0.64925 | 0.59969 | 0.55066 | 0.51813 | 0.47535 | 0.41132 | 0.34596
2016-06-08 | 0.28923 | 0.24621 | 0.21716 | 0.19324 | 0.18593 | 0.18315 | 0.18366 | 0.19942 | 0.25733 | 0.34502 | 0.43841 | 0.52498 | 0.57906 | 0.59172 | 0.57746 | 0.56863 | 0.55203 | 0.53452 | 0.50152 | 0.46281 | 0.44153 | 0.40933 | 0.34453 | 0.28626
2016-06-09 | 0.23115 | 0.19591 | 0.17295 | 0.16165 | 0.1601 | 0.17442 | 0.20239 | 0.23521 | 0.2868 | 0.35586 | 0.43852 | 0.52962 | 0.60379 | 0.66806 | 0.70338 | 0.69271 | 0.6739 | 0.62704 | 0.57358 | 0.52766 | 0.50253 | 0.46042 | 0.38707 | 0.31333
2016-06-10 | 0.253 | 0.21439 | 0.19207 | 0.17855 | 0.17512 | 0.18972 | 0.219 | 0.25934 | 0.3208 | 0.39205 | 0.46396 | 0.53335 | 0.58959 | 0.6216 | 0.61988 | 0.57797 | 0.54123 | 0.52425 | 0.51982 | 0.48847 | 0.47825 | 0.43353 | 0.36306 | 0.29417
2016-06-11 | 0.24136 | 0.20588 | 0.1824 | 0.17024 | 0.16751 | 0.18008 | 0.21006 | 0.24517 | 0.29971 | 0.37608 | 0.45078 | 0.51759 | 0.56118 | 0.58868 | 0.56118 | 0.51421 | 0.49099 | 0.48384 | 0.47373 | 0.44371 | 0.42961 | 0.40094 | 0.34084 | 0.27836
2016-06-12 | 0.22709 | 0.19262 | 0.17194 | 0.15967 | 0.15696 | 0.16861 | 0.19699 | 0.22331 | 0.25292 | 0.29445 | 0.35092 | 0.41667 | 0.49211 | 0.56357 | 0.61309 | 0.62419 | 0.59307 | 0.54525 | 0.50994 | 0.4746 | 0.45621 | 0.4177 | 0.34665 | 0.28071
2016-06-13 | 0.22757 | 0.1928 | 0.17152 | 0.15833 | 0.1559 | 0.16734 | 0.19203 | 0.22777 | 0.2846 | 0.34958 | 0.41775 | 0.48823 | 0.546 | 0.57631 | 0.57561 | 0.54253 | 0.50946 | 0.47518 | 0.44544 | 0.4036 | 0.37912 | 0.35516 | 0.31127 | 0.25985
2016-06-14 | 0.2156 | 0.18416 | 0.16345 | 0.15158 | 0.14643 | 0.14849 | 0.15573 | 0.17717 | 0.22998 | 0.30105 | 0.37628 | 0.44937 | 0.50892 | 0.55967 | 0.58367 | 0.58181 | 0.5511 | 0.52097 | 0.47523 | 0.42747 | 0.40981 | 0.38036 | 0.33271 | 0.28143
2016-06-15 | 0.23606 | 0.20493 | 0.18158 | 0.1681 | 0.1643 | 0.16768 | 0.17386 | 0.19487 | 0.25393 | 0.33329 | 0.41164 | 0.48841 | 0.55441 | 0.59819 | 0.62405 | 0.61428 | 0.58034 | 0.53888 | 0.49624 | 0.45338 | 0.44505 | 0.42549 | 0.36987 | 0.31188
2016-06-16 | 0.25516 | 0.2205 | 0.19957 | 0.18695 | 0.18272 | 0.19625 | 0.22382 | 0.2541 | 0.29572 | 0.35132 | 0.42972 | 0.5109 | 0.56977 | 0.62386 | 0.66251 | 0.68574 | 0.69979 | 0.68985 | 0.64061 | 0.55973 | 0.52316 | 0.47837 | 0.40237 | 0.32774
2016-06-17 | 0.26566 | 0.22685 | 0.19968 | 0.18452 | 0.17929 | 0.19078 | 0.21889 | 0.25165 | 0.29486 | 0.34463 | 0.39574 | 0.44499 | 0.48923 | 0.52937 | 0.54327 | 0.54302 | 0.53237 | 0.52279 | 0.50349 | 0.47223 | 0.454 | 0.43044 | 0.35832 | 0.29004
2016-06-18 | 0.2331 | 0.19908 | 0.17855 | 0.16604 | 0.16402 | 0.17692 | 0.20691 | 0.23971 | 0.28779 | 0.34586 | 0.41401 | 0.48273 | 0.52182 | 0.53599 | 0.52675 | 0.502 | 0.47454 | 0.45163 | 0.42961 | 0.40809 | 0.39987 | 0.37912 | 0.32319 | 0.26359
2016-06-19 | 0.2135 | 0.18362 | 0.16628 | 0.1564 | 0.15388 | 0.16662 | 0.19495 | 0.22625 | 0.2769 | 0.34075 | 0.41472 | 0.47749 | 0.53188 | 0.57281 | 0.57619 | 0.54055 | 0.50808 | 0.47576 | 0.4441 | 0.41493 | 0.39982 | 0.36849 | 0.31649 | 0.25695
2016-06-20 | 0.20802 | 0.17738 | 0.15866 | 0.14872 | 0.14624 | 0.15703 | 0.1824 | 0.21482 | 0.267 | 0.33742 | 0.41024 | 0.4818 | 0.53969 | 0.57377 | 0.56382 | 0.51511 | 0.48524 | 0.45922 | 0.43763 | 0.40997 | 0.39395 | 0.37448 | 0.32908 | 0.27633
2016-06-21 | 0.22677 | 0.19487 | 0.17351 | 0.16152 | 0.15636 | 0.15839 | 0.16348 | 0.18935 | 0.25814 | 0.34399 | 0.42145 | 0.49838 | 0.56288 | 0.60183 | 0.59004 | 0.54861 | 0.51391 | 0.48636 | 0.45383 | 0.42085 | 0.40477 | 0.38598 | 0.34133 | 0.28644
2016-06-22 | 0.23672 | 0.2065 | 0.18355 | 0.16982 | 0.16223 | 0.16179 | 0.16379 | 0.18942 | 0.25474 | 0.34256 | 0.42462 | 0.49188 | 0.55816 | 0.60889 | 0.64223 | 0.64742 | 0.62558 | 0.57753 | 0.5191 | 0.47061 | 0.45151 | 0.4238 | 0.36804 | 0.30091
2016-06-23 | 0.24409 | 0.21234 | 0.19107 | 0.17876 | 0.17614 | 0.19019 | 0.21893 | 0.25635 | 0.31555 | 0.3876 | 0.47154 | 0.55191 | 0.62691 | 0.68978 | 0.72667 | 0.73514 | 0.72038 | 0.68873 | 0.64364 | 0.58328 | 0.54482 | 0.49536 | 0.4209 | 0.3382
2016-06-24 | 0.27483 | 0.23379 | 0.20841 | 0.19262 | 0.18749 | 0.19983 | 0.22842 | 0.26579 | 0.32918 | 0.40499 | 0.49583 | 0.57944 | 0.65576 | 0.72631 | 0.76937 | 0.79334 | 0.79768 | 0.76811 | 0.72989 | 0.66607 | 0.63217 | 0.57536 | 0.48764 | 0.39743
2016-06-25 | 0.32567 | 0.27659 | 0.24297 | 0.22303 | 0.21572 | 0.22729 | 0.25597 | 0.29463 | 0.36104 | 0.44858 | 0.54823 | 0.62951 | 0.70634 | 0.769 | 0.8089 | 0.81291 | 0.77956 | 0.73701 | 0.68491 | 0.61922 | 0.58027 | 0.53139 | 0.45859 | 0.37376
2016-06-26 | 0.30655 | 0.25818 | 0.22769 | 0.20906 | 0.20202 | 0.21172 | 0.24041 | 0.27752 | 0.34409 | 0.43452 | 0.53072 | 0.61158 | 0.67708 | 0.72159 | 0.7665 | 0.78142 | 0.78179 | 0.75836 | 0.71668 | 0.65094 | 0.60562 | 0.55234 | 0.47015 | 0.38223
2016-06-27 | 0.3115 | 0.26653 | 0.23623 | 0.21794 | 0.21207 | 0.22442 | 0.24867 | 0.28532 | 0.35172 | 0.43691 | 0.5211 | 0.60099 | 0.65345 | 0.69916 | 0.73946 | 0.74387 | 0.72831 | 0.69076 | 0.62512 | 0.55936 | 0.52419 | 0.47657 | 0.41916 | 0.35012
2016-06-28 | 0.28424 | 0.24066 | 0.21319 | 0.19354 | 0.18204 | 0.17295 | 0.19834 | 0.21439 | 0.28545 | 0.37897 | 0.46156 | 0.55259 | 0.63051 | 0.68102 | 0.7127 | 0.73672 | 0.73384 | 0.71703 | 0.66819 | 0.60294 | 0.56736 | 0.52498 | 0.45797 | 0.3828
2016-06-29 | 0.31857 | 0.27342 | 0.24198 | 0.22082 | 0.20902 | 0.20452 | 0.20308 | 0.22145 | 0.29536 | 0.39648 | 0.49998 | 0.60047 | 0.68268 | 0.72409 | 0.72595 | 0.69824 | 0.6768 | 0.64297 | 0.57804 | 0.52049 | 0.48735 | 0.45445 | 0.39395 | 0.32476
2016-06-30 | 0.26918 | 0.23067 | 0.20623 | 0.1924 | 0.19071 | 0.20569 | 0.23452 | 0.26588 | 0.32195 | 0.40243 | 0.48419 | 0.56011 | 0.62432 | 0.68137 | 0.71718 | 0.73499 | 0.71917 | 0.66012 | 0.60431 | 0.55466 | 0.52797 | 0.48888 | 0.42604 | 0.35077
2016-07-01 | 0.28851 | 0.24821 | 0.22474 | 0.21106 | 0.20787 | 0.22347 | 0.25631 | 0.28482 | 0.3228 | 0.37948 | 0.44147 | 0.50791 | 0.55147 | 0.57148 | 0.59126 | 0.59982 | 0.6148 | 0.60549 | 0.58078 | 0.55823 | 0.54643 | 0.50021 | 0.42593 | 0.35102
2016-07-02 | 0.28469 | 0.24646 | 0.22256 | 0.21002 | 0.20608 | 0.21877 | 0.24863 | 0.28098 | 0.33825 | 0.41743 | 0.51018 | 0.57912 | 0.62226 | 0.62764 | 0.60229 | 0.57868 | 0.57243 | 0.56345 | 0.54612 | 0.51505 | 0.50384 | 0.47912 | 0.42058 | 0.34576
2016-07-03 | 0.29177 | 0.25178 | 0.2295 | 0.21509 | 0.2128 | 0.22538 | 0.25529 | 0.28878 | 0.3473 | 0.43452 | 0.53556 | 0.62021 | 0.68296 | 0.7286 | 0.76679 | 0.78819 | 0.77956 | 0.72388 | 0.66524 | 0.60968 | 0.57644 | 0.53913 | 0.47246 | 0.39532
2016-07-04 | 0.33092 | 0.28227 | 0.24863 | 0.22701 | 0.21591 | 0.21564 | 0.22018 | 0.23496 | 0.29888 | 0.40232 | 0.50844 | 0.59839 | 0.65549 | 0.684 | 0.69383 | 0.69132 | 0.62266 | 0.54308 | 0.48888 | 0.44242 | 0.41407 | 0.37933 | 0.36064 | 0.32276
2016-07-05 | 0.27395 | 0.23496 | 0.21048 | 0.19498 | 0.18767 | 0.18797 | 0.19251 | 0.20581 | 0.25588 | 0.31843 | 0.39828 | 0.45911 | 0.5121 | 0.56483 | 0.57154 | 0.53243 | 0.49743 | 0.47373 | 0.45084 | 0.42736 | 0.41283 | 0.39074 | 0.34983 | 0.29856
2016-07-06 | 0.25415 | 0.2205 | 0.19848 | 0.18402 | 0.17951 | 0.18026 | 0.18341 | 0.1977 | 0.25453 | 0.31833 | 0.38104 | 0.40675 | 0.43342 | 0.45814 | 0.48116 | 0.48483 | 0.47813 | 0.46047 | 0.43275 | 0.39147 | 0.38369 | 0.36753 | 0.32304 | 0.26913
2016-07-07 | 0.22761 | 0.19942 | 0.18301 | 0.17509 | 0.1747 | 0.18979 | 0.2181 | 0.2506 | 0.30215 | 0.35968 | 0.42194 | 0.46504 | 0.48565 | 0.50182 | 0.50755 | 0.52419 | 0.52419 | 0.52146 | 0.5094 | 0.49388 | 0.48209 | 0.45462 | 0.39353 | 0.32538
2016-07-08 | 0.26766 | 0.2289 | 0.20429 | 0.19063 | 0.18684 | 0.19863 | 0.22721 | 0.26217 | 0.31696 | 0.39855 | 0.486 | 0.57008 | 0.63988 | 0.67307 | 0.66655 | 0.62797 | 0.58901 | 0.55572 | 0.52182 | 0.47837 | 0.44359 | 0.40616 | 0.34908 | 0.28932
2016-07-09 | 0.23803 | 0.20672 | 0.18749 | 0.16951 | 0.171 | 0.18804 | 0.21779 | 0.24964 | 0.30627 | 0.38869 | 0.46958 | 0.55459 | 0.61257 | 0.62964 | 0.57797 | 0.5379 | 0.51904 | 0.49182 | 0.45973 | 0.44141 | 0.42555 | 0.43935 | 0.34468 | 0.28644
2016-07-10 | 0.2331 | 0.20074 | 0.18229 | 0.17218 | 0.16923 | 0.18204 | 0.21149 | 0.2465 | 0.30266 | 0.3769 | 0.43907 | 0.48355 | 0.5259 | 0.55678 | 0.55553 | 0.53501 | 0.50456 | 0.47229 | 0.44617 | 0.41954 | 0.41229 | 0.3899 | 0.3406 | 0.28352
2016-07-11 | 0.23216 | 0.20055 | 0.18151 | 0.17184 | 0.16958 | 0.18129 | 0.20661 | 0.24218 | 0.30669 | 0.38499 | 0.46785 | 0.54792 | 0.61165 | 0.66504 | 0.69719 | 0.70507 | 0.69824 | 0.67425 | 0.63585 | 0.57906 | 0.54662 | 0.5121 | 0.44875 | 0.37922
2016-07-12 | 0.31805 | 0.27531 | 0.24471 | 0.22621 | 0.21222 | 0.21234 | 0.21595 | 0.23379 | 0.29449 | 0.38781 | 0.47119 | 0.55172 | 0.62021 | 0.65916 | 0.67073 | 0.6684 | 0.65787 | 0.62333 | 0.57663 | 0.51517 | 0.48524 | 0.44505 | 0.39021 | 0.33174
2016-07-13 | 0.28729 | 0.25448 | 0.23188 | 0.21486 | 0.20395 | 0.19972 | 0.20059 | 0.21983 | 0.28752 | 0.37269 | 0.45163 | 0.52791 | 0.58649 | 0.61691 | 0.6423 | 0.66025 | 0.65691 | 0.63251 | 0.5934 | 0.54451 | 0.51849 | 0.49111 | 0.42978 | 0.36144
2016-07-14 | 0.30308 | 0.2626 | 0.23399 | 0.21889 | 0.21494 | 0.22677 | 0.25546 | 0.2886 | 0.35251 | 0.43513 | 0.52401 | 0.60314 | 0.66326 | 0.67984 | 0.66737 | 0.66073 | 0.658 | 0.65671 | 0.63974 | 0.58495 | 0.53753 | 0.48811 | 0.41694 | 0.3432
2016-07-15 | 0.28312 | 0.24425 | 0.21924 | 0.20383 | 0.20028 | 0.21237 | 0.24272 | 0.27386 | 0.32448 | 0.40141 | 0.47194 | 0.53581 | 0.57612 | 0.57644 | 0.55904 | 0.52809 | 0.50707 | 0.49252 | 0.4863 | 0.4631 | 0.45536 | 0.4311 | 0.37325 | 0.30958
2016-07-16 | 0.2581 | 0.22125 | 0.19751 | 0.18622 | 0.18463 | 0.20036 | 0.23803 | 0.27127 | 0.33295 | 0.41062 | 0.48028 | 0.53568 | 0.57123 | 0.54438 | 0.51403 | 0.48964 | 0.46826 | 0.44858 | 0.4358 | 0.4145 | 0.41743 | 0.40216 | 0.35291 | 0.29495
2016-07-17 | 0.24563 | 0.21459 | 0.1917 | 0.18086 | 0.17983 | 0.19417 | 0.22542 | 0.25372 | 0.32023 | 0.39142 | 0.46688 | 0.53624 | 0.53796 | 0.5265 | 0.5124 | 0.53544 | 0.56711 | 0.57084 | 0.5637 | 0.53458 | 0.51132 | 0.47837 | 0.40627 | 0.33879
2016-07-18 | 0.2743 | 0.23521 | 0.21079 | 0.19539 | 0.18968 | 0.20089 | 0.22657 | 0.25899 | 0.32371 | 0.41164 | 0.50063 | 0.58727 | 0.66258 | 0.72067 | 0.75726 | 0.77764 | 0.77771 | 0.73903 | 0.6686 | 0.59793 | 0.55522 | 0.51078 | 0.44275 | 0.37469
2016-07-19 | 0.3116 | 0.26575 | 0.23541 | 0.21693 | 0.20547 | 0.20474 | 0.20864 | 0.2283 | 0.3028 | 0.39881 | 0.49193 | 0.57804 | 0.64702 | 0.69881 | 0.72081 | 0.72838 | 0.74641 | 0.73255 | 0.67777 | 0.62074 | 0.58797 | 0.53864 | 0.46808 | 0.39971
2016-07-20 | 0.33581 | 0.28995 | 0.25661 | 0.23431 | 0.22176 | 0.2165 | 0.21708 | 0.22966 | 0.29833 | 0.39802 | 0.49052 | 0.58868 | 0.66764 | 0.72238 | 0.74932 | 0.73377 | 0.71995 | 0.69817 | 0.65162 | 0.59579 | 0.573 | 0.53354 | 0.46768 | 0.3889
2016-07-21 | 0.32295 | 0.27903 | 0.24901 | 0.23127 | 0.22697 | 0.23909 | 0.27018 | 0.3004 | 0.35666 | 0.43785 | 0.52998 | 0.61257 | 0.66716 | 0.67673 | 0.64506 | 0.61362 | 0.58072 | 0.55178 | 0.52286 | 0.49152 | 0.48548 | 0.44292 | 0.384 | 0.32023
2016-07-22 | 0.26329 | 0.22681 | 0.20707 | 0.19347 | 0.19148 | 0.20848 | 0.23848 | 0.2704 | 0.32947 | 0.4028 | 0.47471 | 0.53225 | 0.56831 | 0.58894 | 0.61783 | 0.63498 | 0.62193 | 0.5838 | 0.55103 | 0.51547 | 0.50557 | 0.46889 | 0.40424 | 0.33879
2016-07-23 | 0.28442 | 0.24688 | 0.22224 | 0.2073 | 0.20357 | 0.21595 | 0.25094 | 0.28009 | 0.33928 | 0.40563 | 0.4686 | 0.52188 | 0.56433 | 0.60595 | 0.64756 | 0.66936 | 0.67763 | 0.67067 | 0.66531 | 0.6179 | 0.58978 | 0.54836 | 0.46768 | 0.39069
2016-07-24 | 0.32376 | 0.27593 | 0.24554 | 0.22757 | 0.22137 | 0.23269 | 0.25904 | 0.29081 | 0.35391 | 0.44214 | 0.52943 | 0.45338 | 0.6649 | 0.69895 | 0.71931 | 0.73896 | 0.76635 | 0.75048 | 0.72602 | 0.66799 | 0.61698 | 0.56869 | 0.47854 | 0.394
2016-07-25 | 0.32884 | 0.27894 | 0.24851 | 0.22862 | 0.21932 | 0.23047 | 0.25661 | 0.28991 | 0.36306 | 0.45349 | 0.54234 | 0.62924 | 0.68435 | 0.71512 | 0.7438 | 0.77113 | 0.7749 | 0.74728 | 0.69146 | 0.62552 | 0.59184 | 0.54166 | 0.47211 | 0.40125
2016-07-26 | 0.34291 | 0.29733 | 0.26909 | 0.24617 | 0.23261 | 0.23039 | 0.23615 | 0.25191 | 0.31489 | 0.40927 | 0.5051 | 0.57358 | 0.60373 | 0.62061 | 0.61559 | 0.59709 | 0.59728 | 0.58367 | 0.55397 | 0.51385 | 0.50355 | 0.46373 | 0.40483 | 0.35296
2016-07-27 | 0.30045 | 0.26178 | 0.23647 | 0.21869 | 0.20948 | 0.20688 | 0.20898 | 0.22248 | 0.29733 | 0.395 | 0.48583 | 0.5737 | 0.6483 | 0.70839 | 0.7483 | 0.77542 | 0.78461 | 0.77416 | 0.7281 | 0.66237 | 0.63311 | 0.58553 | 0.50611 | 0.42648
2016-07-28 | 0.35391 | 0.30846 | 0.27619 | 0.25686 | 0.25153 | 0.26519 | 0.29499 | 0.32582 | 0.39421 | 0.49011 | 0.58213 | 0.67418 | 0.73982 | 0.80279 | 0.86123 | 0.89458 | 0.90678 | 0.89323 | 0.85928 | 0.79401 | 0.75514 | 0.69369 | 0.5872 | 0.48396
2016-07-29 | 0.40067 | 0.34641 | 0.30972 | 0.28819 | 0.27889 | 0.28928 | 0.31758 | 0.34576 | 0.41585 | 0.5042 | 0.59534 | 0.68213 | 0.74207 | 0.78402 | 0.80513 | 0.78864 | 0.77261 | 0.71917 | 0.65617 | 0.60249 | 0.58053 | 0.53618 | 0.45916 | 0.38974
2016-07-30 | 0.32567 | 0.28599 | 0.25729 | 0.24127 | 0.23505 | 0.24784 | 0.2816 | 0.30958 | 0.37392 | 0.45219 | 0.52182 | 0.60817 | 0.6856 | 0.75668 | 0.79521 | 0.79836 | 0.75266 | 0.68005 | 0.62997 | 0.58251 | 0.55359 | 0.51156 | 0.43552 | 0.36468
2016-07-31 | 0.30174 | 0.26054 | 0.23411 | 0.21904 | 0.21393 | 0.22518 | 0.25644 | 0.28169 | 0.33581 | 0.42145 | 0.52073 | 0.61704 | 0.68386 | 0.7296 | 0.74561 | 0.7276 | 0.67259 | 0.62273 | 0.582 | 0.53778 | 0.52474 | 0.488 | 0.42249 | 0.35301
2016-08-01 | 0.2981 | 0.25972 | 0.23059 | 0.2181 | 0.21137 | 0.22378 | 0.25039 | 0.28545 | 0.35042 | 0.44175 | 0.5309 | 0.6146 | 0.68123 | 0.72989 | 0.7715 | 0.79424 | 0.79095 | 0.74677 | 0.68352 | 0.62419 | 0.6004 | 0.55284 | 0.4746 | 0.40317
2016-08-02 | 0.34031 | 0.2924 | 0.26092 | 0.24008 | 0.22882 | 0.22782 | 0.23439 | 0.24926 | 0.31796 | 0.41245 | 0.50444 | 0.58021 | 0.64203 | 0.67818 | 0.71129 | 0.7098 | 0.69839 | 0.66943 | 0.61909 | 0.5697 | 0.55122 | 0.51499 | 0.44937 | 0.38733
2016-08-03 | 0.32894 | 0.28689 | 0.25729 | 0.23844 | 0.22749 | 0.22617 | 0.23099 | 0.23827 | 0.29081 | 0.36422 | 0.42429 | 0.49294 | 0.52754 | 0.53802 | 0.54185 | 0.55135 | 0.55929 | 0.54941 | 0.52371 | 0.49909 | 0.47778 | 0.43896 | 0.37654 | 0.31286
2016-08-04 | 0.25801 | 0.22402 | 0.20319 | 0.19133 | 0.19052 | 0.2065 | 0.23905 | 0.26471 | 0.31753 | 0.39021 | 0.4686 | 0.5408 | 0.56137 | 0.55197 | 0.5194 | 0.48723 | 0.45627 | 0.42292 | 0.40232 | 0.38702 | 0.39728 | 0.37258 | 0.32702 | 0.27885
2016-08-05 | 0.23525 | 0.20753 | 0.19207 | 0.1838 | 0.18337 | 0.19729 | 0.23164 | 0.26152 | 0.31957 | 0.40014 | 0.47506 | 0.55041 | 0.61368 | 0.65304 | 0.64499 | 0.63887 | 0.64492 | 0.65053 | 0.62871 | 0.58136 | 0.56036 | 0.5082 | 0.42879 | 0.35616
2016-08-06 | 0.28991 | 0.25006 | 0.22315 | 0.20695 | 0.20395 | 0.21556 | 0.246 | 0.27708 | 0.3432 | 0.43253 | 0.52091 | 0.62207 | 0.69621 | 0.76106 | 0.80249 | 0.80588 | 0.77025 | 0.73219 | 0.68192 | 0.63351 | 0.61204 | 0.56156 | 0.46992 | 0.39226
2016-08-07 | 0.32218 | 0.27752 | 0.24951 | 0.23172 | 0.22534 | 0.23749 | 0.26909 | 0.2982 | 0.37079 | 0.4659 | 0.55936 | 0.65508 | 0.73406 | 0.79065 | 0.80257 | 0.79559 | 0.78417 | 0.76444 | 0.71306 | 0.65617 | 0.60595 | 0.53925 | 0.44482 | 0.36575
2016-08-08 | 0.301 | 0.25605 | 0.23075 | 0.21607 | 0.20964 | 0.2333 | 0.25284 | 0.28049 | 0.32802 | 0.40435 | 0.48133 | 0.57046 | 0.6563 | 0.73125 | 0.77121 | 0.77364 | 0.76041 | 0.70472 | 0.63887 | 0.58015 | 0.55967 | 0.51313 | 0.44555 | 0.38686
2016-08-09 | 0.31886 | 0.27562 | 0.24525 | 0.22661 | 0.21775 | 0.21775 | 0.22367 | 0.24206 | 0.31767 | 0.4196 | 0.51602 | 0.60725 | 0.6795 | 0.72939 | 0.76473 | 0.78595 | 0.78298 | 0.73816 | 0.66696 | 0.60092 | 0.57663 | 0.5262 | 0.45672 | 0.39648
2016-08-10 | 0.33523 | 0.29195 | 0.25874 | 0.23844 | 0.22653 | 0.22236 | 0.22426 | 0.23521 | 0.30632 | 0.4067 | 0.50426 | 0.60784 | 0.68484 | 0.74532 | 0.77512 | 0.78105 | 0.77579 | 0.75514 | 0.70077 | 0.63364 | 0.60366 | 0.5424 | 0.45854 | 0.37943
2016-08-11 | 0.31235 | 0.26748 | 0.23856 | 0.22172 | 0.21642 | 0.23087 | 0.26221 | 0.28675 | 0.34784 | 0.44248 | 0.53975 | 0.64553 | 0.7314 | 0.78834 | 0.80317 | 0.79903 | 0.80121 | 0.78714 | 0.74547 | 0.68324 | 0.65889 | 0.58425 | 0.49843 | 0.40729
2016-08-12 | 0.33504 | 0.28946 | 0.25542 | 0.23558 | 0.22922 | 0.2416 | 0.2736 | 0.30091 | 0.36428 | 0.45519 | 0.54507 | 0.63298 | 0.7 | 0.75383 | 0.77394 | 0.77239 | 0.78446 | 0.77638 | 0.74837 | 0.6888 | 0.65304 | 0.58392 | 0.4937 | 0.41164
2016-08-13 | 0.33801 | 0.29536 | 0.26415 | 0.23963 | 0.23342 | 0.24658 | 0.28027 | 0.30874 | 0.37881 | 0.47281 | 0.56673 | 0.67225 | 0.75332 | 0.81192 | 0.84224 | 0.85811 | 0.85803 | 0.82103 | 0.76547 | 0.69593 | 0.66785 | 0.60444 | 0.51132 | 0.42642
2016-08-14 | 0.35666 | 0.3122 | 0.28259 | 0.26406 | 0.25597 | 0.26635 | 0.29999 | 0.32673 | 0.39569 | 0.49406 | 0.59243 | 0.67542 | 0.7507 | 0.79199 | 0.79783 | 0.74496 | 0.66963 | 0.61441 | 0.56989 | 0.53329 | 0.52596 | 0.47813 | 0.4165 | 0.34473
2016-08-15 | 0.28806 | 0.25237 | 0.22625 | 0.21474 | 0.21176 | 0.22713 | 0.26298 | 0.29495 | 0.3625 | 0.44315 | 0.52748 | 0.59249 | 0.64405 | 0.63304 | 0.54408 | 0.49058 | 0.45627 | 0.43325 | 0.40525 | 0.37928 | 0.38275 | 0.35626 | 0.32052 | 0.27743
2016-08-16 | 0.23606 | 0.21041 | 0.19376 | 0.18301 | 0.17763 | 0.17958 | 0.18957 | 0.20646 | 0.27079 | 0.37484 | 0.47315 | 0.55166 | 0.62984 | 0.64418 | 0.68518 | 0.65406 | 0.59936 | 0.54488 | 0.49542 | 0.45502 | 0.44415 | 0.41315 | 0.36921 | 0.31333
2016-08-17 | 0.26635 | 0.23391 | 0.21098 | 0.19561 | 0.18932 | 0.18961 | 0.19643 | 0.20979 | 0.27088 | 0.36967 | 0.47142 | 0.56137 | 0.64109 | 0.71136 | 0.72331 | 0.7098 | 0.71668 | 0.71405 | 0.68282 | 0.63291 | 0.6175 | 0.56332 | 0.47662 | 0.38426
2016-08-18 | 0.32118 | 0.27509 | 0.24604 | 0.22934 | 0.22578 | 0.2488 | 0.29072 | 0.31038 | 0.36008 | 0.45496 | 0.55472 | 0.6527 | 0.73068 | 0.79626 | 0.82667 | 0.85174 | 0.85578 | 0.83931 | 0.80415 | 0.74293 | 0.71931 | 0.63505 | 0.52328 | 0.43392
2016-08-19 | 0.35516 | 0.30669 | 0.27399 | 0.25406 | 0.24817 | 0.26779 | 0.31235 | 0.33068 | 0.38478 | 0.47883 | 0.57084 | 0.66826 | 0.75063 | 0.80882 | 0.84386 | 0.88674 | 0.90902 | 0.88626 | 0.84417 | 0.77298 | 0.74496 | 0.66435 | 0.55091 | 0.45462
2016-08-20 | 0.37531 | 0.32476 | 0.29177 | 0.26809 | 0.26062 | 0.27827 | 0.32118 | 0.27294 | 0.39016 | 0.48548 | 0.57708 | 0.68095 | 0.7515 | 0.82247 | 0.85213 | 0.85803 | 0.8557 | 0.83279 | 0.78417 | 0.72595 | 0.70042 | 0.63144 | 0.53102 | 0.43641
2016-08-21 | 0.3687 | 0.31924 | 0.28635 | 0.26614 | 0.25814 | 0.27686 | 0.32228 | 0.3436 | 0.39971 | 0.48741 | 0.58437 | 0.6847 | 0.76026 | 0.82842 | 0.86778 | 0.90854 | 0.90998 | 0.85066 | 0.79028 | 0.71051 | 0.69285 | 0.61731 | 0.52298 | 0.4295
2016-08-22 | 0.35256 | 0.30655 | 0.27531 | 0.25639 | 0.24888 | 0.26622 | 0.31103 | 0.33126 | 0.38546 | 0.4804 | 0.57269 | 0.66751 | 0.7467 | 0.80588 | 0.82835 | 0.87743 | 0.8903 | 0.85508 | 0.79933 | 0.71896 | 0.67708 | 0.59917 | 0.51463 | 0.43591
2016-08-23 | 0.36341 | 0.31611 | 0.28022 | 0.25673 | 0.24268 | 0.24144 | 0.24788 | 0.26195 | 0.33227 | 0.44315 | 0.5478 | 0.64837 | 0.72939 | 0.78625 | 0.81238 | 0.83378 | 0.8461 | 0.82888 | 0.77534 | 0.69951 | 0.66456 | 0.6021 | 0.52925 | 0.4487
2016-08-24 | 0.37381 | 0.32242 | 0.28491 | 0.26028 | 0.24579 | 0.24033 | 0.24099 | 0.24972 | 0.32366 | 0.4316 | 0.52962 | 0.63907 | 0.73111 | 0.79986 | 0.84255 | 0.8652 | 0.86755 | 0.85477 | 0.8043 | 0.73759 | 0.70938 | 0.62698 | 0.52827 | 0.43885
2016-08-25 | 0.37402 | 0.32252 | 0.29436 | 0.2781 | 0.27717 | 0.30215 | 0.35132 | 0.37156 | 0.41067 | 0.49453 | 0.58258 | 0.6634 | 0.71611 | 0.73723 | 0.74192 | 0.74062 | 0.74489 | 0.72824 | 0.6797 | 0.63612 | 0.62525 | 0.55334 | 0.47061 | 0.38457
2016-08-26 | 0.32774 | 0.28964 | 0.26423 | 0.24968 | 0.24708 | 0.26922 | 0.31673 | 0.33494 | 0.37639 | 0.45911 | 0.53778 | 0.61421 | 0.67046 | 0.72216 | 0.75785 | 0.787 | 0.80212 | 0.78916 | 0.74554 | 0.68151 | 0.65882 | 0.5847 | 0.48011 | 0.39548
2016-08-27 | 0.32128 | 0.27593 | 0.24504 | 0.22725 | 0.22082 | 0.23901 | 0.2829 | 0.29865 | 0.34433 | 0.4316 | 0.51457 | 0.60001 | 0.67245 | 0.73384 | 0.78261 | 0.81821 | 0.83947 | 0.82621 | 0.78238 | 0.71228 | 0.69006 | 0.61355 | 0.51054 | 0.42506
2016-08-28 | 0.35281 | 0.30665 | 0.27434 | 0.25372 | 0.24542 | 0.26462 | 0.31263 | 0.33116 | 0.37747 | 0.44943 | 0.50988 | 0.56408 | 0.62904 | 0.69796 | 0.7629 | 0.80467 | 0.82323 | 0.79162 | 0.7286 | 0.67887 | 0.64925 | 0.57053 | 0.48127 | 0.4012
2016-08-29 | 0.32995 | 0.28788 | 0.26079 | 0.24284 | 0.23815 | 0.25754 | 0.30521 | 0.32976 | 0.3828 | 0.4779 | 0.57415 | 0.65121 | 0.70966 | 0.76701 | 0.8086 | 0.83248 | 0.82445 | 0.77246 | 0.70817 | 0.64661 | 0.62379 | 0.55641 | 0.48221 | 0.41715
2016-08-30 | 0.35676 | 0.31286 | 0.28254 | 0.26139 | 0.25241 | 0.26096 | 0.26406 | 0.275 | 0.33479 | 0.43807 | 0.53538 | 0.63425 | 0.70415 | 0.76019 | 0.80287 | 0.82156 | 0.81897 | 0.77446 | 0.69874 | 0.63652 | 0.61408 | 0.55029 | 0.48261 | 0.42123
2016-08-31 | 0.35877 | 0.31131 | 0.27756 | 0.25797 | 0.2445 | 0.23872 | 0.24222 | 0.25195 | 0.31985 | 0.42989 | 0.52128 | 0.6085 | 0.68463 | 0.7386 | 0.76319 | 0.77121 | 0.75449 | 0.72223 | 0.65617 | 0.59644 | 0.57919 | 0.52067 | 0.45338 | 0.38713
2016-09-01 | 0.32908 | 0.29163 | 0.26436 | 0.24483 | 0.2386 | 0.24231 | 0.25377 | 0.25904 | 0.32342 | 0.43253 | 0.53415 | 0.63967 | 0.70148 | 0.75026 | 0.79334 | 0.80829 | 0.79626 | 0.76635 | 0.71647 | 0.65698 | 0.63907 | 0.56641 | 0.47535 | 0.39749
2016-09-02 | 0.33039 | 0.2868 | 0.2578 | 0.24136 | 0.2359 | 0.25516 | 0.29976 | 0.31843 | 0.36114 | 0.44617 | 0.52833 | 0.61876 | 0.68665 | 0.72982 | 0.77749 | 0.80565 | 0.81162 | 0.7858 | 0.72946 | 0.66915 | 0.63471 | 0.54463 | 0.44746 | 0.36144
2016-09-03 | 0.29636 | 0.25576 | 0.23095 | 0.21536 | 0.21129 | 0.22978 | 0.27575 | 0.29363 | 0.33179 | 0.40285 | 0.45627 | 0.51547 | 0.57453 | 0.63961 | 0.68825 | 0.70486 | 0.71497 | 0.69146 | 0.65046 | 0.59871 | 0.58322 | 0.5168 | 0.43264 | 0.34958
2016-09-04 | 0.28806 | 0.24838 | 0.22406 | 0.20967 | 0.20581 | 0.2239 | 0.27106 | 0.28806 | 0.31531 | 0.37639 | 0.446 | 0.50749 | 0.56143 | 0.61428 | 0.63706 | 0.64675 | 0.65841 | 0.64082 | 0.60948 | 0.58136 | 0.57345 | 0.50737 | 0.42303 | 0.34992
2016-09-05 | 0.28923 | 0.25128 | 0.2285 | 0.21478 | 0.21265 | 0.2318 | 0.28196 | 0.30063 | 0.34187 | 0.42396 | 0.5106 | 0.59411 | 0.66881 | 0.72781 | 0.76216 | 0.76429 | 0.73104 | 0.6662 | 0.60066 | 0.55791 | 0.53354 | 0.47437 | 0.41315 | 0.35686
2016-09-06 | 0.30201 | 0.26831 | 0.24347 | 0.22701 | 0.21928 | 0.21916 | 0.22882 | 0.245 | 0.29962 | 0.37917 | 0.44639 | 0.50069 | 0.53366 | 0.52931 | 0.51886 | 0.50528 | 0.47941 | 0.45911 | 0.43591 | 0.42412 | 0.42423 | 0.39189 | 0.35371 | 0.31272
2016-09-07 | 0.26988 | 0.23415 | 0.21118 | 0.19591 | 0.19027 | 0.19126 | 0.19901 | 0.20925 | 0.2575 | 0.32716 | 0.39638 | 0.47119 | 0.53648 | 0.58335 | 0.60575 | 0.59042 | 0.56389 | 0.52809 | 0.47668 | 0.46042 | 0.45968 | 0.41337 | 0.35206 | 0.29245
2016-09-08 | 0.2475 | 0.21904 | 0.19811 | 0.186 | 0.18525 | 0.20711 | 0.25233 | 0.27023 | 0.30054 | 0.37788 | 0.4643 | 0.54643 | 0.61559 | 0.67039 | 0.71178 | 0.72946 | 0.72752 | 0.71164 | 0.6546 | 0.62313 | 0.60164 | 0.52669 | 0.44052 | 0.3619
2016-09-09 | 0.29962 | 0.25827 | 0.23374 | 0.21873 | 0.21268 | 0.23051 | 0.27677 | 0.29436 | 0.3262 | 0.39807 | 0.47993 | 0.55892 | 0.62917 | 0.6932 | 0.72323 | 0.75558 | 0.74765 | 0.71355 | 0.65957 | 0.61724 | 0.58849 | 0.50665 | 0.41911 | 0.34335
2016-09-10 | 0.28666 | 0.25203 | 0.22998 | 0.2149 | 0.21172 | 0.2322 | 0.27956 | 0.29595 | 0.32735 | 0.39079 | 0.46981 | 0.53858 | 0.60249 | 0.66005 | 0.69446 | 0.71065 | 0.70429 | 0.67549 | 0.62871 | 0.59443 | 0.57428 | 0.49459 | 0.41175 | 0.33547
2016-09-11 | 0.27743 | 0.24243 | 0.21881 | 0.20455 | 0.20138 | 0.2203 | 0.26731 | 0.28523 | 0.31347 | 0.38088 | 0.44757 | 0.50844 | 0.55528 | 0.58965 | 0.60164 | 0.60536 | 0.5829 | 0.53969 | 0.5014 | 0.48034 | 0.46992 | 0.41672 | 0.36013 | 0.29742
2016-09-12 | 0.23987 | 0.21299 | 0.19472 | 0.18572 | 0.18572 | 0.20634 | 0.2561 | 0.27136 | 0.304 | 0.36185 | 0.41884 | 0.46952 | 0.52182 | 0.57358 | 0.58675 | 0.58168 | 0.58534 | 0.58971 | 0.54985 | 0.50641 | 0.48935 | 0.44024 | 0.38817 | 0.32889
2016-09-13 | 0.26961 | 0.2333 | 0.20914 | 0.19056 | 0.18323 | 0.18254 | 0.19251 | 0.20646 | 0.25119 | 0.32257 | 0.40627 | 0.48829 | 0.55547 | 0.59891 | 0.61678 | 0.61474 | 0.58946 | 0.55422 | 0.49689 | 0.46872 | 0.4514 | 0.39892 | 0.34045 | 0.2846
2016-09-14 | 0.24305 | 0.21164 | 0.19034 | 0.17657 | 0.16861 | 0.16731 | 0.17267 | 0.18026 | 0.23164 | 0.30968 | 0.39184 | 0.47558 | 0.5424 | 0.58894 | 0.61309 | 0.62127 | 0.62253 | 0.591 | 0.53673 | 0.50593 | 0.48976 | 0.43176 | 0.36636 | 0.29774
2016-09-15 | 0.25022 | 0.21779 | 0.19875 | 0.1884 | 0.188 | 0.20814 | 0.25322 | 0.27224 | 0.30604 | 0.38114 | 0.48087 | 0.56231 | 0.63378 | 0.69874 | 0.74583 | 0.77793 | 0.78372 | 0.76246 | 0.70959 | 0.67046 | 0.64203 | 0.55603 | 0.46693 | 0.37095
2016-09-16 | 0.30335 | 0.26411 | 0.23553 | 0.21818 | 0.21342 | 0.23079 | 0.27743 | 0.29518 | 0.32831 | 0.39929 | 0.48384 | 0.56723 | 0.63411 | 0.68574 | 0.67645 | 0.64816 | 0.62538 | 0.59917 | 0.57008 | 0.55879 | 0.53679 | 0.46711 | 0.393 | 0.32175
2016-09-17 | 0.26187 | 0.22786 | 0.2052 | 0.19151 | 0.19041 | 0.21122 | 0.25981 | 0.27721 | 0.30433 | 0.35832 | 0.43204 | 0.49211 | 0.53765 | 0.56256 | 0.59049 | 0.58881 | 0.54948 | 0.50569 | 0.47645 | 0.48133 | 0.47309 | 0.42227 | 0.35416 | 0.28644
2016-09-18 | 0.23909 | 0.20615 | 0.18975 | 0.17883 | 0.17791 | 0.19777 | 0.24542 | 0.2626 | 0.29004 | 0.34715 | 0.40632 | 0.47182 | 0.53827 | 0.60223 | 0.64925 | 0.67632 | 0.66716 | 0.67128 | 0.61362 | 0.58047 | 0.55178 | 0.4811 | 0.40136 | 0.32515
2016-09-19 | 0.26831 | 0.23075 | 0.20925 | 0.19599 | 0.19361 | 0.21272 | 0.26092 | 0.28259 | 0.31113 | 0.37546 | 0.43314 | 0.47084 | 0.48232 | 0.4635 | 0.43231 | 0.41808 | 0.40525 | 0.39279 | 0.37819 | 0.38369 | 0.37742 | 0.34606 | 0.30345 | 0.25912
2016-09-20 | 0.21783 | 0.19166 | 0.17523 | 0.16645 | 0.16206 | 0.16641 | 0.17997 | 0.1983 | 0.23492 | 0.29632 | 0.35641 | 0.40745 | 0.44712 | 0.47402 | 0.47715 | 0.43569 | 0.40248 | 0.38634 | 0.36154 | 0.36692 | 0.36154 | 0.32562 | 0.28442 | 0.24367
2016-09-21 | 0.20779 | 0.18018 | 0.16314 | 0.15253 | 0.14807 | 0.14921 | 0.15756 | 0.16734 | 0.20741 | 0.27695 | 0.34888 | 0.42254 | 0.48641 | 0.53354 | 0.56641 | 0.57906 | 0.57727 | 0.55384 | 0.50289 | 0.48017 | 0.45576 | 0.39353 | 0.3315 | 0.2674
2016-09-22 | 0.22078 | 0.19115 | 0.17267 | 0.16525 | 0.16707 | 0.19041 | 0.23606 | 0.25835 | 0.28846 | 0.34656 | 0.40986 | 0.46969 | 0.5171 | 0.52724 | 0.51445 | 0.49838 | 0.48935 | 0.47188 | 0.46116 | 0.46762 | 0.44583 | 0.38817 | 0.32266 | 0.26208
2016-09-23 | 0.21579 | 0.18662 | 0.16823 | 0.15903 | 0.16 | 0.1842 | 0.23501 | 0.2587 | 0.27101 | 0.30781 | 0.33572 | 0.37043 | 0.39659 | 0.40232 | 0.40525 | 0.4118 | 0.42074 | 0.43541 | 0.42577 | 0.43857 | 0.42736 | 0.37618 | 0.31682 | 0.2561
2016-09-24 | 0.20979 | 0.18193 | 0.16889 | 0.159 | 0.15799 | 0.18147 | 0.23083 | 0.25385 | 0.27316 | 0.31056 | 0.34844 | 0.38807 | 0.41574 | 0.45067 | 0.49176 | 0.52535 | 0.52852 | 0.51475 | 0.49099 | 0.49058 | 0.47732 | 0.42434 | 0.35316 | 0.29195
2016-09-25 | 0.24371 | 0.21114 | 0.19115 | 0.17908 | 0.17837 | 0.19465 | 0.23289 | 0.2584 | 0.29041 | 0.35216 | 0.41829 | 0.46476 | 0.49058 | 0.51397 | 0.54593 | 0.57269 | 0.55341 | 0.50331 | 0.47044 | 0.46533 | 0.44785 | 0.39458 | 0.33203 | 0.27752
2016-09-26 | 0.23172 | 0.20326 | 0.18572 | 0.17565 | 0.17544 | 0.1974 | 0.24508 | 0.27005 | 0.29149 | 0.33416 | 0.393 | 0.46476 | 0.52255 | 0.58239 | 0.60386 | 0.60588 | 0.58405 | 0.54265 | 0.50117 | 0.49488 | 0.47171 | 0.42445 | 0.36641 | 0.34863
2016-09-27 | 0.28675 | 0.23501 | 0.21556 | 0.20205 | 0.19692 | 0.19916 | 0.21075 | 0.22562 | 0.27686 | 0.36033 | 0.43891 | 0.51879 | 0.58585 | 0.63358 | 0.66785 | 0.66957 | 0.62664 | 0.5829 | 0.5262 | 0.5124 | 0.48052 | 0.43325 | 0.37556 | 0.31597
2016-09-28 | 0.26731 | 0.23448 | 0.21168 | 0.19654 | 0.18972 | 0.19063 | 0.1983 | 0.21176 | 0.25665 | 0.33654 | 0.41743 | 0.49802 | 0.57091 | 0.62532 | 0.66046 | 0.67149 | 0.6563 | 0.61296 | 0.55016 | 0.54892 | 0.52529 | 0.4623 | 0.38713 | 0.31498
2016-09-29 | 0.26544 | 0.22874 | 0.20875 | 0.19654 | 0.19658 | 0.21728 | 0.26531 | 0.2872 | 0.31573 | 0.38566 | 0.46745 | 0.55453 | 0.61132 | 0.6608 | 0.68623 | 0.68602 | 0.66867 | 0.62286 | 0.57358 | 0.55391 | 0.49689 | 0.43187 | 0.35706 | 0.29167
2016-09-30 | 0.24024 | 0.20902 | 0.19074 | 0.18022 | 0.18011 | 0.20156 | 0.25465 | 0.27386 | 0.30665 | 0.37417 | 0.44684 | 0.51337 | 0.56958 | 0.58881 | 0.6066 | 0.5788 | 0.57504 | 0.56673 | 0.53599 | 0.53969 | 0.5159 | 0.45587 | 0.38083 | 0.30958
2016-10-01 | 0.25746 | 0.22347 | 0.20509 | 0.19424 | 0.19247 | 0.21548 | 0.26861 | 0.28819 | 0.32271 | 0.39174 | 0.46121 | 0.53433 | 0.59631 | 0.64411 | 0.66518 | 0.70183 | 0.72381 | 0.70162 | 0.64958 | 0.62432 | 0.59081 | 0.51626 | 0.42456 | 0.38062
2016-10-02 | 0.29742 | 0.25001 | 0.22629 | 0.21179 | 0.20814 | 0.22769 | 0.27739 | 0.29609 | 0.33217 | 0.40766 | 0.49123 | 0.56572 | 0.62997 | 0.69895 | 0.73766 | 0.76547 | 0.78194 | 0.75419 | 0.69257 | 0.66217 | 0.62339 | 0.53901 | 0.45197 | 0.36504
2016-10-03 | 0.30248 | 0.2626 | 0.23374 | 0.21791 | 0.21187 | 0.22946 | 0.27739 | 0.29953 | 0.34001 | 0.42118 | 0.50844 | 0.59501 | 0.65732 | 0.72803 | 0.76517 | 0.78551 | 0.78454 | 0.72209 | 0.63659 | 0.59159 | 0.53495 | 0.46964 | 0.40083 | 0.33728
2016-10-04 | 0.28241 | 0.24251 | 0.21865 | 0.20273 | 0.19521 | 0.19781 | 0.2096 | 0.22486 | 0.27969 | 0.36053 | 0.42879 | 0.49311 | 0.55085 | 0.58688 | 0.60034 | 0.5923 | 0.56458 | 0.52407 | 0.47367 | 0.46521 | 0.43807 | 0.38864 | 0.33213 | 0.27787
2016-10-05 | 0.22697 | 0.18855 | 0.16206 | 0.14266 | 0.13248 | 0.12983 | 0.13438 | 0.13882 | 0.16311 | 0.20277 | 0.24571 | 0.27849 | 0.31606 | 0.35117 | 0.38176 | 0.40493 | 0.42802 | 0.41889 | 0.38415 | 0.38135 | 0.3624 | 0.31366 | 0.25934 | 0.20722
2016-10-06 | 0.16955 | 0.14515 | 0.1312 | 0.12424 | 0.12587 | 0.14753 | 0.18917 | 0.20887 | 0.22902 | 0.26861 | 0.31188 | 0.35296 | 0.39855 | 0.4338 | 0.47067 | 0.48244 | 0.49559 | 0.4772 | 0.45888 | 0.47796 | 0.44853 | 0.38927 | 0.32783 | 0.26562
2016-10-07 | 0.21622 | 0.18902 | 0.17239 | 0.16213 | 0.15987 | 0.17919 | 0.22721 | 0.2509 | 0.26204 | 0.30391 | 0.35236 | 0.38859 | 0.41943 | 0.44617 | 0.45985 | 0.4536 | 0.45281 | 0.44203 | 0.43386 | 0.45508 | 0.43099 | 0.38959 | 0.32252 | 0.2544
2016-10-08 | 0.20921 | 0.18226 | 0.16409 | 0.1554 | 0.1564 | 0.17834 | 0.22681 | 0.24683 | 0.26826 | 0.3208 | 0.38504 | 0.44298 | 0.50045 | 0.54699 | 0.58637 | 0.60457 | 0.60301 | 0.5836 | 0.5491 | 0.54941 | 0.51819 | 0.45259 | 0.37809 | 0.30968
2016-10-09 | 0.25313 | 0.22022 | 0.19867 | 0.18351 | 0.18118 | 0.17706 | 0.24467 | 0.26449 | 0.29081 | 0.35686 | 0.42588 | 0.49188 | 0.54432 | 0.59709 | 0.63445 | 0.65978 | 0.66429 | 0.63988 | 0.58669 | 0.57529 | 0.53765 | 0.46768 | 0.39495 | 0.318
2016-10-10 | 0.25925 | 0.22062 | 0.19897 | 0.18409 | 0.18147 | 0.19957 | 0.24592 | 0.26826 | 0.2971 | 0.36458 | 0.43757 | 0.49849 | 0.55541 | 0.60477 | 0.63947 | 0.66346 | 0.66826 | 0.63485 | 0.56932 | 0.54705 | 0.50605 | 0.44701 | 0.38509 | 0.32405
2016-10-11 | 0.26922 | 0.23233 | 0.21017 | 0.19428 | 0.18564 | 0.18608 | 0.19632 | 0.2073 | 0.25516 | 0.34026 | 0.41976 | 0.49288 | 0.55309 | 0.60099 | 0.63465 | 0.65651 | 0.66073 | 0.63211 | 0.5625 | 0.53249 | 0.49176 | 0.4327 | 0.37773 | 0.31696
2016-10-12 | 0.2664 | 0.22866 | 0.20198 | 0.18608 | 0.17865 | 0.17727 | 0.18441 | 0.1899 | 0.24016 | 0.32894 | 0.41078 | 0.48612 | 0.55453 | 0.60105 | 0.63291 | 0.6504 | 0.65236 | 0.62718 | 0.56869 | 0.56376 | 0.52358 | 0.45757 | 0.39347 | 0.32524
2016-10-13 | 0.27303 | 0.23831 | 0.21763 | 0.20581 | 0.20608 | 0.2279 | 0.27417 | 0.29472 | 0.32309 | 0.38744 | 0.46642 | 0.53427 | 0.58431 | 0.62618 | 0.65528 | 0.67466 | 0.67204 | 0.64465 | 0.59372 | 0.59146 | 0.54848 | 0.48186 | 0.40686 | 0.33334
2016-10-14 | 0.27703 | 0.24405 | 0.22482 | 0.2123 | 0.20937 | 0.23208 | 0.28527 | 0.30707 | 0.33601 | 0.40376 | 0.47466 | 0.53815 | 0.58495 | 0.63712 | 0.6662 | 0.67418 | 0.65834 | 0.61823 | 0.58328 | 0.59191 | 0.54414 | 0.47385 | 0.39627 | 0.32104
2016-10-15 | 0.25887 | 0.22224 | 0.20179 | 0.1895 | 0.18975 | 0.21048 | 0.25959 | 0.28357 | 0.30898 | 0.36559 | 0.42287 | 0.48087 | 0.42085 | 0.55898 | 0.56882 | 0.576 | 0.55873 | 0.5317 | 0.49968 | 0.50731 | 0.46596 | 0.40648 | 0.33392 | 0.2694
2016-10-16 | 0.2181 | 0.18698 | 0.16892 | 0.15713 | 0.15201 | 0.16635 | 0.20463 | 0.21885 | 0.23354 | 0.27149 | 0.30996 | 0.34158 | 0.37587 | 0.41234 | 0.44639 | 0.48139 | 0.50176 | 0.4914 | 0.45101 | 0.44729 | 0.41072 | 0.35057 | 0.28523 | 0.22327
2016-10-17 | 0.17565 | 0.14643 | 0.13114 | 0.12259 | 0.12051 | 0.13586 | 0.17173 | 0.18899 | 0.20707 | 0.24289 | 0.27858 | 0.31291 | 0.34281 | 0.37886 | 0.41542 | 0.44965 | 0.46665 | 0.45118 | 0.40397 | 0.38833 | 0.34938 | 0.29888 | 0.25436 | 0.20779
2016-10-18 | 0.17201 | 0.14292 | 0.12611 | 0.11701 | 0.11299 | 0.1166 | 0.128 | 0.14036 | 0.1739 | 0.22287 | 0.26822 | 0.3086 | 0.35122 | 0.39053 | 0.42785 | 0.45757 | 0.46866 | 0.4514 | 0.40376 | 0.39126 | 0.35396 | 0.30521 | 0.26255 | 0.21583
2016-10-19 | 0.17834 | 0.15145 | 0.13334 | 0.12297 | 0.11877 | 0.11894 | 0.12665 | 0.13432 | 0.16892 | 0.22141 | 0.27276 | 0.32028 | 0.37294 | 0.41574 | 0.45174 | 0.47379 | 0.48145 | 0.46424 | 0.42697 | 0.43005 | 0.39595 | 0.33835 | 0.28335 | 0.2291
2016-10-20 | 0.18619 | 0.15783 | 0.14212 | 0.13426 | 0.13472 | 0.15283 | 0.19184 | 0.21361 | 0.23938 | 0.29358 | 0.35122 | 0.40365 | 0.45061 | 0.48894 | 0.5248 | 0.5355 | 0.52809 | 0.50337 | 0.47953 | 0.48805 | 0.44589 | 0.38384 | 0.31867 | 0.25712
2016-10-21 | 0.20841 | 0.1814 | 0.16659 | 0.15759 | 0.15826 | 0.17862 | 0.22578 | 0.25144 | 0.26161 | 0.29609 | 0.33679 | 0.3626 | 0.38067 | 0.38959 | 0.39174 | 0.39363 | 0.38964 | 0.38192 | 0.38166 | 0.40424 | 0.37572 | 0.33227 | 0.27712 | 0.21928
2016-10-22 | 0.18015 | 0.15583 | 0.14254 | 0.1362 | 0.1377 | 0.15533 | 0.20406 | 0.2299 | 0.24107 | 0.27176 | 0.31305 | 0.35676 | 0.39063 | 0.4208 | 0.44348 | 0.45661 | 0.44892 | 0.42994 | 0.42123 | 0.43574 | 0.40472 | 0.35481 | 0.29354 | 0.23448
2016-10-23 | 0.19063 | 0.16724 | 0.15237 | 0.14371 | 0.14276 | 0.16148 | 0.20891 | 0.23464 | 0.24107 | 0.26713 | 0.29861 | 0.32606 | 0.34973 | 0.36524 | 0.37985 | 0.38666 | 0.3827 | 0.37176 | 0.36367 | 0.37835 | 0.36488 | 0.32347 | 0.27119 | 0.22038
2016-10-24 | 0.18133 | 0.15706 | 0.14378 | 0.1381 | 0.13989 | 0.15736 | 0.19695 | 0.22355 | 0.24041 | 0.27417 | 0.30372 | 0.32558 | 0.33669 | 0.34883 | 0.35827 | 0.36686 | 0.36595 | 0.35456 | 0.34502 | 0.35027 | 0.32443 | 0.2924 | 0.2575 | 0.21342
2016-10-25 | 0.17166 | 0.14438 | 0.1277 | 0.11773 | 0.11427 | 0.11689 | 0.12779 | 0.14203 | 0.17194 | 0.21708 | 0.25806 | 0.29036 | 0.31957 | 0.34769 | 0.36941 | 0.38551 | 0.38587 | 0.36656 | 0.33266 | 0.32817 | 0.29879 | 0.26484 | 0.23035 | 0.1899
2016-10-26 | 0.15679 | 0.13429 | 0.12138 | 0.11274 | 0.10927 | 0.10996 | 0.11698 | 0.12818 | 0.15474 | 0.19905 | 0.24165 | 0.27589 | 0.3066 | 0.33806 | 0.36433 | 0.38499 | 0.39437 | 0.38088 | 0.35062 | 0.35978 | 0.32812 | 0.27969 | 0.22814 | 0.17773
2016-10-27 | 0.14092 | 0.11963 | 0.10805 | 0.103 | 0.10476 | 0.12244 | 0.16128 | 0.1855 | 0.19871 | 0.23415 | 0.2725 | 0.3093 | 0.34138 | 0.3769 | 0.40879 | 0.43896 | 0.45496 | 0.44292 | 0.41857 | 0.42879 | 0.38723 | 0.32726 | 0.26553 | 0.20619
2016-10-28 | 0.16481 | 0.14029 | 0.12575 | 0.11865 | 0.11903 | 0.13791 | 0.18022 | 0.2033 | 0.21838 | 0.26139 | 0.30437 | 0.34829 | 0.38634 | 0.43558 | 0.47275 | 0.50027 | 0.51373 | 0.49796 | 0.4655 | 0.47419 | 0.4289 | 0.3713 | 0.30414 | 0.24169
2016-10-29 | 0.19651 | 0.16768 | 0.14969 | 0.14017 | 0.14014 | 0.15813 | 0.20486 | 0.22633 | 0.24094 | 0.29472 | 0.34261 | 0.39011 | 0.43741 | 0.47895 | 0.513 | 0.54315 | 0.54917 | 0.5214 | 0.479 | 0.47912 | 0.4363 | 0.37706 | 0.30935 | 0.24425
2016-10-30 | 0.19214 | 0.16318 | 0.14502 | 0.13525 | 0.13411 | 0.15152 | 0.1948 | 0.21783 | 0.23196 | 0.2792 | 0.33358 | 0.3813 | 0.42396 | 0.45996 | 0.48139 | 0.4982 | 0.50988 | 0.48759 | 0.45803 | 0.46401 | 0.4226 | 0.37074 | 0.3079 | 0.24658
2016-10-31 | 0.19658 | 0.16655 | 0.14704 | 0.13754 | 0.13555 | 0.1528 | 0.1964 | 0.22058 | 0.23639 | 0.28254 | 0.32822 | 0.37212 | 0.40606 | 0.43044 | 0.44892 | 0.46304 | 0.46613 | 0.43691 | 0.38624 | 0.35978 | 0.3122 | 0.27368 | 0.23083 | 0.18717
2016-11-01 | 0.14804 | 0.12394 | 0.11102 | 0.10414 | 0.10166 | 0.10446 | 0.11669 | 0.12983 | 0.15833 | 0.19651 | 0.22673 | 0.24127 | 0.24692 | 0.24675 | 0.24846 | 0.24959 | 0.246 | 0.23285 | 0.22386 | 0.2368 | 0.21657 | 0.1924 | 0.16505 | 0.1387
2016-11-02 | 0.44002 | 0.096873 | 0.094612 | 0.094432 | 0.097449 | 0.10667 | 0.12385 | 0.15866 | 0.19243 | 0.20691 | 0.20898 | 0.20497 | 0.2013 | 0.19558 | 0.19302 | 0.1903 | 0.19137 | 0.20756 | 0.24136 | 0.23156 | 0.21474 | 0.18749 | 0.15537 | 0.12905
2016-11-03 | 0.10902 | 0.10303 | 0.099743 | 0.10099 | 0.10827 | 0.13484 | 0.18456 | 0.2063 | 0.2121 | 0.21959 | 0.22878 | 0.23578 | 0.2366 | 0.23786 | 0.23521 | 0.23115 | 0.23476 | 0.25073 | 0.28594 | 0.27412 | 0.25174 | 0.21556 | 0.17632 | 0.14194
2016-11-04 | 0.11995 | 0.10681 | 0.099769 | 0.098421 | 0.10174 | 0.12209 | 0.15903 | 0.18804 | 0.21245 | 0.23225 | 0.25216 | 0.27014 | 0.27889 | 0.28693 | 0.29127 | 0.29477 | 0.28919 | 0.29833 | 0.33504 | 0.32342 | 0.29705 | 0.25237 | 0.21083 | 0.17225
2016-11-05 | 0.14349 | 0.12519 | 0.11617 | 0.11192 | 0.11475 | 0.13454 | 0.17369 | 0.18797 | 0.22617 | 0.26601 | 0.2982 | 0.32428 | 0.34207 | 0.35097 | 0.35436 | 0.34769 | 0.33664 | 0.34522 | 0.37922 | 0.36205 | 0.33353 | 0.29095 | 0.23909 | 0.19137
2016-11-06 | 0.15693 | 0.13571 | 0.12279 | 0.1162 | 0.11721 | 0.13738 | 0.17526 | 0.20577 | 0.23963 | 0.28014 | 0.32271 | 0.36013 | 0.39011 | 0.41299 | 0.42412 | 0.42331 | 0.40456 | 0.38702 | 0.40574 | 0.37778 | 0.33484 | 0.28259 | 0.22786 | 0.18165
2016-11-07 | 0.1464 | 0.12545 | 0.1131 | 0.10846 | 0.10957 | 0.12686 | 0.16552 | 0.19254 | 0.22402 | 0.26174 | 0.2976 | 0.33126 | 0.35938 | 0.38296 | 0.39326 | 0.39105 | 0.37013 | 0.35356 | 0.36453 | 0.32957 | 0.2949 | 0.25631 | 0.21924 | 0.18305
2016-11-08 | 0.15119 | 0.12977 | 0.11592 | 0.11013 | 0.10896 | 0.11392 | 0.12638 | 0.1525 | 0.20387 | 0.25014 | 0.28442 | 0.313 | 0.3381 | 0.34883 | 0.34725 | 0.33567 | 0.31943 | 0.32467 | 0.33635 | 0.30711 | 0.27836 | 0.24617 | 0.21381 | 0.1789
2016-11-09 | 0.15126 | 0.12968 | 0.11775 | 0.11172 | 0.1093 | 0.11271 | 0.1213 | 0.14029 | 0.18026 | 0.21447 | 0.23484 | 0.24721 | 0.24876 | 0.24256 | 0.23619 | 0.22629 | 0.22406 | 0.24679 | 0.26757 | 0.25233 | 0.23063 | 0.20077 | 0.17124 | 0.13907
2016-11-10 | 0.11563 | 0.10352 | 0.097318 | 0.094767 | 0.097921 | 0.1124 | 0.15139 | 0.18608 | 0.20277 | 0.22398 | 0.2409 | 0.25627 | 0.26774 | 0.27801 | 0.28312 | 0.28725 | 0.28259 | 0.29 | 0.31829 | 0.29755 | 0.26648 | 0.22665 | 0.18793 | 0.15083
2016-11-11 | 0.12097 | 0.10501 | 0.096821 | 0.093865 | 0.09596 | 0.10816 | 0.13444 | 0.16416 | 0.19258 | 0.21963 | 0.24099 | 0.25691 | 0.27206 | 0.28644 | 0.29326 | 0.29962 | 0.29408 | 0.29705 | 0.32462 | 0.30516 | 0.27364 | 0.23346 | 0.19203 | 0.15132
2016-11-12 | 0.12054 | 0.10422 | 0.097108 | 0.094174 | 0.097764 | 0.11535 | 0.15547 | 0.18093 | 0.19968 | 0.2249 | 0.25212 | 0.27761 | 0.30095 | 0.32577 | 0.34296 | 0.34923 | 0.33982 | 0.33348 | 0.35731 | 0.33372 | 0.29948 | 0.25716 | 0.21079 | 0.16717
2016-11-13 | 0.13525 | 0.11773 | 0.10761 | 0.10457 | 0.107 | 0.1248 | 0.16498 | 0.19243 | 0.21853 | 0.25347 | 0.28662 | 0.3123 | 0.33825 | 0.3619 | 0.37269 | 0.37417 | 0.36074 | 0.35346 | 0.37438 | 0.34983 | 0.31361 | 0.268 | 0.21747 | 0.17379
2016-11-14 | 0.14045 | 0.12025 | 0.10974 | 0.10444 | 0.10569 | 0.12168 | 0.16132 | 0.18968 | 0.21607 | 0.24604 | 0.27368 | 0.29267 | 0.31103 | 0.32471 | 0.33285 | 0.33275 | 0.31862 | 0.31413 | 0.32908 | 0.30229 | 0.27241 | 0.23749 | 0.2049 | 0.17076
2016-11-15 | 0.14247 | 0.12341 | 0.11322 | 0.10786 | 0.10739 | 0.11299 | 0.12716 | 0.151 | 0.19181 | 0.22946 | 0.25563 | 0.2765 | 0.29077 | 0.30354 | 0.30832 | 0.30562 | 0.29399 | 0.29167 | 0.30837 | 0.28276 | 0.25627 | 0.22874 | 0.20123 | 0.17274
2016-11-16 | 0.14553 | 0.12863 | 0.11816 | 0.11251 | 0.11086 | 0.1154 | 0.12388 | 0.14343 | 0.19321 | 0.24438 | 0.28473 | 0.31602 | 0.34335 | 0.36104 | 0.36865 | 0.36819 | 0.35396 | 0.35132 | 0.37325 | 0.34928 | 0.31423 | 0.275 | 0.23594 | 0.19491
2016-11-17 | 0.16358 | 0.14582 | 0.13614 | 0.13202 | 0.13738 | 0.1601 | 0.20619 | 0.23594 | 0.27303 | 0.32678 | 0.38197 | 0.42648 | 0.45968 | 0.47842 | 0.48092 | 0.47281 | 0.45587 | 0.45638 | 0.4735 | 0.4383 | 0.38833 | 0.32764 | 0.27101 | 0.21517
2016-11-18 | 0.17569 | 0.15224 | 0.13701 | 0.12947 | 0.13129 | 0.14853 | 0.19539 | 0.2249 | 0.25022 | 0.28018 | 0.30114 | 0.30516 | 0.29495 | 0.28402 | 0.26961 | 0.25559 | 0.25622 | 0.2846 | 0.3146 | 0.30511 | 0.28254 | 0.24926 | 0.20818 | 0.17257
2016-11-19 | 0.14921 | 0.13926 | 0.13531 | 0.13586 | 0.14521 | 0.17495 | 0.2407 | 0.2725 | 0.28585 | 0.29245 | 0.28887 | 0.27531 | 0.25929 | 0.24767 | 0.23872 | 0.23541 | 0.24099 | 0.27412 | 0.30926 | 0.30349 | 0.28603 | 0.25326 | 0.21373 | 0.1765
2016-11-20 | 0.15178 | 0.14007 | 0.13726 | 0.13845 | 0.14833 | 0.17798 | 0.23676 | 0.26268 | 0.25665 | 0.25656 | 0.25436 | 0.25165 | 0.24742 | 0.24313 | 0.23623 | 0.23289 | 0.23439 | 0.26458 | 0.29934 | 0.29399 | 0.27478 | 0.24334 | 0.20547 | 0.16892
2016-11-21 | 0.14282 | 0.1277 | 0.12265 | 0.11966 | 0.12388 | 0.15276 | 0.1977 | 0.22605 | 0.23639 | 0.24658 | 0.25529 | 0.25729 | 0.25018 | 0.24525 | 0.2393 | 0.23395 | 0.23709 | 0.26122 | 0.27686 | 0.26286 | 0.24467 | 0.2205 | 0.1938 | 0.16501
2016-11-22 | 0.13913 | 0.12359 | 0.11532 | 0.11246 | 0.1135 | 0.12013 | 0.13611 | 0.15913 | 0.20168 | 0.2426 | 0.26774 | 0.28178 | 0.28254 | 0.28165 | 0.27721 | 0.2697 | 0.26835 | 0.29 | 0.3072 | 0.29559 | 0.27898 | 0.25512 | 0.22918 | 0.1958
2016-11-23 | 0.16617 | 0.14817 | 0.13478 | 0.12743 | 0.12608 | 0.13044 | 0.13982 | 0.16246 | 0.2205 | 0.28617 | 0.33334 | 0.36565 | 0.38681 | 0.40253 | 0.40541 | 0.40003 | 0.3799 | 0.38791 | 0.41337 | 0.39616 | 0.36666 | 0.325 | 0.2816 | 0.24127
2016-11-24 | 0.19458 | 0.16858 | 0.15467 | 0.14947 | 0.15362 | 0.17537 | 0.21881 | 0.25195 | 0.29838 | 0.35411 | 0.40847 | 0.46854 | 0.51734 | 0.54296 | 0.55522 | 0.5506 | 0.52188 | 0.5115 | 0.53243 | 0.49719 | 0.45236 | 0.38896 | 0.33523 | 0.27333
2016-11-25 | 0.22446 | 0.19347 | 0.17706 | 0.17083 | 0.17236 | 0.19495 | 0.24029 | 0.27355 | 0.32104 | 0.37459 | 0.42445 | 0.45916 | 0.47941 | 0.49429 | 0.49246 | 0.48244 | 0.4611 | 0.46803 | 0.48759 | 0.46167 | 0.42041 | 0.37397 | 0.32128 | 0.27294
2016-11-26 | 0.2293 | 0.20175 | 0.18467 | 0.17604 | 0.17611 | 0.1891 | 0.21865 | 0.24867 | 0.28689 | 0.3155 | 0.31748 | 0.31066 | 0.30017 | 0.28411 | 0.26531 | 0.24754 | 0.23815 | 0.25763 | 0.27991 | 0.267 | 0.24629 | 0.22554 | 0.19935 | 0.16834
2016-11-27 | 0.14216 | 0.12602 | 0.11819 | 0.11623 | 0.11827 | 0.12776 | 0.14653 | 0.17621 | 0.21358 | 0.23996 | 0.25631 | 0.26286 | 0.26242 | 0.25351 | 0.24351 | 0.22826 | 0.20898 | 0.20126 | 0.2068 | 0.19232 | 0.18269 | 0.17421 | 0.16125 | 0.14327
2016-11-28 | 0.12707 | 0.11787 | 0.11427 | 0.11549 | 0.12203 | 0.13633 | 0.16078 | 0.18869 | 0.2172 | 0.23415 | 0.23647 | 0.22882 | 0.21952 | 0.21125 | 0.20372 | 0.1989 | 0.19927 | 0.22442 | 0.25487 | 0.24604 | 0.23273 | 0.22474 | 0.19882 | 0.17131
2016-11-29 | 0.1483 | 0.13651 | 0.13044 | 0.12968 | 0.13325 | 0.14086 | 0.15823 | 0.18172 | 0.20848 | 0.22133 | 0.22299 | 0.22192 | 0.2181 | 0.21389 | 0.20879 | 0.20379 | 0.19942 | 0.21669 | 0.24 | 0.22938 | 0.21334 | 0.19576 | 0.17323 | 0.14762
2016-11-30 | 0.1243 | 0.11021 | 0.10344 | 0.10091 | 0.10214 | 0.10747 | 0.1181 | 0.13593 | 0.16892 | 0.1964 | 0.21439 | 0.22657 | 0.23566 | 0.24037 | 0.24132 | 0.23815 | 0.23354 | 0.2522 | 0.28675 | 0.27452 | 0.2547 | 0.22594 | 0.19347 | 0.15596
2016-12-01 | 0.12959 | 0.11367 | 0.10613 | 0.10379 | 0.10777 | 0.12833 | 0.17086 | 0.19695 | 0.2207 | 0.2483 | 0.27885 | 0.30377 | 0.31569 | 0.32023 | 0.31456 | 0.30437 | 0.29499 | 0.31658 | 0.35336 | 0.34183 | 0.31545 | 0.27505 | 0.23063 | 0.18373
2016-12-02 | 0.14804 | 0.1277 | 0.11552 | 0.11088 | 0.11407 | 0.13318 | 0.17784 | 0.20319 | 0.2224 | 0.25153 | 0.28103 | 0.2998 | 0.31089 | 0.31791 | 0.3155 | 0.30734 | 0.29641 | 0.32009 | 0.35621 | 0.34291 | 0.31682 | 0.27801 | 0.23136 | 0.18413
2016-12-03 | 0.14759 | 0.12596 | 0.11512 | 0.11013 | 0.11226 | 0.13147 | 0.18004 | 0.20323 | 0.22709 | 0.26303 | 0.29217 | 0.31682 | 0.33591 | 0.34502 | 0.35216 | 0.35551 | 0.33928 | 0.34685 | 0.37979 | 0.362 | 0.33116 | 0.28828 | 0.23983 | 0.18899
2016-12-04 | 0.15142 | 0.13041 | 0.11903 | 0.11429 | 0.11704 | 0.13723 | 0.18126 | 0.20791 | 0.23127 | 0.26657 | 0.29641 | 0.32242 | 0.34325 | 0.35266 | 0.35897 | 0.36134 | 0.34369 | 0.35206 | 0.38707 | 0.37197 | 0.3431 | 0.3028 | 0.25119 | 0.2004
2016-12-05 | 0.16108 | 0.13655 | 0.12406 | 0.11911 | 0.12103 | 0.14083 | 0.18553 | 0.21272 | 0.24148 | 0.28437 | 0.31838 | 0.34227 | 0.35571 | 0.35446 | 0.35311 | 0.35807 | 0.35142 | 0.36018 | 0.37917 | 0.35601 | 0.32702 | 0.2924 | 0.25482 | 0.21156
2016-12-06 | 0.17243 | 0.14714 | 0.1323 | 0.12341 | 0.1199 | 0.12379 | 0.13645 | 0.15789 | 0.20688 | 0.26088 | 0.30419 | 0.33445 | 0.35561 | 0.36895 | 0.375 | 0.37013 | 0.34844 | 0.33933 | 0.35381 | 0.32071 | 0.28995 | 0.25938 | 0.22335 | 0.18427
2016-12-07 | 0.14791 | 0.1271 | 0.11424 | 0.10624 | 0.10406 | 0.10714 | 0.11537 | 0.13114 | 0.17253 | 0.21904 | 0.25157 | 0.27382 | 0.28581 | 0.29249 | 0.29449 | 0.28581 | 0.27412 | 0.28788 | 0.32457 | 0.30026 | 0.27514 | 0.24057 | 0.19901 | 0.15766
2016-12-08 | 0.1262 | 0.10877 | 0.10051 | 0.097711 | 0.10094 | 0.11969 | 0.16037 | 0.18535 | 0.20277 | 0.22414 | 0.24347 | 0.25648 | 0.2651 | 0.27215 | 0.27544 | 0.27943 | 0.27787 | 0.2976 | 0.33757 | 0.32601 | 0.29481 | 0.25368 | 0.20887 | 0.16172
2016-12-09 | 0.12824 | 0.11198 | 0.10419 | 0.10206 | 0.10555 | 0.12677 | 0.17646 | 0.20228 | 0.21614 | 0.22769 | 0.23468 | 0.23619 | 0.23558 | 0.23289 | 0.22866 | 0.22252 | 0.22554 | 0.25831 | 0.30331 | 0.29824 | 0.27894 | 0.24788 | 0.2063 | 0.16676
2016-12-10 | 0.1391 | 0.12779 | 0.12265 | 0.12566 | 0.13447 | 0.17041 | 0.24062 | 0.28451 | 0.2804 | 0.26661 | 0.25597 | 0.24326 | 0.23265 | 0.2255 | 0.21685 | 0.21358 | 0.21822 | 0.25622 | 0.31211 | 0.31206 | 0.30372 | 0.27567 | 0.23501 | 0.19365
2016-12-11 | 0.16851 | 0.15719 | 0.15461 | 0.15547 | 0.16717 | 0.2063 | 0.28617 | 0.3275 | 0.30968 | 0.29199 | 0.27075 | 0.25699 | 0.24367 | 0.23383 | 0.22474 | 0.22097 | 0.22598 | 0.26242 | 0.30912 | 0.30535 | 0.29381 | 0.26592 | 0.22248 | 0.1828
2016-12-12 | 0.15626 | 0.14333 | 0.13891 | 0.13838 | 0.14947 | 0.1851 | 0.25224 | 0.28828 | 0.2909 | 0.29041 | 0.28143 | 0.27009 | 0.25669 | 0.24558 | 0.23439 | 0.23051 | 0.23664 | 0.27695 | 0.31743 | 0.30982 | 0.30068 | 0.2788 | 0.24804 | 0.21323
2016-12-13 | 0.18377 | 0.17159 | 0.16597 | 0.16665 | 0.17313 | 0.19122 | 0.22078 | 0.25857 | 0.28223 | 0.2808 | 0.26406 | 0.24905 | 0.23815 | 0.22757 | 0.21838 | 0.21361 | 0.2123 | 0.23668 | 0.26796 | 0.25776 | 0.24704 | 0.2316 | 0.20914 | 0.18561
2016-12-14 | 0.1629 | 0.14943 | 0.14492 | 0.14531 | 0.14986 | 0.16328 | 0.18917 | 0.22386 | 0.25788 | 0.26187 | 0.24784 | 0.23741 | 0.22946 | 0.22299 | 0.21869 | 0.2149 | 0.21505 | 0.24082 | 0.28635 | 0.28054 | 0.26735 | 0.2438 | 0.20623 | 0.17243
2016-12-15 | 0.14895 | 0.1377 | 0.13686 | 0.13923 | 0.15237 | 0.18855 | 0.26247 | 0.30511 | 0.30141 | 0.28027 | 0.26519 | 0.25343 | 0.25069 | 0.24633 | 0.24115 | 0.24037 | 0.2416 | 0.27123 | 0.32042 | 0.31531 | 0.29586 | 0.26195 | 0.21869 | 0.1772
2016-12-16 | 0.14856 | 0.13583 | 0.13132 | 0.13294 | 0.14206 | 0.17481 | 0.24355 | 0.27889 | 0.27509 | 0.26101 | 0.25187 | 0.24725 | 0.24571 | 0.24642 | 0.24558 | 0.24667 | 0.24729 | 0.26996 | 0.31371 | 0.30544 | 0.28183 | 0.244 | 0.20251 | 0.16132
2016-12-17 | 0.13056 | 0.11569 | 0.11005 | 0.10941 | 0.11672 | 0.14295 | 0.19647 | 0.22866 | 0.232 | 0.23594 | 0.2395 | 0.2416 | 0.24583 | 0.25107 | 0.25661 | 0.26225 | 0.25947 | 0.28022 | 0.31881 | 0.30637 | 0.28076 | 0.24838 | 0.20573 | 0.16236
2016-12-18 | 0.13196 | 0.1166 | 0.11058 | 0.11027 | 0.11712 | 0.14175 | 0.1958 | 0.22922 | 0.24144 | 0.2488 | 0.25191 | 0.24934 | 0.24892 | 0.25686 | 0.26178 | 0.26303 | 0.26049 | 0.2796 | 0.31833 | 0.30604 | 0.28657 | 0.25292 | 0.2121 | 0.17024
2016-12-19 | 0.14001 | 0.1248 | 0.11773 | 0.11663 | 0.12294 | 0.14724 | 0.19658 | 0.23229 | 0.24529 | 0.25284 | 0.25955 | 0.26221 | 0.26191 | 0.26436 | 0.26432 | 0.26333 | 0.2584 | 0.2732 | 0.30562 | 0.28842 | 0.26583 | 0.23881 | 0.20948 | 0.17369
2016-12-20 | 0.14432 | 0.12626 | 0.11744 | 0.1135 | 0.1131 | 0.12162 | 0.13879 | 0.16335 | 0.19834 | 0.22737 | 0.24421 | 0.24729 | 0.25985 | 0.26135 | 0.26286 | 0.26329 | 0.25848 | 0.27158 | 0.30026 | 0.27885 | 0.25597 | 0.23107 | 0.20172 | 0.1682
2016-12-21 | 0.13735 | 0.11752 | 0.10613 | 0.10105 | 0.10035 | 0.10403 | 0.11401 | 0.13169 | 0.17 | 0.21272 | 0.24111 | 0.25652 | 0.27294 | 0.27792 | 0.27417 | 0.26726 | 0.26169 | 0.28326 | 0.3181 | 0.30382 | 0.28424 | 0.25661 | 0.22038 | 0.17784
2016-12-22 | 0.14295 | 0.12191 | 0.11007 | 0.10444 | 0.10613 | 0.1201 | 0.14659 | 0.17562 | 0.21822 | 0.2632 | 0.30354 | 0.33053 | 0.34928 | 0.36347 | 0.37351 | 0.36849 | 0.35137 | 0.36134 | 0.4003 | 0.37897 | 0.34814 | 0.31277 | 0.26774 | 0.2121
2016-12-23 | 0.16906 | 0.14178 | 0.12563 | 0.1179 | 0.11894 | 0.13358 | 0.16051 | 0.19023 | 0.23725 | 0.28995 | 0.33217 | 0.36377 | 0.38744 | 0.39701 | 0.37567 | 0.35336 | 0.33411 | 0.34158 | 0.37675 | 0.35661 | 0.3286 | 0.30781 | 0.27854 | 0.24268
2016-12-24 | 0.20228 | 0.17351 | 0.15596 | 0.14853 | 0.14685 | 0.15693 | 0.1766 | 0.20319 | 0.25874 | 0.32851 | 0.38796 | 0.43033 | 0.45315 | 0.45717 | 0.46019 | 0.44932 | 0.43768 | 0.44825 | 0.4582 | 0.40782 | 0.36311 | 0.32735 | 0.29431 | 0.2501
2016-12-25 | 0.20879 | 0.1794 | 0.155 | 0.13745 | 0.12599 | 0.124 | 0.12866 | 0.14206 | 0.17646 | 0.21533 | 0.24169 | 0.2555 | 0.26041 | 0.25686 | 0.24938 | 0.23399 | 0.2181 | 0.22486 | 0.24405 | 0.23399 | 0.22598 | 0.21369 | 0.19221 | 0.16362
2016-12-26 | 0.13636 | 0.11885 | 0.11125 | 0.10733 | 0.10916 | 0.11929 | 0.13763 | 0.16057 | 0.19188 | 0.22351 | 0.24938 | 0.26045 | 0.26015 | 0.25364 | 0.24968 | 0.24688 | 0.24934 | 0.27841 | 0.31108 | 0.29911 | 0.27739 | 0.25161 | 0.22216 | 0.18553
2016-12-27 | 0.15191 | 0.12959 | 0.11586 | 0.10982 | 0.10985 | 0.11429 | 0.12638 | 0.14055 | 0.17667 | 0.22534 | 0.267 | 0.29568 | 0.31423 | 0.32037 | 0.32061 | 0.31066 | 0.29875 | 0.31253 | 0.34443 | 0.32419 | 0.29609 | 0.26731 | 0.23168 | 0.19027
2016-12-28 | 0.15487 | 0.1309 | 0.11675 | 0.10902 | 0.10531 | 0.107 | 0.11563 | 0.12737 | 0.17065 | 0.22458 | 0.26874 | 0.30423 | 0.33014 | 0.34888 | 0.35897 | 0.35862 | 0.34769 | 0.34453 | 0.37587 | 0.35132 | 0.31895 | 0.28366 | 0.2414 | 0.19328
2016-12-29 | 0.1563 | 0.13318 | 0.12013 | 0.11461 | 0.1152 | 0.12638 | 0.15126 | 0.17671 | 0.22212 | 0.2796 | 0.32981 | 0.36448 | 0.38322 | 0.39174 | 0.39807 | 0.40131 | 0.38864 | 0.38509 | 0.42183 | 0.39379 | 0.35726 | 0.31056 | 0.26324 | 0.20964
2016-12-30 | 0.16635 | 0.1407 | 0.12617 | 0.11859 | 0.11787 | 0.1292 | 0.15257 | 0.17731 | 0.21661 | 0.26493 | 0.31225 | 0.35356 | 0.38057 | 0.40009 | 0.40547 | 0.39886 | 0.38358 | 0.38343 | 0.4196 | 0.392 | 0.35907 | 0.31446 | 0.2697 | 0.21944
2016-12-31 | 0.17734 | 0.14982 | 0.13417 | 0.12608 | 0.1254 | 0.13559 | 0.15766 | 0.18449 | 0.22299 | 0.26618 | 0.30326 | 0.32586 | 0.33135 | 0.33494 | 0.33382 | 0.32687 | 0.32884 | 0.36392 | 0.39542 | 0.35847 | 0.31658 | 0.27373 | 0.23326 | 0.20239

## Conductor Losses
OPC 012920
FPL RC-16
Conductor Losses - From Handwritten PDF
Dated 10/26/2010
Losses = I2R
I = current/amps
R = resistance of conductor
OH FEEDERS 568.3 kcmil ACAR
22500 | current/amps2
0.03287 | ohm/kft at 40º C
739.575 | w/kft
1000000
0.00073958 | mW/kft
48206 | kft
35.652 | mW/kft
3 | conductors
106.9559 | mW in losses
OH FEEDERS 3/0 AAAC
10000 | current/amps2
0.11378 | ohm/kft at 50º C
1137.8 | w/kft
1000000
0.0011378 | mW/kft
6051 | kft
6.8848 | mW/kft
3 | conductors
20.6545 | mW in losses
OH FEEDERS 1/0 AAAC
5625 | current/amps2
0.18049 | ohm/kft at 50º C
1015.2563 | w/kft
1000000
0.0010153 | mW/kft
3707 | kft
3.7636 | mW/kft
3 | conductors
11.2907 | mW in losses
OH LATERALS 1/0 AAAC
625 | current/amps2
0.18049 | ohm/kft at 50º C
112.8063 | w/kft
1000000
0.00011281 | mW/kft
119563 | kft
13.4875 | mW/kft
1 | conductors
13.4875 | mW in losses
UG FEEDERS 25kV, 1000 kcmil AL
22500 | current/amps2
0.0209 | ohm/kft at 58º C
470.25 | w/kft
1000000
0.00047025 | mW/kft
21268 | kft
10.0013 | mW/kft
3 | conductors
30.0038 | mW in losses
UG FEEDERS 25kV, 1/0 AL
625 | current/amps2
0.1886 | ohm/kft at 58º C
117.875 | w/kft
1000000
0.00011788 | mW/kft
1144 | kft
0.13485 | mW/kft
3 | conductors
0.40455 | mW in losses
UG LATERALS 25kV, 1/0 AL
625 | current/amps2
0.1886 | ohm/kft at 58º C
117.875 | w/kft
1000000
0.00011788 | mW/kft
114546 | kft
13.5021 | mW/kft
1 | conductors
13.5021 | mW in losses
196.2989 | mW in total cable losses