## 2018 Annual Cable Losses Energy
OPC 012926
FPL RC-16
2018 FCST (RC2016 - DRY RUN) - ESTIMATED PRIMARY LINE (CABLE) ENERGY LOSSES
[10 empty] | 2018 FCST NEL = | 119562.9643 | GWH |  | 1989 NEL = | 69956 | GWH
|  |  | Estimated Annual Cable Losses (GWH) = |  |  |  | 561.8933 |  |  | Cable Losses % NEL = | 0.46996 |  |  | Cable Losses % NEL = | 1.2994
CL = Conductor losses at peak (hour, day, month - mW); conductor losses are proportional to the square of the load current (load). Conductor losses vary with load over time.
CLE = mwh associated to conductor losses: 1 mW at peak = 1 mW p.u. = 1 mWh at the peak hour, varying over time.
CLEF = Hourly factor for energy on conductors. Changes with time over a daily/monthly load cycle. CLEF is the square of the p.u. load.
More generally:
| HL (Hourly Load p.u.) | CLEF (HL^2) | CLEF*CL (Mwh)
| 1 | 1 | 1*CL
| 0.98814 | 0.97642 | 0.9764*CL | [10 empty] | CONDUCTOR LOSSES (CL MW)
| 0.96386 | 0.92902 | 0.9290*CL | [10 empty] | Total | 196
| 0.91823 | 0.84314 | 0.8431*CL
| . | . | .
| . | . | .
| . | . | .
Hourly Energy (CLE) = CLEF*CL
Peak = Summer Peak (April to October)
Hourly Energy
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | MWH/Day
2018-01-01 | 32.7587 | 30.4184 | 27.3513 | 25.3519 | 24.505 | 24.9179 | 26.2311 | 27.339 | 32.5248 | 41.6328 | 51.1751 | 58.2765 | 62.6975 | 64.4793 | 63.9449 | 62.3183 | 60.658 | 62.0784 | 68.2529 | 64.545 | 59.1279 | 53.3741 | 46.1815 | 37.8649 | 1108.0053
2018-01-02 | 30.8263 | 26.6945 | 24.084 | 22.8823 | 22.5478 | 23.935 | 29.6236 | 34.6879 | 42.9489 | 53.7937 | 63.4035 | 70.4448 | 75.7041 | 79.4754 | 81.1949 | 80.3224 | 77.1153 | 75.7754 | 81.5115 | 75.4194 | 67.5973 | 59.3801 | 50.8075 | 41.6177 | 1291.7931
2018-01-03 | 33.6689 | 28.5011 | 25.5112 | 24.1185 | 24.0037 | 25.6176 | 30.6576 | 35.8061 | 42.3149 | 48.2635 | 51.8383 | 53.0242 | 53.0328 | 52.0576 | 51.0831 | 50.4828 | 50.1757 | 55.0884 | 62.92 | 60.74 | 56.3898 | 51.3426 | 44.8791 | 37.9514 | 1049.4689
2018-01-04 | 32.2518 | 28.695 | 26.6643 | 25.8075 | 25.9145 | 27.2169 | 30.1031 | 34.1321 | 40.8365 | 47.261 | 51.2337 | 52.1251 | 51.2839 | 49.9523 | 48.2717 | 46.7317 | 47.0521 | 51.9142 | 56.3634 | 53.3399 | 49.6056 | 45.2089 | 39.9813 | 34.221 | 996.1674
2018-01-05 | 28.7954 | 25.1931 | 23.0449 | 21.8533 | 21.6133 | 22.6367 | 25.152 | 28.2207 | 34.6948 | 41.6403 | 49.8861 | 55.3492 | 58.2943 | 59.2359 | 59.1549 | 58.0534 | 56.548 | 57.813 | 65.1102 | 61.3432 | 56.2581 | 48.9814 | 41.1061 | 33.4182 | 1033.3966
2018-01-06 | 26.5014 | 23.0336 | 21.0836 | 20.4069 | 20.9442 | 24.1933 | 31.6567 | 36.8851 | 41.9731 | 49.3258 | 57.5198 | 63.0407 | 67.5588 | 70.033 | 69.2617 | 66.3431 | 63.6366 | 67.7127 | 74.8212 | 70.6905 | 61.9034 | 51.8889 | 44.1532 | 36.333 | 1160.9005
2018-01-07 | 30.8653 | 28.0284 | 27.3268 | 27.8862 | 30.5799 | 37.1271 | 51.058 | 62.2814 | 67.5973 | 70.8479 | 69.5541 | 65.9815 | 62.642 | 59.4162 | 56.9357 | 56.777 | 60.176 | 71.7072 | 85.9753 | 86.998 | 83.2635 | 74.0037 | 63.1987 | 53.357 | 1383.5841
2018-01-08 | 46.3566 | 42.8876 | 41.6781 | 41.1436 | 42.4291 | 48.4343 | 60.74 | 67.1843 | 66.5243 | 66.5243 | 65.7062 | 62.4292 | 58.0801 | 54.103 | 50.7908 | 49.515 | 50.4496 | 56.1967 | 63.2825 | 60.9956 | 55.8377 | 47.9633 | 39.5755 | 31.5975 | 1270.4248
2018-01-09 | 25.7718 | 22.9944 | 21.7386 | 21.2882 | 22.1826 | 26.0875 | 35.0194 | 41.5875 | 43.7654 | 47.8176 | 50.6992 | 52.2942 | 52.4381 | 51.67 | 50.6992 | 50.3582 | 50.9661 | 55.8989 | 63.7486 | 62.226 | 57.4311 | 50.2089 | 42.1932 | 33.8184 | 1032.903
2018-01-10 | 27.1741 | 23.3491 | 21.2828 | 20.5287 | 20.9763 | 24.2163 | 32.3715 | 38.4793 | 43.4487 | 49.8613 | 55.2535 | 58.8315 | 60.8677 | 62.4199 | 62.4754 | 62.1337 | 61.6552 | 62.3922 | 69.1352 | 65.3275 | 59.4973 | 52.5992 | 45.8799 | 38.7555 | 1118.9119
2018-01-11 | 31.1911 | 26.8701 | 24.13 | 22.8543 | 22.5922 | 23.8321 | 26.7308 | 30.6382 | 40.3446 | 52.1336 | 61.1967 | 67.1939 | 71.8261 | 74.7099 | 75.8976 | 75.2468 | 72.0444 | 69.4858 | 73.6921 | 68.2819 | 61.5542 | 54.0428 | 46.7717 | 39.245 | 1212.5058
2018-01-12 | 31.8809 | 27.1254 | 24.3489 | 22.804 | 22.0506 | 22.5089 | 24.372 | 26.955 | 33.8116 | 41.663 | 47.7286 | 51.3845 | 54.7157 | 56.874 | 57.4843 | 56.7681 | 55.1145 | 53.974 | 60.485 | 58.1604 | 53.0072 | 46.1895 | 39.0108 | 31.4267 | 999.8436
2018-01-13 | 25.7718 | 22.8767 | 21.5861 | 21.4559 | 22.6479 | 27.4309 | 37.6636 | 44.5583 | 47.4462 | 51.4432 | 55.1058 | 57.9198 | 60.5487 | 62.6142 | 63.9543 | 64.9215 | 64.3572 | 65.4978 | 73.873 | 71.9749 | 64.7049 | 55.2622 | 45.777 | 36.1358 | 1165.5277
2018-01-14 | 28.7013 | 24.5919 | 22.5311 | 21.5101 | 21.9135 | 25.5585 | 34.4129 | 40.3074 | 45.3663 | 52.752 | 59.317 | 63.3104 | 65.4031 | 65.5073 | 64.6108 | 62.226 | 61.5817 | 64.4793 | 72.4521 | 70.3172 | 63.8888 | 55.21 | 45.3033 | 35.7081 | 1166.9601
2018-01-15 | 28.3826 | 24.6558 | 22.6757 | 22.0231 | 22.4701 | 26.5798 | 36.2344 | 42.5359 | 44.8869 | 48.1011 | 49.8118 | 49.9357 | 48.5729 | 47.2449 | 45.7849 | 45.0988 | 45.8166 | 51.0413 | 58.2943 | 56.6184 | 52.2434 | 45.7611 | 38.1101 | 30.483 | 983.3624
2018-01-16 | 25.3637 | 22.8264 | 22.1001 | 22.3704 | 23.9865 | 29.815 | 42.3529 | 51.628 | 53.2972 | 53.9053 | 53.8881 | 52.2857 | 49.8779 | 47.3898 | 45.2718 | 44.2465 | 45.2954 | 51.9142 | 67.4819 | 70.7101 | 69.9645 | 65.5073 | 58.6253 | 51.4097 | 1121.5134
2018-01-17 | 46.5959 | 44.7616 | 45.0281 | 46.5959 | 50.184 | 59.8769 | 79.1108 | 92.0336 | 90.1355 | 80.9737 | 71.4499 | 62.2998 | 55.1753 | 49.7293 | 46.0862 | 44.1377 | 44.4881 | 50.1343 | 59.9222 | 59.1819 | 56.8122 | 52.2688 | 47.261 | 41.5347 | 1375.7773
2018-01-18 | 36.3824 | 34.2004 | 33.5672 | 33.8388 | 35.3386 | 38.8867 | 45.2718 | 54.1288 | 60.5305 | 61.2608 | 58.9841 | 54.4478 | 49.8696 | 45.9275 | 42.5664 | 40.7916 | 40.8141 | 45.5872 | 57.0329 | 59.1729 | 59.1639 | 58.1961 | 55.6717 | 52.1589 | 1153.7908
2018-01-19 | 49.7128 | 48.8914 | 49.5232 | 51.4264 | 54.56 | 59.8226 | 68.456 | 79.6423 | 86.4097 | 81.1106 | 70.1211 | 60.176 | 52.7775 | 47.6398 | 43.6958 | 40.6424 | 39.7523 | 42.3529 | 51.9985 | 51.3593 | 48.9486 | 44.2388 | 39.686 | 33.6961 | 1296.6401
2018-01-20 | 29.6236 | 27.7874 | 27.3758 | 27.8985 | 30.1352 | 34.8328 | 43.2792 | 52.0744 | 55.4711 | 53.9311 | 51.872 | 49.9275 | 47.6801 | 45.983 | 44.7068 | 44.0056 | 44.1299 | 47.1565 | 56.2142 | 55.4624 | 50.6492 | 43.9901 | 36.4318 | 29.1164 | 1029.7347
2018-01-21 | 24.1472 | 21.7277 | 20.7679 | 20.7625 | 21.8533 | 26.5376 | 36.8851 | 43.7267 | 45.2797 | 45.7611 | 46.2531 | 46.2372 | 46.0465 | 45.201 | 44.4647 | 43.719 | 44.0056 | 47.9795 | 56.302 | 55.9864 | 51.4264 | 44.5349 | 37.0131 | 30.0389 | 946.6571
2018-01-22 | 25.0465 | 23.287 | 23.0056 | 23.8892 | 26.616 | 33.9682 | 49.2519 | 60.2487 | 58.5447 | 60.658 | 59.1639 | 56.223 | 52.9561 | 49.2766 | 46.7637 | 45.4294 | 46.3407 | 52.7265 | 68.2722 | 72.8809 | 72.7411 | 68.3302 | 61.7103 | 54.2408 | 1191.5712
2018-01-23 | 49.9853 | 48.9814 | 50.0432 | 52.4466 | 57.0506 | 69.1449 | 92.2919 | 104.673 | 97.5456 | 86.2141 | 76.0812 | 65.5925 | 57.4223 | 51.0245 | 46.9399 | 44.9104 | 45.0752 | 49.9275 | 62.5309 | 64.9781 | 62.9386 | 57.3868 | 49.1945 | 41.6554 | 1484.0344
2018-01-24 | 36.5378 | 34.812 | 34.7017 | 35.6453 | 38.5083 | 46.9479 | 63.786 | 73.6319 | 73.5315 | 70.278 | 66.2098 | 60.5214 | 55.6804 | 51.6784 | 48.4995 | 46.7077 | 47.1726 | 51.502 | 61.839 | 62.0969 | 59.326 | 54.7936 | 49.3505 | 42.9642 | 1266.7223
2018-01-25 | 37.9802 | 35.5824 | 34.6397 | 34.9087 | 36.1851 | 39.2377 | 44.8869 | 52.5059 | 60.1579 | 59.7051 | 55.2448 | 50.566 | 46.9719 | 44.2232 | 42.1628 | 40.6349 | 39.9739 | 41.9504 | 49.0387 | 48.2798 | 45.0517 | 41.2487 | 36.326 | 31.0866 | 1048.549
2018-01-26 | 26.9004 | 24.3027 | 23.2306 | 22.7817 | 23.1236 | 24.7488 | 27.9851 | 32.7587 | 40.0775 | 44.1221 | 45.9989 | 45.8007 | 45.6899 | 45.5872 | 44.981 | 44.34 | 44.2154 | 46.4761 | 53.9998 | 53.7422 | 49.0633 | 42.788 | 36.0234 | 28.8582 | 917.5954
2018-01-27 | 23.5474 | 20.6507 | 19.441 | 19.1225 | 20.2066 | 24.2796 | 33.9478 | 40.0257 | 42.6962 | 45.9275 | 49.7375 | 52.3196 | 54.4737 | 56.2756 | 57.1124 | 58.1783 | 58.6611 | 59.5515 | 66.8969 | 66.0291 | 59.29 | 49.9109 | 40.4338 | 31.2238 | 1049.9391
2018-01-28 | 24.4066 | 21.0192 | 19.4564 | 18.8523 | 19.6012 | 23.451 | 32.3915 | 38.7482 | 41.7536 | 45.9751 | 50.5327 | 53.8709 | 57.0594 | 59.7774 | 61.8114 | 63.3756 | 63.9169 | 64.1696 | 70.6806 | 69.5053 | 63.1987 | 53.3655 | 43.9979 | 34.6535 | 1095.5707
2018-01-29 | 27.388 | 23.6668 | 21.9518 | 21.353 | 22.1716 | 26.4894 | 36.0094 | 43.1792 | 46.4682 | 51.1416 | 54.7417 | 57.813 | 44.3945 | 57.2894 | 56.0827 | 56.5656 | 58.3569 | 63.1801 | 69.5151 | 67.9247 | 63.6086 | 55.8901 | 47.1083 | 37.9874 | 1110.277
2018-01-30 | 31.9007 | 28.5011 | 26.8701 | 26.5195 | 27.7689 | 32.8861 | 44.7303 | 52.786 | 57.0417 | 61.2242 | 63.5806 | 63.2732 | 61.9218 | 60.3486 | 58.6163 | 57.6263 | 58.2943 | 62.3553 | 69.8569 | 68.6594 | 63.3197 | 55.8989 | 46.3247 | 37.3484 | 1217.653
2018-01-31 | 31.2695 | 27.9913 | 26.7006 | 26.1593 | 26.9976 | 31.7621 | 42.6351 | 49.9027 | 52.9646 | 57.0152 | 60.0581 | 61.7746 | 62.1337 | 61.6735 | 60.8221 | 61.3158 | 60.6124 | 61.7379 | 67.1555 | 65.0347 | 59.4071 | 52.6161 | 45.2325 | 37.3698 | 1190.3419
2018-02-01 | 30.7224 | 26.5798 | 24.13 | 22.8879 | 22.6646 | 23.7522 | 26.7489 | 31.4005 | 40.6722 | 50.4579 | 57.5553 | 61.6368 | 64.7331 | 66.6293 | 67.8283 | 68.2529 | 67.2131 | 64.6861 | 67.6357 | 64.997 | 58.3569 | 51.2923 | 44.161 | 36.6369 | 1141.631
2018-02-02 | 29.9109 | 25.754 | 23.2588 | 21.9135 | 21.4505 | 21.8806 | 23.7465 | 27.1741 | 36.8709 | 47.0762 | 53.9912 | 58.5984 | 64.5826 | 68.9797 | 72.1636 | 73.6519 | 73.4713 | 70.6118 | 70.5627 | 64.1134 | 58.33 | 54.9322 | 50.4911 | 40.4412 | 1153.9573
2018-02-03 | 32.305 | 26.2371 | 24.0439 | 23.1404 | 23.718 | 27.6519 | 36.4954 | 42.4977 | 48.353 | 56.3371 | 64.9215 | 71.2226 | 76.3161 | 80.3853 | 83.413 | 84.657 | 82.5498 | 79.7363 | 84.1304 | 81.9557 | 72.9708 | 63.2545 | 52.1251 | 41.2938 | 1359.7115
2018-02-04 | 33.0473 | 28.6136 | 26.0995 | 24.9179 | 25.1755 | 28.7327 | 37.7426 | 43.6416 | 49.1617 | 57.6885 | 65.915 | 72.3028 | 77.4959 | 80.8474 | 83.1355 | 84.4634 | 83.2315 | 79.8199 | 84.2914 | 83.4451 | 75.4905 | 65.0724 | 54.4046 | 43.3947 | 1388.131
2018-02-05 | 35.054 | 30.0389 | 27.4983 | 26.2012 | 26.4232 | 30.483 | 40.2332 | 46.3566 | 52.0998 | 61.3066 | 69.9449 | 76.7562 | 81.1844 | 84.3559 | 86.3336 | 85.423 | 81.8498 | 78.9132 | 82.9436 | 80.7318 | 72.8909 | 62.8922 | 51.7626 | 41.0236 | 1412.7004
2018-02-06 | 32.8794 | 27.8676 | 25.4108 | 24.1933 | 24.5397 | 28.14 | 37.4342 | 43.387 | 49.1699 | 56.2668 | 62.8273 | 67.8379 | 72.0444 | 76.071 | 77.7845 | 78.8301 | 77.8361 | 76.582 | 81.0158 | 79.8931 | 72.2332 | 62.4477 | 51.5776 | 40.538 | 1326.8073
2018-02-07 | 32.2518 | 27.6519 | 24.7023 | 23.4 | 23.5985 | 27.223 | 36.2696 | 42.4596 | 46.6438 | 52.328 | 58.0088 | 63.5433 | 66.9352 | 67.5011 | 72.0146 | 73.311 | 72.9408 | 71.9948 | 72.462 | 68.6982 | 63.3756 | 54.9409 | 47.6236 | 39.267 | 1229.1455
2018-02-08 | 32.3183 | 27.5167 | 24.8362 | 23.5361 | 23.4397 | 24.505 | 27.5781 | 32.1788 | 41.6554 | 52.6161 | 61.6276 | 67.4915 | 71.5488 | 73.5616 | 74.8515 | 74.044 | 72.2531 | 69.6517 | 71.2818 | 67.9729 | 61.3432 | 54.2408 | 46.9479 | 39.6344 | 1216.6312
2018-02-09 | 32.5982 | 27.8614 | 25.1696 | 23.8207 | 23.5247 | 24.4297 | 26.6281 | 30.193 | 37.2912 | 44.4257 | 49.4821 | 52.2012 | 54.7763 | 56.3634 | 57.0682 | 56.4776 | 55.0797 | 54.6551 | 59.7955 | 60.5942 | 54.7936 | 47.4784 | 40.2035 | 31.8941 | 1026.8054
2018-02-10 | 25.7362 | 22.5478 | 21.2882 | 21.089 | 22.1056 | 26.5979 | 36.644 | 43.2099 | 46.1895 | 50.035 | 54.465 | 57.4489 | 60.285 | 62.5401 | 63.4874 | 64.4793 | 64.6579 | 63.9449 | 69.106 | 70.4153 | 63.6179 | 54.5255 | 44.6756 | 35.0748 | 1144.1666
2018-02-11 | 28.2145 | 24.3085 | 22.52 | 21.9463 | 22.6924 | 26.9672 | 37.0701 | 43.6262 | 47.1565 | 52.0913 | 56.7329 | 61.1693 | 65.0253 | 68.5238 | 70.6806 | 72.9408 | 73.6017 | 72.3127 | 76.2548 | 76.7562 | 70.4153 | 58.9302 | 47.8661 | 37.2412 | 1235.044
2018-02-12 | 29.1101 | 25.0289 | 22.6813 | 21.7331 | 22.2322 | 25.9562 | 35.2621 | 40.9712 | 45.6741 | 52.0576 | 57.9554 | 62.9386 | 66.7726 | 69.9841 | 70.8184 | 69.5248 | 67.7994 | 68.1176 | 74.5583 | 72.9308 | 66.2288 | 56.8651 | 44.9575 | 34.2963 | 1204.4548
2018-02-13 | 27.4493 | 23.5134 | 21.7822 | 21.1266 | 21.8861 | 25.9503 | 35.7081 | 42.4977 | 46.3009 | 48.8096 | 51.1081 | 51.931 | 52.3873 | 52.2519 | 51.7878 | 51.0663 | 50.3499 | 50.3665 | 56.3898 | 58.8135 | 55.1318 | 49.0551 | 41.4593 | 33.5536 | 1020.6762
2018-02-14 | 27.9109 | 25.3107 | 24.4645 | 24.7488 | 26.61 | 33.0406 | 47.2851 | 57.6619 | 57.4489 | 54.7849 | 52.6756 | 49.2191 | 46.5479 | 44.7616 | 43.6494 | 43.6107 | 43.5798 | 44.4023 | 50.126 | 51.2839 | 47.6882 | 43.0179 | 38.0451 | 32.5048 | 1010.3786
2018-02-15 | 28.047 | 25.3813 | 24.0209 | 23.5304 | 23.7408 | 25.4226 | 28.8771 | 34.1184 | 40.2926 | 44.5037 | 46.9799 | 47.2369 | 46.0862 | 44.934 | 43.9281 | 43.5567 | 43.3485 | 43.9048 | 48.3123 | 49.3752 | 45.9989 | 41.7083 | 36.9633 | 31.2434 | 911.5111
2018-02-16 | 26.7913 | 24.4182 | 24.1128 | 24.3893 | 24.9529 | 27.486 | 32.2452 | 39.2963 | 45.4925 | 47.3817 | 46.4761 | 44.4023 | 43.2484 | 42.4139 | 42.0338 | 42.1704 | 42.6351 | 43.5104 | 48.5239 | 50.3333 | 46.3646 | 41.2788 | 36.2062 | 29.9428 | 916.1063
2018-02-17 | 25.3872 | 23.0786 | 22.3427 | 22.5756 | 24.0496 | 28.3265 | 36.1499 | 44.0833 | 48.8178 | 50.6908 | 51.544 | 51.7457 | 52.0576 | 52.6331 | 53.2374 | 54.1202 | 54.586 | 54.8456 | 59.254 | 60.7491 | 54.8542 | 47.0842 | 38.2836 | 30.4765 | 1040.9732
2018-02-18 | 24.4355 | 21.2451 | 20.1803 | 19.908 | 21.0031 | 25.3813 | 35.5057 | 42.6427 | 45.5319 | 48.4425 | 51.2337 | 53.5794 | 55.663 | 57.9198 | 60.0672 | 62.143 | 62.8922 | 61.7562 | 64.8085 | 66.3145 | 59.8045 | 50.4496 | 41.4066 | 31.9734 | 1084.2878
2018-02-19 | 25.399 | 21.815 | 20.2856 | 19.679 | 20.4069 | 24.3258 | 33.6757 | 39.7007 | 43.4949 | 48.0281 | 52.8285 | 57.1036 | 60.5669 | 63.9917 | 67.3474 | 70.6216 | 71.4301 | 69.4566 | 71.272 | 72.0941 | 65.441 | 55.8727 | 45.7295 | 35.7221 | 1156.2883
2018-02-20 | 28.0904 | 24.0898 | 21.9957 | 20.9174 | 21.2181 | 25.0172 | 34.1184 | 40.3594 | 45.9433 | 52.9221 | 59.9313 | 64.9404 | 69.7103 | 73.5415 | 76.2956 | 78.7158 | 79.0483 | 76.7459 | 79.4024 | 80.7738 | 74.185 | 64.997 | 53.9998 | 43.6726 | 1290.6316
2018-02-21 | 35.1095 | 29.6045 | 26.9004 | 25.5999 | 25.6769 | 29.1859 | 38.5955 | 45.2403 | 53.9482 | 63.8888 | 72.9508 | 79.9454 | 84.9263 | 88.2243 | 88.6314 | 87.6977 | 82.3162 | 78.0013 | 79.8722 | 77.4959 | 70.1505 | 61.1601 | 52.9391 | 43.5721 | 1421.6332
2018-02-22 | 35.45 | 29.6555 | 26.7308 | 24.9354 | 24.476 | 25.0641 | 27.7812 | 32.752 | 44.4959 | 56.6712 | 66.286 | 73.7725 | 79.8826 | 83.3062 | 84.657 | 85.2609 | 83.0715 | 77.5474 | 76.6332 | 74.4977 | 66.4861 | 58.4105 | 50.2172 | 41.4367 | 1329.4776
2018-02-23 | 33.8048 | 28.7389 | 25.7006 | 24.0037 | 23.2531 | 23.5247 | 25.2107 | 29.2998 | 40.0109 | 52.1251 | 62.5864 | 71.0647 | 81.5009 | 83.2422 | 84.7432 | 86.1055 | 84.8186 | 81.3004 | 81.2582 | 81.522 | 73.9635 | 62.3737 | 52.4296 | 41.4367 | 1334.018
2018-02-24 | 32.5982 | 28.2767 | 25.6058 | 24.13 | 24.3085 | 27.9047 | 35.8831 | 42.4291 | 49.3012 | 58.2854 | 67.1843 | 73.8328 | 80.6267 | 85.4338 | 88.4552 | 90.8143 | 88.7085 | 85.4338 | 88.5763 | 89.2161 | 79.0483 | 67.0022 | 54.258 | 42.4367 | 1429.7498
2018-02-25 | 33.3101 | 28.2145 | 25.3519 | 23.8378 | 23.9522 | 27.5658 | 36.559 | 42.1856 | 48.4181 | 56.0302 | 63.3011 | 69.681 | 76.02 | 81.7652 | 86.388 | 89.1387 | 88.3233 | 83.5841 | 84.5279 | 84.5602 | 75.6838 | 63.8608 | 52.2942 | 40.5306 | 1385.0838
2018-02-26 | 31.7159 | 26.7066 | 23.8321 | 22.5478 | 22.6423 | 25.7065 | 34.0842 | 40.0183 | 45.2875 | 51.5272 | 60.3759 | 66.6388 | 72.482 | 76.6025 | 79.2877 | 79.8408 | 77.4444 | 75.8059 | 80.1128 | 79.9767 | 72.6713 | 62.985 | 51.9479 | 41.384 | 1301.6243
2018-02-27 | 33.1685 | 28.8205 | 26.616 | 25.6117 | 25.9265 | 29.5218 | 38.8284 | 44.4569 | 47.9795 | 52.5313 | 57.7241 | 56.6096 | 61.9495 | 62.6975 | 62.4199 | 61.7379 | 60.2668 | 62.679 | 67.2514 | 68.079 | 62.4754 | 53.357 | 43.549 | 34.7017 | 1168.9588
2018-02-28 | 27.9665 | 24.4297 | 22.8711 | 22.3925 | 23.1011 | 27.3146 | 37.3985 | 43.8583 | 45.983 | 47.3093 | 48.3692 | 48.6952 | 48.7606 | 49.293 | 49.8779 | 50.6992 | 51.2169 | 50.541 | 52.9221 | 54.3615 | 49.7953 | 44.091 | 37.757 | 31.1388 | 990.1433
2018-03-01 | 25.754 | 22.62 | 20.9924 | 20.3014 | 20.5711 | 22.2654 | 25.7184 | 30.7678 | 37.7426 | 42.7115 | 45.9989 | 47.7448 | 49.4409 | 51.1416 | 52.4211 | 54.0858 | 54.2925 | 52.888 | 53.0072 | 54.9756 | 49.721 | 44.1377 | 38.1317 | 31.4398 | 948.8714
2018-03-02 | 26.0636 | 22.9215 | 21.2289 | 19.7673 | 19.5546 | 20.3647 | 22.4146 | 26.2072 | 34.4197 | 42.0869 | 47.2932 | 51.242 | 54.3701 | 57.5198 | 59.7684 | 61.7746 | 62.4292 | 60.886 | 61.5083 | 63.7673 | 57.4311 | 49.3834 | 40.9038 | 32.4715 | 1015.7777
2018-03-03 | 26.8216 | 22.5533 | 20.3805 | 19.596 | 20.0439 | 23.6099 | 31.7357 | 37.4629 | 43.0026 | 49.5974 | 56.1265 | 61.151 | 66.2764 | 71.4301 | 74.8009 | 77.8877 | 78.8197 | 76.5001 | 76.4694 | 77.9187 | 69.1741 | 58.0445 | 46.9318 | 35.9392 | 1222.274
2018-03-04 | 28.0966 | 23.5872 | 21.2882 | 20.1698 | 20.4122 | 23.7123 | 31.8809 | 37.8361 | 43.087 | 49.6056 | 55.8464 | 61.2059 | 66.2479 | 71.0844 | 75.328 | 78.5499 | 79.3398 | 76.8997 | 77.1461 | 78.084 | 70.4153 | 60.4941 | 49.2766 | 38.5228 | 1238.1168
2018-03-05 | 30.2638 | 25.9622 | 23.6156 | 22.6757 | 23.0561 | 26.5798 | 35.7921 | 42.0338 | 47.2128 | 54.9409 | 62.06 | 68.4947 | 74.0843 | 77.7948 | 79.2982 | 79.7885 | 77.8567 | 75.3686 | 77.0845 | 77.9497 | 71.2917 | 61.5909 | 50.7408 | 39.8409 | 1305.377
2018-03-06 | 31.7225 | 27.3941 | 24.842 | 23.8036 | 23.9694 | 27.4125 | 36.164 | 42.3834 | 49.6798 | 57.6974 | 63.9824 | 69.4078 | 73.1308 | 72.3625 | 70.6315 | 60.6671 | 56.074 | 56.821 | 62.0692 | 63.1615 | 58.1783 | 50.6242 | 42.4672 | 34.0433 | 1178.6894
2018-03-07 | 27.4799 | 23.7636 | 22.293 | 21.6296 | 22.2433 | 25.9801 | 34.9226 | 41.0386 | 46.9639 | 52.1336 | 56.5568 | 58.6074 | 59.687 | 59.7864 | 59.696 | 59.7774 | 58.9931 | 56.9093 | 57.9643 | 58.7238 | 54.3874 | 47.2771 | 40.2555 | 32.0462 | 1079.1158
2018-03-08 | 27.0158 | 23.5531 | 22.0341 | 21.4884 | 21.9025 | 23.3322 | 27.1437 | 32.9331 | 39.5314 | 43.5644 | 44.7538 | 44.6599 | 44.4647 | 44.3867 | 44.9889 | 45.8878 | 46.3725 | 45.9275 | 47.2932 | 49.754 | 45.5556 | 40.7319 | 35.165 | 29.9557 | 892.3957
2018-03-09 | 24.5571 | 0 | 21.744 | 20.2908 | 19.7881 | 20.4439 | 22.3482 | 25.2518 | 29.7958 | 35.8901 | 41.2562 | 43.7267 | 47.1806 | 49.1453 | 50.6076 | 52.769 | 55.045 | 56.1528 | 54.4996 | 54.9756 | 57.6086 | 51.1751 | 43.3485 | 33.2898 | 910.8903
2018-03-10 | 25.9503 | 21.5807 | 19.6064 | 19.0101 | 19.7101 | 23.0168 | 31.0801 | 37.793 | 39.9221 | 44.2621 | 49.7705 | 53.2289 | 57.2628 | 60.0219 | 64.254 | 68.485 | 72.0742 | 72.3227 | 69.3396 | 68.5528 | 69.7396 | 59.9132 | 49.8448 | 38.4938 | 1135.2355
2018-03-11 | 29.2681 | 24.176 | 21.5644 | 20.3225 | 20.3172 | 23.5417 | 31.604 | 38.0884 | 39.9369 | 45.0517 | 49.8531 | 54.5255 | 58.7507 | 62.7624 | 66.6484 | 71.1338 | 75.0237 | 76.1833 | 73.5014 | 72.1835 | 73.5215 | 64.7614 | 53.7594 | 40.9936 | 1187.4725
2018-03-12 | 32.1987 | 26.7792 | 24.1645 | 23.0505 | 23.2983 | 26.7731 | 35.7221 | 35.3316 | 44.1765 | 50.6575 | 59.1459 | 66.4003 | 72.3028 | 76.449 | 78.7262 | 83.2101 | 85.9644 | 84.6785 | 80.1652 | 78.3219 | 79.1108 | 69.7298 | 58.7238 | 46.5081 | 1341.5891
2018-03-13 | 36.4601 | 30.4184 | 27.0767 | 25.3754 | 24.9412 | 27.615 | 35.3038 | 40.6125 | 42.2312 | 47.1887 | 51.058 | 53.3912 | 54.707 | 55.5409 | 56.1178 | 56.7241 | 57.9109 | 57.6263 | 54.4046 | 54.017 | 56.1791 | 49.5726 | 41.354 | 32.4248 | 1068.2513
2018-03-14 | 25.7599 | 22.3316 | 20.5287 | 20.0911 | 20.9763 | 24.988 | 35.2205 | 43.6262 | 45.6267 | 47.4381 | 48.8423 | 49.1863 | 49.0387 | 49.408 | 49.8861 | 50.7658 | 52.0407 | 51.9648 | 50.0019 | 49.8366 | 51.6532 | 46.6438 | 40.0997 | 33.1752 | 979.1301
2018-03-15 | 26.2851 | 22.5478 | 20.4069 | 19.4771 | 19.653 | 20.9335 | 23.7408 | 28.8394 | 35.158 | 41.4819 | 46.6438 | 49.7293 | 52.0069 | 53.9482 | 56.2668 | 58.6969 | 61.3799 | 61.8482 | 58.8584 | 56.0302 | 56.6712 | 50.6825 | 44.2388 | 35.8971 | 1001.4218
2018-03-16 | 29.2239 | 24.988 | 22.4479 | 21.0836 | 20.5446 | 20.8907 | 22.6924 | 25.6532 | 32.139 | 41.6026 | 48.9814 | 54.7503 | 59.5425 | 63.3383 | 67.1268 | 69.7787 | 71.0253 | 70.5921 | 67.1459 | 65.8581 | 68.1563 | 61.0961 | 52.735 | 41.9883 | 1123.3807
2018-03-17 | 33.5536 | 28.4949 | 25.8372 | 24.9062 | 25.4108 | 29.1986 | 37.8217 | 44.9889 | 49.0961 | 57.7063 | 67.8187 | 75.1859 | 80.7213 | 83.6055 | 85.1313 | 86.2141 | 86.5403 | 84.1519 | 81.4692 | 83.0608 | 82.9436 | 74.2455 | 64.5544 | 52.328 | 1444.9845
2018-03-18 | 42.5435 | 36.6794 | 33.8592 | 32.5382 | 32.3316 | 35.3247 | 43.5258 | 48.7606 | 47.8499 | 50.8242 | 53.8109 | 55.4711 | 56.9093 | 58.9302 | 61.6184 | 64.5356 | 67.6742 | 68.6594 | 65.953 | 64.6297 | 66.2288 | 58.2765 | 48.1904 | 37.0274 | 1232.1519
2018-03-19 | 28.42 | 23.815 | 21.5155 | 20.5287 | 20.7892 | 24.1128 | 32.2851 | 38.472 | 41.1736 | 46.7077 | 52.4974 | 56.9711 | 60.0219 | 63.8421 | 67.7127 | 71.5389 | 73.9836 | 74.1346 | 70.1995 | 67.5876 | 69.3981 | 61.4716 | 51.5692 | 40.248 | 1178.9957
2018-03-20 | 31.683 | 26.5738 | 24.0496 | 22.6757 | 22.7594 | 25.9145 | 34.0501 | 40.5008 | 43.4641 | 48.9159 | 54.9496 | 59.6779 | 63.506 | 67.6165 | 71.4499 | 74.5684 | 76.6435 | 75.9078 | 72.3525 | 69.4956 | 70.9957 | 61.7654 | 51.2504 | 40.2852 | 1231.0512
2018-03-21 | 30.9758 | 25.6117 | 22.5533 | 20.9495 | 20.9121 | 23.3944 | 29.8086 | 36.0656 | 40.2852 | 47.02 | 54.327 | 60.4213 | 65.4883 | 70.7298 | 75.8874 | 80.2071 | 81.9239 | 80.2385 | 74.3665 | 70.1603 | 70.5037 | 62.5124 | 54.3529 | 44.981 | 1243.6763
2018-03-22 | 36.3542 | 31.0736 | 27.6888 | 25.754 | 24.9938 | 25.8015 | 28.3639 | 31.8743 | 38.2546 | 49.2355 | 58.2943 | 63.3756 | 67.9825 | 71.5785 | 74.0944 | 76.8689 | 80.5007 | 80.4272 | 75.8161 | 70.4055 | 69.7885 | 61.6552 | 52.5313 | 42.4901 | 1265.2029
2018-03-23 | 34.0228 | 28.227 | 24.9938 | 23.1911 | 22.3538 | 22.7092 | 24.3546 | 26.9976 | 33.2966 | 43.8041 | 54.0428 | 62.4384 | 70.9563 | 78.7574 | 84.27 | 89.0062 | 91.0932 | 90.8589 | 86.7363 | 81.8392 | 82.6243 | 72.3625 | 61.27 | 48.6626 | 1338.8686
2018-03-24 | 38.6682 | 32.2054 | 28.2083 | 26.616 | 26.4112 | 29.1164 | 35.3803 | 41.3088 | 45.7453 | 52.3788 | 57.8931 | 61.8574 | 63.4128 | 63.2359 | 61.5909 | 60.5214 | 60.6306 | 61.2883 | 61.1784 | 61.839 | 60.8677 | 53.4852 | 45.5477 | 36.1499 | 1165.5372
2018-03-25 | 29.0407 | 24.2796 | 21.4884 | 20.5075 | 20.7892 | 23.434 | 30.1609 | 36.0866 | 39.9 | 45.8562 | 50.2669 | 54.8629 | 58.5894 | 61.2425 | 63.7486 | 65.7726 | 67.5396 | 67.6838 | 64.997 | 61.839 | 62.9943 | 54.7849 | 44.5896 | 34.0842 | 1104.5386
2018-03-26 | 25.9562 | 21.744 | 19.5339 | 18.7965 | 19.374 | 22.5478 | 30.3282 | 37.8145 | 42.4901 | 44.9732 | 46.988 | 47.004 | 46.0385 | 44.8713 | 44.1221 | 43.7035 | 44.4569 | 44.981 | 44.7147 | 47.2771 | 51.1834 | 46.2531 | 38.9816 | 31.7159 | 905.8496
2018-03-27 | 25.7659 | 22.5311 | 20.9442 | 20.5817 | 21.2936 | 24.5571 | 32.2054 | 38.2185 | 41.384 | 46.0385 | 48.4099 | 49.5974 | 50.1509 | 50.6076 | 50.5493 | 50.4413 | 50.6242 | 50.4994 | 49.8696 | 52.142 | 54.2839 | 49.0305 | 41.8444 | 33.866 | 975.4364
2018-03-28 | 27.3452 | 23.3209 | 21.3422 | 20.3225 | 20.7252 | 23.4963 | 29.9813 | 35.9322 | 40.5082 | 47.1405 | 54.2494 | 58.6701 | 61.8114 | 63.6833 | 65.2235 | 66.1908 | 66.0195 | 63.9824 | 61.0412 | 61.0687 | 62.2814 | 56.9093 | 50.3499 | 42.2084 | 1123.8036
2018-03-29 | 35.0056 | 30.3991 | 27.572 | 26.1593 | 25.8669 | 26.8519 | 29.5409 | 33.6757 | 40.3297 | 50.3333 | 59.7503 | 66.6675 | 69.808 | 71.5092 | 71.1535 | 69.4371 | 67.2131 | 64.9215 | 61.4074 | 60.4213 | 57.9999 | 50.8742 | 44.5974 | 37.0915 | 1178.5862
2018-03-30 | 30.2187 | 25.7659 | 22.8487 | 21.4667 | 20.971 | 21.4884 | 23.6156 | 26.3992 | 31.8941 | 39.7818 | 45.7295 | 48.8668 | 50.325 | 51.4348 | 52.4974 | 53.3997 | 54.3184 | 54.1116 | 51.9395 | 50.433 | 53.263 | 46.8678 | 38.9305 | 30.1545 | 946.7215
2018-03-31 | 23.6042 | 20.4228 | 18.4934 | 17.8897 | 18.5891 | 22.7761 | 31.335 | 37.4557 | 39.6418 | 42.7727 | 46.1259 | 48.8914 | 50.916 | 53.3741 | 55.5845 | 57.4577 | 58.3479 | 57.3868 | 56.2844 | 57.6441 | 60.167 | 52.5992 | 43.4409 | 33.4114 | 1004.6116
2018-04-01 | 25.9145 | 21.9135 | 20.002 | 19.2454 | 19.7621 | 23.3096 | 32.7855 | 39.3257 | 41.8066 | 45.2954 | 48.8096 | 51.9395 | 54.5168 | 57.9376 | 62.1891 | 67.1364 | 71.7964 | 73.5014 | 70.9169 | 66.4289 | 67.4723 | 58.9033 | 47.2771 | 36.0164 | 1124.2019
2018-04-02 | 27.6888 | 23.0898 | 20.7625 | 19.6116 | 19.908 | 23.4793 | 32.139 | 37.5632 | 40.2109 | 45.3899 | 49.9771 | 54.3097 | 57.3602 | 61.2242 | 67.3186 | 73.0108 | 77.4341 | 79.319 | 75.7856 | 71.0943 | 72.0444 | 63.1429 | 50.9494 | 39.1352 | 1181.9485
2018-04-03 | 30.071 | 24.9471 | 22.2543 | 21.1858 | 21.418 | 25.1461 | 33.2763 | 38.6464 | 42.4596 | 48.5239 | 54.5946 | 59.8769 | 64.8085 | 69.6908 | 76.6537 | 81.4059 | 84.8293 | 83.4558 | 79.6736 | 74.2959 | 77.0845 | 67.5492 | 54.6984 | 42.216 | 1278.7616
2018-04-04 | 32.5715 | 27.1985 | 24.1128 | 22.6646 | 22.5034 | 25.7896 | 34.6672 | 39.8704 | 44.1221 | 51.2672 | 58.5984 | 64.9592 | 70.0526 | 75.46 | 80.8369 | 85.661 | 89.6475 | 89.2713 | 84.4204 | 76.2956 | 74.6189 | 66.4289 | 56.3634 | 45.5951 | 1342.9767
2018-04-05 | 36.2485 | 30.2059 | 26.5677 | 24.424 | 23.5815 | 23.8778 | 26.3811 | 29.7065 | 38.385 | 49.6056 | 59.1459 | 67.3474 | 74.3968 | 81.8922 | 87.2382 | 91.2832 | 92.8321 | 91.8204 | 85.1421 | 76.6844 | 75.7754 | 67.1555 | 57.4666 | 47.1887 | 1364.3523
2018-04-06 | 37.5847 | 31.2041 | 26.9672 | 24.5745 | 23.6099 | 23.7522 | 25.4226 | 27.8614 | 36.7219 | 48.5484 | 59.092 | 67.2802 | 75.1453 | 82.3586 | 89.2603 | 93.804 | 96.0493 | 95.8889 | 90.4913 | 83.4237 | 83.6696 | 73.1708 | 61.0412 | 47.4059 | 1404.3282
2018-04-07 | 38.009 | 32.086 | 29.0407 | 27.615 | 28.0037 | 32.0595 | 41.3464 | 47.1324 | 52.5822 | 63.4035 | 75.0541 | 85.9211 | 95.4084 | 104.2187 | 111.4088 | 116.984 | 120.4638 | 119.0683 | 112.2872 | 106.5002 | 104.7928 | 91.3614 | 75.969 | 61.4441 | 1772.1599
2018-04-08 | 50.3167 | 42.6657 | 37.4342 | 34.8259 | 34.8673 | 38.6464 | 49.0961 | 55.1318 | 60.3304 | 68.0404 | 77.5474 | 85.8777 | 90.9481 | 93.6454 | 93.1028 | 90.2578 | 91.7868 | 85.7368 | 74.6897 | 69.6029 | 70.278 | 61.1327 | 49.3998 | 38.2185 | 1543.5792
2018-04-09 | 30.5411 | 25.8788 | 23.3491 | 22.1221 | 22.0396 | 25.1755 | 33.4791 | 37.793 | 40.0923 | 44.9183 | 48.8505 | 51.0078 | 52.3111 | 53.4083 | 55.21 | 57.4489 | 59.6237 | 61.0321 | 59.5154 | 57.4045 | 60.6397 | 53.588 | 43.1254 | 33.2831 | 1051.8375
2018-04-10 | 26.0398 | 22.1826 | 20.0806 | 19.3277 | 19.6893 | 23.0673 | 31.604 | 36.644 | 39.1571 | 43.4872 | 47.6721 | 50.8158 | 52.9987 | 55.5583 | 58.3926 | 61.545 | 63.7673 | 63.7113 | 61.5266 | 60.0128 | 63.208 | 55.5234 | 45.5793 | 35.2413 | 1056.8322
2018-04-11 | 27.7442 | 23.1799 | 20.9602 | 20.0491 | 20.3488 | 23.4453 | 31.7423 | 36.942 | 40.7543 | 47.3173 | 53.6222 | 58.1337 | 61.3524 | 64.6391 | 67.7031 | 68.8437 | 69.2033 | 67.4531 | 64.2728 | 61.8758 | 63.534 | 57.8041 | 50.2752 | 41.4367 | 1142.6327
2018-04-12 | 33.5604 | 28.4886 | 25.1344 | 23.3039 | 22.5533 | 23.1292 | 25.8312 | 29.3949 | 38.074 | 48.8096 | 57.8575 | 65.318 | 70.5823 | 75.4295 | 78.4048 | 81.1633 | 82.1995 | 81.0474 | 75.0439 | 68.3689 | 68.3205 | 61.9955 | 52.7095 | 43.9203 | 1260.6405
2018-04-13 | 36.0164 | 30.3797 | 27.0827 | 24.9646 | 24.1013 | 24.4182 | 26.2431 | 28.94 | 36.6156 | 47.0682 | 55.7765 | 62.4199 | 68.5044 | 72.6713 | 74.4472 | 75.8874 | 76.265 | 75.5515 | 72.1735 | 71.1732 | 74.2253 | 66.7631 | 56.7593 | 45.319 | 1253.7667
2018-04-14 | 36.326 | 30.9889 | 28.2021 | 26.6643 | 26.8034 | 30.2638 | 39.333 | 44.9967 | 51.5104 | 62.2075 | 72.9109 | 82.8158 | 91.2049 | 99.7883 | 106.8506 | 113.0073 | 116.2891 | 115.2067 | 108.3797 | 100.0572 | 98.9254 | 87.0089 | 71.727 | 56.1704 | 1697.6382
2018-04-15 | 44.3478 | 37.47 | 33.4791 | 30.8523 | 30.3604 | 33.6078 | 42.9872 | 48.3936 | 56.5568 | 69.0185 | 80.3014 | 91.272 | 99.6364 | 105.8132 | 108.2945 | 110.2265 | 108.8186 | 100.4672 | 96.3132 | 90.6806 | 91.0932 | 80.7002 | 66.0861 | 51.7878 | 1708.5645
2018-04-16 | 41.2337 | 34.7086 | 30.8913 | 29.0029 | 28.6136 | 31.6172 | 40.0035 | 44.4881 | 47.8418 | 53.2374 | 57.9643 | 61.3158 | 64.8933 | 69.1352 | 72.2829 | 74.6796 | 76.1526 | 75.6125 | 73.1008 | 72.5118 | 75.2671 | 69.0574 | 57.9643 | 45.7928 | 1327.3685
2018-04-17 | 37.0345 | 31.7951 | 28.9148 | 27.4615 | 27.6642 | 31.2499 | 40.2184 | 45.8245 | 51.0413 | 59.335 | 67.1172 | 72.3724 | 74.1649 | 75.5617 | 76.0914 | 75.2874 | 74.0742 | 71.5686 | 69.2715 | 67.8957 | 69.6224 | 64.4981 | 55.7852 | 45.4846 | 1339.3343
2018-04-18 | 37.0772 | 31.683 | 28.4075 | 26.6824 | 26.4172 | 29.1606 | 35.1997 | 40.702 | 48.581 | 59.353 | 68.8825 | 75.5922 | 79.8826 | 84.6678 | 87.0416 | 86.6165 | 85.6718 | 84.5602 | 79.9454 | 74.6492 | 74.9325 | 68.8243 | 60.5305 | 51.4348 | 1426.4956
2018-04-19 | 42.3606 | 36.8141 | 33.1685 | 30.8913 | 30.1352 | 30.8393 | 32.212 | 34.3443 | 40.844 | 52.82 | 63.6926 | 71.727 | 78.5395 | 83.7125 | 86.6056 | 88.5873 | 88.2683 | 84.3022 | 76.8382 | 68.1563 | 66.6675 | 59.317 | 51.1751 | 40.7916 | 1372.8097
2018-04-20 | 32.3915 | 26.7429 | 23.2024 | 21.4559 | 20.7412 | 21.1158 | 22.8711 | 25.0348 | 31.6698 | 39.3697 | 43.9901 | 47.9552 | 50.7075 | 52.735 | 54.1202 | 55.2187 | 55.9339 | 55.184 | 53.3143 | 52.2603 | 55.9951 | 51.8299 | 43.9513 | 34.5434 | 972.3342
2018-04-21 | 27.1985 | 22.8599 | 20.6986 | 19.6842 | 19.9968 | 23.2249 | 30.8198 | 35.3316 | 39.267 | 44.5974 | 49.8779 | 54.0858 | 58.5089 | 62.1983 | 66.5052 | 70.0134 | 72.9009 | 72.6414 | 70.4251 | 67.405 | 69.7201 | 61.6919 | 50.541 | 39.6491 | 1149.8429
2018-04-22 | 30.6447 | 25.2695 | 22.8487 | 21.4234 | 21.4505 | 25.0816 | 33.3439 | 37.3055 | 41.5724 | 47.1164 | 53.2374 | 59.6508 | 64.7049 | 68.9602 | 73.4914 | 79.1628 | 83.1995 | 83.9695 | 80.858 | 76.2343 | 78.3012 | 69.3299 | 56.0915 | 43.0486 | 1276.2966
2018-04-23 | 33.5739 | 28.1648 | 24.9997 | 23.1742 | 22.8879 | 25.9443 | 33.6417 | 29.1986 | 43.233 | 49.721 | 56.3283 | 61.4899 | 67.9247 | 76.071 | 85.2069 | 92.3818 | 97.7305 | 99.1 | 94.9062 | 87.1289 | 86.3336 | 78.2184 | 64.3572 | 47.8095 | 1409.5262
2018-04-24 | 37.8505 | 31.8148 | 26.6703 | 24.6035 | 24.6674 | 26.5798 | 34.1457 | 39.0474 | 44.8086 | 53.6651 | 63.2918 | 71.9551 | 80.3328 | 88.1474 | 94.9746 | 101.8793 | 105.9817 | 105.4404 | 99.4497 | 90.4134 | 89.6808 | 79.7467 | 65.0913 | 51.0245 | 1531.2628
2018-04-25 | 39.8926 | 32.6918 | 28.5323 | 26.2491 | 25.7303 | 28.6512 | 36.4106 | 41.1961 | 47.559 | 56.9799 | 67.8572 | 78.0943 | 87.5663 | 96.7385 | 104.9964 | 112.2252 | 116.2765 | 115.169 | 106.7901 | 95.0545 | 91.9101 | 82.0404 | 68.9214 | 55.7852 | 1643.3182
2018-04-26 | 43.9281 | 35.9322 | 31.1258 | 28.1897 | 26.5677 | 26.6764 | 28.4949 | 32.2253 | 42.4901 | 55.4624 | 68.6206 | 80.9737 | 91.3167 | 99.5314 | 104.6252 | 109.2584 | 111.6806 | 110.2388 | 102.3048 | 90.714 | 87.5882 | 78.6951 | 67.3858 | 55.9076 | 1609.9333
2018-04-27 | 45.7295 | 38.4285 | 33.3506 | 30.4765 | 28.695 | 28.3888 | 29.3949 | 32.325 | 43.719 | 58.6521 | 72.7012 | 85.0881 | 95.3284 | 104.0277 | 110.0055 | 115.2318 | 117.3385 | 115.9235 | 108.6356 | 98.6347 | 97.2223 | 86.987 | 72.0047 | 58.3122 | 1706.6013
2018-04-28 | 47.4945 | 40.702 | 36.6369 | 34.2004 | 33.9955 | 37.8649 | 46.7397 | 52.3703 | 60.3304 | 72.2133 | 86.769 | 99.8935 | 110.3371 | 119.6306 | 127.5895 | 133.8622 | 135.5459 | 134.8793 | 127.4706 | 116.6299 | 113.605 | 100.1392 | 82.1782 | 65.8391 | 2016.9173
2018-04-29 | 53.7937 | 46.0068 | 41.2487 | 38.61 | 38.1751 | 41.799 | 50.5244 | 56.2493 | 66.0861 | 79.4545 | 93.8153 | 106.7781 | 116.7942 | 125.1435 | 131.1019 | 135.4097 | 134.5127 | 131.3968 | 125.3137 | 115.634 | 112.0394 | 99.403 | 82.0828 | 65.7726 | 2087.1454
2018-04-30 | 53.4168 | 46.3009 | 41.9277 | 39.5755 | 39.4284 | 43.0563 | 52.1167 | 57.8753 | 67.4819 | 80.9632 | 95.237 | 107.25 | 116.5542 | 124.9081 | 130.1393 | 133.7946 | 131.8934 | 121.6995 | 114.3544 | 106.6934 | 106.1745 | 95.1115 | 78.9028 | 63.5993 | 2048.4546
2018-05-01 | 51.5524 | 44.3244 | 39.7892 | 37.4557 | 36.807 | 40.6722 | 50.0432 | 55.9776 | 64.5544 | 77.8877 | 92.6969 | 104.6252 | 114.5421 | 123.3181 | 129.0472 | 131.9606 | 130.4999 | 122.8768 | 111.6311 | 103.2774 | 102.5179 | 90.7252 | 75.8671 | 61.5174 | 1994.1667
2018-05-02 | 50.4496 | 43.3331 | 39.0328 | 36.5095 | 35.8621 | 39.4725 | 48.3855 | 54.3874 | 61.9218 | 73.6519 | 84.4096 | 92.9223 | 98.0315 | 104.0874 | 108.5381 | 110.9031 | 109.4296 | 105.0324 | 98.4373 | 89.8027 | 89.6364 | 78.0013 | 67.0693 | 56.1791 | 1775.4863
2018-05-03 | 46.3486 | 39.4872 | 35.1858 | 32.6918 | 31.453 | 32.1324 | 34.5021 | 38.3705 | 46.532 | 57.5553 | 67.2994 | 74.3463 | 77.6917 | 79.319 | 78.4048 | 74.2858 | 65.1857 | 61.8114 | 58.7776 | 57.9554 | 60.0037 | 56.2581 | 50.1923 | 42.9949 | 1298.7849
2018-05-04 | 36.164 | 31.1976 | 28.2892 | 26.3992 | 25.8193 | 25.8312 | 26.5316 | 27.3941 | 34.1184 | 42.5893 | 49.8366 | 55.3405 | 61.2059 | 66.4575 | 71.1634 | 76.5923 | 80.9421 | 83.1888 | 81.2477 | 74.4674 | 72.2332 | 63.9543 | 53.9397 | 41.3615 | 1236.2646
2018-05-05 | 32.5582 | 26.3871 | 24.1645 | 22.6256 | 22.6701 | 25.9205 | 32.9398 | 37.678 | 43.6339 | 52.066 | 61.4349 | 69.8276 | 78.2288 | 86.3228 | 94.0988 | 100.8663 | 106.9716 | 107.8445 | 102.9091 | 87.5991 | 88.0157 | 77.2592 | 58.7059 | 47.7529 | 1488.4808
2018-05-06 | 36.9918 | 30.9238 | 27.1498 | 25.0231 | 24.5339 | 27.4309 | 34.7431 | 39.6197 | 45.8878 | 55.3666 | 65.6494 | 76.4081 | 87.2054 | 95.8087 | 104.3023 | 111.9032 | 116.8701 | 116.5415 | 110.4108 | 94.8265 | 96.681 | 85.6935 | 70.2191 | 54.5168 | 1634.7069
2018-05-07 | 43.4409 | 36.5732 | 32.8525 | 30.4894 | 29.9877 | 33.0204 | 40.8888 | 46.0862 | 54.017 | 64.3384 | 76.5411 | 87.3475 | 97.4878 | 107.2016 | 116.3395 | 120.9779 | 124.4509 | 123.474 | 115.9235 | 105.3324 | 102.838 | 93.0351 | 76.5206 | 61.0687 | 1820.2331
2018-05-08 | 48.7442 | 41.6856 | 37.4772 | 34.5503 | 33.8797 | 36.878 | 44.9026 | 49.9192 | 58.6342 | 69.808 | 81.9451 | 92.5618 | 102.0092 | 111.2853 | 118.6984 | 125.4316 | 129.5927 | 128.4366 | 121.8286 | 110.2388 | 105.9456 | 94.986 | 79.3815 | 64.3572 | 1923.1774
2018-05-09 | 50.433 | 42.5206 | 38.3415 | 35.2899 | 34.5571 | 37.6995 | 45.7691 | 50.941 | 59.263 | 70.602 | 82.3905 | 92.6068 | 101.832 | 110.3862 | 118.329 | 124.3596 | 127.431 | 124.3856 | 115.1314 | 102.6838 | 97.6727 | 87.906 | 75.9384 | 63.6646 | 1890.1343
2018-05-10 | 52.4635 | 45.1459 | 40.5306 | 37.377 | 35.9042 | 36.2766 | 37.8217 | 42.0035 | 54.2408 | 68.3012 | 79.5275 | 88.6204 | 98.2981 | 104.8526 | 109.1972 | 112.4484 | 112.2624 | 109.8706 | 103.1823 | 91.8317 | 92.8997 | 84.7862 | 74.6492 | 63.2173 | 1775.7086
2018-05-11 | 52.752 | 45.6583 | 40.7543 | 37.7426 | 36.3119 | 35.9462 | 36.5166 | 39.0474 | 48.4914 | 61.2425 | 72.3326 | 81.4587 | 89.8803 | 97.3031 | 102.9329 | 105.7771 | 106.8506 | 103.9084 | 97.8925 | 89.5036 | 89.6586 | 84.1304 | 72.273 | 58.4999 | 1686.8649
2018-05-12 | 46.9799 | 40.1368 | 36.1499 | 34.1389 | 33.9682 | 37.5058 | 45.7216 | 50.9243 | 58.5984 | 70.4153 | 83.3276 | 94.3714 | 103.8607 | 111.5693 | 117.3512 | 122.501 | 124.4378 | 122.8249 | 117.4653 | 109.5888 | 107.444 | 95.557 | 79.2877 | 64.3009 | 1908.4268
2018-05-13 | 52.3957 | 45.4136 | 40.7618 | 38.0307 | 37.4485 | 40.9637 | 49.3505 | 54.4823 | 62.0047 | 73.9434 | 86.0187 | 95.7057 | 104.9006 | 111.1743 | 115.9109 | 119.9123 | 121.9965 | 119.6818 | 113.0198 | 104.2426 | 102.9091 | 93.7813 | 78.5188 | 63.0593 | 1925.6265
2018-05-14 | 52.2942 | 45.3584 | 40.4784 | 37.7642 | 37.2555 | 38.6682 | 50.0681 | 54.2063 | 62.5401 | 75.7448 | 87.9608 | 100.0338 | 109.0506 | 114.9306 | 119.1576 | 119.03 | 117.7952 | 115.1439 | 108.0876 | 99.9987 | 100.5728 | 91.1826 | 77.105 | 62.06 | 1916.4876
2018-05-15 | 50.3416 | 43.2869 | 38.8284 | 36.4813 | 36.3965 | 39.8187 | 48.231 | 53.2118 | 60.1216 | 72.4023 | 84.066 | 90.4691 | 92.8997 | 92.4155 | 88.5433 | 84.1304 | 82.9436 | 82.7732 | 80.5217 | 76.8894 | 76.8894 | 71.2621 | 60.2123 | 48.9977 | 1592.1337
2018-05-16 | 39.7376 | 34.3443 | 31.0736 | 29.0849 | 28.7891 | 32.2984 | 40.1813 | 43.9048 | 46.7797 | 52.1927 | 57.0329 | 60.576 | 62.1891 | 63.3011 | 65.6304 | 66.9831 | 68.5141 | 66.9161 | 62.818 | 57.6796 | 55.6019 | 51.2253 | 44.1999 | 35.9743 | 1197.0279
2018-05-17 | 28.8833 | 24.6209 | 21.8752 | 20.3964 | 19.9602 | 20.4545 | 22.0561 | 25.2577 | 32.7186 | 41.4669 | 49.3094 | 55.7328 | 60.6489 | 65.318 | 69.9547 | 73.7122 | 76.122 | 75.6634 | 71.2522 | 63.9824 | 61.8758 | 57.8753 | 49.787 | 41.4669 | 1130.3907
2018-05-18 | 34.0842 | 28.9777 | 25.6709 | 23.5361 | 22.6034 | 22.7929 | 23.3604 | 26.0099 | 34.1184 | 44.746 | 54.2063 | 61.9218 | 68.6788 | 74.3867 | 79.7258 | 83.7018 | 86.6165 | 85.9536 | 80.5322 | 73.1208 | 72.2929 | 67.0405 | 56.3985 | 44.8791 | 1275.3552
2018-05-19 | 35.8271 | 30.1673 | 26.864 | 25.3048 | 25.3754 | 28.4699 | 35.6453 | 40.2109 | 47.4784 | 56.8122 | 66.1812 | 74.6492 | 82.2101 | 90.0356 | 95.4541 | 100.8193 | 103.7773 | 103.3011 | 98.4257 | 89.2713 | 86.1489 | 78.2288 | 65.0158 | 50.8409 | 1536.5147
2018-05-20 | 40.2926 | 33.764 | 30.2509 | 28.2021 | 27.6273 | 30.3411 | 37.2484 | 42.788 | 50.1757 | 59.9584 | 70.3368 | 79.3919 | 86.9652 | 93.4983 | 98.2633 | 102.1629 | 104.4697 | 103.4439 | 99.2864 | 89.847 | 87.0416 | 78.2495 | 64.6767 | 51.0413 | 1589.3229
2018-05-21 | 40.4636 | 33.8388 | 29.93 | 27.5474 | 26.9125 | 29.5982 | 36.6581 | 41.9883 | 48.4262 | 57.1743 | 66.448 | 75.1048 | 82.6881 | 91.1602 | 99.5314 | 105.4044 | 109.0261 | 107.5289 | 101.3722 | 91.4509 | 87.0307 | 79.2565 | 65.7821 | 51.6112 | 1585.9328
2018-05-22 | 39.9665 | 33.1685 | 28.7577 | 26.6039 | 26.2311 | 29.0786 | 36.1569 | 41.1061 | 48.5647 | 58.1783 | 69.252 | 80.5742 | 91.686 | 102.9922 | 111.8042 | 119.4771 | 124.3987 | 122.8768 | 115.9235 | 104.0993 | 97.6149 | 89.4372 | 73.0808 | 57.2628 | 1728.292
2018-05-23 | 44.6287 | 36.9847 | 32.139 | 29.4393 | 28.3826 | 30.8133 | 37.1699 | 43.5953 | 52.769 | 64.8367 | 78.4669 | 93.0125 | 106.1865 | 120.2071 | 130.8743 | 138.0773 | 140.4241 | 137.2537 | 127.6424 | 111.73 | 105.3203 | 96.52 | 81.9345 | 67.3666 | 1935.7746
2018-05-24 | 54.733 | 46.0544 | 39.7597 | 35.6942 | 33.5739 | 33.0069 | 33.5468 | 37.8433 | 50.4413 | 66.2669 | 82.1888 | 98.1937 | 112.6594 | 123.1622 | 129.7525 | 133.3214 | 133.1593 | 130.1259 | 119.9635 | 107.3348 | 102.151 | 93.227 | 80.3853 | 67.3378 | 1943.8834
2018-05-25 | 56.1178 | 47.3978 | 41.2712 | 37.4414 | 35.1927 | 34.358 | 34.7086 | 37.4414 | 47.3978 | 61.2883 | 77.9703 | 92.438 | 106.1263 | 115.6592 | 121.4802 | 124.8689 | 126.0088 | 121.3256 | 111.73 | 101.1132 | 97.881 | 89.9912 | 76.9715 | 64.8367 | 1861.0158
2018-05-26 | 53.2801 | 45.7691 | 40.5753 | 37.3341 | 35.6103 | 35.6383 | 36.3965 | 40.0553 | 52.5737 | 69.4566 | 86.4206 | 99.6364 | 111.4088 | 119.861 | 124.699 | 127.2462 | 127.3254 | 123.396 | 113.9544 | 103.1823 | 100.9721 | 91.7868 | 77.4547 | 62.4292 | 1916.4621
2018-05-27 | 51.0747 | 43.5644 | 38.9524 | 36.2555 | 35.3734 | 38.7118 | 46.0941 | 53.0498 | 63.1058 | 76.5923 | 90.7029 | 104.2068 | 114.6799 | 123.0195 | 127.9863 | 130.3529 | 126.5872 | 116.9713 | 108.2214 | 99.987 | 99.0534 | 90.6472 | 76.5411 | 60.886 | 1952.617
2018-05-28 | 49.4985 | 42.3377 | 38.0956 | 35.5475 | 34.9433 | 38.204 | 45.8562 | 51.9142 | 61.1784 | 73.2108 | 86.6056 | 101.2544 | 112.2376 | 121.6221 | 126.8638 | 128.3704 | 128.2246 | 123.1492 | 115.37 | 107.0079 | 104.386 | 95.1457 | 80.2804 | 65.1196 | 1966.4236
2018-05-29 | 52.735 | 44.6208 | 40.0849 | 37.4271 | 36.5095 | 39.5314 | 47.0682 | 53.135 | 61.0138 | 71.5686 | 83.3383 | 92.157 | 97.6612 | 101.3486 | 98.7742 | 95.9691 | 94.201 | 91.9887 | 89.9801 | 84.0231 | 83.4558 | 77.9084 | 67.0022 | 54.6378 | 1696.1398
2018-05-30 | 43.5721 | 36.3683 | 33.0607 | 31.0866 | 30.7289 | 33.601 | 40.3817 | 46.1815 | 54.8369 | 68.5238 | 81.7863 | 93.3739 | 102.9566 | 110.6445 | 115.282 | 118.3036 | 117.4526 | 111.1373 | 100.2329 | 91.6524 | 89.1608 | 81.9133 | 71.2127 | 60.4304 | 1763.881
2018-05-31 | 50.5743 | 42.7957 | 37.757 | 34.6328 | 33.4656 | 33.2628 | 34.6328 | 39.2304 | 51.8131 | 67.732 | 83.413 | 96.5315 | 105.4164 | 111.273 | 112.2624 | 111.3594 | 108.0876 | 101.0897 | 93.2609 | 85.3149 | 84.27 | 79.142 | 70.2583 | 59.5334 | 1727.1089
2018-06-01 | 50.5161 | 43.0409 | 38.4575 | 35.3943 | 33.7708 | 33.6893 | 34.3169 | 37.5345 | 47.9228 | 62.1799 | 76.623 | 88.3233 | 98.5069 | 105.765 | 109.5765 | 108.6234 | 104.0516 | 96.3821 | 88.1804 | 82.7519 | 82.6455 | 78.9859 | 69.3591 | 57.511 | 1664.1085
2018-06-02 | 47.7205 | 41.4593 | 38.0451 | 36.1992 | 36.4248 | 40.4784 | 48.1904 | 53.7079 | 59.065 | 65.5546 | 72.0543 | 75.8569 | 79.6632 | 82.2525 | 84.0124 | 83.9267 | 83.5199 | 81.5115 | 79.4754 | 77.2592 | 77.96 | 73.662 | 63.1058 | 51.6196 | 1532.7245
2018-06-03 | 42.0869 | 36.164 | 32.7186 | 30.7289 | 30.6123 | 34.016 | 41.3765 | 46.4044 | 51.4516 | 59.0021 | 67.0501 | 74.2253 | 79.6423 | 83.6696 | 85.3797 | 85.9428 | 83.8517 | 81.6171 | 77.8567 | 74.6492 | 75.6939 | 70.2583 | 60.2033 | 48.581 | 1453.1825
2018-06-04 | 39.0255 | 33.1887 | 29.7703 | 28.0594 | 28.0346 | 31.2107 | 38.0523 | 39.1278 | 49.2519 | 59.3711 | 68.4076 | 75.9282 | 81.2793 | 87.884 | 92.7758 | 96.1411 | 98.7393 | 99.2631 | 95.9004 | 88.2683 | 84.5925 | 78.5499 | 67.261 | 54.0256 | 1544.1082
2018-06-05 | 43.2715 | 36.6794 | 32.5115 | 30.0582 | 29.2935 | 31.9734 | 37.973 | 44.8086 | 54.9669 | 67.2035 | 80.9106 | 94.0307 | 104.6611 | 114.8679 | 122.1387 | 127.4706 | 129.7259 | 128.7285 | 122.4622 | 110.116 | 103.4082 | 93.1819 | 78.0323 | 61.793 | 1880.2669
2018-06-06 | 50.0267 | 41.6781 | 36.4177 | 33.2628 | 31.8412 | 34.0092 | 38.8867 | 45.872 | 58.0267 | 72.811 | 89.5589 | 106.1986 | 120.4124 | 131.6383 | 139.7456 | 144.3466 | 145.8685 | 143.0844 | 134.2551 | 120.6564 | 112.0642 | 102.7431 | 87.9389 | 73.7122 | 2095.0551
2018-06-07 | 60.886 | 51.6616 | 45.4846 | 41.7763 | 39.3037 | 38.4503 | 39.1644 | 44.0988 | 57.8575 | 74.3766 | 92.9449 | 110.583 | 122.799 | 131.6248 | 136.9387 | 138.3799 | 133.4295 | 126.0088 | 116.39 | 106.8748 | 100.5611 | 92.2581 | 79.8303 | 67.1459 | 2048.8284
2018-06-08 | 56.1353 | 47.7852 | 42.1476 | 37.5058 | 36.0866 | 35.5475 | 35.6453 | 38.7046 | 49.944 | 66.9639 | 85.0881 | 101.8911 | 112.3864 | 114.8428 | 112.0765 | 110.3617 | 107.141 | 103.7416 | 97.3377 | 89.8248 | 85.6935 | 79.4441 | 66.8682 | 55.5583 | 1768.7217
2018-06-09 | 44.8634 | 38.0235 | 33.5672 | 31.3743 | 31.0736 | 33.8524 | 39.2817 | 45.6504 | 55.663 | 69.0671 | 85.1097 | 102.7905 | 117.1865 | 129.6593 | 136.5146 | 134.4449 | 130.794 | 121.6995 | 111.3223 | 102.4113 | 97.534 | 89.3598 | 75.125 | 60.813 | 1917.181
2018-06-10 | 49.1043 | 41.6101 | 37.2769 | 34.6535 | 33.9887 | 36.8212 | 42.5054 | 50.3333 | 62.2629 | 76.0914 | 90.0467 | 103.5153 | 114.4295 | 120.6436 | 120.3097 | 112.1756 | 105.0444 | 101.7494 | 100.8898 | 94.8037 | 92.8208 | 84.1411 | 70.4644 | 57.0947 | 1832.7766
2018-06-11 | 46.8437 | 39.9591 | 35.4012 | 33.0406 | 32.5115 | 34.9502 | 40.7692 | 47.5833 | 58.1693 | 72.9908 | 87.4897 | 100.4555 | 108.9162 | 114.2544 | 108.9162 | 99.8 | 95.2941 | 93.906 | 91.9438 | 86.1164 | 83.381 | 77.8154 | 66.1527 | 54.0256 | 1710.6859
2018-06-12 | 44.0755 | 37.3841 | 33.3709 | 30.9889 | 30.4636 | 32.7253 | 38.2329 | 43.3408 | 49.0879 | 57.1478 | 68.108 | 80.8685 | 95.5112 | 109.3807 | 118.9917 | 121.1452 | 115.1063 | 105.8252 | 98.9719 | 92.1121 | 88.5433 | 81.0685 | 67.2802 | 54.4823 | 1694.2127
2018-06-13 | 44.1687 | 37.4199 | 33.2898 | 30.7289 | 30.2573 | 32.4781 | 37.2698 | 44.2076 | 55.2361 | 67.8476 | 81.079 | 94.7581 | 105.9697 | 111.8537 | 111.7177 | 105.2963 | 98.8788 | 92.2244 | 86.4532 | 78.3323 | 73.5817 | 68.9311 | 60.4122 | 50.433 | 1632.8253
2018-06-14 | 41.8444 | 35.7431 | 31.7225 | 29.4202 | 28.42 | 28.8205 | 30.2252 | 34.3854 | 44.6365 | 58.4284 | 73.0308 | 87.2163 | 98.7742 | 108.6234 | 113.2811 | 112.9203 | 106.9595 | 101.1132 | 92.2357 | 82.9649 | 79.5379 | 73.8227 | 64.5732 | 54.6205 | 1613.3199
2018-06-15 | 45.8166 | 39.7745 | 35.2413 | 32.625 | 31.8875 | 32.5448 | 33.7436 | 37.8217 | 49.2848 | 64.6861 | 79.8931 | 94.7923 | 107.6017 | 116.0999 | 121.1195 | 119.2215 | 112.6345 | 104.5893 | 96.3132 | 87.9937 | 86.3771 | 82.5817 | 71.7865 | 60.5305 | 1744.9603
2018-06-16 | 49.5232 | 42.7957 | 38.7337 | 36.2837 | 35.4639 | 38.0884 | 43.4409 | 49.3176 | 57.3957 | 68.1852 | 83.4023 | 99.1582 | 110.583 | 121.0809 | 128.5825 | 133.0919 | 135.8184 | 133.8893 | 124.3335 | 108.6356 | 101.5371 | 92.8434 | 78.0943 | 63.6086 | 1973.887
2018-06-17 | 51.5608 | 44.0289 | 38.7555 | 35.8131 | 34.7982 | 37.0274 | 42.4825 | 48.8423 | 57.2274 | 66.8874 | 76.8074 | 86.3662 | 94.9518 | 102.7431 | 105.4404 | 105.3924 | 103.3249 | 101.4664 | 97.719 | 91.6524 | 88.1145 | 83.5413 | 69.5443 | 56.2932 | 1720.7808
2018-06-18 | 45.2403 | 38.6391 | 34.6535 | 32.2253 | 31.8346 | 34.3374 | 40.159 | 46.524 | 55.8552 | 67.1268 | 80.3538 | 93.6907 | 101.2779 | 104.0277 | 102.2338 | 97.4301 | 92.1009 | 87.6539 | 83.381 | 79.2044 | 77.6092 | 73.5817 | 62.7253 | 51.1583 | 1613.024
2018-06-19 | 41.4367 | 35.6383 | 32.2718 | 30.3539 | 29.8661 | 32.3383 | 37.8361 | 43.9126 | 53.7422 | 66.1337 | 80.4902 | 92.6744 | 103.2298 | 111.1743 | 111.829 | 104.9125 | 98.6115 | 92.3368 | 86.1924 | 80.5322 | 77.5989 | 71.5191 | 61.4257 | 49.8696 | 1625.926
2018-06-20 | 40.3743 | 34.4266 | 30.7938 | 28.8645 | 28.3826 | 30.4765 | 35.4012 | 41.6932 | 51.8215 | 65.4883 | 79.6214 | 93.5096 | 104.7449 | 111.3594 | 109.4296 | 99.9754 | 94.1783 | 89.1277 | 84.9371 | 79.5692 | 76.4592 | 72.6813 | 63.8701 | 53.6308 | 1600.8164
2018-06-21 | 44.0134 | 37.8217 | 33.6757 | 31.3481 | 30.3475 | 30.7419 | 31.7291 | 36.7503 | 50.1012 | 66.7631 | 81.7969 | 96.727 | 109.2461 | 116.8069 | 114.5171 | 106.4761 | 99.7415 | 94.3941 | 88.0816 | 81.6806 | 78.5602 | 74.9123 | 66.2479 | 55.5932 | 1658.0733
2018-06-22 | 45.9433 | 40.0775 | 35.6243 | 32.9599 | 31.4858 | 31.4005 | 31.7885 | 36.7644 | 49.4409 | 66.4861 | 82.4117 | 95.4655 | 108.331 | 118.1764 | 124.6467 | 125.6544 | 121.4158 | 112.0889 | 100.7489 | 91.339 | 87.632 | 82.2525 | 71.4301 | 58.4015 | 1781.9658
2018-06-23 | 47.3737 | 41.2111 | 37.0843 | 34.6948 | 34.1868 | 36.9135 | 42.4901 | 49.754 | 61.2425 | 75.2265 | 91.518 | 107.1168 | 121.6737 | 133.8758 | 141.0347 | 142.6788 | 139.8148 | 133.6728 | 124.9212 | 113.2064 | 105.741 | 96.1411 | 81.6911 | 65.6399 | 2058.9034
2018-06-24 | 53.3399 | 45.3742 | 40.4487 | 37.3841 | 36.3895 | 38.7847 | 44.3322 | 51.586 | 63.8888 | 78.6017 | 96.2329 | 112.4608 | 127.2726 | 140.9652 | 149.3221 | 153.9752 | 154.8183 | 149.0791 | 141.6606 | 129.2733 | 122.6953 | 111.6682 | 94.6443 | 77.1358 | 2251.3333
2018-06-25 | 63.208 | 53.6822 | 47.1565 | 43.2869 | 41.8671 | 44.1143 | 49.6798 | 57.1832 | 70.0722 | 87.0634 | 106.4036 | 122.1775 | 137.0893 | 149.2506 | 156.9947 | 157.7725 | 151.3013 | 143.0424 | 132.93 | 120.1814 | 112.6221 | 103.1348 | 89.0062 | 72.5417 | 2311.7618
2018-06-26 | 59.4973 | 50.1095 | 44.1921 | 40.5753 | 39.2084 | 41.0911 | 46.6598 | 53.8624 | 66.7822 | 84.3344 | 103.0041 | 118.6984 | 131.4102 | 140.05 | 148.7651 | 151.6613 | 151.7333 | 147.1855 | 139.0964 | 126.3373 | 117.5414 | 107.2016 | 91.2496 | 74.185 | 2274.4314
2018-06-27 | 60.4577 | 51.7289 | 45.8482 | 42.2997 | 41.1586 | 43.5567 | 48.2635 | 55.3753 | 68.2625 | 84.797 | 101.1367 | 116.6426 | 126.8243 | 135.6957 | 143.5185 | 144.3747 | 141.3544 | 134.0654 | 121.3256 | 108.5625 | 101.7376 | 92.4943 | 81.3531 | 67.9536 | 2158.787
2018-06-28 | 55.1666 | 46.7077 | 41.3765 | 37.5632 | 35.3316 | 33.5672 | 38.4938 | 41.6101 | 55.4014 | 73.5516 | 89.5811 | 107.25 | 122.3715 | 132.1757 | 138.3248 | 142.9864 | 142.4274 | 139.1654 | 129.6859 | 117.0219 | 110.116 | 101.8911 | 88.8849 | 74.2959 | 2094.9478
2018-06-29 | 61.8298 | 53.0668 | 46.9639 | 42.8569 | 40.5678 | 39.6933 | 39.4138 | 42.9795 | 57.3248 | 76.951 | 97.0379 | 116.5415 | 132.4987 | 140.535 | 140.8958 | 135.5186 | 131.3566 | 124.7904 | 112.188 | 101.0191 | 94.5874 | 88.2024 | 76.4592 | 63.0314 | 2056.3098
2018-06-30 | 52.2434 | 44.7694 | 40.0257 | 37.3412 | 37.0131 | 39.9221 | 45.5161 | 51.6028 | 62.4847 | 78.1047 | 93.974 | 108.7088 | 121.171 | 132.243 | 139.193 | 142.6509 | 139.5797 | 128.1187 | 117.2878 | 107.6502 | 102.4705 | 94.8835 | 82.6881 | 68.079 | 2067.7213
2018-07-01 | 55.9951 | 48.1742 | 43.6185 | 40.9637 | 40.3446 | 43.3716 | 49.7458 | 55.2796 | 62.6512 | 73.6519 | 85.6827 | 98.5766 | 107.0321 | 110.9154 | 114.7551 | 116.4153 | 119.3237 | 117.516 | 112.7215 | 108.3432 | 106.054 | 97.084 | 82.6668 | 68.1273 | 1959.0096
2018-07-02 | 55.2535 | 47.8337 | 43.1946 | 40.7618 | 39.9961 | 42.4596 | 48.2554 | 54.5341 | 65.6494 | 81.0158 | 99.0185 | 112.3988 | 120.7721 | 121.8157 | 116.8954 | 112.312 | 111.1003 | 109.3562 | 105.9937 | 99.9637 | 97.7884 | 92.99 | 81.6277 | 67.1076 | 1968.094
2018-07-03 | 56.6272 | 48.8668 | 44.5427 | 41.7461 | 41.3013 | 43.7422 | 49.5479 | 56.0477 | 67.405 | 84.3344 | 103.9442 | 120.3739 | 132.5526 | 141.4101 | 148.8221 | 152.9752 | 151.3013 | 140.4934 | 129.1137 | 118.329 | 111.8785 | 104.6371 | 91.6972 | 76.7254 | 2258.415
2018-07-04 | 64.2259 | 54.7849 | 48.2554 | 44.06 | 41.905 | 41.852 | 42.7345 | 45.603 | 58.0088 | 78.084 | 98.6812 | 116.1377 | 127.2198 | 132.7547 | 134.662 | 134.1737 | 120.8493 | 105.4044 | 94.8835 | 85.8669 | 80.3643 | 73.6218 | 69.9938 | 62.642 | 1956.7684
2018-07-05 | 53.1692 | 45.603 | 40.8514 | 37.8433 | 36.4248 | 36.4813 | 37.3627 | 39.9443 | 49.6633 | 61.8022 | 77.3003 | 89.1056 | 99.3913 | 109.6255 | 110.9277 | 103.3368 | 96.543 | 91.9438 | 87.5006 | 82.9436 | 80.1233 | 75.8365 | 67.8957 | 57.9465 | 1669.5657
2018-07-06 | 49.3258 | 42.7957 | 38.5228 | 35.7151 | 34.8397 | 34.9848 | 35.5964 | 38.3705 | 49.3998 | 61.7838 | 73.9534 | 78.9444 | 84.1197 | 88.918 | 93.3852 | 94.0988 | 92.7983 | 89.3708 | 83.991 | 75.9792 | 74.4674 | 71.3312 | 62.6975 | 52.235 | 1537.6244
2018-07-07 | 44.1765 | 38.7046 | 35.5196 | 33.9819 | 33.9069 | 36.8354 | 42.3301 | 48.6381 | 58.6432 | 69.808 | 81.8922 | 90.2578 | 94.2577 | 97.3954 | 98.5069 | 101.7376 | 101.7376 | 101.2073 | 98.8672 | 95.8545 | 93.5662 | 88.2353 | 76.3774 | 63.1522 | 1725.5898
2018-07-08 | 51.9479 | 44.4257 | 39.6491 | 36.9989 | 36.2625 | 38.5519 | 44.0988 | 50.8826 | 61.5174 | 77.3518 | 94.3259 | 110.6445 | 124.19 | 130.6335 | 129.3664 | 121.8803 | 114.3169 | 107.8566 | 101.2779 | 92.8434 | 86.0947 | 78.8301 | 67.7512 | 56.1528 | 1897.8508
2018-07-09 | 46.1974 | 40.122 | 36.3895 | 32.8995 | 33.1887 | 36.4954 | 42.2692 | 48.4506 | 59.4432 | 75.4397 | 91.1379 | 107.6381 | 118.8896 | 122.2034 | 112.1756 | 104.3979 | 100.7371 | 95.4541 | 89.2271 | 85.6718 | 82.5924 | 85.2717 | 66.8969 | 55.5932 | 1768.782
2018-07-10 | 45.2403 | 38.9597 | 35.3803 | 33.4182 | 32.8458 | 35.3316 | 41.0461 | 47.8418 | 58.7418 | 73.1508 | 85.2177 | 93.8493 | 102.0683 | 108.0633 | 107.8202 | 103.8369 | 97.9273 | 91.6636 | 86.5947 | 81.427 | 80.0186 | 75.6736 | 66.1051 | 55.0277 | 1677.2497
2018-07-11 | 45.0595 | 38.9232 | 35.2274 | 33.3506 | 32.9129 | 35.1858 | 40.0997 | 47.004 | 59.5244 | 74.72 | 90.8032 | 106.3433 | 118.7111 | 129.0738 | 135.3144 | 136.8428 | 135.5186 | 130.8609 | 123.409 | 112.3864 | 106.0901 | 99.3913 | 87.0962 | 73.6017 | 2027.4507
2018-07-12 | 61.7287 | 53.4339 | 47.4945 | 43.9048 | 41.1886 | 41.2111 | 41.9125 | 45.3742 | 57.1566 | 75.2671 | 91.4509 | 107.0805 | 120.3739 | 127.9333 | 130.1793 | 129.7259 | 127.6821 | 120.9779 | 111.9156 | 99.987 | 94.1783 | 86.3771 | 75.7347 | 64.3854 | 1996.6538
2018-07-13 | 55.759 | 49.3916 | 45.0046 | 41.7007 | 39.5829 | 38.7628 | 38.9305 | 42.6657 | 55.8027 | 72.3326 | 87.6539 | 102.4587 | 113.8296 | 119.733 | 124.6598 | 128.1451 | 127.4971 | 122.7601 | 115.169 | 105.6808 | 100.6315 | 95.317 | 83.413 | 70.1505 | 1977.0322
2018-07-14 | 58.8225 | 50.9661 | 45.4136 | 42.4825 | 41.7158 | 44.0134 | 49.5809 | 56.0126 | 68.4173 | 84.4526 | 101.7022 | 117.0599 | 128.7285 | 131.9472 | 129.5261 | 128.2379 | 127.7085 | 127.4574 | 124.1639 | 113.5302 | 104.3262 | 94.7354 | 80.9211 | 66.6102 | 2118.532
2018-07-15 | 54.9496 | 47.4059 | 42.5511 | 39.5608 | 38.8721 | 41.2186 | 47.1083 | 53.1521 | 62.9757 | 77.9084 | 91.5964 | 103.9919 | 111.8166 | 111.8785 | 108.5015 | 102.4942 | 98.4141 | 95.5913 | 94.3827 | 89.8803 | 88.3782 | 83.6696 | 72.4421 | 60.0853 | 1818.8255
2018-07-16 | 50.0929 | 42.9412 | 38.3343 | 36.1429 | 35.8341 | 38.8867 | 46.1974 | 52.6501 | 64.6202 | 79.6945 | 93.2157 | 103.9681 | 110.8661 | 105.6568 | 99.7649 | 95.0317 | 90.8812 | 87.0634 | 84.5817 | 80.4482 | 81.0158 | 78.053 | 68.4947 | 57.2451 | 1721.6808
2018-07-17 | 47.6721 | 41.6479 | 37.2055 | 35.1026 | 34.9018 | 37.6852 | 43.7499 | 49.2437 | 62.1522 | 75.969 | 90.6138 | 104.0755 | 104.4099 | 102.1865 | 99.4497 | 103.9204 | 110.0669 | 110.7922 | 109.4051 | 103.7535 | 99.2398 | 92.8434 | 78.8508 | 65.7537 | 1840.6908
2018-07-18 | 53.2374 | 45.6504 | 40.9113 | 37.9225 | 36.8141 | 38.9889 | 43.9746 | 50.2669 | 62.8273 | 79.8931 | 97.1647 | 113.9794 | 128.5958 | 139.8701 | 146.9726 | 150.9274 | 150.9418 | 143.4344 | 129.7659 | 116.0495 | 107.7595 | 99.1349 | 85.9319 | 72.7212 | 2173.7357
2018-07-19 | 60.4759 | 51.5776 | 45.6899 | 42.1021 | 39.8778 | 39.7376 | 40.4933 | 44.3088 | 58.7687 | 77.4032 | 95.4769 | 112.188 | 125.5758 | 135.6276 | 139.8978 | 141.3683 | 144.8671 | 142.1762 | 131.5443 | 120.4766 | 114.1168 | 104.5414 | 90.8478 | 77.5783 | 2176.7178
2018-07-20 | 65.1763 | 56.2756 | 49.8035 | 45.4767 | 43.0409 | 42.0186 | 42.1324 | 44.574 | 57.902 | 77.2489 | 95.2028 | 114.2544 | 129.5794 | 140.2023 | 145.4308 | 142.4135 | 139.7318 | 135.505 | 126.4688 | 115.634 | 111.2113 | 103.551 | 90.7697 | 75.4803 | 2189.084
2018-07-21 | 62.679 | 54.1547 | 48.3286 | 44.8869 | 44.0522 | 46.4044 | 52.4381 | 58.3032 | 69.2228 | 84.9802 | 102.8617 | 118.8896 | 129.4862 | 131.3431 | 125.1959 | 119.0938 | 112.7091 | 107.0926 | 101.4782 | 95.3969 | 94.2237 | 85.9644 | 74.528 | 62.1522 | 2025.8655
2018-07-22 | 51.0998 | 44.0212 | 40.1887 | 37.5488 | 37.1627 | 40.4636 | 46.2849 | 52.4805 | 63.9449 | 78.1771 | 92.1346 | 103.3011 | 110.3002 | 114.3044 | 119.9123 | 123.2401 | 120.7078 | 113.306 | 106.9474 | 100.0455 | 98.1242 | 91.0039 | 78.4566 | 65.7537 | 1928.9099
2018-07-23 | 55.2014 | 47.9147 | 43.1331 | 40.2332 | 39.5093 | 41.9125 | 48.7034 | 54.3615 | 65.8486 | 78.7262 | 90.9481 | 101.2897 | 109.5275 | 117.6048 | 125.6807 | 129.9125 | 131.5175 | 130.166 | 129.127 | 119.9251 | 114.467 | 106.4278 | 90.7697 | 75.8263 | 2088.7335
2018-07-24 | 62.8365 | 53.5537 | 47.6559 | 44.1687 | 42.9642 | 45.1617 | 50.2752 | 56.4425 | 68.6885 | 85.8127 | 102.7549 | 87.9937 | 129.0472 | 135.6548 | 139.6073 | 143.4204 | 148.7365 | 145.6566 | 140.9097 | 129.646 | 119.7458 | 110.3739 | 92.8772 | 76.4694 | 2260.4533
2018-07-25 | 63.8234 | 54.1374 | 48.231 | 44.3711 | 42.5664 | 44.7303 | 49.8035 | 56.2668 | 70.4644 | 88.0157 | 105.2603 | 122.1258 | 132.8221 | 138.793 | 144.3606 | 149.6654 | 150.3961 | 145.0361 | 134.2008 | 121.4029 | 114.8679 | 105.1283 | 91.63 | 77.8774 | 2295.9769
2018-07-26 | 66.5529 | 57.7063 | 52.2265 | 47.7771 | 45.1459 | 44.7147 | 45.8324 | 48.8914 | 61.1144 | 79.4336 | 98.0315 | 111.3223 | 117.1738 | 120.4509 | 119.4771 | 115.8857 | 115.9235 | 113.2811 | 107.5167 | 99.7299 | 97.7305 | 90.0023 | 78.5706 | 68.5044 | 2002.9957
2018-07-27 | 58.3122 | 50.8075 | 45.8958 | 42.4444 | 40.6573 | 40.1516 | 40.5604 | 43.1792 | 57.7063 | 76.6639 | 94.2918 | 111.347 | 125.825 | 137.4868 | 145.2334 | 150.4966 | 152.2814 | 150.2527 | 141.3127 | 128.556 | 122.8768 | 113.6425 | 98.2285 | 82.7732 | 2250.9828
2018-07-28 | 68.6885 | 59.8679 | 53.6051 | 49.8531 | 48.8178 | 51.4684 | 57.254 | 63.2359 | 76.5104 | 95.1229 | 112.9825 | 130.8475 | 143.5886 | 155.8097 | 167.1506 | 173.625 | 175.9915 | 173.363 | 166.7727 | 154.1058 | 146.5616 | 134.6349 | 113.9669 | 93.9287 | 2667.7529
2018-07-29 | 77.7639 | 67.2323 | 60.1125 | 55.9339 | 54.1288 | 56.1441 | 61.6368 | 67.1076 | 80.7108 | 97.8578 | 115.546 | 132.391 | 144.0235 | 152.166 | 156.2627 | 153.062 | 149.9517 | 139.5797 | 127.3518 | 116.9334 | 112.6718 | 104.0635 | 89.1166 | 75.6431 | 2447.391
2018-07-30 | 63.208 | 55.506 | 49.9357 | 46.8277 | 45.6188 | 48.1011 | 54.6551 | 60.0853 | 72.5716 | 87.7634 | 101.2779 | 118.0365 | 133.0649 | 146.8592 | 154.3383 | 154.9493 | 146.0805 | 131.9875 | 122.268 | 113.0571 | 107.444 | 99.2864 | 84.5279 | 70.779 | 2268.2294
2018-07-31 | 58.5626 | 50.566 | 45.4372 | 42.513 | 41.5196 | 43.7035 | 49.7705 | 54.6724 | 65.1763 | 81.7969 | 101.0661 | 119.7586 | 132.7277 | 141.6049 | 144.7122 | 141.2154 | 130.5399 | 120.8621 | 112.9576 | 104.374 | 101.8438 | 94.7126 | 81.9981 | 68.5141 | 2130.6052
2018-08-01 | 57.8575 | 50.408 | 44.7538 | 42.3301 | 41.0236 | 43.4332 | 48.5973 | 55.4014 | 68.0115 | 85.7368 | 103.0397 | 119.2854 | 132.2161 | 141.6606 | 149.7369 | 154.1494 | 153.511 | 144.9375 | 132.6603 | 121.1452 | 116.5289 | 107.2985 | 92.1121 | 78.2495 | 2284.0844
2018-08-02 | 66.0481 | 56.7505 | 50.6409 | 46.5959 | 44.4101 | 44.2154 | 45.4925 | 48.3774 | 61.7103 | 80.05 | 97.9041 | 112.6097 | 124.6075 | 131.6248 | 138.0498 | 137.7613 | 135.5459 | 129.9258 | 120.1558 | 110.5707 | 106.9837 | 99.952 | 87.2163 | 75.1757 | 2152.374
2018-08-03 | 63.8421 | 55.6804 | 49.9357 | 46.277 | 44.1532 | 43.897 | 44.8321 | 46.2451 | 56.4425 | 70.6905 | 82.348 | 95.6714 | 102.3876 | 104.4218 | 105.1643 | 107.0079 | 108.5503 | 106.633 | 101.6432 | 96.8651 | 92.7307 | 85.1961 | 73.0808 | 60.7218 | 1844.4176
2018-08-04 | 50.0764 | 43.4795 | 39.4358 | 37.1342 | 36.9775 | 40.0775 | 46.3964 | 51.3761 | 61.6276 | 75.7347 | 90.9481 | 104.9605 | 108.9529 | 107.1289 | 100.8076 | 94.5647 | 88.5543 | 82.0828 | 78.084 | 75.1149 | 77.105 | 72.3127 | 63.4687 | 54.1202 | 1680.5211
2018-08-05 | 45.6583 | 40.2777 | 37.2769 | 35.6732 | 35.5894 | 38.2908 | 44.9575 | 50.7575 | 62.0231 | 77.6607 | 92.202 | 106.8264 | 119.1066 | 126.7452 | 125.1828 | 123.9945 | 125.1697 | 126.2584 | 122.0224 | 112.8333 | 108.7576 | 98.6347 | 83.2208 | 69.1255 | 2008.2451
2018-08-06 | 56.2668 | 48.5321 | 43.31 | 40.1664 | 39.5829 | 41.8368 | 47.7448 | 53.7765 | 66.6102 | 83.9481 | 101.1014 | 120.7335 | 135.124 | 147.7111 | 155.7512 | 156.4089 | 149.4937 | 142.1065 | 132.3506 | 122.9546 | 118.7876 | 108.9895 | 91.2049 | 76.1322 | 2280.6244
2018-08-07 | 62.5309 | 53.8624 | 48.4262 | 44.9732 | 43.7344 | 46.0941 | 52.2265 | 57.8753 | 71.965 | 90.4245 | 108.5625 | 127.1407 | 142.4693 | 153.453 | 155.7658 | 154.411 | 152.1948 | 148.3658 | 138.3936 | 127.3518 | 117.6048 | 104.6611 | 86.3336 | 70.9858 | 2359.8061
2018-08-08 | 58.4194 | 49.6963 | 44.7851 | 41.9352 | 40.6871 | 45.2797 | 49.0715 | 54.4391 | 63.6646 | 78.4773 | 93.4191 | 110.7183 | 127.3782 | 141.9252 | 149.6797 | 150.1523 | 147.5831 | 136.7744 | 123.9945 | 112.5973 | 108.6234 | 99.5897 | 86.475 | 75.0845 | 2190.4503
2018-08-09 | 61.885 | 53.4938 | 47.5994 | 43.9824 | 42.2616 | 42.2616 | 43.4101 | 46.9799 | 61.6552 | 81.4376 | 100.1509 | 117.8587 | 131.88 | 141.5631 | 148.4228 | 152.5414 | 151.964 | 143.2663 | 129.4462 | 116.6299 | 111.9156 | 102.1274 | 88.6424 | 76.951 | 2238.3263
2018-08-10 | 65.063 | 56.6624 | 50.2172 | 46.277 | 43.9668 | 43.1561 | 43.5258 | 45.6504 | 59.4522 | 78.934 | 97.8694 | 117.973 | 132.9165 | 144.6559 | 150.4392 | 151.5893 | 150.5684 | 146.5616 | 136.0093 | 122.9805 | 117.1612 | 105.2723 | 88.9952 | 73.6419 | 2269.5386
2018-08-11 | 60.6215 | 51.9142 | 46.3009 | 43.0332 | 42.0035 | 44.8086 | 50.8909 | 55.6543 | 67.5107 | 85.8777 | 104.7568 | 125.2875 | 141.9531 | 153.0041 | 155.8827 | 155.0804 | 155.5032 | 152.7727 | 144.6841 | 132.6064 | 127.8804 | 113.3932 | 96.7385 | 79.0483 | 2387.2068
2018-08-12 | 65.0253 | 56.1791 | 49.5726 | 45.7216 | 44.4881 | 46.8918 | 53.1009 | 58.4015 | 70.7003 | 88.3453 | 105.7891 | 122.8508 | 135.8593 | 146.3068 | 150.2097 | 149.9088 | 152.2526 | 150.6832 | 145.2475 | 133.6863 | 126.7452 | 113.3309 | 95.8202 | 79.8931 | 2387.01
2018-08-13 | 65.602 | 57.3248 | 51.2672 | 46.5081 | 45.3033 | 47.858 | 54.396 | 59.9222 | 73.5215 | 91.7644 | 109.9933 | 130.4731 | 146.2078 | 157.5816 | 163.4656 | 166.5462 | 166.5311 | 159.3488 | 148.5654 | 135.0696 | 129.6193 | 117.3132 | 99.2398 | 82.7626 | 2506.1845
2018-08-14 | 69.2228 | 60.5942 | 54.8456 | 51.2504 | 49.6798 | 51.6952 | 58.2229 | 63.4128 | 76.7972 | 95.8889 | 114.9808 | 131.0885 | 145.699 | 153.714 | 154.8474 | 144.5856 | 129.9658 | 119.2471 | 110.6076 | 103.5034 | 102.0801 | 92.7983 | 80.8369 | 66.9065 | 2282.4707
2018-08-15 | 55.9076 | 48.9814 | 43.9126 | 41.6781 | 41.0986 | 44.0833 | 51.0413 | 57.2451 | 70.3564 | 86.0078 | 102.3758 | 114.9933 | 124.9996 | 122.8638 | 105.5967 | 95.2142 | 88.5543 | 84.0875 | 78.6536 | 73.6118 | 74.2858 | 69.1449 | 62.2075 | 53.8452 | 1790.7461
2018-08-16 | 45.8166 | 40.8365 | 37.6062 | 35.5196 | 34.4747 | 34.8535 | 36.7928 | 40.0701 | 52.5568 | 72.7511 | 91.8317 | 107.0684 | 122.2422 | 125.0258 | 132.9839 | 126.9429 | 116.3269 | 105.753 | 96.1526 | 88.3123 | 86.2032 | 80.1861 | 71.6577 | 60.813 | 1842.7773
2018-08-17 | 51.6952 | 45.3978 | 40.9487 | 37.9658 | 36.7432 | 36.7999 | 38.1245 | 40.717 | 52.5737 | 71.7468 | 91.4956 | 108.9529 | 124.4248 | 138.0635 | 140.3825 | 137.7613 | 139.0964 | 138.5864 | 132.5256 | 122.8379 | 119.8482 | 109.3317 | 92.5055 | 74.5785 | 2123.1034
2018-08-18 | 62.3368 | 53.3912 | 47.7529 | 44.5115 | 43.8196 | 48.2879 | 56.4249 | 60.2396 | 69.8862 | 88.3013 | 107.6623 | 126.6794 | 141.8138 | 154.5418 | 160.4434 | 165.3105 | 166.0936 | 162.8977 | 156.0726 | 144.192 | 139.6073 | 123.2531 | 101.5607 | 84.2163 | 2509.2964
2018-08-19 | 68.9311 | 59.5244 | 53.1777 | 49.3094 | 48.166 | 51.9732 | 60.6215 | 64.179 | 74.6796 | 92.9336 | 110.7922 | 129.6992 | 145.6849 | 156.9801 | 163.7799 | 172.1023 | 176.4263 | 172.0102 | 163.8397 | 150.0234 | 144.5856 | 128.9409 | 106.9232 | 88.2353 | 2633.5187
2018-08-20 | 72.841 | 63.0314 | 56.6272 | 52.0322 | 50.5826 | 54.0084 | 62.3368 | 52.9731 | 75.7245 | 94.2237 | 112.0022 | 132.1623 | 145.8544 | 159.6295 | 165.3857 | 166.5311 | 166.0785 | 161.6311 | 152.1948 | 140.8958 | 135.9411 | 122.5528 | 103.0635 | 84.7001 | 2583.0037
2018-08-21 | 71.5587 | 61.9587 | 55.5757 | 51.6532 | 50.1012 | 53.7336 | 62.5494 | 66.6866 | 77.5783 | 94.5988 | 113.4181 | 132.8895 | 147.5547 | 160.7844 | 168.4235 | 176.3331 | 176.6128 | 165.1 | 153.3806 | 137.8986 | 134.472 | 119.8098 | 101.5018 | 83.3596 | 2617.5326
2018-08-22 | 68.427 | 59.4973 | 53.4339 | 49.7623 | 48.3042 | 51.67 | 60.3668 | 64.2915 | 74.811 | 93.2383 | 111.1496 | 129.5527 | 144.9234 | 156.4089 | 160.7696 | 170.2961 | 172.7936 | 165.9579 | 155.1387 | 139.5382 | 131.4102 | 116.2891 | 99.8818 | 84.6032 | 2562.5153
2018-08-23 | 70.5332 | 61.3524 | 54.3874 | 49.8283 | 47.1003 | 46.8597 | 48.1092 | 50.8409 | 64.4887 | 86.0078 | 106.3192 | 125.8381 | 141.5631 | 152.5992 | 157.6697 | 161.8245 | 164.2143 | 160.8734 | 150.4822 | 135.7639 | 128.9808 | 116.8575 | 102.7194 | 87.0853 | 2472.2984
2018-08-24 | 72.5517 | 62.5772 | 55.297 | 50.5161 | 47.7044 | 46.6438 | 46.7717 | 48.4669 | 62.818 | 83.766 | 102.7905 | 124.0336 | 141.8974 | 155.2407 | 163.5254 | 167.9229 | 168.378 | 165.8976 | 156.1018 | 143.1543 | 137.6789 | 121.6866 | 102.5297 | 85.1745 | 2513.1247
2018-08-25 | 72.5916 | 62.5957 | 57.1301 | 53.974 | 53.7937 | 58.6432 | 68.1852 | 72.1139 | 79.705 | 95.9806 | 113.0695 | 128.755 | 138.986 | 143.0844 | 143.9954 | 143.7428 | 144.5715 | 141.3405 | 131.9203 | 123.461 | 121.3513 | 107.3955 | 91.339 | 74.6391 | 2422.3643
2018-08-26 | 63.6086 | 56.2142 | 51.2839 | 48.4588 | 47.9552 | 52.2519 | 61.4716 | 65.0064 | 73.0508 | 89.1056 | 104.374 | 119.2087 | 130.1259 | 140.1608 | 147.0861 | 152.7437 | 155.6783 | 153.1633 | 144.6981 | 132.2699 | 127.8672 | 113.4804 | 93.1819 | 76.7562 | 2399.2014
2018-08-27 | 62.3553 | 53.5537 | 47.559 | 44.1066 | 42.8569 | 46.3885 | 54.9062 | 57.9643 | 66.83 | 83.766 | 99.8701 | 116.4531 | 130.5132 | 142.4274 | 151.8919 | 158.8028 | 162.9276 | 160.3545 | 151.8486 | 138.2423 | 133.9299 | 119.081 | 99.0883 | 82.4967 | 2408.2141
2018-08-28 | 68.4753 | 59.5154 | 53.246 | 49.2437 | 47.6317 | 51.3593 | 60.6762 | 64.2728 | 73.2609 | 87.2273 | 98.9603 | 109.4786 | 122.087 | 135.4642 | 148.0667 | 156.1749 | 159.7773 | 153.6415 | 141.4101 | 131.7591 | 126.0088 | 110.7307 | 93.4078 | 77.8671 | 2379.7425
2018-08-29 | 64.0385 | 55.8727 | 50.6159 | 47.1324 | 46.2213 | 49.9853 | 59.2359 | 64.0011 | 74.2959 | 92.7532 | 111.4334 | 126.3899 | 137.7338 | 148.865 | 156.9361 | 161.5716 | 160.014 | 149.9231 | 137.4456 | 125.4971 | 121.068 | 107.9903 | 93.5888 | 80.9632 | 2423.5721
2018-08-30 | 69.2422 | 60.7218 | 54.8369 | 50.7325 | 48.9896 | 50.6492 | 51.2504 | 53.3741 | 64.9781 | 85.0234 | 103.9084 | 123.0973 | 136.665 | 147.5405 | 155.8243 | 159.4521 | 158.9503 | 150.3101 | 135.614 | 123.539 | 119.1832 | 106.8022 | 93.6681 | 81.7546 | 2386.1072
2018-08-31 | 69.6322 | 60.4213 | 53.8709 | 50.0681 | 47.4542 | 46.3327 | 47.012 | 48.8995 | 62.0784 | 83.4344 | 101.172 | 118.1001 | 132.876 | 143.3504 | 148.1237 | 149.6797 | 146.4342 | 140.1746 | 127.3518 | 115.7598 | 112.4112 | 101.0544 | 87.9937 | 75.1352 | 2268.8206
2018-09-01 | 63.8701 | 56.6008 | 51.3091 | 47.5187 | 46.3088 | 47.0281 | 49.2519 | 50.2752 | 62.7717 | 83.9481 | 103.6701 | 124.1509 | 136.1458 | 145.6143 | 153.9752 | 156.8775 | 154.5418 | 148.7365 | 139.055 | 127.5103 | 124.0336 | 109.9319 | 92.2581 | 77.1461 | 2352.5296
2018-09-02 | 64.1228 | 55.663 | 50.035 | 46.8437 | 45.7849 | 49.5232 | 58.1783 | 61.8022 | 70.0917 | 86.5947 | 102.5416 | 120.0917 | 133.2674 | 141.6466 | 150.8987 | 156.365 | 157.5228 | 152.5125 | 141.577 | 129.8725 | 123.1882 | 105.7049 | 86.8453 | 70.1505 | 2360.8243
2018-09-03 | 57.5198 | 49.6386 | 44.8242 | 41.799 | 41.0086 | 44.5974 | 53.5195 | 56.9887 | 64.3947 | 78.1874 | 88.5543 | 100.0455 | 111.5076 | 124.1379 | 133.5782 | 136.8018 | 138.7654 | 134.2008 | 126.2453 | 116.2008 | 113.1939 | 100.3031 | 83.9695 | 67.8476 | 2107.8297
2018-09-04 | 55.9076 | 48.2067 | 43.4872 | 40.6946 | 39.9443 | 43.4564 | 52.6077 | 55.9076 | 61.1967 | 73.0508 | 86.562 | 98.4953 | 108.9651 | 119.2215 | 123.6431 | 125.5233 | 127.7878 | 124.3726 | 118.2909 | 112.8333 | 111.2976 | 98.4721 | 82.104 | 67.915 | 2019.9433
2018-09-05 | 56.1353 | 48.7687 | 44.3478 | 41.6856 | 41.2712 | 44.9889 | 54.7243 | 58.3479 | 66.3527 | 82.2843 | 99.1 | 115.3072 | 129.8058 | 141.2571 | 147.9244 | 148.3373 | 141.8834 | 129.2999 | 116.5794 | 108.2823 | 103.551 | 92.0672 | 80.1861 | 69.2617 | 2161.7496
2018-09-06 | 58.6163 | 52.0744 | 47.253 | 44.06 | 42.5588 | 42.5359 | 44.4101 | 47.551 | 58.1515 | 73.5917 | 86.6382 | 97.1762 | 103.5748 | 102.7312 | 100.7019 | 98.0662 | 93.0464 | 89.1056 | 84.6032 | 82.3162 | 82.3374 | 76.0608 | 68.6497 | 60.6944 | 1736.5048
2018-09-07 | 52.3788 | 45.4451 | 40.9861 | 38.0235 | 36.9278 | 37.12 | 38.6245 | 40.6125 | 49.9771 | 63.4967 | 76.9305 | 91.4509 | 104.1232 | 113.2188 | 117.5667 | 114.5922 | 109.4418 | 102.4942 | 92.5168 | 89.3598 | 89.2161 | 80.228 | 68.3302 | 56.7593 | 1749.8207
2018-09-08 | 48.0362 | 42.513 | 38.4503 | 36.1007 | 35.9532 | 40.1961 | 48.9732 | 52.4466 | 58.33 | 73.341 | 90.1133 | 106.054 | 119.4771 | 130.1126 | 138.146 | 141.577 | 141.2015 | 138.1185 | 127.0483 | 120.9393 | 116.769 | 102.222 | 85.4987 | 70.2387 | 2101.8563
2018-09-09 | 58.1515 | 50.126 | 45.3663 | 42.452 | 41.2788 | 44.7381 | 53.7165 | 57.1301 | 63.3104 | 77.2592 | 93.148 | 108.4772 | 122.1129 | 134.5399 | 140.3686 | 146.6466 | 145.1065 | 138.49 | 128.0127 | 119.797 | 114.2168 | 98.3329 | 81.3426 | 66.6388 | 2170.7593
2018-09-10 | 55.6368 | 48.9159 | 44.6365 | 41.7083 | 41.0911 | 45.0674 | 54.258 | 57.44 | 63.534 | 75.8467 | 91.1826 | 104.5295 | 116.9334 | 128.1054 | 134.7842 | 137.9261 | 136.6924 | 131.1019 | 122.0224 | 115.37 | 111.4581 | 95.992 | 79.914 | 65.1102 | 2099.2567
2018-09-11 | 53.8452 | 47.0521 | 42.4672 | 39.7007 | 39.0839 | 42.7574 | 51.8805 | 55.3579 | 60.8403 | 73.9233 | 86.8671 | 98.6812 | 107.7716 | 114.442 | 116.769 | 117.4906 | 113.1317 | 104.7449 | 97.3147 | 93.227 | 91.2049 | 80.879 | 69.896 | 57.7241 | 1857.0523
2018-09-12 | 46.5559 | 41.3389 | 37.793 | 36.0445 | 36.0445 | 40.0479 | 49.7045 | 52.6671 | 59.0021 | 70.2289 | 81.2898 | 91.1267 | 101.2779 | 111.3223 | 113.8795 | 112.8954 | 113.605 | 114.4545 | 106.7176 | 98.2865 | 94.9746 | 85.4446 | 75.3381 | 63.8327 | 1833.8728
2018-09-13 | 52.328 | 45.2797 | 40.5902 | 36.9847 | 35.5615 | 35.4291 | 37.3627 | 40.0701 | 48.7524 | 62.6049 | 78.8508 | 94.7695 | 107.808 | 116.2386 | 119.7074 | 119.3109 | 114.4045 | 107.5653 | 96.4396 | 90.9705 | 87.6101 | 77.4238 | 66.0766 | 55.2361 | 1767.3749
2018-09-14 | 47.1726 | 41.0761 | 36.942 | 34.2689 | 32.7253 | 32.4715 | 33.513 | 34.9848 | 44.9575 | 60.1035 | 76.0506 | 92.3031 | 105.2723 | 114.3044 | 118.9917 | 120.5793 | 120.8235 | 114.705 | 104.1709 | 98.1937 | 95.0545 | 83.7981 | 71.1042 | 57.7863 | 1771.3526
2018-09-15 | 48.5647 | 42.2692 | 38.5737 | 36.5661 | 36.4883 | 40.3966 | 49.1453 | 52.837 | 59.3981 | 73.9736 | 93.3287 | 109.1361 | 123.0065 | 135.614 | 144.7544 | 150.9849 | 152.1082 | 147.9813 | 137.7201 | 130.1259 | 124.6075 | 107.9174 | 90.6249 | 71.9948 | 2198.1174
2018-09-16 | 58.8763 | 51.2588 | 45.7137 | 42.3453 | 41.4217 | 44.7929 | 53.8452 | 57.2894 | 63.7206 | 77.4959 | 93.906 | 110.0914 | 123.0714 | 133.0919 | 131.2895 | 125.7987 | 121.3771 | 116.2891 | 110.6445 | 108.4528 | 104.1829 | 90.6583 | 76.2752 | 62.4477 | 2044.3362
2018-09-17 | 50.8242 | 44.2232 | 39.8261 | 37.1699 | 36.9562 | 40.9936 | 50.4247 | 53.8023 | 59.065 | 69.5443 | 83.8517 | 95.5112 | 104.3501 | 109.185 | 114.6048 | 114.2794 | 106.6451 | 98.1473 | 92.4718 | 93.4191 | 91.8204 | 81.9557 | 68.737 | 55.5932 | 1793.4013
2018-09-18 | 46.4044 | 40.0109 | 36.8283 | 34.7086 | 34.5296 | 38.385 | 47.6317 | 50.9661 | 56.2932 | 67.3762 | 78.8612 | 91.574 | 104.4697 | 116.8828 | 126.0088 | 131.2627 | 129.4862 | 130.2861 | 119.0938 | 112.6594 | 107.0926 | 93.3739 | 77.898 | 63.1058 | 1935.1888
2018-09-19 | 52.0744 | 44.7851 | 40.6125 | 38.0379 | 37.5775 | 41.2863 | 50.6409 | 54.8456 | 60.3849 | 72.8709 | 84.066 | 91.3838 | 93.6115 | 89.9579 | 83.9052 | 81.1422 | 78.6536 | 76.2343 | 73.4012 | 74.4674 | 73.2509 | 67.1651 | 58.8943 | 50.2918 | 1569.5413
2018-09-20 | 42.2768 | 37.1984 | 34.0092 | 32.305 | 31.453 | 32.2984 | 34.9295 | 38.4865 | 45.5951 | 57.511 | 69.1741 | 79.0795 | 86.7799 | 91.9999 | 92.6068 | 84.5602 | 78.115 | 74.9832 | 70.1701 | 71.2127 | 70.1701 | 63.1987 | 55.2014 | 47.2932 | 1420.6076
2018-09-21 | 40.3297 | 34.971 | 31.6633 | 29.6045 | 28.7389 | 28.9588 | 30.5799 | 32.4781 | 40.2555 | 53.7508 | 67.7127 | 82.0086 | 94.4055 | 103.551 | 109.9319 | 112.3864 | 112.0394 | 107.4925 | 97.6034 | 93.1931 | 88.4552 | 76.3774 | 64.3384 | 51.8973 | 1612.7235
2018-09-22 | 42.8493 | 37.0986 | 33.513 | 32.0727 | 32.4248 | 36.9562 | 45.8166 | 50.1426 | 55.9864 | 67.261 | 79.5484 | 91.1602 | 100.3617 | 102.3285 | 99.8467 | 96.727 | 94.9746 | 91.5852 | 89.5036 | 90.7586 | 86.5294 | 75.3381 | 62.6234 | 50.8659 | 1646.2724
2018-09-23 | 41.8822 | 36.2203 | 32.6517 | 30.8653 | 31.054 | 35.7501 | 45.6109 | 50.2089 | 52.5992 | 59.7412 | 65.1574 | 71.8955 | 76.9715 | 78.084 | 78.6536 | 79.9244 | 81.6594 | 84.5064 | 82.6349 | 85.1205 | 82.9436 | 73.0108 | 61.4899 | 49.7045 | 1468.3403
2018-09-24 | 40.717 | 35.3108 | 32.7788 | 30.8588 | 30.6641 | 35.2205 | 44.8008 | 49.2684 | 53.0157 | 60.2759 | 67.6261 | 75.3178 | 80.6897 | 87.4678 | 95.4427 | 101.9619 | 102.5771 | 99.9052 | 95.2941 | 95.2142 | 92.6406 | 82.3586 | 68.5431 | 56.6624 | 1614.6121
2018-09-25 | 47.3012 | 40.9787 | 37.0986 | 34.7569 | 34.6191 | 37.7786 | 45.201 | 50.1509 | 56.3634 | 68.3496 | 81.1844 | 90.2022 | 95.2142 | 99.7532 | 105.9576 | 111.1496 | 107.4076 | 97.6843 | 91.3055 | 90.3133 | 86.9216 | 76.582 | 64.4417 | 53.8624 | 1704.5774
2018-09-26 | 44.9732 | 39.4505 | 36.0445 | 34.0911 | 34.0501 | 38.3125 | 47.5671 | 52.4127 | 56.5744 | 64.8556 | 76.2752 | 90.2022 | 101.4193 | 113.0322 | 117.1992 | 117.5921 | 113.3558 | 105.3203 | 97.2685 | 96.0493 | 91.5516 | 82.3799 | 71.114 | 67.6646 | 1788.7558
2018-09-27 | 55.6543 | 45.6109 | 41.8368 | 39.2157 | 38.2185 | 38.6536 | 40.9038 | 43.7886 | 53.7336 | 69.9351 | 85.1853 | 100.6901 | 113.7048 | 122.9676 | 129.6193 | 129.9525 | 121.6221 | 113.1317 | 102.1274 | 99.4497 | 93.2609 | 84.0875 | 72.8909 | 61.3249 | 1897.5657
2018-09-28 | 51.8805 | 45.5082 | 41.0836 | 38.1462 | 36.8212 | 36.9989 | 38.4865 | 41.0986 | 49.8118 | 65.318 | 81.0158 | 96.658 | 110.8045 | 121.3642 | 128.1849 | 130.3262 | 127.3782 | 118.9662 | 106.7781 | 106.5364 | 101.9501 | 89.7251 | 75.1352 | 61.1327 | 1901.1089
2018-09-29 | 51.5188 | 44.3945 | 40.5157 | 38.1462 | 38.1534 | 42.1704 | 51.4936 | 55.7416 | 61.2791 | 74.8515 | 90.7252 | 107.6259 | 118.6474 | 128.2511 | 133.1863 | 133.1458 | 129.7792 | 120.8878 | 111.3223 | 107.5046 | 96.4396 | 83.8195 | 69.3007 | 56.6096 | 1985.5098
2018-09-30 | 46.6278 | 40.5678 | 37.0202 | 34.9779 | 34.9571 | 39.1205 | 49.4245 | 53.1521 | 59.5154 | 72.6215 | 86.7254 | 99.6364 | 110.5461 | 114.2794 | 117.7317 | 112.3368 | 111.6064 | 109.9933 | 104.0277 | 104.7449 | 100.1275 | 88.4773 | 73.9132 | 60.0853 | 1862.2161
2018-10-01 | 49.9688 | 43.3716 | 39.804 | 37.6995 | 37.3555 | 41.8217 | 52.1336 | 55.9339 | 62.6327 | 76.0302 | 89.5146 | 103.7058 | 115.7347 | 125.0127 | 129.1004 | 136.2141 | 140.4795 | 136.1731 | 126.0744 | 121.171 | 114.6674 | 100.1977 | 82.4011 | 73.873 | 2091.0709
2018-10-02 | 57.7241 | 48.5239 | 43.9203 | 41.1061 | 40.3966 | 44.1921 | 53.8366 | 57.4666 | 64.4699 | 79.1212 | 95.3398 | 109.7971 | 122.268 | 135.6548 | 143.1683 | 148.5654 | 151.7622 | 146.3776 | 134.4178 | 128.5162 | 120.9908 | 104.6132 | 87.7196 | 70.8479 | 2230.796
2018-10-03 | 58.7059 | 50.9661 | 45.3663 | 42.2921 | 41.1211 | 44.5349 | 53.8366 | 58.1337 | 65.991 | 81.744 | 98.6812 | 115.4831 | 127.5763 | 141.2988 | 148.5083 | 152.4547 | 152.267 | 140.1469 | 123.552 | 114.8178 | 103.825 | 91.1491 | 77.7948 | 65.4599 | 2195.7066
2018-10-04 | 54.8109 | 47.0682 | 42.4367 | 39.3477 | 37.8865 | 38.3922 | 40.6797 | 43.6416 | 54.2839 | 69.9743 | 83.2208 | 95.7057 | 106.9111 | 113.9045 | 116.5163 | 114.9557 | 109.5765 | 101.714 | 91.9326 | 90.2911 | 85.0234 | 75.4295 | 64.4605 | 53.9311 | 1772.0944
2018-10-05 | 44.0522 | 36.5944 | 31.453 | 27.6888 | 25.7125 | 25.199 | 26.0816 | 26.9429 | 31.6567 | 39.355 | 47.6882 | 54.0514 | 61.3432 | 68.1563 | 74.0944 | 78.5913 | 83.0715 | 81.3004 | 74.5583 | 74.0138 | 70.3368 | 60.8768 | 50.3333 | 40.2184 | 1233.3701
2018-10-06 | 32.9062 | 28.1711 | 25.4639 | 24.1128 | 24.4297 | 28.6324 | 36.7148 | 40.538 | 44.4491 | 52.1336 | 60.5305 | 68.5044 | 77.3518 | 84.1948 | 91.3502 | 93.6341 | 96.187 | 92.6181 | 89.0614 | 92.7645 | 87.0525 | 75.5515 | 63.6273 | 51.5524 | 1461.5319
2018-10-07 | 41.9656 | 36.6865 | 33.4588 | 31.4661 | 31.028 | 34.7775 | 44.0988 | 48.6952 | 50.8576 | 58.9841 | 68.3882 | 75.4194 | 81.4059 | 86.5947 | 89.2492 | 88.0376 | 87.884 | 85.791 | 84.2055 | 88.3233 | 83.6482 | 75.6125 | 62.5957 | 49.3752 | 1518.5486
2018-10-08 | 40.6051 | 35.3734 | 31.8479 | 30.1609 | 30.3539 | 34.6122 | 44.0212 | 47.9066 | 52.066 | 62.2629 | 74.7301 | 85.9753 | 97.1301 | 106.1624 | 113.8046 | 117.3385 | 117.0346 | 113.2686 | 106.5726 | 106.633 | 100.5728 | 87.8402 | 73.3811 | 60.1035 | 1769.7575
2018-10-09 | 49.1289 | 42.7421 | 38.5591 | 35.6173 | 35.165 | 34.3648 | 47.4865 | 51.3342 | 56.4425 | 69.2617 | 82.6562 | 95.4655 | 105.6448 | 115.8857 | 123.1363 | 128.0525 | 128.9277 | 124.19 | 113.867 | 111.6558 | 104.3501 | 90.7697 | 76.6537 | 61.7195 | 1923.0766
2018-10-10 | 50.3167 | 42.8186 | 38.6173 | 35.7291 | 35.2205 | 38.7337 | 47.7286 | 52.066 | 57.6619 | 70.7593 | 84.9263 | 96.75 | 107.7959 | 117.3765 | 124.1118 | 128.7683 | 129.6992 | 123.2142 | 110.4969 | 106.1745 | 98.2169 | 86.7581 | 74.7402 | 62.8922 | 1921.5728
2018-10-11 | 52.2519 | 45.0909 | 40.7916 | 37.7067 | 36.0304 | 36.1148 | 38.1028 | 40.2332 | 49.5232 | 66.0386 | 81.4692 | 95.6599 | 107.347 | 116.6426 | 123.1752 | 127.4178 | 128.2379 | 122.6823 | 109.1728 | 103.3487 | 95.4427 | 83.9803 | 73.311 | 61.5174 | 1871.289
2018-10-12 | 51.7037 | 44.3789 | 39.2011 | 36.1148 | 34.6741 | 34.406 | 35.7921 | 36.8567 | 46.6118 | 63.8421 | 79.7258 | 94.3486 | 107.6259 | 116.6552 | 122.8379 | 126.2321 | 126.6136 | 121.7253 | 110.3739 | 109.4174 | 101.6197 | 88.8077 | 76.3672 | 63.1244 | 1869.0559
2018-10-13 | 52.9902 | 46.2531 | 42.2388 | 39.9443 | 39.9961 | 44.231 | 53.2118 | 57.2009 | 62.7068 | 75.196 | 90.5247 | 103.6939 | 113.4056 | 121.5318 | 127.1802 | 130.9412 | 130.433 | 125.1174 | 115.2318 | 114.7927 | 106.4519 | 93.5209 | 78.9651 | 64.6955 | 2030.4549
2018-10-14 | 53.768 | 47.3656 | 43.6339 | 41.2036 | 40.6349 | 45.0438 | 55.3666 | 59.5966 | 65.2141 | 78.3634 | 92.1234 | 104.4458 | 113.5302 | 123.6561 | 129.2999 | 130.8475 | 127.7746 | 119.9891 | 113.2064 | 114.8804 | 105.6087 | 91.9662 | 76.91 | 62.3091 | 2036.7379
2018-10-15 | 50.2421 | 43.1331 | 39.1644 | 36.7786 | 36.8283 | 40.8514 | 50.3831 | 55.0363 | 59.9675 | 70.9563 | 82.0722 | 93.3287 | 81.6806 | 108.4893 | 110.3985 | 111.7919 | 108.4406 | 103.1942 | 96.9803 | 98.4605 | 90.4357 | 78.8924 | 64.8085 | 52.2857 | 1764.6002
2018-10-16 | 42.3301 | 36.2907 | 32.7855 | 30.4959 | 29.5028 | 32.2851 | 39.7154 | 42.4748 | 45.3269 | 52.6925 | 60.1579 | 66.2955 | 72.9508 | 80.0291 | 86.6382 | 93.4305 | 97.3839 | 95.3741 | 87.5334 | 86.8126 | 79.7154 | 68.0404 | 55.3579 | 43.3331 | 1456.9526
2018-10-17 | 34.0911 | 28.42 | 25.4521 | 23.7921 | 23.3887 | 26.3691 | 33.3303 | 36.6794 | 40.1887 | 47.1405 | 54.0686 | 60.7309 | 66.5338 | 73.5315 | 80.6267 | 87.271 | 90.5692 | 87.5663 | 78.4048 | 75.3686 | 67.809 | 58.0088 | 49.3669 | 40.3297 | 1289.0379
2018-10-18 | 33.3844 | 27.7381 | 24.476 | 22.7092 | 21.9299 | 22.6312 | 24.842 | 27.2413 | 33.7504 | 43.2561 | 52.0576 | 59.895 | 68.1659 | 75.7958 | 83.0395 | 88.8077 | 90.9593 | 87.6101 | 78.3634 | 75.9384 | 68.6982 | 59.2359 | 50.9577 | 41.8898 | 1263.3727
2018-10-19 | 34.6122 | 29.3949 | 25.8788 | 23.8664 | 23.0505 | 23.0842 | 24.5803 | 26.0696 | 32.7855 | 42.9719 | 52.9391 | 62.1614 | 72.3824 | 80.6897 | 87.6758 | 91.955 | 93.4418 | 90.1022 | 82.869 | 83.4665 | 76.8484 | 65.6683 | 54.993 | 44.4647 | 1325.9515
2018-10-20 | 36.1358 | 30.6317 | 27.5843 | 26.0577 | 26.1473 | 29.6618 | 37.2341 | 41.4593 | 46.4602 | 56.9799 | 68.1659 | 78.3426 | 87.4568 | 94.8949 | 101.8556 | 103.9323 | 102.4942 | 97.6959 | 93.069 | 94.724 | 86.5403 | 74.4977 | 61.8482 | 49.9027 | 1553.7722
2018-10-21 | 40.4487 | 35.2066 | 32.3316 | 30.5864 | 30.716 | 34.6672 | 43.8196 | 48.8014 | 50.7742 | 57.4666 | 65.3653 | 70.3761 | 73.883 | 75.6125 | 76.0302 | 76.3978 | 75.6227 | 74.1246 | 74.0742 | 78.4566 | 72.9209 | 64.4887 | 53.7851 | 42.5588 | 1378.5147
2018-10-22 | 34.9641 | 30.2445 | 27.6642 | 26.4352 | 26.7247 | 30.148 | 39.6049 | 44.6208 | 46.7877 | 52.7435 | 60.7582 | 69.2422 | 75.8161 | 81.67 | 86.0729 | 88.6204 | 87.1289 | 83.4451 | 81.7546 | 84.5709 | 78.5499 | 68.8631 | 56.9711 | 45.5082 | 1408.9095
2018-10-23 | 36.9989 | 32.4581 | 29.5727 | 27.8923 | 27.7073 | 31.3415 | 40.5455 | 45.5398 | 46.7877 | 51.8468 | 57.9554 | 63.2825 | 67.8765 | 70.8873 | 73.7222 | 75.0439 | 74.2757 | 72.1537 | 70.5823 | 73.4312 | 70.8184 | 62.7809 | 52.6331 | 42.7727 | 1298.9065
2018-10-24 | 35.1927 | 30.483 | 27.9047 | 26.8034 | 27.1498 | 30.5411 | 38.2257 | 43.387 | 46.6598 | 53.2118 | 58.9482 | 63.1894 | 65.3464 | 67.7031 | 69.5346 | 71.2029 | 71.0253 | 68.8146 | 66.9639 | 67.9825 | 62.9664 | 56.7505 | 49.9771 | 41.4217 | 1241.3855
2018-10-25 | 33.3168 | 28.0222 | 24.7837 | 22.8487 | 22.1771 | 22.6869 | 24.8012 | 27.5658 | 33.3709 | 42.1324 | 50.0846 | 56.3546 | 62.0231 | 67.4819 | 71.6973 | 74.8212 | 74.892 | 71.1436 | 64.5638 | 63.6926 | 57.991 | 51.4013 | 44.7068 | 36.8567 | 1129.4166
2018-10-26 | 30.4313 | 26.0636 | 23.5588 | 21.8806 | 21.2073 | 21.3422 | 22.7036 | 24.877 | 30.0325 | 38.6318 | 46.8998 | 53.5452 | 59.5064 | 65.6115 | 70.7101 | 74.72 | 76.5411 | 73.9233 | 68.0501 | 69.8276 | 63.6833 | 54.2839 | 44.2777 | 34.4953 | 1116.8038
2018-10-27 | 27.3513 | 23.2193 | 20.971 | 19.9916 | 20.333 | 23.7636 | 31.3022 | 36.0024 | 38.5664 | 45.4451 | 52.888 | 60.0309 | 66.2574 | 73.1508 | 79.3398 | 85.1961 | 88.3013 | 85.9644 | 81.2371 | 83.2208 | 75.1555 | 63.5153 | 51.5356 | 40.0183 | 1272.7572
2018-10-28 | 31.9866 | 27.2291 | 24.4066 | 23.028 | 23.1011 | 26.7671 | 34.9779 | 39.4578 | 42.3834 | 50.7325 | 59.074 | 67.5973 | 74.9832 | 84.5387 | 91.7532 | 97.0955 | 99.7065 | 96.6465 | 90.3467 | 92.0336 | 83.2422 | 72.0643 | 59.029 | 46.9078 | 1439.0884
2018-10-29 | 38.139 | 32.5448 | 29.0533 | 27.2046 | 27.1985 | 30.69 | 39.7597 | 43.9281 | 46.7637 | 57.2009 | 66.4957 | 75.7143 | 84.894 | 92.9561 | 99.5664 | 105.4164 | 106.5847 | 101.1956 | 92.9674 | 92.99 | 84.6785 | 73.1808 | 60.04 | 47.4059 | 1556.5684
2018-10-30 | 37.2912 | 31.6698 | 28.1462 | 26.2491 | 26.0278 | 29.4075 | 37.8074 | 42.2768 | 45.0203 | 54.1891 | 64.7426 | 74.0037 | 82.2843 | 89.2713 | 93.4305 | 96.6925 | 98.9603 | 94.6329 | 88.8959 | 90.0578 | 82.0192 | 71.9551 | 59.7593 | 47.858 | 1492.6488
2018-10-31 | 38.1534 | 32.325 | 28.5386 | 26.6945 | 26.3091 | 29.6555 | 38.1173 | 42.811 | 45.8799 | 54.8369 | 63.7019 | 72.2232 | 78.8093 | 83.5413 | 87.1289 | 89.8692 | 90.4691 | 84.797 | 74.9629 | 69.8276 | 60.5942 | 53.118 | 44.8008 | 36.326 | 1353.4904
2018-11-01 | 28.7327 | 24.0553 | 21.5481 | 20.2119 | 19.7309 | 20.275 | 22.6479 | 25.199 | 30.7289 | 38.139 | 44.0056 | 46.8277 | 47.9228 | 47.8904 | 48.2229 | 48.4425 | 47.7448 | 45.1931 | 43.4487 | 45.9592 | 42.0338 | 37.3412 | 32.033 | 26.9186 | 855.2529
2018-11-02 | 85.4013 | 18.8015 | 18.3628 | 18.3277 | 18.9133 | 20.7039 | 24.0381 | 30.7938 | 37.3484 | 40.159 | 40.5604 | 39.7818 | 39.0693 | 37.9586 | 37.4629 | 36.9349 | 37.1413 | 40.2852 | 46.8437 | 44.9418 | 41.6781 | 36.3895 | 30.1545 | 25.0465 | 847.0984
2018-11-03 | 21.1589 | 19.9968 | 19.3585 | 19.6012 | 21.0138 | 26.1713 | 35.8201 | 40.0405 | 41.1661 | 42.6198 | 44.4023 | 45.7611 | 45.9195 | 46.1656 | 45.6504 | 44.8634 | 45.5635 | 48.6626 | 55.4973 | 53.2033 | 48.8586 | 41.8368 | 34.221 | 27.5474 | 915.0999
2018-11-04 | 23.2813 | 20.7306 | 19.3637 | 19.102 | 19.7465 | 23.6952 | 30.8653 | 36.4954 | 41.2337 | 45.0752 | 48.9404 | 52.4296 | 54.1288 | 55.6892 | 56.5304 | 57.2097 | 56.1265 | 57.902 | 65.0253 | 62.7717 | 57.653 | 48.9814 | 40.9188 | 33.4317 | 1027.3273
2018-11-05 | 27.8491 | 24.2969 | 22.5478 | 21.7222 | 22.2709 | 26.1114 | 33.7096 | 36.4813 | 43.897 | 51.628 | 57.8753 | 62.9386 | 66.3908 | 68.1176 | 68.7758 | 67.4819 | 65.3369 | 67.0022 | 73.6017 | 70.2682 | 64.7331 | 56.4689 | 46.4044 | 37.1413 | 1183.051
2018-11-06 | 30.4572 | 26.3391 | 23.8321 | 22.5533 | 22.7482 | 26.6643 | 34.016 | 39.9369 | 46.5081 | 54.3701 | 62.6327 | 69.896 | 75.7143 | 80.1547 | 82.3162 | 82.157 | 78.5188 | 75.1149 | 78.747 | 73.321 | 64.9875 | 54.8456 | 44.2232 | 35.2552 | 1285.3093
2018-11-07 | 28.4137 | 24.3489 | 21.9518 | 21.0514 | 21.2666 | 24.6209 | 32.1257 | 37.3698 | 43.4795 | 50.7992 | 57.7596 | 64.2915 | 69.7494 | 74.3261 | 76.3263 | 75.8976 | 71.836 | 68.6206 | 70.7495 | 63.9636 | 57.2363 | 49.7458 | 42.5511 | 35.5266 | 1184.0078
2018-11-08 | 29.3441 | 25.1872 | 22.4978 | 21.3747 | 21.1481 | 22.1111 | 24.5281 | 29.5982 | 39.5681 | 48.5484 | 55.2014 | 60.7491 | 65.6209 | 67.7031 | 67.3954 | 65.148 | 61.9955 | 63.0129 | 65.2802 | 59.6057 | 54.0256 | 47.7771 | 41.497 | 34.7224 | 1093.6401
2018-11-09 | 29.3568 | 25.1696 | 22.8543 | 21.6841 | 21.2127 | 21.8752 | 23.5417 | 27.2291 | 34.9848 | 41.6252 | 45.5793 | 47.9795 | 48.2798 | 47.0762 | 45.8403 | 43.9203 | 43.4872 | 47.8985 | 51.931 | 48.9732 | 44.7616 | 38.967 | 33.2359 | 26.9915 | 884.4548
2018-11-10 | 22.4424 | 20.0911 | 18.8879 | 18.3929 | 19.005 | 21.815 | 29.3822 | 36.1148 | 39.355 | 43.4718 | 46.7557 | 49.7375 | 51.9648 | 53.9568 | 54.9496 | 55.7503 | 54.8456 | 56.2844 | 61.7746 | 57.7507 | 51.7205 | 43.9901 | 36.4742 | 29.2745 | 974.1872
2018-11-11 | 23.4793 | 20.3805 | 18.7914 | 18.2177 | 18.6244 | 20.9924 | 26.0935 | 31.8611 | 37.377 | 42.6275 | 46.7717 | 49.8613 | 52.803 | 55.5932 | 56.9181 | 58.1515 | 57.0771 | 57.653 | 63.0036 | 59.2269 | 53.1095 | 45.3112 | 37.2698 | 29.3695 | 980.5641
2018-11-12 | 23.3944 | 20.2276 | 18.8472 | 18.2777 | 18.9744 | 22.387 | 30.1737 | 35.1164 | 38.7555 | 43.6494 | 48.9323 | 53.8795 | 58.4105 | 63.2266 | 66.5625 | 67.7801 | 65.953 | 64.7237 | 69.3494 | 64.7708 | 58.1247 | 49.9109 | 40.9113 | 32.4448 | 1074.7835
2018-11-13 | 26.2491 | 22.8487 | 20.8853 | 20.2961 | 20.7679 | 24.222 | 32.0197 | 37.3484 | 42.4139 | 49.1945 | 55.6281 | 60.6124 | 65.6494 | 70.2387 | 72.3326 | 72.6215 | 70.0134 | 68.6013 | 72.6614 | 67.8957 | 60.8677 | 52.0154 | 42.2084 | 33.73 | 1161.3216
2018-11-14 | 27.2596 | 23.3378 | 21.299 | 20.2698 | 20.5128 | 23.6156 | 31.3088 | 36.8141 | 41.9352 | 47.7529 | 53.118 | 56.8034 | 60.3668 | 63.0222 | 64.6014 | 64.5826 | 61.839 | 60.9681 | 63.8701 | 58.6701 | 52.871 | 46.0941 | 39.7671 | 33.1415 | 1073.821
2018-11-15 | 27.6519 | 23.9522 | 21.9738 | 20.9335 | 20.8426 | 21.9299 | 24.679 | 29.3061 | 37.2269 | 44.5349 | 49.6138 | 53.6651 | 56.4337 | 58.9122 | 59.8407 | 59.317 | 57.0594 | 56.6096 | 59.8498 | 54.8802 | 49.7375 | 44.3945 | 39.0547 | 33.5265 | 1005.9256
2018-11-16 | 28.2456 | 24.9646 | 22.9327 | 21.8369 | 21.5155 | 22.398 | 24.0439 | 27.8368 | 37.4987 | 47.4301 | 55.2622 | 61.3341 | 66.6388 | 70.0722 | 71.5488 | 71.4597 | 68.6982 | 68.1852 | 72.4421 | 67.7898 | 60.9864 | 53.3741 | 45.7928 | 37.8289 | 1150.116
2018-11-17 | 31.7489 | 28.3016 | 26.4232 | 25.6236 | 26.6643 | 31.0736 | 40.0183 | 45.7928 | 52.9902 | 63.4221 | 74.1346 | 82.7732 | 89.2161 | 92.8547 | 93.34 | 91.7644 | 88.4773 | 88.5763 | 91.8989 | 85.0665 | 75.3686 | 63.5899 | 52.5992 | 41.7612 | 1483.4794
2018-11-18 | 34.0979 | 29.5473 | 26.5919 | 25.1285 | 25.4816 | 28.8268 | 37.9225 | 43.6494 | 48.5647 | 54.3787 | 58.4463 | 59.2269 | 57.2451 | 55.1232 | 52.328 | 49.6056 | 49.7293 | 55.2361 | 61.0595 | 59.2179 | 54.8369 | 48.3774 | 40.404 | 33.4926 | 1088.5182
2018-11-19 | 28.9588 | 27.028 | 26.2611 | 26.3691 | 28.1835 | 33.9546 | 46.7157 | 52.888 | 55.4798 | 56.7593 | 56.0652 | 53.4339 | 50.325 | 48.0687 | 46.3327 | 45.6899 | 46.7717 | 53.2033 | 60.0219 | 58.9033 | 55.5147 | 49.1535 | 41.4819 | 34.2552 | 1081.8189
2018-11-20 | 29.4583 | 27.1863 | 26.6401 | 26.8701 | 28.7891 | 34.5434 | 45.9513 | 50.9828 | 49.8118 | 49.7953 | 49.3669 | 48.8423 | 48.02 | 47.1887 | 45.8482 | 45.201 | 45.4925 | 51.351 | 58.098 | 57.0594 | 53.3314 | 47.2288 | 39.8778 | 32.7855 | 1039.7199
2018-11-21 | 27.7196 | 24.7837 | 23.8036 | 23.2249 | 24.0439 | 29.6491 | 38.3705 | 43.8738 | 45.8799 | 47.858 | 49.5479 | 49.9357 | 48.5565 | 47.5994 | 46.4442 | 45.4057 | 46.0147 | 50.6992 | 53.7336 | 51.0162 | 47.4865 | 42.7957 | 37.6134 | 32.0264 | 978.0822
2018-11-22 | 27.0037 | 23.9865 | 22.3814 | 21.8259 | 22.0286 | 23.3152 | 26.4172 | 30.8848 | 39.1425 | 47.0842 | 51.9648 | 54.6897 | 54.8369 | 54.6638 | 53.8023 | 52.3449 | 52.0829 | 56.2844 | 59.6237 | 57.3691 | 54.1461 | 49.515 | 44.4803 | 38.0018 | 1017.8758
2018-11-23 | 32.2518 | 28.7577 | 26.1593 | 24.7313 | 24.4702 | 25.3165 | 27.1376 | 31.5317 | 42.7957 | 55.5409 | 64.6955 | 70.9661 | 75.0743 | 78.1253 | 78.6847 | 77.6401 | 73.7323 | 75.2874 | 80.228 | 76.8894 | 71.1634 | 63.0779 | 54.6551 | 46.8277 | 1305.7402
2018-11-24 | 37.7642 | 32.7186 | 30.0197 | 29.0092 | 29.815 | 34.0365 | 42.4672 | 48.8995 | 57.9109 | 68.7273 | 79.2773 | 90.937 | 100.4086 | 105.3804 | 107.7595 | 106.8627 | 101.2897 | 99.2748 | 103.3368 | 96.497 | 87.7963 | 75.4905 | 65.063 | 53.0498 | 1683.7914
2018-11-25 | 43.5644 | 37.5488 | 34.3648 | 33.155 | 33.452 | 37.8361 | 46.6358 | 53.0924 | 62.3091 | 72.7012 | 82.3799 | 89.1166 | 93.0464 | 95.9347 | 95.5798 | 93.6341 | 89.4925 | 90.8366 | 94.6329 | 89.6032 | 81.596 | 72.5816 | 62.3553 | 52.9731 | 1638.4226
2018-11-26 | 44.5037 | 39.1571 | 35.8411 | 34.1662 | 34.1799 | 36.7006 | 42.4367 | 48.2635 | 55.6804 | 61.2333 | 61.6184 | 60.2941 | 58.2586 | 55.1405 | 51.4936 | 48.0443 | 46.2213 | 50.0019 | 54.327 | 51.8215 | 47.8014 | 43.7731 | 38.69 | 32.6718 | 1132.3202
2018-11-27 | 27.5904 | 24.4587 | 22.9383 | 22.5589 | 22.9551 | 24.7954 | 28.4387 | 34.2004 | 41.4518 | 46.5719 | 49.7458 | 51.0162 | 50.9327 | 49.2027 | 47.261 | 44.301 | 40.5604 | 39.062 | 40.1368 | 37.3269 | 35.4569 | 33.8116 | 31.2957 | 27.8059 | 873.8751
2018-11-28 | 24.6616 | 22.8767 | 22.1771 | 22.4146 | 23.6838 | 26.4593 | 31.2041 | 36.6227 | 42.1552 | 45.4451 | 45.8958 | 44.4101 | 42.6046 | 41.0011 | 39.5387 | 38.6027 | 38.6755 | 43.5567 | 49.4656 | 47.7529 | 45.1695 | 43.6185 | 38.5882 | 33.2494 | 889.8296
2018-11-29 | 28.7828 | 26.4954 | 25.3165 | 25.1696 | 25.861 | 27.339 | 30.7095 | 35.2691 | 40.4636 | 42.9565 | 43.2792 | 43.0716 | 42.3301 | 41.5121 | 40.5231 | 39.5534 | 38.7046 | 42.0565 | 46.5799 | 44.5193 | 41.4066 | 37.9946 | 33.6214 | 28.6512 | 872.1667
2018-11-30 | 24.1243 | 21.3909 | 20.0753 | 19.5857 | 19.8245 | 20.8586 | 22.9215 | 26.3811 | 32.7855 | 38.1173 | 41.6101 | 43.9746 | 45.7374 | 46.6518 | 46.8357 | 46.2213 | 45.3269 | 48.9486 | 55.6543 | 53.2801 | 49.4327 | 43.8506 | 37.5488 | 30.2702 | 881.4079
2018-12-01 | 25.152 | 22.0616 | 20.5976 | 20.1435 | 20.9174 | 24.9062 | 33.1617 | 38.2257 | 42.8339 | 48.1904 | 54.1202 | 58.9572 | 61.27 | 62.1522 | 61.0504 | 59.074 | 57.254 | 61.4441 | 68.5819 | 66.3431 | 61.2242 | 53.3826 | 44.7616 | 35.6592 | 1101.4647
2018-12-02 | 28.7327 | 24.7837 | 22.4202 | 21.5209 | 22.1386 | 25.8491 | 34.5159 | 39.4358 | 43.1638 | 48.8178 | 54.5428 | 58.1872 | 60.3395 | 61.7011 | 61.2333 | 59.6508 | 57.5287 | 62.1245 | 69.1352 | 66.5529 | 61.4899 | 53.9568 | 44.9026 | 35.7361 | 1118.4599
2018-12-03 | 28.6449 | 24.4471 | 22.3427 | 21.3747 | 21.7877 | 25.5171 | 34.9433 | 39.4431 | 44.0755 | 51.0496 | 56.7065 | 61.4899 | 65.1952 | 66.9639 | 68.3496 | 68.9991 | 65.8486 | 67.3186 | 73.7122 | 70.2583 | 64.2728 | 55.9514 | 46.5479 | 36.6794 | 1181.919
2018-12-04 | 29.3885 | 25.3107 | 23.1011 | 22.1826 | 22.7147 | 26.6341 | 35.1788 | 40.352 | 44.8869 | 51.7373 | 57.5287 | 62.5772 | 66.6197 | 68.4463 | 69.6712 | 70.1309 | 66.7057 | 68.3302 | 75.125 | 72.1934 | 66.5911 | 58.7687 | 48.7524 | 38.894 | 1211.8214
2018-12-05 | 31.263 | 26.5014 | 24.0783 | 23.1179 | 23.4907 | 27.3329 | 36.0094 | 41.2863 | 46.8678 | 55.1927 | 61.793 | 66.4289 | 69.038 | 68.7952 | 68.5334 | 69.4956 | 68.2046 | 69.9058 | 73.5917 | 69.0963 | 63.4687 | 56.7505 | 49.4574 | 41.0611 | 1230.7605
2018-12-06 | 33.4656 | 28.5573 | 25.6769 | 23.9522 | 23.2701 | 24.0267 | 26.4834 | 30.6447 | 40.1516 | 50.6325 | 59.038 | 64.9121 | 69.0185 | 71.6082 | 72.7811 | 71.836 | 67.6261 | 65.8581 | 68.6691 | 62.2445 | 56.2756 | 50.3416 | 43.3485 | 35.7641 | 1166.1823
2018-12-07 | 28.7076 | 24.6674 | 22.1716 | 20.6189 | 20.1961 | 20.7945 | 22.3925 | 25.4521 | 33.4859 | 42.513 | 48.8259 | 53.1436 | 55.4711 | 56.7681 | 57.1566 | 55.4711 | 53.2033 | 55.8727 | 62.9943 | 58.2765 | 53.3997 | 46.6917 | 38.6245 | 30.5994 | 987.4981
2018-12-08 | 24.4934 | 21.1105 | 19.5081 | 18.9642 | 19.5908 | 23.2306 | 31.1258 | 35.9743 | 39.355 | 43.5026 | 47.253 | 49.7788 | 51.4516 | 52.82 | 53.4596 | 54.2322 | 53.9311 | 57.7596 | 65.5167 | 63.2732 | 57.2186 | 49.2355 | 40.538 | 31.3874 | 1004.7104
2018-12-09 | 24.8887 | 21.7331 | 20.2224 | 19.8089 | 20.4863 | 24.6035 | 34.2484 | 39.2597 | 41.9504 | 44.1921 | 45.5477 | 45.8403 | 45.7216 | 45.201 | 44.3789 | 43.1869 | 43.7731 | 50.1343 | 58.8674 | 57.8842 | 54.1374 | 48.1092 | 40.0405 | 32.3649 | 946.5808
2018-12-10 | 26.9976 | 24.8012 | 23.8036 | 24.3893 | 26.0995 | 33.0742 | 46.6997 | 55.2187 | 54.4219 | 51.7457 | 49.6798 | 47.2128 | 45.1538 | 43.7654 | 42.0869 | 41.4518 | 42.3529 | 49.7293 | 60.576 | 60.5669 | 58.9482 | 53.5024 | 45.6109 | 37.5847 | 1045.473
2018-12-11 | 32.7052 | 30.5088 | 30.0069 | 30.1737 | 32.4448 | 40.0405 | 55.5409 | 63.562 | 60.1035 | 56.6712 | 52.5483 | 49.8779 | 47.2932 | 45.3821 | 43.6185 | 42.8876 | 43.8583 | 50.9327 | 59.9947 | 59.263 | 57.024 | 51.6112 | 43.1792 | 35.4778 | 1114.7057
2018-12-12 | 30.3282 | 27.8182 | 26.9611 | 26.858 | 29.0092 | 35.9252 | 48.9568 | 55.9514 | 56.4601 | 56.3634 | 54.6205 | 52.4211 | 49.8201 | 47.664 | 45.4925 | 44.7381 | 45.9275 | 53.7508 | 61.6092 | 60.1307 | 58.3569 | 54.1116 | 48.1417 | 41.384 | 1112.8003
2018-12-13 | 35.6662 | 33.3033 | 32.212 | 32.3449 | 33.601 | 37.1128 | 42.8493 | 50.184 | 54.7763 | 54.4996 | 51.2504 | 48.3367 | 46.2213 | 44.1687 | 42.3834 | 41.4593 | 41.2036 | 45.9354 | 52.0069 | 50.0267 | 47.9471 | 44.9497 | 40.5902 | 36.0234 | 1039.0524
2018-12-14 | 31.6172 | 29.0029 | 28.1276 | 28.2021 | 29.0849 | 31.6896 | 36.7148 | 43.4487 | 50.0515 | 50.8242 | 48.1011 | 46.0782 | 44.5349 | 43.2792 | 42.4444 | 41.7083 | 41.7385 | 46.7397 | 55.5757 | 54.4478 | 51.8889 | 47.3173 | 40.0257 | 33.4656 | 996.1088
2018-12-15 | 28.9085 | 26.7247 | 26.5617 | 27.0219 | 29.5727 | 36.5944 | 50.941 | 59.2179 | 58.4999 | 54.396 | 51.4684 | 49.1863 | 48.6544 | 47.8095 | 46.8037 | 46.6518 | 46.8918 | 52.6416 | 62.1891 | 61.1967 | 57.4223 | 50.8409 | 42.4444 | 34.3923 | 1097.0318
2018-12-16 | 28.8331 | 26.3631 | 25.4875 | 25.8015 | 27.572 | 33.9273 | 47.2691 | 54.1288 | 53.3912 | 50.6575 | 48.8832 | 47.9876 | 47.6882 | 47.8257 | 47.664 | 47.8742 | 47.9957 | 52.3957 | 60.886 | 59.281 | 54.6984 | 47.3576 | 39.3037 | 31.3088 | 1054.5807
2018-12-17 | 25.3401 | 22.4534 | 21.3584 | 21.2343 | 22.6534 | 27.7442 | 38.1317 | 44.3789 | 45.0281 | 45.7928 | 46.4841 | 46.8918 | 47.7125 | 48.7279 | 49.8035 | 50.8993 | 50.3582 | 54.3874 | 61.8758 | 59.4613 | 54.4909 | 48.2067 | 39.9295 | 31.512 | 1004.8564
2018-12-18 | 25.6117 | 22.6312 | 21.4613 | 21.4017 | 22.7315 | 27.5106 | 38.0018 | 44.4881 | 46.8597 | 48.2879 | 48.8914 | 48.3936 | 48.3123 | 49.8531 | 50.8075 | 51.0496 | 50.5577 | 54.2666 | 61.7838 | 59.3981 | 55.6193 | 49.0879 | 41.1661 | 33.0406 | 1021.2131
2018-12-19 | 27.1741 | 24.222 | 22.8487 | 22.6367 | 23.8607 | 28.5761 | 38.1534 | 45.0831 | 47.6075 | 49.0715 | 50.3748 | 50.8909 | 50.8325 | 51.3091 | 51.3007 | 51.1081 | 50.1509 | 53.0242 | 59.317 | 55.9776 | 51.5944 | 46.3486 | 40.6573 | 33.7096 | 1025.8297
2018-12-20 | 28.0098 | 24.505 | 22.7929 | 22.0286 | 21.9518 | 23.6042 | 26.9368 | 31.7028 | 38.4938 | 44.1299 | 47.3978 | 47.9957 | 50.433 | 50.7242 | 51.0162 | 51.0998 | 50.1675 | 52.7095 | 58.2765 | 54.1202 | 49.6798 | 44.8477 | 39.1498 | 32.645 | 964.4182
2018-12-21 | 26.6583 | 22.8096 | 20.5976 | 19.6116 | 19.4771 | 20.1908 | 22.1276 | 25.5585 | 32.9935 | 41.2863 | 46.7957 | 49.787 | 52.9731 | 53.9397 | 53.2118 | 51.872 | 50.7908 | 54.9756 | 61.7379 | 58.9661 | 55.1666 | 49.8035 | 42.7727 | 34.5159 | 968.6193
2018-12-22 | 27.7442 | 23.6611 | 21.3639 | 20.2698 | 20.5976 | 23.3096 | 28.4512 | 34.0842 | 42.3529 | 51.0831 | 58.9122 | 64.1509 | 67.7898 | 70.543 | 72.4919 | 71.5191 | 68.1949 | 70.1309 | 77.6917 | 73.5516 | 67.5684 | 60.7035 | 51.9648 | 41.1661 | 1209.2963
2018-12-23 | 32.8123 | 27.5167 | 24.3835 | 22.8823 | 23.0842 | 25.9265 | 31.1519 | 36.9207 | 46.0465 | 56.2756 | 64.4699 | 70.602 | 75.196 | 77.0537 | 72.9109 | 68.5819 | 64.8461 | 66.2955 | 73.1208 | 69.213 | 63.7767 | 59.7412 | 54.06 | 47.1003 | 1253.9681
2018-12-24 | 39.2597 | 33.6757 | 30.2702 | 28.8268 | 28.5011 | 30.4572 | 34.2757 | 39.4358 | 50.2172 | 63.758 | 75.2975 | 83.5199 | 87.9499 | 88.7305 | 89.3155 | 87.2054 | 84.9479 | 86.998 | 88.929 | 79.1524 | 70.4742 | 63.534 | 57.1213 | 48.5402 | 1470.393
2018-12-25 | 40.5231 | 34.819 | 30.0838 | 26.6764 | 24.4529 | 24.0668 | 24.9704 | 27.572 | 34.2484 | 41.7914 | 46.9078 | 49.5891 | 50.541 | 49.8531 | 48.4018 | 45.4136 | 42.3301 | 43.6416 | 47.3656 | 45.4136 | 43.8583 | 41.4744 | 37.3055 | 31.7555 | 933.0553
2018-12-26 | 26.4653 | 23.0673 | 21.5916 | 20.8319 | 21.1858 | 23.1517 | 26.7126 | 31.1649 | 37.2412 | 43.3793 | 48.4018 | 50.5493 | 50.4911 | 49.2273 | 48.4588 | 47.9147 | 48.3936 | 54.0342 | 60.3759 | 58.0534 | 53.8366 | 48.8341 | 43.1177 | 36.0094 | 972.4896
2018-12-27 | 29.4837 | 25.152 | 22.4867 | 21.3152 | 21.3206 | 22.1826 | 24.5281 | 27.2779 | 34.2894 | 43.7344 | 51.8215 | 57.3868 | 60.9864 | 62.1799 | 62.226 | 60.2941 | 57.9821 | 60.658 | 66.8491 | 62.92 | 57.4666 | 51.8805 | 44.9653 | 36.9278 | 1066.3149
2018-12-28 | 30.0582 | 25.4049 | 22.659 | 21.1589 | 20.4386 | 20.7679 | 22.4424 | 24.7197 | 33.1213 | 43.5876 | 52.1589 | 59.047 | 64.076 | 67.7127 | 69.6712 | 69.6029 | 67.4819 | 66.8682 | 72.9508 | 68.1852 | 61.9034 | 55.0537 | 46.8517 | 37.513 | 1123.4352
2018-12-29 | 30.3346 | 25.8491 | 23.3152 | 22.2433 | 22.3593 | 24.5281 | 29.3568 | 34.2963 | 43.11 | 54.2666 | 64.0104 | 70.7396 | 74.3766 | 76.0302 | 77.2592 | 77.8877 | 75.4295 | 74.7402 | 81.871 | 76.4285 | 69.3396 | 60.2759 | 51.0914 | 40.6871 | 1279.8265
2018-12-30 | 32.2851 | 27.3085 | 24.4876 | 23.0168 | 22.8767 | 25.0758 | 29.6109 | 34.4129 | 42.0414 | 51.4181 | 60.6033 | 68.6206 | 73.8629 | 77.6504 | 78.6951 | 77.4135 | 74.4472 | 74.4169 | 81.4376 | 76.0812 | 69.6908 | 61.0321 | 52.3449 | 42.5893 | 1281.4195
2018-12-31 | 34.4197 | 29.0786 | 26.0398 | 24.4702 | 24.3373 | 26.3151 | 30.5994 | 35.8061 | 43.2792 | 51.6616 | 58.8584 | 63.2452 | 64.3103 | 65.0064 | 64.7896 | 63.4408 | 63.8234 | 70.6315 | 76.7459 | 69.5736 | 61.4441 | 53.1265 | 45.2718 | 39.2817 | 1185.556
[25 empty] | 561893.3076 | Annual MWHs
Note on L5: AJZ: Taken from Load Forecast (FNG)
Note on A13: AJZ: NOTES: Variable losses vary with the amount of electricity distributed and are, more precisely, proportional to the square of the current. Consequently, a 1% increase in current leads to an increase in losses of more than 1%. - Electrical Engineering Portal

## 2018 Hourly Load - RC2016
OPC 012927
FPL RC-16
2018 FORECASTED Hourly Loads - RC2016
BASED ON 2014 RAW DATA
FORECASTED
SUMMER PEAK |  | 24606.279
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | MAX | 2014 Hourly Load | 116299005
2018-01-01 | 10059.6184 | 9693.6271 | 9191.9313 | 8849.5856 | 8700.5161 | 8773.5087 | 9001.7392 | 9189.8752 | 10023.6361 | 11340.5876 | 12573.2379 | 13417.2794 | 13916.9191 | 14113.2796 | 14054.6799 | 13874.7685 | 13688.6886 | 13848.0388 | 14520.3934 | 14120.476 | 13514.9456 | 12840.5348 | 11944.0619 | 10815.2463 | 14520.3934 | 2018 Forecasted (FNG) NEL | 119562964.2862
2018-01-02 | 9758.3952 | 9080.9002 | 8625.4673 | 8407.5175 | 8345.8336 | 8598.7377 | 9566.147 | 10351.5889 | 11518.4429 | 12890.91 | 13995.0521 | 14751.7081 | 15292.4704 | 15668.7423 | 15837.345 | 15752.0156 | 15434.3434 | 15299.6669 | 15868.187 | 15263.6846 | 14450.485 | 13543.7314 | 12528.003 | 11338.5315 | 15868.187
2018-01-03 | 10198.4072 | 9383.1514 | 8877.3433 | 8631.6357 | 8611.0744 | 8895.8485 | 9731.6655 | 10517.1074 | 11433.1135 | 12210.3308 | 12654.455 | 12798.3842 | 12799.4122 | 12681.1847 | 12561.9291 | 12487.9084 | 12449.87 | 13045.1198 | 13941.5927 | 13697.9412 | 13198.3015 | 12593.7992 | 11774.4312 | 10827.5831 | 13941.5927 | Ratio 2013 to 2018 | 1.0281
2018-01-04 | 9981.4854 | 9415.0215 | 9075.7599 | 8928.7466 | 8947.2518 | 9169.3139 | 9643.2519 | 10268.3156 | 11231.6127 | 12082.8507 | 12580.4343 | 12689.4092 | 12586.6027 | 12422.1123 | 12211.3589 | 12014.9984 | 12056.121 | 12663.7076 | 13195.2173 | 12836.4226 | 12378.9335 | 11817.6099 | 11113.3852 | 10281.6804 | 13195.2173
2018-01-05 | 9431.4705 | 8821.8278 | 8437.3314 | 8216.2974 | 8171.0625 | 8362.2826 | 8814.6314 | 9336.8885 | 10352.6169 | 11341.6157 | 12413.8878 | 13075.9618 | 13419.3356 | 13527.2824 | 13518.0298 | 13391.5778 | 13216.8067 | 13363.82 | 14182.16 | 13765.7935 | 13182.8806 | 12300.8006 | 11268.6231 | 10160.3687 | 14182.16 | Applied above ratio to 2013 historical hourly loads
2018-01-06 | 9048.0022 | 8435.2753 | 8070.3121 | 7939.7478 | 8043.5824 | 8645.0006 | 9888.9595 | 10674.4014 | 11386.8506 | 12343.9793 | 13329.8939 | 13954.9575 | 14446.3727 | 14708.5294 | 14627.3122 | 14315.8084 | 14020.7537 | 14462.8218 | 15203.0287 | 14777.4097 | 13828.5055 | 12660.6234 | 11678.8211 | 10594.2123 | 15203.0287
2018-01-07 | 9764.5636 | 9305.0185 | 9187.819 | 9281.373 | 9719.3288 | 10709.3556 | 12558.845 | 13870.6562 | 14450.485 | 14793.8588 | 14658.1542 | 14276.742 | 13910.7507 | 13547.8437 | 13262.0416 | 13243.5364 | 13634.2012 | 14883.3005 | 16296.8902 | 16393.5283 | 16037.8177 | 15119.7555 | 13972.4347 | 12838.4787 | 16393.5283 | Resulting Total Hourly Load | 119562964.2862
2018-01-08 | 11966.6794 | 11510.2184 | 11346.756 | 11273.7634 | 11448.5345 | 12231.9202 | 13697.9412 | 14406.2782 | 14335.3417 | 14335.3417 | 14246.9281 | 13887.1052 | 13394.662 | 12927.9204 | 12525.9469 | 12367.6248 | 12483.7962 | 13175.6841 | 13981.6872 | 13726.7271 | 13133.5334 | 12172.2924 | 11056.8416 | 9879.7069 | 14406.2782
2018-01-09 | 8922.5782 | 8428.0788 | 8194.708 | 8109.3786 | 8277.9813 | 8977.0657 | 10400.936 | 11334.4193 | 11627.4178 | 12153.7872 | 12514.6381 | 12709.9705 | 12727.4476 | 12633.8937 | 12514.6381 | 12472.4875 | 12547.5362 | 13140.7299 | 14033.0905 | 13864.4878 | 13319.6132 | 12453.9823 | 11416.6645 | 10221.0246 | 14033.0905
2018-01-10 | 9162.1174 | 8492.8469 | 8108.3505 | 7963.3933 | 8049.7508 | 8649.1128 | 9999.9906 | 10902.6319 | 11585.2672 | 12410.8036 | 13064.653 | 13481.0195 | 13712.3341 | 13886.0772 | 13892.2456 | 13854.2072 | 13800.7478 | 13882.993 | 14613.9474 | 14205.8055 | 13557.0963 | 12746.9809 | 11904.9955 | 10941.6983 | 14613.9474
2018-01-11 | 9815.9669 | 9110.7141 | 8633.6919 | 8402.3772 | 8354.0581 | 8580.2325 | 9087.0686 | 9728.5813 | 11163.7604 | 12690.4373 | 13749.3445 | 14407.3062 | 14895.6372 | 15191.72 | 15312.0037 | 15246.2075 | 14918.2547 | 14650.9577 | 15087.8854 | 14523.4776 | 13789.439 | 12920.7239 | 12020.1388 | 11010.5787 | 15312.0037
2018-01-12 | 9923.9137 | 9153.8929 | 8672.7584 | 8393.1246 | 8253.3077 | 8338.6371 | 8676.8706 | 9125.1071 | 10219.9965 | 11344.6999 | 12142.4785 | 12598.9395 | 13000.913 | 13254.8451 | 13325.7816 | 13242.5083 | 13048.204 | 12912.4994 | 13669.1554 | 13403.9146 | 12796.328 | 11945.09 | 10977.6806 | 9852.9772 | 13669.1554
2018-01-13 | 8922.5782 | 8406.4895 | 8165.9222 | 8141.2486 | 8364.3388 | 9205.2961 | 10786.4605 | 11732.2805 | 12106.4962 | 12606.136 | 13047.1759 | 13376.1568 | 13676.3519 | 13907.6665 | 14055.7079 | 14161.5987 | 14099.9147 | 14224.3106 | 15106.3906 | 14911.0582 | 14137.9532 | 13065.6811 | 11891.6306 | 10565.4265 | 15106.3906 | 2014 Historical Summer Peak | 22720
2018-01-14 | 9416.0495 | 8715.9371 | 8342.7494 | 8151.5293 | 8227.6061 | 8885.5679 | 10310.4663 | 11158.6201 | 11838.1712 | 12765.4861 | 13536.535 | 13984.7714 | 14214.03 | 14225.3387 | 14127.6725 | 13864.4878 | 13792.5232 | 14113.2796 | 14960.4053 | 14738.3433 | 14048.5115 | 13059.5127 | 11829.9467 | 10502.7145 | 14960.4053
2018-01-15 | 9363.6182 | 8727.2458 | 8369.4791 | 8248.1674 | 8331.4407 | 9061.367 | 10579.8194 | 11462.9274 | 11775.4592 | 12189.7695 | 12404.6352 | 12420.0561 | 12249.3973 | 12080.7946 | 11892.6587 | 11803.217 | 11896.7709 | 12556.7888 | 13419.3356 | 13225.0312 | 12703.8021 | 11889.5745 | 10850.2005 | 9703.9078 | 13419.3356 | Ratioed 2018 Projected Summer Peak | 23357.6422
2018-01-16 | 8851.6417 | 8397.2369 | 8262.5603 | 8312.9355 | 8607.9902 | 9596.989 | 11438.2538 | 12628.7534 | 12831.2822 | 12904.2749 | 12902.2187 | 12708.9425 | 12412.8597 | 12099.2998 | 11825.8344 | 11691.1579 | 11828.9186 | 12663.7076 | 14438.1482 | 14779.4659 | 14701.3329 | 14225.3387 | 13457.374 | 12602.0237 | 14779.4659
2018-01-17 | 11997.5213 | 11759.0102 | 11793.9644 | 11997.5213 | 12450.8981 | 13600.275 | 15632.76 | 16861.298 | 16686.5269 | 15815.7556 | 14856.5708 | 13872.7123 | 13055.4005 | 12394.3545 | 11931.7252 | 11676.765 | 11723.0279 | 12444.7297 | 13605.4154 | 13521.114 | 13247.6487 | 12706.8863 | 12082.8507 | 11327.2228 | 16861.298 | FNG Forecasted Summer Peak | 24606.279
2018-01-18 | 10601.4087 | 10278.5963 | 10182.9862 | 10224.1088 | 10448.227 | 10960.2035 | 11825.8344 | 12931.0046 | 13674.2957 | 13756.541 | 13498.4966 | 12969.043 | 12411.8316 | 11911.1639 | 11467.0397 | 11225.4443 | 11228.5285 | 11866.957 | 13273.3503 | 13520.0859 | 13519.0579 | 13408.0268 | 13114.0002 | 12693.5215 | 13756.541
2018-01-19 | 12392.2984 | 12289.4919 | 12368.6529 | 12604.0798 | 12982.4078 | 13594.1066 | 14541.9828 | 15685.1913 | 16338.0128 | 15829.1205 | 14717.782 | 13634.2012 | 12768.5703 | 12131.1698 | 11618.1653 | 11204.883 | 11081.5152 | 11438.2538 | 12673.9883 | 12595.8553 | 12296.6883 | 11690.1298 | 11072.2626 | 10202.5194 | 16338.0128
2018-01-20 | 9566.147 | 9264.9239 | 9196.0436 | 9283.4291 | 9648.3923 | 10373.1783 | 11562.6497 | 12683.2408 | 13090.3547 | 12907.3591 | 12658.5673 | 12419.0281 | 12136.3101 | 11918.3603 | 11751.8137 | 11659.2879 | 11675.7369 | 12069.4859 | 13177.7402 | 13089.3266 | 12508.4698 | 11657.2317 | 10608.6052 | 9483.9018 | 13177.7402
2018-01-21 | 8636.7761 | 8192.6519 | 8009.6563 | 8008.6282 | 8216.2974 | 9054.1706 | 10674.4014 | 11622.2775 | 11826.8625 | 11889.5745 | 11953.3145 | 11951.2584 | 11926.5848 | 11816.5818 | 11719.9437 | 11621.2495 | 11659.2879 | 12174.3486 | 13188.0209 | 13151.0105 | 12604.0798 | 11729.1963 | 10692.9065 | 9632.9713 | 13188.0209
2018-01-22 | 8796.1262 | 8481.5382 | 8430.135 | 8590.5131 | 9067.5354 | 10243.642 | 12334.7267 | 13642.4257 | 13448.1214 | 13688.6886 | 13519.0579 | 13178.7683 | 12790.1596 | 12337.8109 | 12019.1107 | 11846.3957 | 11964.6232 | 12762.4019 | 14522.4496 | 15004.6122 | 14990.2192 | 14528.6179 | 13806.9162 | 12944.3694 | 15004.6122
2018-01-23 | 12426.2245 | 12300.8006 | 12433.421 | 12728.4757 | 13275.4064 | 14614.9754 | 16884.9435 | 17981.8891 | 17358.8815 | 16319.5076 | 15330.5088 | 14234.5913 | 13318.5852 | 12554.7327 | 12041.7281 | 11778.5434 | 11800.1328 | 12419.0281 | 13898.414 | 14167.767 | 13943.6488 | 13314.4729 | 12327.5303 | 11343.6718 | 17981.8891
2018-01-24 | 10624.0262 | 10370.0941 | 10353.645 | 10493.4619 | 10906.7441 | 12042.7562 | 14037.2028 | 15081.717 | 15071.4364 | 14734.231 | 14301.4155 | 13673.2677 | 13115.0282 | 12634.9218 | 12240.1447 | 12011.9142 | 12071.542 | 12613.3324 | 13821.3091 | 13850.0949 | 13537.5631 | 13010.1656 | 12347.0635 | 11520.4991 | 15081.717
2018-01-25 | 10831.6954 | 10484.2093 | 10344.3924 | 10384.487 | 10572.6229 | 11009.5506 | 11775.4592 | 12735.6722 | 13632.1451 | 13580.7418 | 13063.625 | 12498.1891 | 12045.8404 | 11688.0737 | 11412.5522 | 11203.855 | 11112.3572 | 11383.7664 | 12307.997 | 12212.387 | 11797.0486 | 11288.1563 | 10593.1842 | 9799.5179 | 13632.1451
2018-01-26 | 9115.8545 | 8664.5338 | 8471.2576 | 8389.0123 | 8451.7243 | 8743.6949 | 9297.822 | 10059.6184 | 11126.7501 | 11674.7088 | 11920.4164 | 11894.7148 | 11880.3219 | 11866.957 | 11787.796 | 11703.4947 | 11687.0456 | 11982.1004 | 12915.5836 | 12884.7416 | 12311.0812 | 11496.8536 | 10548.9774 | 9441.7511 | 12915.5836
2018-01-27 | 8528.8292 | 7987.0388 | 7749.5558 | 7685.8157 | 7900.6814 | 8660.4216 | 10240.5578 | 11119.5536 | 11484.5168 | 11911.1639 | 12395.3826 | 12713.0547 | 12972.1272 | 13184.9367 | 13282.6029 | 13405.9707 | 13461.4862 | 13563.2647 | 14375.4362 | 14281.8823 | 13533.4508 | 12416.9719 | 11176.0972 | 9821.1072 | 14375.4362
2018-01-28 | 8683.039 | 8057.9753 | 7752.64 | 7631.3283 | 7781.4258 | 8511.3521 | 10003.0748 | 10940.6703 | 11357.0367 | 11917.3322 | 12494.0768 | 12900.1626 | 13276.4345 | 13588.9663 | 13818.2249 | 13991.9679 | 14051.5957 | 14079.3534 | 14776.3817 | 14653.0138 | 13972.4347 | 12839.5068 | 11658.2598 | 10346.4486 | 14776.3817
2018-01-29 | 9198.0997 | 8550.4186 | 8234.8026 | 8121.7154 | 8275.9252 | 9045.946 | 10546.9213 | 11549.2849 | 11981.0723 | 12569.1256 | 13003.9972 | 13363.82 | 11710.6911 | 13303.1642 | 13162.3192 | 13218.8628 | 13426.532 | 13970.3785 | 14654.0419 | 14485.4392 | 14017.6695 | 13139.7018 | 12063.3175 | 10832.7234 | 14654.0419
2018-01-30 | 9926.9979 | 9383.1514 | 9110.7141 | 9051.0864 | 9261.8397 | 10079.1516 | 11754.8979 | 12769.5983 | 13274.3784 | 13752.4287 | 14014.5853 | 13980.6592 | 13830.5617 | 13653.7344 | 13456.3459 | 13342.2307 | 13419.3356 | 13878.8807 | 14690.0242 | 14563.5722 | 13985.7995 | 13140.7299 | 11962.5671 | 10741.2256 | 14690.0242
2018-01-31 | 9828.3037 | 9298.8501 | 9081.9283 | 8989.4024 | 9132.3035 | 9905.4086 | 11476.2923 | 12415.9439 | 12791.1877 | 13271.2942 | 13620.8363 | 13814.1126 | 13854.2072 | 13802.8039 | 13707.1938 | 13762.7093 | 13683.5483 | 13810.0003 | 14403.194 | 14173.9354 | 13546.8156 | 12749.037 | 11820.6941 | 10744.3098 | 14403.194
2018-02-01 | 9741.9462 | 9061.367 | 8633.6919 | 8408.5456 | 8367.423 | 8565.8396 | 9090.1528 | 9848.865 | 11208.9953 | 12484.8243 | 13334.0061 | 13798.6916 | 14141.0374 | 14346.6504 | 14475.1586 | 14520.3934 | 14409.3624 | 14135.897 | 14454.5973 | 14169.8232 | 13426.532 | 12587.6308 | 11679.8492 | 10638.4191 | 14520.3934
2018-02-02 | 9612.41 | 8919.494 | 8476.3979 | 8227.6061 | 8140.2206 | 8221.4377 | 8564.8115 | 9162.1174 | 10672.3452 | 12059.2052 | 12914.5555 | 13454.2898 | 14124.5883 | 14597.4983 | 14930.5915 | 15083.7732 | 15065.268 | 14769.1852 | 14764.0449 | 14073.185 | 13423.4478 | 13026.6146 | 12488.9365 | 11177.1253 | 15083.7732
2018-02-03 | 9989.7099 | 9002.7673 | 8618.2709 | 8454.8085 | 8559.6712 | 9242.3065 | 10617.8578 | 11457.7871 | 12221.6396 | 13192.1331 | 14161.5987 | 14832.9253 | 15354.1543 | 15758.184 | 16052.2106 | 16171.4662 | 15968.9373 | 15694.4439 | 16121.091 | 15911.3657 | 15013.8647 | 13978.603 | 12689.4092 | 11294.3247 | 16171.4662
2018-02-04 | 10103.8252 | 9401.6566 | 8979.1218 | 8773.5087 | 8818.7436 | 9421.1898 | 10797.7692 | 11610.9688 | 12323.418 | 13349.4271 | 14269.5455 | 14944.9844 | 15472.3818 | 15803.4188 | 16025.4809 | 16152.961 | 16034.7335 | 15702.6684 | 16136.512 | 16055.2948 | 15270.881 | 14178.0477 | 12963.9027 | 11578.0707 | 16152.961
2018-02-05 | 10406.0763 | 9632.9713 | 9216.6049 | 8996.5989 | 9034.6373 | 9703.9078 | 11148.3394 | 11966.6794 | 12686.325 | 13761.6813 | 14699.2768 | 15398.3611 | 15836.3169 | 16142.6804 | 16330.8163 | 16244.4588 | 15901.085 | 15613.2268 | 16006.9758 | 15792.1101 | 15005.6402 | 13938.5085 | 12645.2024 | 11257.3144 | 16330.8163
2018-02-06 | 10078.1235 | 9278.2888 | 8859.8662 | 8645.0006 | 8706.6845 | 9323.5236 | 10753.5624 | 11577.0426 | 12324.4461 | 13183.9086 | 13931.312 | 14476.1866 | 14918.2547 | 15329.4808 | 15501.1677 | 15605.0023 | 15506.308 | 15380.884 | 15819.8679 | 15709.8649 | 14937.7879 | 13889.1614 | 12622.585 | 11190.4901 | 15819.8679
2018-02-07 | 9981.4854 | 9242.3065 | 8735.4703 | 8502.0995 | 8538.0818 | 9170.3419 | 10584.9597 | 11452.6468 | 12003.6897 | 12714.0828 | 13386.4375 | 14010.4731 | 14379.5485 | 14440.2043 | 14915.1705 | 15048.819 | 15010.7805 | 14913.1143 | 14961.4334 | 14567.6844 | 13991.9679 | 13027.6427 | 12129.1137 | 11013.6629 | 15048.819
2018-02-08 | 9991.7661 | 9219.6891 | 8759.1158 | 8526.7731 | 8509.296 | 8700.5161 | 9229.9697 | 9970.1767 | 11343.6718 | 12749.037 | 13797.6636 | 14439.1763 | 14866.8514 | 15074.5206 | 15206.1129 | 15123.8677 | 14939.844 | 14668.4348 | 14839.0936 | 14490.5795 | 13765.7935 | 12944.3694 | 12042.7562 | 11065.0662 | 15206.1129
2018-02-09 | 10034.9448 | 9277.2607 | 8817.7155 | 8578.1763 | 8524.717 | 8687.1513 | 9069.5915 | 9657.6448 | 10733.0011 | 11714.8034 | 12363.5126 | 12698.6618 | 13008.1095 | 13195.2173 | 13277.4626 | 13208.5822 | 13044.0917 | 12993.7165 | 13591.0224 | 13681.4922 | 13010.1656 | 12110.6085 | 11144.2272 | 9925.9699 | 13681.4922
2018-02-10 | 8916.4098 | 8345.8336 | 8109.3786 | 8071.3402 | 8263.5884 | 9064.4512 | 10639.4472 | 11553.3971 | 11945.09 | 12432.3929 | 12971.0991 | 13321.6694 | 13646.538 | 13899.442 | 14004.3047 | 14113.2796 | 14132.8128 | 14054.6799 | 14610.8632 | 14748.6239 | 14018.6976 | 12978.2956 | 11747.7015 | 10409.1605 | 14748.6239
2018-02-11 | 9335.8604 | 8665.5619 | 8340.6933 | 8233.7745 | 8372.5633 | 9127.1632 | 10701.1311 | 11608.9127 | 12069.4859 | 12685.297 | 13238.3961 | 13746.2603 | 14172.9074 | 14549.1793 | 14776.3817 | 15010.7805 | 15078.6328 | 14946.0124 | 15347.9859 | 15398.3611 | 14748.6239 | 13492.3282 | 12159.9556 | 10725.8046 | 15398.3611
2018-02-12 | 9482.8738 | 8793.042 | 8370.5072 | 8193.6799 | 8287.2339 | 8954.4482 | 10436.9183 | 11250.1179 | 11878.2658 | 12681.1847 | 13380.2691 | 13943.6488 | 14362.0714 | 14703.389 | 14790.7746 | 14655.07 | 14472.0744 | 14506.0005 | 15176.299 | 15009.7525 | 14303.4717 | 13253.8171 | 11784.7118 | 10292.9892 | 15176.299
2018-02-13 | 9208.3803 | 8522.6608 | 8202.9325 | 8078.5366 | 8222.4658 | 8953.4202 | 10502.7145 | 11457.7871 | 11959.4829 | 12279.2112 | 12565.0133 | 12665.7637 | 12721.2793 | 12704.8302 | 12648.2866 | 12559.873 | 12471.4594 | 12473.5155 | 13198.3015 | 13478.9633 | 13050.2601 | 12310.0532 | 11316.9421 | 10180.9301 | 13478.9633
2018-02-14 | 9285.4852 | 8842.3891 | 8693.3197 | 8743.6949 | 9066.5073 | 10102.7971 | 12085.9349 | 13346.3429 | 13321.6694 | 13009.1375 | 12756.2335 | 12330.6145 | 11991.3529 | 11759.0102 | 11611.9969 | 11606.8565 | 11602.7443 | 11711.7192 | 12443.7016 | 12586.6027 | 12137.3382 | 11527.6955 | 10840.9479 | 10020.5519 | 13346.3429
2018-02-15 | 9308.1027 | 8854.7259 | 8614.1586 | 8525.745 | 8563.7834 | 8861.9224 | 9444.8353 | 10266.2595 | 11156.564 | 11725.084 | 12046.8685 | 12079.7665 | 11931.7252 | 11781.6276 | 11649.0072 | 11599.6601 | 11571.9023 | 11645.923 | 12216.4992 | 12350.1477 | 11920.4164 | 11350.8683 | 10685.7101 | 9824.1914 | 12350.1477
2018-02-16 | 9097.3493 | 8685.0951 | 8630.6077 | 8679.9548 | 8779.6771 | 9214.5487 | 9980.4573 | 11017.7752 | 11854.6203 | 12098.2717 | 11982.1004 | 11711.7192 | 11558.5375 | 11446.4784 | 11395.0751 | 11413.5803 | 11476.2923 | 11593.4917 | 12243.2289 | 12469.4033 | 11967.7074 | 11292.2686 | 10575.7071 | 9617.5503 | 12469.4033
2018-02-17 | 8855.754 | 8443.4998 | 8307.7952 | 8350.9739 | 8619.299 | 9354.3656 | 10567.4826 | 11669.5685 | 12280.2393 | 12513.6101 | 12618.4727 | 12643.1463 | 12681.1847 | 12751.0932 | 12824.0858 | 12929.9765 | 12985.492 | 13016.334 | 13529.3385 | 13698.9693 | 13017.362 | 12060.2333 | 10874.8741 | 9702.8797 | 13698.9693
2018-02-18 | 8688.1793 | 8101.1541 | 7895.541 | 7842.0816 | 8054.8911 | 8854.7259 | 10472.9006 | 11477.3203 | 11859.7606 | 12232.9483 | 12580.4343 | 12865.2084 | 13112.9721 | 13376.1568 | 13621.8644 | 13855.2352 | 13938.5085 | 13812.0565 | 14149.2619 | 14312.7242 | 13592.0505 | 12483.7962 | 11309.7457 | 9938.3067 | 14312.7242
2018-02-19 | 8857.8101 | 8209.1009 | 7916.1023 | 7796.8468 | 7939.7478 | 8668.6461 | 10199.4352 | 11074.3187 | 11591.4356 | 12180.5169 | 12774.7387 | 13281.5748 | 13678.408 | 14059.8202 | 14423.7553 | 14770.2133 | 14854.5146 | 14647.8735 | 14838.0656 | 14923.395 | 14218.1422 | 13137.6457 | 11885.4622 | 10504.7706 | 14923.395
2018-02-20 | 9315.2991 | 8626.4954 | 8243.0271 | 8038.4421 | 8096.0138 | 8790.9859 | 10266.2595 | 11165.8166 | 11913.22 | 12786.0474 | 13606.4434 | 14163.6548 | 14674.6032 | 15072.4645 | 15352.0982 | 15593.6935 | 15626.5916 | 15397.3331 | 15661.5458 | 15796.2224 | 15138.2606 | 14169.8232 | 12915.5836 | 11615.0811 | 15796.2224
2018-02-21 | 10414.3009 | 9563.0628 | 9115.8545 | 8892.7643 | 8906.1292 | 9495.2105 | 10919.0809 | 11821.7222 | 12909.4152 | 14048.5115 | 15011.8086 | 15715.0052 | 16197.1678 | 16508.6716 | 16546.71 | 16459.3245 | 15946.3199 | 15522.757 | 15707.8088 | 15472.3818 | 14720.8661 | 13745.2322 | 12788.1035 | 11601.7162 | 16546.71
2018-02-22 | 10464.6761 | 9571.2874 | 9087.0686 | 8776.5929 | 8695.3758 | 8799.2104 | 9263.8959 | 10058.5903 | 11724.056 | 13231.1996 | 14309.6401 | 15096.11 | 15708.8368 | 16041.93 | 16171.4662 | 16229.0379 | 16019.3125 | 15477.5222 | 15386.0244 | 15170.1307 | 14331.2294 | 13432.7004 | 12455.0104 | 11313.8579 | 16229.0379
2018-02-23 | 10218.9685 | 9422.2179 | 8910.2414 | 8611.0744 | 8475.3698 | 8524.717 | 8824.912 | 9513.7157 | 11117.4975 | 12689.4092 | 13904.5823 | 14816.4762 | 15867.1589 | 16035.7616 | 16179.6907 | 16309.2269 | 16186.8872 | 15847.6256 | 15843.5134 | 15869.215 | 15115.6432 | 13880.9368 | 12726.4196 | 11313.8579 | 16309.2269
2018-02-24 | 10034.9448 | 9346.1411 | 8893.7924 | 8633.6919 | 8665.5619 | 9284.4572 | 10528.4161 | 11448.5345 | 12340.8951 | 13418.3075 | 14406.2782 | 15102.2784 | 15781.8295 | 16245.4869 | 16530.261 | 16749.2389 | 16553.9065 | 16245.4869 | 16541.5697 | 16601.1975 | 15626.5916 | 14386.7449 | 12946.4255 | 11449.5626 | 16749.2389
2018-02-25 | 10143.9197 | 9335.8604 | 8849.5856 | 8581.2605 | 8601.8218 | 9227.9136 | 10627.1104 | 11415.6364 | 12229.8641 | 13156.1509 | 13983.7434 | 14671.519 | 15324.3404 | 15892.8605 | 16335.9566 | 16594.001 | 16517.9242 | 16068.6597 | 16159.1294 | 16162.2136 | 15290.4143 | 14045.4273 | 12709.9705 | 11189.4621 | 16594.001
2018-02-26 | 9898.2121 | 9082.9564 | 8580.2325 | 8345.8336 | 8363.3107 | 8911.2695 | 10261.1191 | 11118.5256 | 11827.8906 | 12616.4166 | 13656.8186 | 14347.6785 | 14963.4895 | 15382.9402 | 15650.2371 | 15704.7246 | 15467.2415 | 15302.7511 | 15731.4543 | 15718.0894 | 14983.0228 | 13948.7892 | 12667.8199 | 11306.6615 | 15731.4543
2018-02-27 | 10122.3303 | 9435.5828 | 9067.5354 | 8894.8204 | 8949.3079 | 9549.698 | 10951.979 | 11718.9157 | 12174.3486 | 12738.7564 | 13353.5394 | 13224.0032 | 13833.6458 | 13916.9191 | 13886.0772 | 13810.0003 | 13644.4818 | 13914.863 | 14413.4746 | 14501.8883 | 13892.2456 | 12838.4787 | 11598.632 | 10353.645 | 14501.8883
2018-02-28 | 9294.7378 | 8687.1513 | 8405.4614 | 8317.0478 | 8447.6121 | 9185.7629 | 10748.4221 | 11639.7546 | 11918.3603 | 12089.0191 | 12223.6957 | 12264.8183 | 12273.0428 | 12339.8671 | 12412.8597 | 12514.6381 | 12578.3782 | 12495.1049 | 12786.0474 | 12958.7623 | 12402.579 | 11670.5966 | 10799.8253 | 9807.7424 | 12958.7623
2018-03-01 | 8919.494 | 8359.1985 | 8052.835 | 7919.1865 | 7971.6179 | 8293.4023 | 8913.3256 | 9749.1427 | 10797.7692 | 11486.5729 | 11920.4164 | 12144.5347 | 12358.3722 | 12569.1256 | 12725.3915 | 12925.8642 | 12950.5378 | 12781.9351 | 12796.328 | 13031.755 | 12393.3264 | 11676.765 | 10853.2847 | 9855.0334 | 13031.755
2018-03-02 | 8972.9534 | 8414.714 | 8098.0699 | 7814.3239 | 7772.1732 | 7931.5233 | 8321.16 | 8997.627 | 10311.4943 | 11402.2716 | 12086.963 | 12581.4624 | 12959.7904 | 13329.8939 | 13587.9383 | 13814.1126 | 13887.1052 | 13714.3903 | 13784.2987 | 14035.1466 | 13319.6132 | 12351.1758 | 11240.8653 | 10015.4116 | 14035.1466
2018-03-03 | 9102.4896 | 8346.8617 | 7934.6075 | 7780.3977 | 7868.8113 | 8540.1379 | 9901.2963 | 10757.6747 | 11525.6394 | 12377.9055 | 13167.4596 | 13744.2042 | 14308.612 | 14854.5146 | 15200.9726 | 15511.4483 | 15603.9742 | 15372.6595 | 15369.5753 | 15514.5325 | 14618.0596 | 13390.5497 | 12040.7001 | 10536.6406 | 15603.9742
2018-03-04 | 9316.3272 | 8536.0257 | 8109.3786 | 7893.4849 | 7940.7759 | 8558.6431 | 9923.9137 | 10811.134 | 11536.9481 | 12378.9335 | 13134.5615 | 13750.3726 | 14305.5278 | 14818.5323 | 15254.432 | 15577.2445 | 15655.3774 | 15412.7541 | 15437.4276 | 15530.9816 | 14748.6239 | 13670.1835 | 12337.8109 | 10908.8002 | 15655.3774
2018-03-05 | 9668.9536 | 8955.4763 | 8541.166 | 8369.4791 | 8439.3875 | 9061.367 | 10515.0513 | 11395.0751 | 12076.6824 | 13027.6427 | 13845.9826 | 14546.0951 | 15127.98 | 15502.1957 | 15651.2652 | 15699.5843 | 15508.3641 | 15258.5443 | 15431.2592 | 15517.6167 | 14840.1217 | 13793.5513 | 12519.7785 | 11093.852 | 15699.5843
2018-03-06 | 9899.2402 | 9199.1278 | 8760.1439 | 8575.0922 | 8604.906 | 9202.2119 | 10569.5387 | 11442.3661 | 12388.1861 | 13350.4552 | 14058.7921 | 14642.7332 | 15030.3138 | 14951.1528 | 14771.2413 | 13689.7167 | 13161.2912 | 13248.6767 | 13847.0107 | 13968.3224 | 13405.9707 | 12505.3856 | 11453.6748 | 10254.9508 | 15030.3138
2018-03-07 | 9213.5207 | 8567.8957 | 8298.5426 | 8174.1467 | 8289.29 | 8958.5605 | 10386.5431 | 11259.3705 | 12044.8123 | 12690.4373 | 13217.8348 | 13455.3178 | 13578.6857 | 13589.9944 | 13579.7137 | 13588.9663 | 13499.5246 | 13258.9574 | 13381.2971 | 13468.6827 | 12961.8465 | 12084.9069 | 11151.4236 | 9949.6154 | 13589.9944
2018-03-08 | 9135.3877 | 8529.8573 | 8250.2235 | 8147.417 | 8225.55 | 8489.7627 | 9156.9771 | 10086.3481 | 11050.6732 | 11600.6881 | 11757.9821 | 11745.6453 | 11719.9437 | 11709.6631 | 11788.8241 | 11906.0235 | 11968.7355 | 11911.1639 | 12086.963 | 12397.4387 | 11862.8448 | 11217.2198 | 10422.5254 | 9619.6064 | 12397.4387
2018-03-09 | 8709.7687 | 0 | 8195.7361 | 7917.1304 | 7818.4361 | 7946.9443 | 8308.8233 | 8832.1085 | 9593.9048 | 10529.4442 | 11289.1844 | 11622.2775 | 12072.5701 | 12321.3619 | 12503.3294 | 12767.5422 | 13039.9795 | 13170.5438 | 12975.2114 | 13031.755 | 13340.1745 | 12573.2379 | 11571.9023 | 10140.8355 | 13340.1745
2018-03-10 | 8953.4202 | 8164.8941 | 7782.4539 | 7663.1983 | 7803.0152 | 8432.1911 | 9798.4898 | 10804.9657 | 11105.1607 | 11693.214 | 12399.4948 | 12823.0577 | 13300.08 | 13616.7241 | 14088.606 | 14545.067 | 14921.3389 | 14947.0405 | 14635.5367 | 14552.2634 | 14677.6874 | 13604.3873 | 12408.7474 | 10904.688 | 14947.0405
2018-03-11 | 9508.5754 | 8641.9164 | 8161.8099 | 7923.2988 | 7922.2707 | 8527.8012 | 9880.735 | 10847.1163 | 11107.2168 | 11797.0486 | 12409.7755 | 12978.2956 | 13471.7669 | 13924.1156 | 14348.7065 | 14823.6727 | 15223.59 | 15340.7895 | 15068.3522 | 14932.6476 | 15070.4083 | 14144.1215 | 12886.7978 | 11253.2021 | 15340.7895
2018-03-12 | 9973.2609 | 9095.2932 | 8639.8603 | 8438.3595 | 8483.5943 | 9094.2651 | 10504.7706 | 10447.199 | 11681.9053 | 12509.4978 | 13517.0018 | 14321.9768 | 14944.9844 | 15367.5192 | 15594.7216 | 16032.6774 | 16295.8621 | 16173.5223 | 15736.5946 | 15554.6271 | 15632.76 | 14676.6593 | 13468.6827 | 11986.2126 | 16295.8621
2018-03-13 | 10612.7175 | 9693.6271 | 9145.6684 | 8853.6978 | 8777.621 | 9236.1381 | 10443.0867 | 11200.7708 | 11421.8048 | 12073.5982 | 12558.845 | 12842.591 | 12999.8849 | 13098.5792 | 13166.4315 | 13237.368 | 13375.1287 | 13342.2307 | 12963.9027 | 12917.6397 | 13173.628 | 12374.8213 | 11302.5492 | 10008.2151 | 13375.1287
2018-03-14 | 8920.5221 | 8305.7391 | 7963.3933 | 7878.0639 | 8049.7508 | 8785.8455 | 10430.7499 | 11608.9127 | 11872.0974 | 12105.4682 | 12283.3235 | 12326.5022 | 12307.997 | 12354.26 | 12413.8878 | 12522.8627 | 12679.1286 | 12669.876 | 12428.2807 | 12407.7194 | 12631.8376 | 12003.6897 | 11129.8343 | 10123.3584 | 12679.1286
2018-03-15 | 9010.9918 | 8345.8336 | 7939.7478 | 7756.7522 | 7791.7064 | 8041.5263 | 8563.7834 | 9438.667 | 10421.4973 | 11320.0263 | 12003.6897 | 12394.3545 | 12675.0163 | 12909.4152 | 13183.9086 | 13465.5985 | 13769.9058 | 13822.3371 | 13484.1037 | 13156.1509 | 13231.1996 | 12512.582 | 11690.1298 | 10530.4722 | 13822.3371
2018-03-16 | 9501.3789 | 8785.8455 | 8327.3284 | 8070.3121 | 7966.4775 | 8033.3018 | 8372.5633 | 8902.0169 | 9964.0083 | 11336.4754 | 12300.8006 | 13005.0253 | 13562.2366 | 13987.8556 | 14400.1098 | 14681.7997 | 14812.364 | 14767.1291 | 14402.1659 | 14263.3771 | 14510.1128 | 13738.0358 | 12763.4299 | 11388.9067 | 14812.364
2018-03-17 | 10180.9301 | 9382.1234 | 8933.8869 | 8771.4526 | 8859.8662 | 9497.2667 | 10809.0779 | 11788.8241 | 12315.1935 | 13351.4832 | 14474.1305 | 15240.0391 | 15791.0821 | 16070.7158 | 16216.7011 | 16319.5076 | 16350.3495 | 16123.1471 | 15864.0747 | 16018.2845 | 16006.9758 | 15144.429 | 14121.5041 | 12714.0828 | 16350.3495
2018-03-18 | 11463.9555 | 10644.5875 | 10227.193 | 10025.6922 | 9993.8222 | 10446.1709 | 11595.5478 | 12273.0428 | 12157.8995 | 12530.0591 | 12892.9662 | 13090.3547 | 13258.9574 | 13492.3282 | 13796.6355 | 14119.448 | 14458.7095 | 14563.5722 | 14273.6578 | 14129.7286 | 14303.4717 | 13417.2794 | 12201.0782 | 10694.9627 | 14563.5722
2018-03-19 | 9369.7866 | 8577.1483 | 8152.5573 | 7963.3933 | 8013.7685 | 8630.6077 | 9986.6257 | 10901.6038 | 11277.8757 | 12011.9142 | 12734.6441 | 13266.1538 | 13616.7241 | 14043.3712 | 14462.8218 | 14865.8233 | 15117.6993 | 15133.1203 | 14726.0065 | 14449.4569 | 14641.7051 | 13780.1865 | 12621.5569 | 11150.3956 | 15133.1203
2018-03-20 | 9893.0718 | 9060.3389 | 8619.299 | 8369.4791 | 8384.9001 | 8947.2518 | 10255.9788 | 11185.3498 | 11587.3233 | 12292.5761 | 13028.6708 | 13577.6576 | 14006.3608 | 14452.5411 | 14856.5708 | 15177.3271 | 15387.0524 | 15313.0317 | 14950.1247 | 14651.9858 | 14809.2798 | 13813.0845 | 12582.4905 | 11155.5359 | 15387.0524
2018-03-21 | 9782.0407 | 8894.8204 | 8346.8617 | 8044.6105 | 8037.414 | 8501.0715 | 9595.9609 | 10555.1458 | 11155.5359 | 12052.0088 | 12954.6501 | 13661.959 | 14223.2826 | 14781.522 | 15310.9756 | 15740.7069 | 15908.2815 | 15743.7911 | 15156.7658 | 14721.8942 | 14757.8765 | 13896.3578 | 12957.7343 | 11787.796 | 15908.2815
2018-03-22 | 10597.2965 | 9797.4617 | 9248.4749 | 8919.494 | 8786.8736 | 8927.7185 | 9360.534 | 9922.8857 | 10870.7618 | 12332.6706 | 13419.3356 | 13991.9679 | 14491.6076 | 14869.9356 | 15129.008 | 15409.6699 | 15769.4927 | 15762.2962 | 15303.7791 | 14747.5958 | 14682.8277 | 13800.7478 | 12738.7564 | 11456.759 | 15769.4927
2018-03-23 | 10251.8666 | 9337.9166 | 8786.8736 | 8464.0611 | 8309.8513 | 8375.6475 | 8673.7864 | 9132.3035 | 10141.8636 | 11632.5582 | 12920.7239 | 13888.1333 | 14805.1675 | 15597.8058 | 16134.4558 | 16581.6642 | 16774.9405 | 16753.3511 | 16368.8547 | 15900.057 | 15976.1338 | 14951.1528 | 13757.569 | 12260.706 | 16774.9405
2018-03-24 | 10929.3615 | 9974.2889 | 9334.8324 | 9067.5354 | 9032.5812 | 9483.9018 | 10454.3954 | 11296.3808 | 11887.5184 | 12720.2512 | 13373.0726 | 13823.3652 | 13996.0802 | 13976.5469 | 13793.5513 | 13673.2677 | 13685.6045 | 13759.6251 | 13747.2884 | 13821.3091 | 13712.3341 | 12853.8997 | 11861.8167 | 10567.4826 | 13996.0802
2018-03-25 | 9471.565 | 8660.4216 | 8147.417 | 7959.2811 | 8013.7685 | 8508.2679 | 9652.5045 | 10558.23 | 11102.0765 | 11901.9113 | 12461.1788 | 13018.3901 | 13453.2617 | 13754.4848 | 14033.0905 | 14254.1245 | 14444.3166 | 14459.7376 | 14169.8232 | 13821.3091 | 13949.8172 | 13009.1375 | 11736.3928 | 10261.1191 | 14459.7376
2018-03-26 | 8954.4482 | 8195.7361 | 7768.0609 | 7620.0195 | 7736.1909 | 8345.8336 | 9679.2342 | 10808.0498 | 11456.759 | 11786.768 | 12047.8965 | 12049.9527 | 11925.5568 | 11773.4031 | 11674.7088 | 11619.1933 | 11718.9157 | 11787.796 | 11752.8418 | 12084.9069 | 12574.2659 | 11953.3145 | 10973.5684 | 9898.2121 | 12574.2659
2018-03-27 | 8921.5501 | 8342.7494 | 8043.5824 | 7973.674 | 8110.4067 | 8709.7687 | 9974.2889 | 10865.6215 | 11306.6615 | 11925.5568 | 12228.836 | 12377.9055 | 12446.7858 | 12503.3294 | 12496.133 | 12482.7681 | 12505.3856 | 12489.9646 | 12411.8316 | 12691.4654 | 12949.5097 | 12306.969 | 11369.3735 | 10228.2211 | 12949.5097
2018-03-28 | 9190.9032 | 8487.7066 | 8119.6593 | 7923.2988 | 8001.4317 | 8519.5766 | 9623.7187 | 10535.6126 | 11186.3779 | 12067.4298 | 12945.3975 | 13462.5143 | 13818.2249 | 14025.894 | 14194.4967 | 14299.3594 | 14280.8542 | 14058.7921 | 13731.8674 | 13734.9516 | 13870.6562 | 13258.9574 | 12471.4594 | 11418.7206 | 14299.3594
2018-03-29 | 10398.8799 | 9690.5429 | 9228.9416 | 8989.4024 | 8939.0272 | 9107.6299 | 9552.7822 | 10199.4352 | 11161.7043 | 12469.4033 | 13585.8821 | 14350.7627 | 14684.8839 | 14862.7391 | 14825.7288 | 14645.8174 | 14409.3624 | 14161.5987 | 13772.99 | 13661.959 | 13385.4094 | 12536.2275 | 11737.4208 | 10704.2153 | 14862.7391
2018-03-30 | 9661.7571 | 8921.5501 | 8401.3491 | 8143.3048 | 8048.7228 | 8147.417 | 8541.166 | 9030.5251 | 9925.9699 | 11085.6275 | 11885.4622 | 12286.4077 | 12468.3752 | 12605.1079 | 12734.6441 | 12843.619 | 12953.622 | 12928.9484 | 12666.7918 | 12481.7401 | 12827.17 | 12032.4755 | 10966.3719 | 9651.4765 | 12953.622
2018-03-31 | 8539.1099 | 7942.832 | 7558.3356 | 7433.9397 | 7577.8689 | 8387.9843 | 9838.5843 | 10756.6466 | 11066.0942 | 11494.7974 | 11936.8655 | 12289.4919 | 12541.3678 | 12840.5348 | 13103.7195 | 13322.6974 | 13425.5039 | 13314.4729 | 13185.9647 | 13344.2868 | 13633.1731 | 12746.9809 | 11584.2391 | 10159.3407 | 13633.1731
2018-04-01 | 8947.2518 | 8227.6061 | 7860.5868 | 7710.4893 | 7813.2958 | 8485.6505 | 10063.7306 | 11021.8874 | 11364.2331 | 11828.9186 | 12279.2112 | 12666.7918 | 12977.2675 | 13378.2129 | 13860.3755 | 14401.1379 | 14892.553 | 15068.3522 | 14801.0552 | 14325.061 | 14437.1201 | 13489.244 | 12084.9069 | 10547.9493 | 15068.3522
2018-04-02 | 9248.4749 | 8445.5559 | 8008.6282 | 7783.4819 | 7842.0816 | 8516.4924 | 9964.0083 | 10772.0676 | 11145.2552 | 11841.2554 | 12425.1965 | 12952.5939 | 13311.3887 | 13752.4287 | 14420.6711 | 15017.977 | 15466.2134 | 15653.3213 | 15300.6949 | 14819.5604 | 14918.2547 | 13966.2663 | 12545.4801 | 10995.1577 | 15653.3213
2018-04-03 | 9638.1116 | 8778.6491 | 8291.3461 | 8089.8454 | 8134.0522 | 8813.6033 | 10138.7794 | 10926.2774 | 11452.6468 | 12243.2289 | 12986.5201 | 13600.275 | 14149.2619 | 14672.5471 | 15388.0805 | 15857.9063 | 16187.9152 | 16056.3229 | 15688.2755 | 15149.5694 | 15431.2592 | 14445.3447 | 12998.8569 | 11419.7487 | 16187.9152
2018-04-04 | 10030.8325 | 9166.2297 | 8630.6077 | 8367.423 | 8337.6091 | 8925.6624 | 10348.5047 | 11097.9642 | 11674.7088 | 12584.5466 | 13454.2898 | 14165.7109 | 14710.5855 | 15267.7969 | 15802.3908 | 16267.0763 | 16641.292 | 16606.3378 | 16148.8488 | 15352.0982 | 15182.4674 | 14325.061 | 13195.2173 | 11867.9851 | 16641.292
2018-04-05 | 10581.8755 | 9659.701 | 9059.3109 | 8686.1232 | 8534.9976 | 8588.457 | 9027.4409 | 9579.5119 | 10889.267 | 12378.9335 | 13517.0018 | 14423.7553 | 15159.85 | 15905.1973 | 16416.1457 | 16792.4176 | 16934.2906 | 16841.7647 | 16217.7291 | 15391.1647 | 15299.6669 | 14403.194 | 13323.7255 | 12073.5982 | 16934.2906
2018-04-06 | 10775.1518 | 9818.023 | 9127.1632 | 8712.8529 | 8540.1379 | 8565.8396 | 8861.9224 | 9277.2607 | 10650.7559 | 12246.3131 | 13510.8334 | 14416.5588 | 15235.9268 | 15950.4322 | 16605.3097 | 17022.7042 | 17225.2331 | 17210.8402 | 16719.425 | 16053.2387 | 16076.8842 | 15034.426 | 13731.8674 | 12101.3559 | 17225.2331
2018-04-07 | 10835.8076 | 9955.7838 | 9471.565 | 9236.1381 | 9300.9062 | 9951.6715 | 11301.5212 | 12066.4017 | 12744.9248 | 13995.0521 | 15226.6742 | 16291.7498 | 17167.6614 | 17942.8226 | 18551.4372 | 19009.9543 | 19290.6161 | 19178.557 | 18624.4299 | 18138.155 | 17992.1697 | 16799.6141 | 15319.2001 | 13777.1023 | 19290.6161
2018-04-08 | 12467.3471 | 11480.4045 | 10753.5624 | 10372.1502 | 10378.3186 | 10926.2774 | 12315.1935 | 13050.2601 | 13651.6783 | 14497.776 | 15477.5222 | 16287.6376 | 16761.5756 | 17008.3113 | 16958.9642 | 16697.8356 | 16838.6805 | 16274.2727 | 15189.6639 | 14663.2945 | 14734.231 | 13742.148 | 12353.2319 | 10865.6215 | 17008.3113
2018-04-09 | 9713.1604 | 8941.0834 | 8492.8469 | 8266.6726 | 8251.2516 | 8818.7436 | 10169.6213 | 10804.9657 | 11128.8062 | 11779.5715 | 12284.3515 | 12552.6766 | 12712.0267 | 12844.6471 | 13059.5127 | 13321.6694 | 13571.4892 | 13730.8393 | 13559.1524 | 13316.529 | 13686.6325 | 12866.2365 | 11542.0884 | 10139.8074 | 13730.8393
2018-04-10 | 8968.8411 | 8277.9813 | 7876.0078 | 7726.9383 | 7798.9029 | 8441.4437 | 9880.735 | 10639.4472 | 10998.2419 | 11590.4075 | 12135.2821 | 12529.0311 | 12795.3 | 13100.6353 | 13430.6443 | 13788.411 | 14035.1466 | 14028.9782 | 13786.3548 | 13615.696 | 13973.4627 | 13096.5231 | 11865.929 | 10433.8341 | 14035.1466
2018-04-11 | 9257.7275 | 8462.005 | 8046.6666 | 7869.8394 | 7928.4391 | 8510.324 | 9902.3244 | 10682.6259 | 11220.304 | 12090.0472 | 12870.3487 | 13400.8304 | 13766.8216 | 14130.7567 | 14461.7937 | 14583.1054 | 14621.1438 | 14435.064 | 14090.6622 | 13825.4213 | 14009.445 | 13362.792 | 12462.2068 | 11313.8579 | 14621.1438
2018-04-12 | 10181.9581 | 9381.0953 | 8811.5472 | 8484.6224 | 8346.8617 | 8452.7524 | 8932.8589 | 9529.1367 | 10845.0602 | 12279.2112 | 13368.9604 | 14204.7774 | 14766.101 | 15264.7127 | 15562.8516 | 15834.2608 | 15935.0112 | 15822.9521 | 15225.6462 | 14532.7302 | 14527.5899 | 13838.7862 | 12760.3457 | 11647.9791 | 15935.0112
2018-04-13 | 10547.9493 | 9687.4587 | 9146.6964 | 8781.7333 | 8628.5515 | 8685.0951 | 9003.7954 | 9455.116 | 10635.3349 | 12058.1772 | 13126.337 | 13886.0772 | 14547.1231 | 14983.0228 | 15164.9903 | 15310.9756 | 15349.014 | 15277.0494 | 14931.6195 | 14827.7849 | 15142.3729 | 14361.0433 | 13241.4803 | 11832.0028 | 15349.014
2018-04-14 | 10593.1842 | 9784.0969 | 9333.8043 | 9075.7599 | 9099.4054 | 9668.9536 | 11022.9155 | 11789.8522 | 12614.3605 | 13862.4317 | 15007.6963 | 15994.639 | 16785.2211 | 17557.2981 | 18167.9689 | 18684.0576 | 18953.4107 | 18864.9971 | 18297.5051 | 17580.9436 | 17481.2213 | 16394.5564 | 14885.3566 | 13172.5999 | 18953.4107
2018-04-15 | 11704.5227 | 10758.7027 | 10169.6213 | 9762.5075 | 9684.3745 | 10189.1546 | 11523.5833 | 12226.7799 | 13217.8348 | 14601.6106 | 15749.9595 | 16791.3895 | 17543.9333 | 18079.5553 | 18290.3087 | 18452.743 | 18334.5155 | 17616.9259 | 17248.8786 | 16736.9021 | 16774.9405 | 15789.0259 | 14288.0507 | 12648.2866 | 18452.743
2018-04-16 | 11286.1002 | 10354.6731 | 9768.6759 | 9465.3966 | 9401.6566 | 9882.7911 | 11116.4694 | 11723.0279 | 12156.8714 | 12824.0858 | 13381.2971 | 13762.7093 | 14158.5145 | 14613.9474 | 14942.9282 | 15188.6358 | 15337.7053 | 15283.2178 | 15027.2296 | 14966.5737 | 15248.2636 | 14605.7228 | 13381.2971 | 11893.6867 | 15337.7053
2018-04-17 | 10695.9907 | 9910.5489 | 9451.0037 | 9210.4365 | 9244.3626 | 9825.2195 | 11146.2833 | 11897.799 | 12556.7888 | 13538.5911 | 14399.0817 | 14952.1808 | 15136.2045 | 15278.0775 | 15331.5369 | 15250.3197 | 15126.9519 | 14868.9075 | 14628.3403 | 14482.355 | 14665.3506 | 14115.3357 | 13127.365 | 11853.5922 | 15331.5369
2018-04-18 | 10702.1591 | 9893.0718 | 9367.7305 | 9078.8441 | 9033.6092 | 9491.0983 | 10427.6657 | 11213.1076 | 12250.4254 | 13540.6473 | 14587.2177 | 15281.1617 | 15708.8368 | 16172.4943 | 16397.6406 | 16357.546 | 16268.1043 | 16162.2136 | 15715.0052 | 15185.5516 | 15214.3375 | 14581.0493 | 13674.2957 | 12605.1079 | 16397.6406
2018-04-19 | 11439.2819 | 10664.1207 | 10122.3303 | 9768.6759 | 9648.3923 | 9760.4514 | 9975.317 | 10300.1856 | 11232.6408 | 12773.7106 | 14026.9221 | 14885.3566 | 15576.2164 | 16080.9965 | 16356.5179 | 16542.5977 | 16512.7839 | 16137.54 | 15406.5857 | 14510.1128 | 14350.7627 | 13536.535 | 12573.2379 | 11225.4443 | 16542.5977
2018-04-20 | 10003.0748 | 9089.1248 | 8466.1172 | 8141.2486 | 8004.5159 | 8076.4805 | 8405.4614 | 8794.07 | 9891.0157 | 11028.0558 | 11657.2317 | 12171.2644 | 12515.6662 | 12763.4299 | 12929.9765 | 13060.5408 | 13144.8421 | 13056.4285 | 12833.3384 | 12705.8583 | 13152.0386 | 12653.427 | 11652.0914 | 10329.9995 | 13152.0386
2018-04-21 | 9166.2297 | 8403.4053 | 7996.2914 | 7797.8748 | 7859.5587 | 8470.2295 | 9757.3672 | 10447.199 | 11013.6629 | 11737.4208 | 12412.8597 | 12925.8642 | 13444.0091 | 13861.4036 | 14333.2856 | 14706.4732 | 15006.6683 | 14979.9386 | 14749.652 | 14429.9237 | 14675.6313 | 13804.86 | 12495.1049 | 11067.1223 | 15006.6683
2018-04-22 | 9729.6094 | 8835.1927 | 8401.3491 | 8135.0802 | 8140.2206 | 8802.2946 | 10149.06 | 10735.0572 | 11332.3631 | 12064.3456 | 12824.0858 | 13574.5734 | 14137.9532 | 14595.4422 | 15067.3241 | 15637.9003 | 16031.6493 | 16105.67 | 15804.4469 | 15345.9298 | 15552.5709 | 14634.5087 | 13163.3473 | 11531.8078 | 16105.67
2018-04-23 | 10184.0143 | 9327.6359 | 8787.9017 | 8460.9769 | 8408.5456 | 8952.3921 | 10194.2949 | 9497.2667 | 11556.4813 | 12393.3264 | 13191.1051 | 13782.2426 | 14485.4392 | 15329.4808 | 16223.8975 | 16893.168 | 17375.3306 | 17496.6423 | 17122.4265 | 16405.8651 | 16330.8163 | 15544.3464 | 14099.9147 | 12152.7592 | 17496.6423
2018-04-24 | 10813.1902 | 9913.6331 | 9076.788 | 8717.9932 | 8729.3019 | 9061.367 | 10270.3717 | 10982.8209 | 11765.1786 | 12875.489 | 13982.7153 | 14909.0021 | 15753.0436 | 16501.4751 | 17128.5949 | 17740.2938 | 18093.9482 | 18047.6853 | 17527.4842 | 16712.2285 | 16644.3762 | 15695.472 | 14180.1038 | 12554.7327 | 18093.9482
2018-04-25 | 11101.0484 | 10049.3377 | 9388.2918 | 9004.8234 | 8915.3817 | 9407.825 | 10605.521 | 11280.9599 | 12120.8892 | 13267.1819 | 14478.2428 | 15532.0096 | 16446.9877 | 17286.917 | 18009.6468 | 18619.2895 | 18952.3827 | 18861.9129 | 18162.8286 | 17135.7914 | 16849.9893 | 15919.5902 | 14591.3299 | 13127.365 | 18952.3827
2018-04-26 | 11649.0072 | 10535.6126 | 9805.6862 | 9331.7482 | 9059.3109 | 9077.8161 | 9382.1234 | 9977.3731 | 11456.759 | 13089.3266 | 14559.4599 | 15815.7556 | 16795.5018 | 17534.6807 | 17977.7768 | 18371.5258 | 18574.0547 | 18453.771 | 17777.3041 | 16739.9863 | 16449.0438 | 15591.6374 | 14427.8676 | 13141.7579 | 18574.0547
2018-04-27 | 11885.4622 | 10895.4354 | 10150.0881 | 9702.8797 | 9415.0215 | 9364.6463 | 9529.1367 | 9992.7941 | 11621.2495 | 13460.4582 | 14986.107 | 16212.5888 | 17160.465 | 17926.3736 | 18434.2378 | 18867.0533 | 19038.7401 | 18923.5968 | 18319.0945 | 17455.5197 | 17330.0957 | 16392.5002 | 14914.1424 | 13421.3917 | 19038.7401
2018-04-28 | 12112.6646 | 11213.1076 | 10638.4191 | 10278.5963 | 10247.7543 | 10815.2463 | 12016.0265 | 12719.2231 | 13651.6783 | 14935.7318 | 16371.9389 | 17566.5507 | 18461.9955 | 19223.7919 | 19852.9678 | 20335.1304 | 20462.6105 | 20412.2353 | 19843.7152 | 18981.1685 | 18733.4048 | 17588.1401 | 15932.9551 | 14261.321 | 20462.6105
2018-04-29 | 12890.91 | 11921.4445 | 11288.1563 | 10921.137 | 10859.4531 | 11363.2051 | 12493.0488 | 13181.8525 | 14288.0507 | 15666.6862 | 17023.7323 | 18161.8005 | 18994.5333 | 19661.7477 | 20124.377 | 20452.3299 | 20384.4775 | 20146.9945 | 19675.1125 | 18899.9513 | 18603.8686 | 17523.372 | 15923.7025 | 14254.1245 | 20452.3299
2018-04-30 | 12845.6752 | 11959.4829 | 11380.6822 | 11056.8416 | 11036.2803 | 11532.8358 | 12688.3812 | 13371.0165 | 14438.1482 | 15814.7276 | 17152.2404 | 18201.895 | 18975.0001 | 19643.2425 | 20050.3563 | 20329.9901 | 20185.0329 | 19389.3104 | 18795.0887 | 18154.604 | 18110.3972 | 17140.9317 | 15612.1987 | 14016.6415 | 20329.9901
2018-05-01 | 12619.5008 | 11701.4385 | 11086.6555 | 10756.6466 | 10663.0927 | 11208.9953 | 12433.421 | 13149.9825 | 14121.5041 | 15511.4483 | 16921.9538 | 17977.7768 | 18810.5097 | 19517.8185 | 19966.055 | 20190.1732 | 20078.1141 | 19482.8643 | 18569.9424 | 17861.6054 | 17795.8093 | 16741.0143 | 15308.9195 | 13785.3268 | 20190.1732
2018-05-02 | 12483.7962 | 11569.8462 | 10980.7648 | 10619.9139 | 10525.3319 | 11042.4487 | 12225.7518 | 12961.8465 | 13830.5617 | 15083.7732 | 16147.8207 | 16942.5151 | 17402.0603 | 17931.5139 | 18310.87 | 18509.2865 | 18385.9187 | 18012.731 | 17438.0426 | 16655.6849 | 16640.2639 | 15522.757 | 14393.9414 | 13173.628 | 18509.2865
2018-05-03 | 11965.6513 | 11044.5049 | 10425.6096 | 10049.3377 | 9857.0895 | 9962.9802 | 10323.8311 | 10887.2109 | 11989.2968 | 13334.0061 | 14418.615 | 15154.7097 | 15491.9151 | 15653.3213 | 15562.8516 | 15148.5413 | 14190.3845 | 13818.2249 | 13474.8511 | 13380.2691 | 13614.668 | 13182.8806 | 12451.9262 | 11524.6113 | 15653.3213
2018-05-04 | 10569.5387 | 9816.995 | 9348.1972 | 9030.5251 | 8930.8027 | 8932.8589 | 9053.1425 | 9199.1278 | 10266.2595 | 11470.1239 | 12407.7194 | 13074.9337 | 13750.3726 | 14328.1452 | 14826.7569 | 15381.9121 | 15812.6714 | 16030.6213 | 15842.4853 | 15167.0465 | 14937.7879 | 14055.7079 | 12908.3871 | 11303.5773 | 16030.6213
2018-05-05 | 10028.7764 | 9028.4689 | 8639.8603 | 8360.2265 | 8368.451 | 8948.2798 | 10087.3761 | 10788.5166 | 11609.9407 | 12682.2128 | 13776.0742 | 14686.94 | 15545.3745 | 16329.7882 | 17049.4339 | 17651.8801 | 18178.2495 | 18252.2702 | 17829.7354 | 16450.0719 | 16489.1384 | 15448.7363 | 13466.6266 | 12145.5627 | 18252.2702
2018-05-06 | 10689.8223 | 9773.8162 | 9158.0051 | 8792.0139 | 8705.6564 | 9205.2961 | 10359.8134 | 11063.01 | 11906.0235 | 13078.0179 | 14240.7597 | 15363.4069 | 16413.0615 | 17203.6437 | 17950.0191 | 18592.5598 | 19000.7017 | 18973.972 | 18468.1639 | 17115.2301 | 17281.7767 | 16270.1605 | 14728.0626 | 12977.2675 | 19000.7017
2018-05-07 | 11584.2391 | 10629.1665 | 10074.0113 | 9704.9358 | 9624.7468 | 10099.7129 | 11238.8092 | 11931.7252 | 12917.6397 | 14097.8586 | 15376.7718 | 16426.4264 | 17353.7412 | 18197.7828 | 18957.523 | 19331.7387 | 19607.2602 | 19530.1553 | 18923.5968 | 18038.4327 | 17823.567 | 16952.7958 | 15374.7156 | 13734.9516 | 19607.2602
2018-05-08 | 12270.9867 | 11347.7841 | 10759.7308 | 10331.0276 | 10230.2772 | 10673.3733 | 11777.5154 | 12418 | 13458.402 | 14684.8839 | 15910.3376 | 16909.617 | 17751.6025 | 18541.1566 | 19148.7431 | 19684.3651 | 20008.2057 | 19918.764 | 19399.591 | 18453.771 | 18090.864 | 17129.623 | 15659.4897 | 14099.9147 | 20008.2057
2018-05-09 | 12481.7401 | 11460.8713 | 10883.0986 | 10441.0306 | 10332.0556 | 10791.6008 | 11890.6025 | 12544.452 | 13530.3666 | 14768.1571 | 15953.5164 | 16913.7293 | 17736.1815 | 18466.1078 | 19118.9292 | 19600.0638 | 19840.631 | 19602.1199 | 18858.8287 | 17810.2022 | 17370.1903 | 16478.8577 | 15316.1159 | 14023.8379 | 19840.631
2018-05-10 | 12730.5318 | 11809.3854 | 11189.4621 | 10745.3379 | 10531.5003 | 10585.9878 | 10809.0779 | 11390.9628 | 12944.3694 | 14525.5338 | 15673.8826 | 16545.6819 | 17425.7058 | 17997.3101 | 18366.3855 | 18637.7947 | 18622.3737 | 18422.9291 | 17853.3809 | 16842.7928 | 16940.459 | 16183.803 | 15185.5516 | 13974.4908 | 18637.7947
2018-05-11 | 12765.4861 | 11876.2096 | 11220.304 | 10797.7692 | 10591.1281 | 10537.6687 | 10620.942 | 10982.8209 | 12239.1167 | 13754.4848 | 14948.0686 | 15863.0466 | 16662.8814 | 17337.2922 | 17831.7916 | 18076.4711 | 18167.9689 | 17916.0929 | 17389.7235 | 16627.9272 | 16642.3201 | 16121.091 | 14941.9002 | 13442.9811 | 18167.9689
2018-05-12 | 12046.8685 | 11134.9746 | 10567.4826 | 10269.3437 | 10243.642 | 10763.843 | 11884.4342 | 12542.3959 | 13454.2898 | 14748.6239 | 16043.9861 | 17074.1075 | 17911.9806 | 18564.8021 | 19039.7682 | 19453.0504 | 19606.2322 | 19478.7521 | 19049.0208 | 18399.2836 | 18218.3441 | 17181.0263 | 15650.2371 | 14093.7464 | 19606.2322
2018-05-13 | 12722.3073 | 11844.3396 | 11221.3321 | 10838.8918 | 10755.6185 | 11249.0898 | 12347.0635 | 12973.1552 | 13839.8142 | 15113.5871 | 16301.0024 | 17194.3911 | 18001.4223 | 18531.904 | 18922.5688 | 19246.4093 | 19412.9559 | 19227.9042 | 18685.0857 | 17944.8787 | 17829.7354 | 17020.6481 | 15574.1603 | 13957.0137 | 19412.9559
2018-05-14 | 12709.9705 | 11837.1432 | 11182.2656 | 10800.8534 | 10727.8608 | 10929.3615 | 12436.5052 | 12940.2572 | 13899.442 | 15296.5827 | 16483.998 | 17578.8875 | 18354.0487 | 18842.3797 | 19185.7535 | 19175.4728 | 19075.7505 | 18859.8568 | 18272.8315 | 17575.8033 | 17626.1785 | 16783.165 | 15433.3154 | 13845.9826 | 19185.7535
2018-05-15 | 12470.4313 | 11563.6778 | 10951.979 | 10615.8017 | 10603.4649 | 11090.7678 | 12206.2186 | 12821.0016 | 13628.0328 | 14955.265 | 16114.9226 | 16717.3688 | 16940.459 | 16896.2522 | 16538.4855 | 16121.091 | 16006.9758 | 15990.5267 | 15771.5488 | 15411.726 | 15411.726 | 14837.0375 | 13638.3135 | 12302.8567 | 16940.459
2018-05-16 | 11079.4591 | 10300.1856 | 9797.4617 | 9478.7615 | 9430.4424 | 9988.6819 | 11141.143 | 11645.923 | 12021.1668 | 12697.6338 | 13273.3503 | 13679.4361 | 13860.3755 | 13983.7434 | 14238.7036 | 14384.6888 | 14548.1512 | 14377.4924 | 13930.284 | 13348.3991 | 13105.7757 | 12579.4063 | 11684.9895 | 10541.781 | 14548.1512
2018-05-17 | 9445.8634 | 8721.0774 | 8220.4096 | 7937.6917 | 7852.3623 | 7949.0004 | 8254.3358 | 8833.1365 | 10053.45 | 11317.9702 | 12341.9232 | 13121.1966 | 13687.6606 | 14204.7774 | 14700.3048 | 15089.9416 | 15334.6211 | 15288.3582 | 14836.0095 | 14058.7921 | 13825.4213 | 13371.0165 | 12401.551 | 11317.9702 | 15334.6211
2018-05-18 | 10261.1191 | 9461.2844 | 8905.1011 | 8526.7731 | 8356.1143 | 8391.0685 | 8494.9031 | 8963.7008 | 10266.2595 | 11756.9541 | 12940.2572 | 13830.5617 | 14565.6283 | 15158.8219 | 15693.4159 | 16079.9684 | 16357.546 | 16294.834 | 15772.5769 | 15029.2857 | 14943.9563 | 14390.8572 | 13199.3296 | 11774.4312 | 16357.546
2018-05-19 | 10520.1916 | 9653.5326 | 9109.6861 | 8841.361 | 8853.6978 | 9378.0111 | 10493.4619 | 11145.2552 | 12110.6085 | 13247.6487 | 14298.3313 | 15185.5516 | 15936.0393 | 16677.2743 | 17171.7737 | 17647.7679 | 17904.7842 | 17863.6616 | 17437.0145 | 16606.3378 | 16313.3392 | 15545.3745 | 14171.8793 | 12532.1153 | 17904.7842
2018-05-20 | 11156.564 | 10212.8001 | 9666.8974 | 9333.8043 | 9238.1942 | 9681.2903 | 10726.8327 | 11496.8536 | 12449.87 | 13609.5276 | 14740.3994 | 15660.5178 | 16390.4441 | 16994.9465 | 17422.6216 | 17764.9673 | 17964.412 | 17875.9984 | 17513.0913 | 16659.7972 | 16397.6406 | 15547.4306 | 14134.869 | 12556.7888 | 17964.412
2018-05-21 | 11180.2095 | 10224.1088 | 9615.4942 | 9224.8294 | 9117.9106 | 9562.0348 | 10641.5033 | 11388.9067 | 12230.8921 | 13289.7993 | 14327.1172 | 15231.8146 | 15982.3022 | 16781.1089 | 17534.6807 | 18044.6011 | 18351.9926 | 18225.5405 | 17696.0869 | 16807.8386 | 16396.6125 | 15647.1529 | 14255.1526 | 12626.6973 | 18351.9926
2018-05-22 | 11111.3291 | 10122.3303 | 9425.3021 | 9065.4793 | 9001.7392 | 9477.7334 | 10568.5106 | 11268.6231 | 12248.3692 | 13405.9707 | 14626.2841 | 15776.6891 | 16829.428 | 17836.9319 | 18584.3353 | 19211.4551 | 19603.148 | 19482.8643 | 18923.5968 | 17932.542 | 17365.0499 | 16621.7588 | 15025.1735 | 13300.08 | 19603.148
2018-05-23 | 11741.5331 | 10688.7943 | 9964.0083 | 9536.3332 | 9363.6182 | 9756.3391 | 10715.524 | 11604.8004 | 12767.5422 | 14152.3461 | 15569.02 | 16950.7396 | 18111.4253 | 19270.0548 | 20106.8999 | 20652.8026 | 20827.5737 | 20591.1187 | 19857.0801 | 18578.1669 | 18037.4046 | 17267.3837 | 15909.3096 | 14425.8114 | 20827.5737
2018-05-24 | 13002.9691 | 11927.6129 | 11082.5433 | 10500.6583 | 10184.0143 | 10097.6568 | 10179.902 | 10812.1621 | 12482.7681 | 14307.5839 | 15933.9831 | 17416.4532 | 18655.2718 | 19505.4818 | 20020.5425 | 20294.0078 | 20281.671 | 20049.3283 | 19250.5216 | 18209.0915 | 17763.9393 | 16970.2729 | 15758.184 | 14422.7272 | 20294.0078
2018-05-25 | 13166.4315 | 12100.3279 | 11291.2405 | 10754.5905 | 10426.6376 | 10302.2418 | 10354.6731 | 10754.5905 | 12100.3279 | 13759.6251 | 15519.6728 | 16898.3083 | 18106.285 | 18902.0075 | 19371.8333 | 19640.1583 | 19729.6 | 19359.4965 | 18578.1669 | 17673.4695 | 17388.6954 | 16673.162 | 15419.9505 | 14152.3461 | 19729.6
2018-05-26 | 12829.2261 | 11890.6025 | 11195.6304 | 10739.1695 | 10488.3216 | 10492.4338 | 10603.4649 | 11123.6659 | 12743.8967 | 14647.8735 | 16339.0408 | 17543.9333 | 18551.4372 | 19242.2971 | 19626.7935 | 19826.2381 | 19832.4065 | 19523.9869 | 18762.1906 | 17853.3809 | 17661.1327 | 16838.6805 | 15468.2696 | 13887.1052 | 19832.4065
2018-05-27 | 12560.9011 | 11600.6881 | 10969.4561 | 10582.9036 | 10453.3673 | 10935.5299 | 11932.7532 | 12801.4683 | 13962.154 | 15381.9121 | 16738.9582 | 17941.7945 | 18821.8184 | 19494.173 | 19883.8098 | 20066.8054 | 19774.8349 | 19008.9263 | 18284.1403 | 17574.7752 | 17492.53 | 16733.8179 | 15376.7718 | 13714.3903 | 20066.8054
2018-05-28 | 12365.5687 | 11436.1977 | 10848.1444 | 10479.069 | 10389.6273 | 10863.5654 | 11901.9113 | 12663.7076 | 13747.2884 | 15038.5383 | 16356.5179 | 17685.8063 | 18620.3176 | 19383.142 | 19796.4242 | 19913.6237 | 19902.3149 | 19504.4537 | 18878.362 | 18181.3337 | 17957.2155 | 17144.0159 | 15747.9033 | 14183.188 | 19913.6237
2018-05-29 | 12763.4299 | 11740.505 | 11127.7781 | 10752.5343 | 10619.9139 | 11050.6732 | 12058.1772 | 12811.749 | 13728.7832 | 14868.9075 | 16045.0142 | 16872.6067 | 17369.1622 | 17694.0308 | 17467.8565 | 17218.0366 | 17058.6865 | 16857.1857 | 16672.134 | 16110.8103 | 16056.3229 | 15513.5044 | 14386.7449 | 12991.6604 | 17694.0308
2018-05-30 | 11601.7162 | 10599.3526 | 10105.8813 | 9799.5179 | 9742.9743 | 10188.1265 | 11168.9007 | 11944.0619 | 13015.3059 | 14549.1793 | 15894.9166 | 16983.6377 | 17833.8477 | 18487.6972 | 18871.1655 | 19116.8731 | 19047.9927 | 18528.8198 | 17596.3646 | 16826.3438 | 16596.0571 | 15907.2534 | 14831.8972 | 13662.987 | 19116.8731
2018-05-31 | 12499.2172 | 11497.8816 | 10799.8253 | 10343.3644 | 10167.5652 | 10136.7232 | 10343.3644 | 11008.5226 | 12651.3708 | 14464.8779 | 16052.2106 | 17268.4118 | 18045.6291 | 18540.1285 | 18622.3737 | 18547.325 | 18272.8315 | 17671.4134 | 16973.3571 | 16234.1782 | 16134.4558 | 15635.8442 | 14732.1749 | 13561.2086 | 18622.3737
2018-06-01 | 12492.0207 | 11530.7797 | 10899.5477 | 10456.4515 | 10213.8281 | 10201.4914 | 10296.0734 | 10767.9553 | 12167.1521 | 13859.3475 | 15384.9963 | 16517.9242 | 17444.211 | 18075.443 | 18398.2555 | 18318.0664 | 17928.4297 | 17255.047 | 16504.5593 | 15988.4706 | 15978.1899 | 15620.4232 | 14637.5929 | 13328.8658 | 18398.2555
2018-06-02 | 12141.4505 | 11316.9421 | 10840.9479 | 10574.679 | 10607.5771 | 11182.2656 | 12201.0782 | 12880.6294 | 13507.7492 | 14230.479 | 14919.2827 | 15307.8914 | 15687.2475 | 15940.1515 | 16109.7823 | 16101.5578 | 16062.4913 | 15868.187 | 15668.7423 | 15448.7363 | 15518.6448 | 15084.8012 | 13962.154 | 12627.7253 | 16109.7823
2018-06-03 | 11402.2716 | 10569.5387 | 10053.45 | 9742.9743 | 9724.4691 | 10250.8385 | 11305.6334 | 11972.8478 | 12607.164 | 13500.5527 | 14391.8853 | 15142.3729 | 15685.1913 | 16076.8842 | 16240.3466 | 16293.806 | 16094.3613 | 15878.4676 | 15508.3641 | 15185.5516 | 15291.4424 | 14732.1749 | 13637.2854 | 12250.4254 | 16293.806
2018-06-04 | 10979.7367 | 10125.4145 | 9589.7925 | 9310.1588 | 9306.0465 | 9819.0511 | 10841.976 | 10994.1297 | 12334.7267 | 13542.7034 | 14536.8425 | 15315.0879 | 15845.5695 | 16476.8016 | 16929.1503 | 17233.4576 | 17464.7723 | 17511.0352 | 17211.8682 | 16512.7839 | 16165.2978 | 15577.2445 | 14414.5027 | 12918.6678 | 17511.0352
2018-06-05 | 11561.6217 | 10644.5875 | 10021.5799 | 9636.0555 | 9512.6876 | 9938.3067 | 10830.6673 | 11765.1786 | 13030.7269 | 14408.3343 | 15809.5872 | 17043.2655 | 17980.861 | 18837.2394 | 19424.2646 | 19843.7152 | 20018.4863 | 19941.3814 | 19449.9662 | 18443.4904 | 17872.9142 | 16966.1606 | 15525.8412 | 13816.1687 | 20018.4863
2018-06-06 | 12431.3649 | 11346.756 | 10606.5491 | 10136.7232 | 9917.7454 | 10249.8104 | 10960.2035 | 11903.9674 | 13388.4936 | 14997.4157 | 16633.0675 | 18112.4534 | 19286.5039 | 20165.4996 | 20777.1985 | 21116.46 | 21227.491 | 21023.9341 | 20364.9443 | 19306.0371 | 18605.9247 | 17815.3425 | 16481.9419 | 15089.9416 | 21227.491
2018-06-07 | 13714.3903 | 12632.8656 | 11853.5922 | 11360.1209 | 11018.8032 | 10898.5196 | 10999.27 | 11671.6247 | 13368.9604 | 15157.7939 | 16944.5713 | 18482.5569 | 19476.6959 | 20164.4716 | 20567.4732 | 20675.42 | 20302.2323 | 19729.6 | 18961.6353 | 18170.025 | 17625.1504 | 16881.8593 | 15703.6965 | 14402.1659 | 20675.42
2018-06-08 | 13168.4876 | 12149.675 | 11410.4961 | 10763.843 | 10558.23 | 10479.069 | 10493.4619 | 10934.5019 | 12421.0842 | 14382.6327 | 16212.5888 | 17741.3218 | 18632.6544 | 18835.1832 | 18606.9527 | 18464.0517 | 18192.6425 | 17901.7 | 17340.3764 | 16657.7411 | 16270.1605 | 15665.6581 | 14372.352 | 13100.6353 | 18835.1832
2018-06-09 | 11772.375 | 10837.8637 | 10182.9862 | 9844.7527 | 9797.4617 | 10226.1649 | 11015.719 | 11875.1816 | 13112.9721 | 14606.7509 | 16214.6449 | 17819.4548 | 19026.4034 | 20013.346 | 20535.6031 | 20379.3372 | 20100.7315 | 19389.3104 | 18544.2408 | 17786.5567 | 17357.8535 | 16614.5623 | 15233.8707 | 13706.1658 | 20535.6031
2018-06-10 | 12316.2216 | 11337.5034 | 10730.945 | 10346.4486 | 10246.7262 | 10665.1488 | 11458.8151 | 12469.4033 | 13868.6001 | 15331.5369 | 16678.3024 | 17882.1668 | 18801.2571 | 19305.009 | 19278.2793 | 18615.1773 | 18013.7591 | 17728.985 | 17653.9363 | 17113.174 | 16933.2625 | 16122.1191 | 14753.7642 | 13280.5467 | 19305.009
2018-06-11 | 12029.3914 | 11110.301 | 10457.4796 | 10102.7971 | 10021.5799 | 10390.6554 | 11222.3601 | 12123.9734 | 13404.9426 | 15015.9209 | 16439.7912 | 17615.8979 | 18342.74 | 18786.8642 | 18342.74 | 17558.3262 | 17157.3808 | 17031.9568 | 16853.0735 | 16310.255 | 16049.1264 | 15504.2519 | 14295.2471 | 12918.6678 | 18786.8642
2018-06-12 | 11668.5405 | 10746.3659 | 10153.1723 | 9784.0969 | 9700.8236 | 10054.478 | 10867.6776 | 11570.8743 | 12314.1654 | 13286.7151 | 14504.9724 | 15805.475 | 17176.914 | 18381.8065 | 19172.3886 | 19345.1036 | 18856.7726 | 18080.5833 | 17485.3336 | 16868.4944 | 16538.4855 | 15825.0082 | 14416.5588 | 12973.1552 | 19345.1036
2018-06-13 | 11680.8772 | 10751.5063 | 10140.8355 | 9742.9743 | 9667.9255 | 10016.4396 | 10729.9169 | 11686.0176 | 13062.5969 | 14477.2147 | 15826.0363 | 17109.0617 | 18092.9201 | 18588.4476 | 18577.1389 | 18035.3485 | 17477.1091 | 16878.7751 | 16342.125 | 15555.6551 | 15076.5767 | 14592.358 | 13660.9309 | 12481.7401 | 18588.4476
2018-06-14 | 11369.3735 | 10507.8548 | 9899.2402 | 9533.249 | 9369.7866 | 9435.5828 | 9662.7852 | 10306.354 | 11742.5612 | 13434.7565 | 15020.0331 | 16414.0896 | 17467.8565 | 18318.0664 | 18706.6751 | 18676.8612 | 18177.2215 | 17673.4695 | 16879.8031 | 16009.0319 | 15674.9107 | 15101.2503 | 14123.5602 | 12989.6043 | 18706.6751
2018-06-15 | 11896.7709 | 11084.5994 | 10433.8341 | 10039.0571 | 9924.9418 | 10026.7203 | 10209.7159 | 10809.0779 | 12338.839 | 14135.897 | 15709.8649 | 17112.1459 | 18231.7089 | 18937.9898 | 19343.0475 | 19190.8938 | 18653.2157 | 17974.6926 | 17248.8786 | 16487.0822 | 16334.9286 | 15972.0215 | 14891.525 | 13674.2957 | 19343.0475
2018-06-16 | 12368.6529 | 11497.8816 | 10938.6141 | 10587.0158 | 10466.7322 | 10847.1163 | 11584.2391 | 12342.9513 | 13315.501 | 14513.197 | 16051.1826 | 17501.7826 | 18482.5569 | 19339.9633 | 19930.0727 | 20276.5307 | 20483.1718 | 20337.1865 | 19598.0076 | 18319.0945 | 17710.4799 | 16935.3187 | 15532.0096 | 14017.6695 | 20483.1718
2018-06-17 | 12620.5289 | 11662.3721 | 10941.6983 | 10518.1355 | 10368.0379 | 10694.9627 | 11455.731 | 12283.3235 | 13295.9677 | 14374.4082 | 15403.5015 | 16333.9005 | 17126.5388 | 17815.3425 | 18047.6853 | 18043.573 | 17865.7177 | 17704.3115 | 17374.3025 | 16826.3438 | 16498.3909 | 16064.5474 | 14657.1261 | 13186.9928 | 18047.6853
2018-06-18 | 11821.7222 | 10925.2493 | 10346.4486 | 9977.3731 | 9916.7173 | 10299.1576 | 11138.0588 | 11988.2687 | 13135.5895 | 14400.1098 | 15755.0998 | 17012.4236 | 17687.8624 | 17926.3736 | 17771.1357 | 17348.6009 | 16867.4664 | 16455.2122 | 16049.1264 | 15642.0126 | 15483.6906 | 15076.5767 | 13920.0033 | 12571.1817 | 17926.3736
2018-06-19 | 11313.8579 | 10492.4338 | 9984.5696 | 9683.3465 | 9605.2135 | 9994.8502 | 10811.134 | 11646.9511 | 12884.7416 | 14293.191 | 15768.4646 | 16919.8977 | 17857.4932 | 18531.904 | 18586.3914 | 18002.4504 | 17453.4636 | 16889.0557 | 16317.4515 | 15772.5769 | 15482.6625 | 14863.7672 | 13775.0461 | 12411.8316 | 18586.3914
2018-06-20 | 11167.8727 | 10312.5224 | 9753.2549 | 9442.7792 | 9363.6182 | 9702.8797 | 10457.4796 | 11348.8122 | 12652.3989 | 14223.2826 | 15683.1352 | 16995.9745 | 17988.0575 | 18547.325 | 18385.9187 | 17573.7472 | 17056.6304 | 16592.9729 | 16198.1959 | 15677.9949 | 15368.5472 | 14984.0508 | 14046.4554 | 12871.3768 | 18547.325
2018-06-21 | 11660.3159 | 10809.0779 | 10199.4352 | 9840.6405 | 9682.3184 | 9745.0304 | 9900.2682 | 10654.8681 | 12440.6174 | 14361.0433 | 15895.9447 | 17285.8889 | 18370.4977 | 18995.5614 | 18808.4535 | 18136.0989 | 17553.1859 | 17076.1636 | 16495.3067 | 15884.636 | 15578.2726 | 15212.2813 | 14305.5278 | 13104.7476 | 18995.5614
2018-06-22 | 11913.22 | 11126.7501 | 10490.3777 | 10090.4603 | 9862.2298 | 9848.865 | 9909.5208 | 10656.9243 | 12358.3722 | 14331.2294 | 15955.5725 | 17172.8017 | 18293.3928 | 19106.5925 | 19622.6812 | 19701.8422 | 19366.693 | 18607.9808 | 17641.5995 | 16797.5579 | 16453.1561 | 15940.1515 | 14854.5146 | 13431.6723 | 19701.8422
2018-06-23 | 12097.2437 | 11283.016 | 10703.1872 | 10352.6169 | 10276.5401 | 10678.5136 | 11456.759 | 12397.4387 | 13754.4848 | 15244.1514 | 16814.007 | 18190.5863 | 19387.2543 | 20336.1585 | 20872.8085 | 20994.1202 | 20782.3388 | 20320.7375 | 19644.2706 | 18700.5067 | 18073.3869 | 17233.4576 | 15885.6641 | 14239.7316 | 20994.1202
2018-06-24 | 12836.4226 | 11839.1993 | 11178.1533 | 10746.3659 | 10602.4368 | 10945.8106 | 11702.4666 | 12623.6131 | 14048.5115 | 15582.3848 | 17241.6821 | 18638.8228 | 19828.2943 | 20867.6682 | 21477.3109 | 21809.376 | 21869.0037 | 21459.8338 | 20919.0715 | 19983.5321 | 19468.4714 | 18573.0266 | 17098.781 | 15436.3996 | 21869.0037
2018-06-25 | 13973.4627 | 12877.5452 | 12069.4859 | 11563.6778 | 11372.4577 | 11673.6808 | 12388.1861 | 13290.8274 | 14712.6416 | 16399.6967 | 18129.9305 | 19427.3488 | 20578.7819 | 21472.1706 | 22022.1855 | 22076.6729 | 21619.1839 | 21020.8499 | 20264.1939 | 19267.9987 | 18652.1876 | 17849.2687 | 16581.6642 | 14969.6579 | 22076.6729
2018-06-26 | 13557.0963 | 12441.6455 | 11683.9614 | 11195.6304 | 11005.4384 | 11266.5669 | 12005.7459 | 12899.1345 | 14363.0994 | 16140.6242 | 17837.9599 | 19148.7431 | 20148.0225 | 20799.8159 | 21437.2163 | 21644.8855 | 21650.0259 | 21323.1011 | 20728.8794 | 19755.3016 | 19055.1892 | 18197.7828 | 16789.3334 | 15138.2606 | 21650.0259
2018-06-27 | 13666.0712 | 12641.0902 | 11900.8832 | 11431.0574 | 11275.8195 | 11599.6601 | 12210.3308 | 13079.046 | 14521.4215 | 16184.831 | 17675.5256 | 18982.1966 | 19793.34 | 20473.9192 | 21055.8041 | 21118.5161 | 20896.454 | 20350.5514 | 19359.4965 | 18312.9261 | 17727.957 | 16903.4486 | 15852.766 | 14488.5234 | 21118.5161
2018-06-28 | 13054.3724 | 12011.9142 | 11305.6334 | 10772.0676 | 10447.199 | 10182.9862 | 10904.688 | 11337.5034 | 13082.1302 | 15073.4925 | 16635.1236 | 18201.895 | 19442.7698 | 20206.6223 | 20671.3077 | 21016.7377 | 20975.6151 | 20734.0197 | 20015.4021 | 19013.0385 | 18443.4904 | 17741.3218 | 16570.3555 | 15149.5694 | 21016.7377
2018-06-29 | 13820.281 | 12803.5245 | 12044.8123 | 11506.1061 | 11194.6024 | 11073.2907 | 11034.2242 | 11522.5552 | 13307.2764 | 15417.8944 | 17313.6467 | 18973.972 | 20231.2958 | 20835.7982 | 20862.5279 | 20460.5544 | 20143.9103 | 19633.9899 | 18616.2053 | 17665.245 | 17093.6407 | 16506.6155 | 15368.5472 | 13953.9295 | 20862.5279
2018-06-30 | 12703.8021 | 11760.0383 | 11119.5536 | 10740.1975 | 10692.9065 | 11105.1607 | 11857.7045 | 12625.6692 | 13893.2736 | 15533.0377 | 17038.1252 | 18325.2629 | 19347.1597 | 20211.7626 | 20736.0759 | 20992.0641 | 20764.8617 | 19894.0904 | 19034.6279 | 18235.8212 | 17791.697 | 17120.3704 | 15982.3022 | 14501.8883 | 20992.0641
2018-07-01 | 13152.0386 | 12199.0221 | 11607.8846 | 11249.0898 | 11163.7604 | 11574.9865 | 12396.4106 | 13067.7372 | 13911.7788 | 15083.7732 | 16269.1324 | 17450.3794 | 18183.3899 | 18510.3146 | 18827.9868 | 18963.6914 | 19199.1183 | 19053.1331 | 18660.4121 | 18294.4209 | 18100.1166 | 17317.7589 | 15980.2461 | 14507.0286 | 19199.1183
2018-07-02 | 13064.653 | 12155.8434 | 11551.341 | 11221.3321 | 11115.4414 | 11452.6468 | 12209.3028 | 12979.3236 | 14240.7597 | 15819.8679 | 17489.4458 | 18633.6824 | 19315.2897 | 19398.563 | 19002.7579 | 18626.486 | 18525.7356 | 18379.7503 | 18094.9763 | 17572.7191 | 17380.4709 | 16948.6835 | 15879.4957 | 14398.0537 | 19398.563
2018-07-03 | 13226.0593 | 12286.4077 | 11730.2244 | 11356.0086 | 11295.3528 | 11624.3336 | 12371.7371 | 13158.207 | 14429.9237 | 16140.6242 | 17919.1771 | 19283.4197 | 20235.4081 | 20900.5663 | 21441.3286 | 21738.4395 | 21619.1839 | 20832.714 | 19971.1953 | 19118.9292 | 18590.5037 | 17978.8049 | 16830.456 | 15395.2769 | 21738.4395
2018-07-04 | 14085.5218 | 13009.1375 | 12209.3028 | 11666.4843 | 11377.598 | 11370.4015 | 11489.6571 | 11869.0132 | 13386.4375 | 15530.9816 | 17459.6319 | 18941.0739 | 19824.182 | 20250.8291 | 20395.7863 | 20358.7759 | 19321.4581 | 18044.6011 | 17120.3704 | 16286.6095 | 15756.1278 | 15080.689 | 14704.4171 | 13910.7507 | 20395.7863
2018-07-05 | 12815.8613 | 11869.0132 | 11233.6689 | 10812.1621 | 10607.5771 | 10615.8017 | 10743.2817 | 11108.2449 | 12386.13 | 13817.1968 | 15452.8486 | 16590.9168 | 17522.3439 | 18402.3678 | 18511.3427 | 17866.7458 | 17269.4399 | 16853.0735 | 16440.8193 | 16006.9758 | 15732.4823 | 15305.8353 | 14482.355 | 13379.241 | 18511.3427
2018-07-06 | 12343.9793 | 11497.8816 | 10908.8002 | 10503.7425 | 10374.2063 | 10395.7957 | 10486.2654 | 10887.2109 | 12353.2319 | 13815.1407 | 15114.6151 | 15616.311 | 16120.0629 | 16573.4397 | 16984.6658 | 17049.4339 | 16931.2064 | 16615.5904 | 16107.7262 | 15320.2282 | 15167.0465 | 14844.234 | 13916.9191 | 12702.7741 | 17049.4339
2018-07-07 | 11681.9053 | 10934.5019 | 10474.9567 | 10245.6982 | 10234.3894 | 10667.2049 | 11435.1696 | 12257.6218 | 13459.4301 | 14684.8839 | 15905.1973 | 16697.8356 | 17063.8268 | 17345.5167 | 17444.211 | 17727.957 | 17727.957 | 17681.694 | 17476.081 | 17207.756 | 17001.1148 | 16509.6997 | 15360.3227 | 13967.2943 | 17727.957
2018-07-08 | 12667.8199 | 11714.8034 | 11067.1223 | 10690.8504 | 10583.9316 | 10912.9125 | 11671.6247 | 12537.2556 | 13785.3268 | 15457.9889 | 17069.9952 | 18487.6972 | 19586.6989 | 20088.3948 | 19990.7286 | 19403.7033 | 18792.0045 | 18253.2983 | 17687.8624 | 16935.3187 | 16308.1989 | 15605.0023 | 14466.934 | 13170.5438 | 20088.3948
2018-07-09 | 11946.1181 | 11132.9185 | 10602.4368 | 10081.2077 | 10125.4145 | 10617.8578 | 11426.9451 | 12233.9763 | 13550.9279 | 15265.7407 | 16779.0528 | 18234.7931 | 19164.1641 | 19429.4049 | 18615.1773 | 17958.2436 | 17640.5714 | 17171.7737 | 16602.2255 | 16268.1043 | 15973.0496 | 16230.0659 | 14375.4362 | 13104.7476 | 19429.4049
2018-07-10 | 11821.7222 | 10970.4842 | 10454.3954 | 10160.3687 | 10072.9832 | 10447.199 | 11260.3986 | 12156.8714 | 13470.7388 | 15032.3699 | 16224.9256 | 17026.8165 | 17756.7428 | 18270.7754 | 18250.2141 | 17909.9245 | 17392.8077 | 16827.3718 | 16355.4899 | 15859.9624 | 15722.2017 | 15289.3862 | 14290.1068 | 13037.9234 | 18270.7754
2018-07-11 | 11798.0767 | 10965.3438 | 10431.778 | 10150.0881 | 10083.2639 | 10425.6096 | 11129.8343 | 12049.9527 | 13560.1805 | 15192.7481 | 16748.2108 | 18124.7902 | 19149.7712 | 19968.1111 | 20445.1334 | 20560.2767 | 20460.5544 | 20105.8719 | 19525.015 | 18632.6544 | 18103.2008 | 17522.3439 | 16402.7809 | 15078.6328 | 20560.2767
2018-07-12 | 13808.9723 | 12847.7313 | 12112.6646 | 11645.923 | 11279.9318 | 11283.016 | 11378.6261 | 11839.1993 | 13287.7432 | 15248.2636 | 16807.8386 | 18187.5021 | 19283.4197 | 19879.6975 | 20053.4405 | 20018.4863 | 19860.1643 | 19331.7387 | 18593.5879 | 17574.7752 | 17056.6304 | 16334.9286 | 15295.5546 | 14102.9989 | 20053.4405
2018-07-13 | 13124.2808 | 12352.2038 | 11790.8802 | 11349.8402 | 11057.8697 | 10942.7264 | 10966.3719 | 11480.4045 | 13129.4212 | 14948.0686 | 16455.2122 | 17790.6689 | 18751.9099 | 19232.0164 | 19623.7093 | 19896.1466 | 19845.7714 | 19473.6117 | 18861.9129 | 18068.2466 | 17631.3188 | 17159.4369 | 16052.2106 | 14720.8661 | 19896.1466
2018-07-14 | 13479.9914 | 12547.5362 | 11844.3396 | 11455.731 | 11351.8964 | 11660.3159 | 12375.8493 | 13154.0947 | 14537.8705 | 16151.933 | 17724.8728 | 19016.1227 | 19941.3814 | 20189.1451 | 20003.0653 | 19903.343 | 19862.2204 | 19842.6872 | 19584.6428 | 18727.2364 | 17952.0752 | 17107.0056 | 15810.6153 | 14344.5943 | 20189.1451
2018-07-15 | 13028.6708 | 12101.3559 | 11464.9835 | 11054.7855 | 10958.1474 | 11284.0441 | 12063.3175 | 12813.8051 | 13947.7611 | 15513.5044 | 16821.2034 | 17923.2894 | 18585.3634 | 18590.5037 | 18307.7858 | 17793.7531 | 17435.9864 | 17184.1105 | 17075.1355 | 16662.8814 | 16523.0645 | 16076.8842 | 14959.3773 | 13623.9205 | 18590.5037
2018-07-16 | 12439.5894 | 11517.4149 | 10882.0705 | 10566.4545 | 10521.2196 | 10960.2035 | 11946.1181 | 12753.1493 | 14128.7006 | 15690.3317 | 16969.2448 | 17921.2332 | 18506.2024 | 18066.1904 | 17555.242 | 17133.7353 | 16755.4073 | 16399.6967 | 16164.2697 | 15764.3524 | 15819.8679 | 15527.8974 | 14546.0951 | 13298.0239 | 18506.2024
2018-07-17 | 12135.2821 | 11342.6438 | 10720.6643 | 10413.2728 | 10383.4589 | 10789.5447 | 11625.3617 | 12333.6987 | 13856.2633 | 15319.2001 | 16730.7337 | 17930.4858 | 17959.2716 | 17767.0234 | 17527.4842 | 17917.121 | 18439.3781 | 18500.034 | 18383.8626 | 17902.7281 | 17508.9791 | 16935.3187 | 15607.0584 | 14252.0684 | 18500.034
2018-07-18 | 12824.0858 | 11875.1816 | 11241.8934 | 10823.4708 | 10664.1207 | 10974.5964 | 11655.1756 | 12461.1788 | 13931.312 | 15709.8649 | 17324.9554 | 18764.2467 | 19931.1008 | 20786.4511 | 21307.6801 | 21592.4542 | 21593.4823 | 21049.6358 | 20021.5705 | 18933.8775 | 18245.0738 | 17499.7265 | 16292.7779 | 14988.1631 | 21593.4823
2018-07-19 | 13668.1273 | 12622.585 | 11880.3219 | 11404.3277 | 11098.9923 | 11079.4591 | 11184.3217 | 11699.3824 | 13473.823 | 15463.1292 | 17173.8298 | 18616.2053 | 19695.6738 | 20468.7789 | 20788.5072 | 20897.4821 | 21154.4984 | 20957.1099 | 20158.3032 | 19291.6442 | 18775.5554 | 17970.5804 | 16752.3231 | 15480.6064 | 21154.4984
2018-07-20 | 14189.3564 | 13184.9367 | 12403.6071 | 11852.5641 | 11530.7797 | 11393.019 | 11408.4399 | 11734.3366 | 13374.1007 | 15447.7083 | 17149.1562 | 18786.8642 | 20007.1776 | 20811.1246 | 21195.621 | 20974.587 | 20776.1704 | 20459.5263 | 19765.5823 | 18899.9513 | 18534.9882 | 17885.251 | 16745.1266 | 15269.853 | 21195.621
2018-07-21 | 13914.863 | 12934.0888 | 12218.5554 | 11775.4592 | 11665.4563 | 11972.8478 | 12727.4476 | 13420.3636 | 14623.1999 | 16202.3082 | 17825.6232 | 19164.1641 | 19999.9811 | 20142.8822 | 19665.8599 | 19180.6132 | 18659.3841 | 18188.5302 | 17705.3395 | 17166.6333 | 17060.7426 | 16295.8621 | 15173.2149 | 13856.2633 | 20142.8822
2018-07-22 | 12563.9853 | 11661.344 | 11142.1711 | 10770.0114 | 10714.4959 | 11180.2095 | 11957.4268 | 12732.588 | 14054.6799 | 15540.2341 | 16870.5506 | 17863.6616 | 18458.9114 | 18790.9764 | 19246.4093 | 19511.6502 | 19310.1494 | 18708.7312 | 18176.1934 | 17579.9156 | 17410.2848 | 16766.716 | 15567.9919 | 14252.0684 | 19511.6502
2018-07-23 | 13058.4847 | 12166.124 | 11543.1165 | 11148.3394 | 11047.5891 | 11378.6261 | 12265.8464 | 12958.7623 | 14262.3491 | 15594.7216 | 16761.5756 | 17688.8905 | 18394.1432 | 19060.3295 | 19703.8984 | 20032.8792 | 20156.2471 | 20052.4125 | 19972.2234 | 19247.4374 | 18804.3413 | 18131.9866 | 16745.1266 | 15304.8072 | 20156.2471
2018-07-24 | 13932.3401 | 12862.1242 | 12133.2259 | 11680.8772 | 11520.4991 | 11811.4415 | 12462.2068 | 13204.4699 | 14566.6564 | 16281.4692 | 17816.3706 | 16487.0822 | 19966.055 | 20470.835 | 20766.9178 | 21048.6077 | 21435.1602 | 21212.0701 | 20863.5559 | 20012.3179 | 19233.0445 | 18465.0797 | 16938.4029 | 15369.5753 | 21435.1602
2018-07-25 | 14041.315 | 12932.0326 | 12206.2186 | 11707.6069 | 11467.0397 | 11754.8979 | 12403.6071 | 13183.9086 | 14753.7642 | 16489.1384 | 18032.2643 | 19423.2365 | 20255.9694 | 20706.262 | 21117.4881 | 21501.9845 | 21554.4158 | 21166.8352 | 20360.832 | 19365.6649 | 18837.2394 | 18020.9556 | 16824.2876 | 15510.4202 | 21554.4158
2018-07-26 | 14338.4259 | 13351.4832 | 12701.746 | 12148.6469 | 11809.3854 | 11752.8418 | 11898.8271 | 12289.4919 | 13740.0919 | 15664.63 | 17402.0603 | 18544.2408 | 19025.3753 | 19289.5881 | 19211.4551 | 18920.5126 | 18923.5968 | 18706.6751 | 18224.5125 | 17552.1578 | 17375.3306 | 16674.1901 | 15579.3006 | 14547.1231 | 19289.5881
2018-07-27 | 13421.3917 | 12528.003 | 11907.0516 | 11450.5906 | 11206.9392 | 11137.0307 | 11193.5743 | 11549.2849 | 13351.4832 | 15389.1086 | 17066.911 | 18546.2969 | 19715.2071 | 20608.5958 | 21181.2281 | 21561.6122 | 21689.0923 | 21544.1351 | 20893.3698 | 19928.0166 | 19482.8643 | 18736.489 | 17419.5374 | 15990.5267 | 21689.0923
2018-07-28 | 14566.6564 | 13599.247 | 12868.2926 | 12409.7755 | 12280.2393 | 12609.2201 | 13299.0519 | 13976.5469 | 15373.6876 | 17141.9598 | 18682.0015 | 20104.8438 | 21060.9445 | 21938.9122 | 22723.326 | 23159.2256 | 23316.5196 | 23141.7485 | 22697.6243 | 21818.6286 | 21277.8662 | 20393.7301 | 18763.2187 | 17034.0129 | 23316.5196
2018-07-29 | 15499.1115 | 14411.4185 | 13627.0047 | 13144.8421 | 12931.0046 | 13169.5157 | 13798.6916 | 14398.0537 | 15790.054 | 17386.6393 | 18892.7549 | 20223.0713 | 21092.8145 | 21680.8678 | 21970.7822 | 21744.6079 | 21522.5458 | 20764.8617 | 19834.4626 | 19005.8421 | 18656.2999 | 17929.4578 | 16591.9449 | 15286.302 | 21970.7822
2018-07-30 | 13973.4627 | 13094.4669 | 12420.0561 | 12027.3352 | 11871.0693 | 12189.7695 | 12993.7165 | 13623.9205 | 14972.7421 | 16465.4929 | 17687.8624 | 19095.2837 | 20274.4746 | 21299.4556 | 21835.0776 | 21878.2563 | 21242.912 | 20192.2293 | 19434.5453 | 18688.1699 | 18218.3441 | 17513.0913 | 16159.1294 | 14786.6623 | 21878.2563
2018-07-31 | 13450.1775 | 12498.1891 | 11847.4238 | 11459.8432 | 11325.1667 | 11619.1933 | 12399.4948 | 12995.7727 | 14189.3564 | 15895.9447 | 17669.3573 | 19234.0725 | 20248.7729 | 20914.9592 | 21143.1897 | 20886.1734 | 20081.1983 | 19322.4862 | 18679.9454 | 17956.1875 | 17737.2096 | 17104.9494 | 15915.478 | 14548.1512 | 21143.1897
2018-08-01 | 13368.9604 | 12478.6559 | 11757.9821 | 11435.1696 | 11257.3144 | 11583.211 | 12252.4815 | 13082.1302 | 14494.6918 | 16274.2727 | 17841.0441 | 19196.0341 | 20209.7065 | 20919.0715 | 21507.1248 | 21821.7127 | 21776.4779 | 21159.6387 | 20243.6326 | 19345.1036 | 18972.944 | 18206.0073 | 16868.4944 | 15547.4306 | 21821.7127
2018-08-02 | 14283.9384 | 13240.4522 | 12507.4417 | 11997.5213 | 11712.7473 | 11687.0456 | 11854.6203 | 12224.7237 | 13806.9162 | 15725.2859 | 17390.7516 | 18651.1596 | 19619.597 | 20164.4716 | 20650.7464 | 20629.1571 | 20462.6105 | 20033.9073 | 19265.9426 | 18481.5288 | 18179.2776 | 17571.6911 | 16414.0896 | 15239.011 | 20650.7464
2018-08-03 | 14043.3712 | 13115.0282 | 12420.0561 | 11956.3987 | 11678.8211 | 11644.895 | 11768.2628 | 11952.2865 | 13204.4699 | 14777.4097 | 15949.4041 | 17191.3069 | 17784.5006 | 17960.2997 | 18024.0398 | 18181.3337 | 18311.898 | 18149.4637 | 17719.7324 | 17298.2257 | 16925.038 | 16222.8695 | 15025.1735 | 13695.8851 | 18311.898
2018-08-04 | 12437.5333 | 11589.3794 | 11037.3084 | 10710.3837 | 10687.7662 | 11126.7501 | 11971.8197 | 12597.9114 | 13797.6636 | 15295.5546 | 16761.5756 | 18006.5626 | 18345.8242 | 18191.6144 | 17646.7398 | 17091.5846 | 16539.5136 | 15923.7025 | 15530.9816 | 15232.8426 | 15433.3154 | 14946.0124 | 14002.2485 | 12929.9765 | 18345.8242
2018-08-05 | 11876.2096 | 11154.5078 | 10730.945 | 10497.5741 | 10485.2374 | 10875.9022 | 11784.7118 | 12521.8346 | 13841.8704 | 15488.8309 | 16876.719 | 18165.9128 | 19181.6412 | 19787.1716 | 19664.8319 | 19571.2779 | 19663.8038 | 19749.1332 | 19415.012 | 18669.6647 | 18329.3751 | 17455.5197 | 16033.7055 | 14612.9193 | 19787.1716
2018-08-06 | 13183.9086 | 12244.257 | 11566.762 | 11139.0869 | 11057.8697 | 11368.3454 | 12144.5347 | 12888.8539 | 14344.5943 | 16103.6139 | 17672.4414 | 19312.2055 | 20430.7405 | 21361.1395 | 21934.7999 | 21981.0629 | 21489.6477 | 20951.9696 | 20219.9871 | 19489.0327 | 19155.9396 | 18348.9084 | 16785.2211 | 15335.6492 | 21981.0629
2018-08-07 | 13898.414 | 12899.1345 | 12230.8921 | 11786.768 | 11623.3056 | 11932.7532 | 12701.746 | 13371.0165 | 14910.0302 | 16713.2566 | 18312.9261 | 19818.0136 | 20978.6993 | 21772.3656 | 21935.828 | 21840.2179 | 21682.9239 | 21408.4305 | 20676.4481 | 19834.4626 | 19060.3295 | 17980.861 | 16330.8163 | 14808.2517 | 21935.828
2018-08-08 | 13433.7285 | 12390.2423 | 11762.0944 | 11381.7103 | 11211.0514 | 11826.8625 | 12312.1093 | 12968.0149 | 14023.8379 | 15570.048 | 16987.75 | 18493.8656 | 19836.5188 | 20938.6047 | 21503.0125 | 21536.9387 | 21351.8869 | 20555.1364 | 19571.2779 | 18650.1315 | 18318.0664 | 17539.821 | 16344.1812 | 15229.7584 | 21536.9387
2018-08-09 | 13826.4494 | 12854.9277 | 12126.0295 | 11656.2037 | 11425.9171 | 11425.9171 | 11580.1268 | 12046.8685 | 13800.7478 | 15860.9905 | 17589.1682 | 19080.8908 | 20184.0048 | 20911.875 | 21412.5428 | 21707.5975 | 21666.4749 | 21037.299 | 19996.8969 | 18981.1685 | 18593.5879 | 17761.8831 | 16547.7381 | 15417.8944 | 21707.5975
2018-08-10 | 14177.0196 | 13230.1716 | 12455.0104 | 11956.3987 | 11654.1475 | 11546.2007 | 11595.5478 | 11875.1816 | 13551.956 | 15615.2829 | 17387.6674 | 19090.1434 | 20263.1658 | 21139.0774 | 21557.5 | 21639.7452 | 21566.7526 | 21277.8662 | 20497.5647 | 19491.0889 | 19024.3472 | 18033.2923 | 16580.6362 | 15082.7451 | 21639.7452
2018-08-11 | 13684.5764 | 12663.7076 | 11959.4829 | 11529.7516 | 11390.9628 | 11765.1786 | 12538.2836 | 13111.944 | 14441.2324 | 16287.6376 | 17989.0855 | 19673.0564 | 20940.6608 | 21740.4956 | 21944.0525 | 21887.5089 | 21917.3228 | 21724.0465 | 21141.1336 | 20239.5203 | 19875.5853 | 18715.9277 | 17286.917 | 15626.5916 | 21944.0525
2018-08-12 | 14172.9074 | 13173.628 | 12374.8213 | 11884.4342 | 11723.0279 | 12035.5597 | 12807.6367 | 13431.6723 | 14778.4378 | 16519.9803 | 18077.4991 | 19480.8082 | 20486.256 | 21259.3611 | 21541.0509 | 21519.4616 | 21687.0362 | 21574.9771 | 21182.2562 | 20321.7656 | 19787.1716 | 18710.7873 | 17204.6718 | 15709.8649 | 21687.0362
2018-08-13 | 14235.6194 | 13307.2764 | 12584.5466 | 11986.2126 | 11829.9467 | 12158.9276 | 12962.8746 | 13605.4154 | 15070.4083 | 16836.6244 | 18433.2097 | 20076.058 | 21252.1646 | 22063.3081 | 22471.45 | 22682.2034 | 22681.1753 | 22186.6759 | 21422.8234 | 20426.6282 | 20010.2618 | 19036.684 | 17508.9791 | 15989.4987 | 22682.2034
2018-08-14 | 14623.1999 | 13681.4922 | 13016.334 | 12582.4905 | 12388.1861 | 12636.9779 | 13411.111 | 13996.0802 | 15402.4734 | 17210.8402 | 18846.4919 | 20123.349 | 21215.1543 | 21790.8708 | 21871.0599 | 21133.9371 | 20036.9915 | 19192.9499 | 18484.613 | 17881.1387 | 17757.7709 | 16931.2064 | 15802.3908 | 14376.4643 | 21871.0599
2018-08-15 | 13141.7579 | 12300.8006 | 11646.9511 | 11346.756 | 11267.595 | 11669.5685 | 12556.7888 | 13298.0239 | 14742.4555 | 16299.9744 | 17783.4725 | 18847.52 | 19650.439 | 19481.8363 | 18061.0501 | 17150.1843 | 16539.5136 | 16116.9787 | 15587.5251 | 15079.6609 | 15148.5413 | 14614.9754 | 13862.4317 | 12897.0784 | 19650.439
2018-08-16 | 11896.7709 | 11231.6127 | 10778.236 | 10474.9567 | 10319.7189 | 10376.2624 | 10661.0365 | 11125.722 | 12741.8406 | 14991.2473 | 16842.7928 | 18186.4741 | 19432.4891 | 19652.4951 | 20268.3062 | 19802.5926 | 18956.4949 | 18074.415 | 17234.4857 | 16516.8961 | 16318.4795 | 15738.6507 | 14878.1601 | 13706.1658 | 20268.3062
2018-08-17 | 12636.9779 | 11842.2835 | 11247.0337 | 10829.6392 | 10653.8401 | 10662.0646 | 10852.2567 | 11215.1637 | 12743.8967 | 14887.4127 | 16811.9508 | 18345.8242 | 19605.2041 | 20651.7745 | 20824.4895 | 20629.1571 | 20728.8794 | 20690.841 | 20233.352 | 19479.7801 | 19241.269 | 18377.6942 | 16904.4767 | 15178.3552 | 20824.4895
2018-08-18 | 13876.8246 | 12842.591 | 12145.5627 | 11726.1121 | 11634.6143 | 12213.415 | 13202.4138 | 13641.3976 | 14693.1084 | 16515.8681 | 18236.8493 | 19782.0313 | 20930.3802 | 21849.4705 | 22262.7527 | 22597.902 | 22651.3614 | 22432.3835 | 21957.4174 | 21105.1513 | 20766.9178 | 19512.6782 | 17712.536 | 16129.3155 | 22651.3614
2018-08-19 | 14592.358 | 13560.1805 | 12816.8893 | 12341.9232 | 12197.9941 | 12670.9041 | 13684.5764 | 14080.3815 | 15188.6358 | 16943.5432 | 18500.034 | 20016.4302 | 21214.1262 | 22021.1574 | 22493.0393 | 23057.4472 | 23345.3054 | 23051.2788 | 22497.1516 | 21527.6861 | 21133.9371 | 19957.8305 | 18174.1373 | 16509.6997 | 23345.3054
2018-08-20 | 15000.4999 | 13953.9295 | 13226.0593 | 12678.1005 | 12500.2452 | 12916.6117 | 13876.8246 | 12792.2158 | 15294.5265 | 17060.7426 | 18600.7844 | 20205.5942 | 21226.463 | 22206.2091 | 22603.0423 | 22681.1753 | 22650.3333 | 22344.998 | 21682.9239 | 20862.5279 | 20492.4244 | 19457.1627 | 17843.1003 | 16175.5785 | 22681.1753
2018-08-21 | 14867.8795 | 13834.6739 | 13102.6915 | 12631.8376 | 12440.6174 | 12883.7136 | 13900.4701 | 14352.8188 | 15480.6064 | 17094.6688 | 18717.9838 | 20261.1097 | 21349.8308 | 22286.3982 | 22809.6834 | 23339.137 | 23357.6422 | 22583.5091 | 21767.2253 | 20639.4377 | 20381.3933 | 19238.1848 | 17707.3957 | 16047.0703 | 23357.6422
2018-08-22 | 14538.8986 | 13557.0963 | 12847.7313 | 12398.4668 | 12215.4712 | 12633.8937 | 13655.7906 | 14092.7183 | 15202.0007 | 16971.301 | 18529.8479 | 20005.1215 | 21158.6107 | 21981.0629 | 22285.3702 | 22936.1355 | 23103.7101 | 22642.1088 | 21891.6212 | 20761.7775 | 20148.0225 | 18953.4107 | 17565.5227 | 16166.3259 | 23103.7101
2018-08-23 | 14760.9607 | 13766.8216 | 12961.8465 | 12406.6913 | 12062.2894 | 12031.4475 | 12190.7976 | 12532.1153 | 14114.3077 | 16299.9744 | 18122.734 | 19716.2351 | 20911.875 | 21711.7098 | 22069.4765 | 22358.3628 | 22522.8532 | 22292.5666 | 21560.5842 | 20479.0595 | 19960.9147 | 18999.6737 | 17813.2864 | 16401.7528 | 22522.8532
2018-08-24 | 14970.686 | 13903.5543 | 13069.7934 | 12492.0207 | 12139.3943 | 12003.6897 | 12020.1388 | 12236.0325 | 13930.284 | 16086.1368 | 17819.4548 | 19574.3621 | 20936.5486 | 21898.8176 | 22475.5622 | 22775.7573 | 22806.5992 | 22637.9965 | 21959.4735 | 21029.0744 | 20622.9887 | 19388.2823 | 17796.8373 | 16220.8133 | 22806.5992
2018-08-25 | 14974.7983 | 13905.6104 | 13284.659 | 12912.4994 | 12890.91 | 13459.4301 | 14513.197 | 14925.4511 | 15691.3597 | 17219.0647 | 18689.198 | 19943.4376 | 20720.6549 | 21023.9341 | 21090.7584 | 21072.2532 | 21132.909 | 20895.426 | 20187.089 | 19529.1273 | 19361.5526 | 18214.2318 | 16797.5579 | 15184.5236 | 21132.909
2018-08-26 | 14017.6695 | 13177.7402 | 12586.6027 | 12235.0044 | 12171.2644 | 12704.8302 | 13780.1865 | 14170.8512 | 15022.0893 | 16590.9168 | 17956.1875 | 19189.8657 | 20049.3283 | 20808.0404 | 21315.9047 | 21721.9904 | 21929.6596 | 21751.8043 | 21142.1616 | 20213.8187 | 19874.5572 | 18723.1241 | 16966.1606 | 15398.3611 | 21929.6596
2018-08-27 | 13878.8807 | 12862.1242 | 12120.8892 | 11672.6527 | 11506.1061 | 11970.7916 | 13023.5304 | 13381.2971 | 14368.2398 | 16086.1368 | 17564.4946 | 18966.7756 | 20079.1422 | 20975.6151 | 21661.3346 | 22148.6375 | 22434.4396 | 22256.5843 | 21658.2504 | 20665.1394 | 20340.2707 | 19179.5851 | 17495.6142 | 15963.797 | 22434.4396
2018-08-28 | 14544.0389 | 13559.1524 | 12825.1138 | 12333.6987 | 12130.1417 | 12595.8553 | 13690.7448 | 14090.6622 | 15043.6786 | 16415.1177 | 17484.3055 | 18390.031 | 19420.1524 | 20456.4421 | 21386.8412 | 21964.6138 | 22216.4898 | 21785.7305 | 20900.5663 | 20174.7522 | 19729.6 | 18494.8936 | 16986.7219 | 15509.3922 | 22216.4898
2018-08-29 | 14064.9605 | 13137.6457 | 12504.3575 | 12066.4017 | 11949.2023 | 12426.2245 | 13527.2824 | 14060.8483 | 15149.5694 | 16927.0941 | 18553.4934 | 19759.4139 | 20627.1009 | 21444.4128 | 22018.0732 | 22340.8857 | 22232.9388 | 21520.4896 | 20605.5116 | 19689.5054 | 19338.9352 | 18264.607 | 17003.171 | 15814.7276 | 22340.8857
2018-08-30 | 14625.2561 | 13695.8851 | 13015.3059 | 12518.7504 | 12301.8286 | 12508.4698 | 12582.4905 | 12840.5348 | 14167.767 | 16206.4204 | 17916.0929 | 19500.3414 | 20546.9119 | 21348.8027 | 21939.9402 | 22193.8724 | 22158.9181 | 21548.2474 | 20467.7508 | 19535.2957 | 19187.8096 | 18163.8566 | 17010.3674 | 15891.8325 | 22193.8724
2018-08-31 | 14666.3787 | 13661.959 | 12900.1626 | 12436.5052 | 12107.5243 | 11963.5952 | 12050.9807 | 12290.5199 | 13848.0388 | 16054.2668 | 17678.6098 | 19100.4241 | 20260.0817 | 21043.4674 | 21390.9534 | 21503.0125 | 21268.6136 | 20809.0685 | 19834.4626 | 18910.232 | 18634.7105 | 17668.3292 | 16487.0822 | 15234.8988 | 21503.0125
2018-09-01 | 14046.4554 | 13222.9751 | 12589.6869 | 12115.7488 | 11960.511 | 12053.0369 | 12334.7267 | 12462.2068 | 13925.1437 | 16103.6139 | 17895.5316 | 19583.6147 | 20507.8454 | 21208.9859 | 21809.376 | 22013.9609 | 21849.4705 | 21435.1602 | 20725.7952 | 19846.7994 | 19574.3621 | 18428.0694 | 16881.8593 | 15437.4276 | 22013.9609
2018-09-02 | 14074.2131 | 13112.9721 | 12432.3929 | 12029.3914 | 11892.6587 | 12368.6529 | 13405.9707 | 13817.1968 | 14714.6978 | 16355.4899 | 17797.8654 | 19260.8022 | 20289.8955 | 20918.0434 | 21590.3981 | 21977.9787 | 22059.1958 | 21705.5414 | 20912.9031 | 20029.795 | 19507.5379 | 18070.3027 | 16379.1354 | 14720.8661 | 22059.1958
2018-09-03 | 13329.8939 | 12383.0458 | 11767.2347 | 11363.2051 | 11255.2582 | 11737.4208 | 12858.0119 | 13268.21 | 14104.027 | 15541.2622 | 16539.5136 | 17579.9156 | 18559.6617 | 19582.5867 | 20313.541 | 20557.1925 | 20704.2058 | 20360.832 | 19748.1052 | 18946.2143 | 18699.4786 | 17602.533 | 16105.67 | 14477.2147 | 20704.2058
2018-09-04 | 13141.7579 | 12203.1344 | 11590.4075 | 11212.0795 | 11108.2449 | 11586.2952 | 12748.009 | 13141.7579 | 13749.3445 | 15022.0893 | 16352.4057 | 17443.1829 | 18346.8522 | 19190.8938 | 19543.5202 | 19691.5616 | 19868.3888 | 19601.0918 | 19115.845 | 18669.6647 | 18542.1846 | 17441.1268 | 15925.7586 | 14484.4111 | 19868.3888
2018-09-05 | 13168.4876 | 12274.0709 | 11704.5227 | 11347.7841 | 11291.2405 | 11788.8241 | 13001.9411 | 13425.5039 | 14316.8365 | 15943.2357 | 17496.6423 | 18873.2216 | 20024.6547 | 20889.2576 | 21376.5605 | 21406.3744 | 20935.5205 | 19985.5882 | 18977.0562 | 18289.2806 | 17885.251 | 16864.3822 | 15738.6507 | 14627.3122 | 21406.3744
2018-09-06 | 13456.3459 | 12683.2408 | 12081.8227 | 11666.4843 | 11466.0116 | 11462.9274 | 11712.7473 | 12119.8611 | 13402.8865 | 15077.6048 | 16359.6021 | 17325.9835 | 17887.3071 | 17814.3144 | 17637.4872 | 17405.1445 | 16953.8238 | 16590.9168 | 16166.3259 | 15946.3199 | 15948.376 | 15328.4527 | 14562.5441 | 13692.8009 | 17887.3071
2018-09-07 | 12720.2512 | 11848.4519 | 11252.174 | 10837.8637 | 10680.5698 | 10708.3275 | 10923.1932 | 11200.7708 | 12425.1965 | 14005.3327 | 15415.8382 | 16807.8386 | 17934.5981 | 18701.5347 | 19057.2453 | 18814.6219 | 18386.9468 | 17793.7531 | 16905.5048 | 16614.5623 | 16601.1975 | 15742.763 | 14528.6179 | 13241.4803 | 19057.2453
2018-09-08 | 12181.545 | 11459.8432 | 10898.5196 | 10560.2861 | 10538.6968 | 11143.1991 | 12299.7725 | 12728.4757 | 13423.4478 | 15051.9032 | 16684.4708 | 18100.1166 | 19211.4551 | 20048.3002 | 20657.9429 | 20912.9031 | 20885.1453 | 20655.8868 | 19810.8171 | 19328.6545 | 18992.4772 | 17770.1076 | 16251.6553 | 14730.1187 | 20912.9031
2018-09-09 | 13402.8865 | 12443.7016 | 11838.1712 | 11451.6187 | 11292.2686 | 11755.926 | 12881.6574 | 13284.659 | 13984.7714 | 15448.7363 | 16963.0764 | 18305.7296 | 19422.2085 | 20386.5337 | 20823.4614 | 21284.0346 | 21171.9755 | 20683.6445 | 19885.8659 | 19237.1567 | 18783.78 | 17428.79 | 15851.7379 | 14347.6785 | 21284.0346
2018-09-10 | 13109.8879 | 12292.5761 | 11742.5612 | 11350.8683 | 11266.5669 | 11799.1047 | 12946.4255 | 13320.6413 | 14009.445 | 15306.8633 | 16783.165 | 17969.5523 | 19005.8421 | 19893.0624 | 20405.0388 | 20641.4939 | 20548.968 | 20124.377 | 19415.012 | 18878.362 | 18555.5495 | 17220.0927 | 15711.921 | 14182.16 | 20641.4939
2018-09-11 | 12897.0784 | 12056.121 | 11453.6748 | 11074.3187 | 10987.9613 | 11492.7413 | 12659.5953 | 13076.9898 | 13709.25 | 15111.5309 | 16381.1915 | 17459.6319 | 18246.1018 | 18802.2851 | 18992.4772 | 19051.0769 | 18694.3383 | 17988.0575 | 17338.3202 | 16970.2729 | 16785.2211 | 15806.503 | 14694.1365 | 13353.5394 | 19051.0769
2018-09-12 | 11992.381 | 11300.4931 | 10804.9657 | 10552.0616 | 10552.0616 | 11122.6378 | 12391.2703 | 12755.2054 | 13500.5527 | 14729.0907 | 15846.5976 | 16778.0247 | 17687.8624 | 18544.2408 | 18756.0222 | 18674.8051 | 18733.4048 | 18803.3132 | 18156.6602 | 17424.6777 | 17128.5949 | 16246.515 | 15255.4601 | 14042.3431 | 18803.3132
2018-09-13 | 12714.0828 | 11826.8625 | 11197.6866 | 10688.7943 | 10481.1251 | 10461.5919 | 10743.2817 | 11125.722 | 12272.0147 | 13906.6385 | 15607.0584 | 17110.0898 | 18249.186 | 18949.2985 | 19229.9603 | 19198.0903 | 18799.2009 | 18228.6247 | 17260.1873 | 16763.6318 | 16451.0999 | 15465.1854 | 14287.0226 | 13062.5969 | 19229.9603
2018-09-14 | 12071.542 | 11264.5108 | 10682.6259 | 10288.8769 | 10054.478 | 10015.4116 | 10174.7617 | 10395.7957 | 11784.7118 | 13625.9767 | 15327.4246 | 16885.9715 | 18033.2923 | 18790.9764 | 19172.3886 | 19299.8687 | 19319.402 | 18823.8745 | 17938.7103 | 17416.4532 | 17135.7914 | 16089.221 | 14820.5885 | 13360.7358 | 19319.402
2018-09-15 | 12248.3692 | 11426.9451 | 10915.9967 | 10628.1384 | 10616.8297 | 11170.9569 | 12321.3619 | 12775.7667 | 13545.7876 | 15116.6713 | 16979.5255 | 18361.2452 | 19493.145 | 20467.7508 | 21146.2739 | 21596.5665 | 21676.7555 | 21380.6728 | 20626.0729 | 20049.3283 | 19619.597 | 18258.4386 | 16731.7618 | 14913.1143 | 21676.7555
2018-09-16 | 13486.1598 | 12583.5185 | 11883.4061 | 11437.2258 | 11311.8018 | 11763.1225 | 12897.0784 | 13303.1642 | 14030.0063 | 15472.3818 | 17031.9568 | 18441.4342 | 19498.2853 | 20276.5307 | 20138.77 | 19713.1509 | 19363.6088 | 18953.4107 | 18487.6972 | 18303.6735 | 17939.7384 | 16734.8459 | 15350.0421 | 13889.1614 | 20276.5307
2018-09-17 | 12530.0591 | 11688.0737 | 11091.7959 | 10715.524 | 10684.682 | 11253.2021 | 12480.712 | 12891.9381 | 13507.7492 | 14657.1261 | 16094.3613 | 17176.914 | 17954.1313 | 18365.3574 | 18815.65 | 18788.9203 | 18150.4918 | 17412.3409 | 16901.3925 | 16987.75 | 16841.7647 | 15911.3657 | 14571.7967 | 13104.7476 | 18815.65
2018-09-18 | 11972.8478 | 11117.4975 | 10666.1768 | 10354.6731 | 10327.9434 | 10889.267 | 12130.1417 | 12547.5362 | 13186.9928 | 14426.8395 | 15608.0864 | 16819.1473 | 17964.412 | 19001.7298 | 19729.6 | 20136.7138 | 19999.9811 | 20061.6651 | 19180.6132 | 18655.2718 | 18188.5302 | 16983.6377 | 15512.4764 | 13962.154 | 20136.7138
2018-09-19 | 12683.2408 | 11762.0944 | 11200.7708 | 10839.9199 | 10774.1237 | 11293.2966 | 12507.4417 | 13016.334 | 13657.8467 | 15003.5841 | 16114.9226 | 16801.6702 | 17005.2271 | 16670.0778 | 16099.5016 | 15832.2047 | 15587.5251 | 15345.9298 | 15058.0715 | 15167.0465 | 15042.6506 | 14404.2221 | 13488.2159 | 12464.2629 | 17005.2271
2018-09-20 | 11427.9732 | 10719.6362 | 10249.8104 | 9989.7099 | 9857.0895 | 9988.6819 | 10387.5712 | 10903.6599 | 11867.9851 | 13328.8658 | 14618.0596 | 15629.6758 | 16372.967 | 16858.2138 | 16913.7293 | 16162.2136 | 15534.0658 | 15219.4778 | 14722.9223 | 14831.8972 | 14722.9223 | 13972.4347 | 13058.4847 | 12086.963 | 16913.7293
2018-09-21 | 11161.7043 | 10393.7396 | 9889.9876 | 9563.0628 | 9422.2179 | 9458.2002 | 9719.3288 | 10016.4396 | 11151.4236 | 12885.7697 | 14462.8218 | 15916.506 | 17077.1917 | 17885.251 | 18428.0694 | 18632.6544 | 18603.8686 | 18222.4563 | 17364.0219 | 16967.1887 | 16530.261 | 15360.3227 | 14097.8586 | 12661.6515 | 18632.6544
2018-09-22 | 11505.0781 | 10705.2433 | 10174.7617 | 9953.7276 | 10008.2151 | 10684.682 | 11896.7709 | 12445.7578 | 13151.0105 | 14414.5027 | 15675.9388 | 16781.1089 | 17607.6733 | 17779.3602 | 17562.4385 | 17285.8889 | 17128.5949 | 16820.1754 | 16627.9272 | 16744.0985 | 16349.3215 | 15255.4601 | 13908.6946 | 12535.1995 | 17779.3602
2018-09-23 | 11374.5138 | 10577.7632 | 10043.1693 | 9764.5636 | 9794.3775 | 10508.8829 | 11870.0412 | 12453.9823 | 12746.9809 | 13584.8541 | 14187.3003 | 14902.8337 | 15419.9505 | 15530.9816 | 15587.5251 | 15712.9491 | 15882.5799 | 16157.0733 | 15977.1619 | 16215.673 | 16006.9758 | 15017.977 | 13782.2426 | 12391.2703 | 16215.673
2018-09-24 | 11215.1637 | 10444.1148 | 10062.7026 | 9763.5356 | 9732.6936 | 10430.7499 | 11764.1505 | 12336.7829 | 12797.3561 | 13645.5099 | 14453.5692 | 15253.4039 | 15787.9979 | 16437.7351 | 17170.7456 | 17747.4902 | 17800.9496 | 17567.5788 | 17157.3808 | 17150.1843 | 16916.8135 | 15950.4322 | 14551.2354 | 13230.1716 | 17800.9496
2018-09-25 | 12087.9911 | 11251.146 | 10705.2433 | 10361.8695 | 10341.3082 | 10802.9095 | 11816.5818 | 12446.7858 | 13195.2173 | 14530.6741 | 15836.3169 | 16692.6953 | 17150.1843 | 17554.2139 | 18091.8921 | 18529.8479 | 18215.2599 | 17371.2183 | 16794.4737 | 16702.9759 | 16386.3318 | 15380.884 | 14109.1673 | 12899.1345 | 18529.8479
2018-09-26 | 11786.768 | 11039.3645 | 10552.0616 | 10262.1472 | 10255.9788 | 10878.9864 | 12121.9172 | 12724.3635 | 13219.8909 | 14154.4022 | 15350.0421 | 16692.6953 | 17700.1992 | 18686.1138 | 19027.4314 | 19059.3015 | 18712.8435 | 18037.4046 | 17334.208 | 17225.2331 | 16817.0912 | 15952.4883 | 14821.6165 | 14457.6814 | 19059.3015
2018-09-27 | 13111.944 | 11870.0412 | 11368.3454 | 11006.4664 | 10865.6215 | 10927.3054 | 11240.8653 | 11630.502 | 12883.7136 | 14698.2487 | 16221.8414 | 17636.4592 | 18741.6293 | 19490.0608 | 20010.2618 | 20035.9634 | 19383.142 | 18694.3383 | 17761.8831 | 17527.4842 | 16973.3571 | 16116.9787 | 15005.6402 | 13763.7374 | 20035.9634
2018-09-28 | 12659.5953 | 11856.6764 | 11265.5389 | 10855.3409 | 10665.1488 | 10690.8504 | 10903.6599 | 11267.595 | 12404.6352 | 14204.7774 | 15819.8679 | 17279.7205 | 18501.062 | 19362.5807 | 19899.2308 | 20064.7493 | 19836.5188 | 19170.3325 | 18161.8005 | 18141.2392 | 17746.4621 | 16648.4885 | 15234.8988 | 13742.148 | 20064.7493
2018-09-29 | 12615.3885 | 11710.6911 | 11187.4059 | 10855.3409 | 10856.3689 | 11413.5803 | 12612.3043 | 13122.2247 | 13758.5971 | 15206.1129 | 16741.0143 | 18233.7651 | 19144.6309 | 19904.3711 | 20283.7272 | 20280.643 | 20022.5986 | 19324.5423 | 18544.2408 | 18223.4844 | 17260.1873 | 16091.2771 | 14631.4245 | 13224.0032 | 20283.7272
2018-09-30 | 12001.6336 | 11194.6024 | 10693.9346 | 10394.7676 | 10391.6834 | 10993.1016 | 12356.3161 | 12813.8051 | 13559.1524 | 14977.8825 | 16367.8267 | 17543.9333 | 18479.4727 | 18788.9203 | 19070.6102 | 18628.5421 | 18567.8863 | 18433.2097 | 17926.3736 | 17988.0575 | 17587.112 | 16532.3171 | 15110.5029 | 13623.9205 | 19070.6102
2018-10-01 | 12424.1684 | 11574.9865 | 11088.7117 | 10791.6008 | 10742.2537 | 11366.2893 | 12690.4373 | 13144.8421 | 13909.7227 | 15325.3685 | 16628.9552 | 17898.6158 | 18908.1759 | 19651.467 | 19970.1673 | 20512.9857 | 20831.6859 | 20509.9015 | 19734.7403 | 19347.1597 | 18820.7903 | 17593.2804 | 15954.5444 | 15106.3906 | 20831.6859
2018-10-02 | 13353.5394 | 12243.2289 | 11647.9791 | 11268.6231 | 11170.9569 | 11683.9614 | 12896.0503 | 13323.7255 | 14112.2515 | 15633.7881 | 17161.493 | 18416.7607 | 19434.5453 | 20470.835 | 21030.1025 | 21422.8234 | 21652.082 | 21264.5014 | 20377.2811 | 19924.9324 | 19332.7668 | 17976.7488 | 16461.3806 | 14793.8588 | 21652.082
2018-10-03 | 13466.6266 | 12547.5362 | 11838.1712 | 11430.0293 | 11270.6792 | 11729.1963 | 12896.0503 | 13400.8304 | 14277.77 | 15890.8044 | 17459.6319 | 18887.6146 | 19851.9398 | 20892.3418 | 21418.7112 | 21701.4291 | 21688.0643 | 20807.0124 | 19536.3237 | 18833.1271 | 17908.8965 | 16780.0808 | 15502.1957 | 14220.1984 | 21701.4291
2018-10-04 | 13012.2217 | 12058.1772 | 11449.5626 | 11024.9716 | 10818.3305 | 10890.2951 | 11210.0234 | 11610.9688 | 12949.5097 | 14702.361 | 16033.7055 | 17194.3911 | 18173.1092 | 18758.0783 | 18971.9159 | 18844.4358 | 18398.2555 | 17725.9008 | 16852.0454 | 16700.9198 | 16206.4204 | 15264.7127 | 14111.2235 | 12907.3591 | 18971.9159
2018-10-05 | 11665.4563 | 10632.2507 | 9857.0895 | 9248.4749 | 8912.2976 | 8822.8559 | 8976.0376 | 9123.0509 | 9888.9595 | 11025.9997 | 12137.3382 | 12921.752 | 13765.7935 | 14510.1128 | 15129.008 | 15581.3568 | 16019.3125 | 15847.6256 | 15176.299 | 15120.7835 | 14740.3994 | 13713.3622 | 12469.4033 | 11146.2833 | 16019.3125
2018-10-06 | 10082.2358 | 9328.664 | 8869.1188 | 8630.6077 | 8687.1513 | 9404.7408 | 10649.7278 | 11190.4901 | 11717.8876 | 12690.4373 | 13674.2957 | 14547.1231 | 15457.9889 | 16127.2594 | 16798.586 | 17007.2832 | 17237.5699 | 16914.7574 | 16586.8046 | 16928.1222 | 16398.6686 | 15277.0494 | 14019.7257 | 12619.5008 | 17237.5699
2018-10-07 | 11385.8225 | 10645.6155 | 10166.5371 | 9859.1456 | 9790.2653 | 10364.9537 | 11671.6247 | 12264.8183 | 12534.1714 | 13498.4966 | 14534.7863 | 15263.6846 | 15857.9063 | 16355.4899 | 16604.2817 | 16491.1945 | 16476.8016 | 16279.413 | 16128.2875 | 16517.9242 | 16074.8281 | 15283.2178 | 13905.6104 | 12350.1477 | 16604.2817
2018-10-08 | 11199.7427 | 10453.3673 | 9918.7734 | 9652.5045 | 9683.3465 | 10340.2802 | 11661.344 | 12165.096 | 12682.2128 | 13868.6001 | 15193.7762 | 16296.8902 | 17321.8712 | 18109.3692 | 18749.8538 | 19038.7401 | 19014.0666 | 18705.647 | 18144.3234 | 18149.4637 | 17626.1785 | 16472.6893 | 15056.0154 | 13625.9767 | 19038.7401
2018-10-09 | 12319.3058 | 11490.6852 | 10913.9406 | 10489.3496 | 10422.5254 | 10303.2698 | 12111.6366 | 12592.7711 | 13204.4699 | 14627.3122 | 15979.218 | 17172.8017 | 18065.1624 | 18920.5126 | 19503.4256 | 19888.9501 | 19956.8024 | 19586.6989 | 18754.9941 | 18571.9985 | 17954.1313 | 16745.1266 | 15388.0805 | 13807.9442 | 19956.8024
2018-10-10 | 12467.3471 | 11500.9658 | 10922.1651 | 10505.7987 | 10430.7499 | 10938.6141 | 12142.4785 | 12682.2128 | 13346.3429 | 14784.6062 | 16197.1678 | 17287.945 | 18248.158 | 19041.8243 | 19580.5305 | 19944.4656 | 20016.4302 | 19509.594 | 18475.3604 | 18110.3972 | 17418.5093 | 16370.9109 | 15194.8042 | 13938.5085 | 20016.4302
2018-10-11 | 12704.8302 | 11802.1889 | 11225.4443 | 10792.6289 | 10550.0055 | 10562.3423 | 10849.1725 | 11148.3394 | 12368.6529 | 14282.9104 | 15864.0747 | 17190.2788 | 18210.1196 | 18982.1966 | 19506.5098 | 19839.603 | 19903.343 | 19467.4434 | 18364.3294 | 17867.7738 | 17170.7456 | 16106.6981 | 15048.819 | 13785.3268 | 19903.343
2018-10-12 | 12638.006 | 11708.635 | 11004.4103 | 10562.3423 | 10349.5328 | 10309.4382 | 10515.0513 | 10670.2891 | 11999.5775 | 14043.3712 | 15693.4159 | 17072.0513 | 18233.7651 | 18983.2246 | 19479.7801 | 19747.0771 | 19776.891 | 19391.3665 | 18465.0797 | 18384.8907 | 17717.6763 | 16563.1591 | 15359.2947 | 13964.2101 | 19776.891
2018-10-13 | 12794.2719 | 11953.3145 | 11422.8329 | 11108.2449 | 11115.4414 | 11689.1018 | 12821.0016 | 13292.8835 | 13917.9472 | 15241.0672 | 16722.5092 | 17897.5877 | 18716.9557 | 19375.9455 | 19821.0978 | 20112.0403 | 20072.9738 | 19659.6916 | 18867.0533 | 18831.071 | 18134.0427 | 16997.0026 | 15618.3671 | 14136.9251 | 20112.0403
2018-10-14 | 12887.8258 | 12096.2156 | 11609.9407 | 11281.9879 | 11203.855 | 11796.0205 | 13078.0179 | 13568.405 | 14193.4687 | 15558.7393 | 16869.5225 | 17962.3558 | 18727.2364 | 19544.5482 | 19985.5882 | 20104.8438 | 19867.3607 | 19252.5777 | 18700.5067 | 18838.2674 | 18062.0782 | 16855.1296 | 15413.7821 | 13873.7404 | 20104.8438
2018-10-15 | 12458.0946 | 11543.1165 | 10999.27 | 10658.9804 | 10666.1768 | 11233.6689 | 12475.5717 | 13038.9514 | 13610.5557 | 14805.1675 | 15922.6744 | 16979.5255 | 15884.636 | 18306.7577 | 18467.1359 | 18583.3072 | 18302.6454 | 17854.409 | 17308.5064 | 17440.0987 | 16714.2846 | 15611.1706 | 14149.2619 | 12708.9425 | 18583.3072
2018-10-16 | 11435.1696 | 10588.0439 | 10063.7306 | 9705.9639 | 9546.6138 | 9986.6257 | 11076.3749 | 11454.7029 | 11833.0309 | 12758.2896 | 13632.1451 | 14310.6681 | 15011.8086 | 15723.2298 | 16359.6021 | 16988.7781 | 17344.4886 | 17164.5772 | 16443.9035 | 16376.0512 | 15692.3878 | 14497.776 | 13076.9898 | 11569.8462 | 17344.4886
2018-10-17 | 10262.1472 | 9369.7866 | 8867.0627 | 8573.036 | 8500.0434 | 9025.3847 | 10147.0039 | 10644.5875 | 11142.1711 | 12067.4298 | 12923.8081 | 13696.9132 | 14336.3697 | 15071.4364 | 15781.8295 | 16419.2299 | 16726.6214 | 16446.9877 | 15562.8516 | 15258.5443 | 14473.1024 | 13386.4375 | 12349.1196 | 11161.7043 | 16726.6214
2018-10-18 | 10155.2284 | 9256.6994 | 8695.3758 | 8375.6475 | 8230.6903 | 8361.2546 | 8760.1439 | 9173.4261 | 10210.7439 | 11559.5655 | 12681.1847 | 13602.3312 | 14511.1408 | 15301.723 | 16016.2283 | 16563.1591 | 16762.6037 | 16451.0999 | 15558.7393 | 15316.1159 | 14567.6844 | 13527.2824 | 12546.5082 | 11375.5419 | 16762.6037
2018-10-19 | 10340.2802 | 9529.1367 | 8941.0834 | 8586.4009 | 8438.3595 | 8444.5279 | 8713.881 | 8973.9815 | 10063.7306 | 11521.5271 | 12788.1035 | 13857.2913 | 14953.2089 | 15787.9979 | 16457.2683 | 16854.1015 | 16989.8061 | 16683.4427 | 15999.7793 | 16057.351 | 15407.6137 | 14242.8158 | 13033.8111 | 11719.9437 | 16989.8061
2018-10-20 | 10565.4265 | 9727.5533 | 9230.9978 | 8971.9253 | 8987.3463 | 9572.3154 | 10724.7766 | 11316.9421 | 11980.0442 | 13267.1819 | 14511.1408 | 15556.6832 | 16436.707 | 17121.3985 | 17738.2376 | 17918.149 | 17793.7531 | 17372.2464 | 16955.88 | 17105.9775 | 16350.3495 | 15170.1307 | 13822.3371 | 12415.9439 | 17918.149
2018-10-21 | 11178.1533 | 10428.6938 | 9993.8222 | 9720.3568 | 9740.9181 | 10348.5047 | 11634.6143 | 12278.1831 | 12523.8907 | 13323.7255 | 14209.9177 | 14744.5116 | 15107.4187 | 15283.2178 | 15325.3685 | 15362.3789 | 15284.2459 | 15132.0922 | 15126.9519 | 15567.9919 | 15008.7244 | 14114.3077 | 12889.882 | 11466.0116 | 15567.9919
2018-10-22 | 10392.7115 | 9665.8694 | 9244.3626 | 9036.6934 | 9086.0406 | 9650.4484 | 11060.9539 | 11740.505 | 12022.1949 | 12764.458 | 13699.9974 | 14625.2561 | 15303.7791 | 15883.6079 | 16306.1427 | 16545.6819 | 16405.8651 | 16055.2948 | 15891.8325 | 16163.2417 | 15577.2445 | 14585.1615 | 13266.1538 | 11856.6764 | 16545.6819
2018-10-23 | 10690.8504 | 10013.3554 | 9557.9225 | 9282.401 | 9251.5591 | 9839.6124 | 11191.5182 | 11860.7887 | 12022.1949 | 12655.4831 | 13380.2691 | 13981.6872 | 14480.2989 | 14797.971 | 15090.9696 | 15225.6462 | 15147.5132 | 14929.5634 | 14766.101 | 15061.1557 | 14790.7746 | 13926.1717 | 12751.0932 | 11494.7974 | 15225.6462
2018-10-24 | 10426.6376 | 9703.9078 | 9284.4572 | 9099.4054 | 9158.0051 | 9713.1604 | 10866.6496 | 11577.0426 | 12005.7459 | 12821.0016 | 13494.3843 | 13971.4066 | 14207.8616 | 14461.7937 | 14656.098 | 14830.8691 | 14812.364 | 14580.0212 | 14382.6327 | 14491.6076 | 13946.733 | 13240.4522 | 12425.1965 | 11311.8018 | 14830.8691
2018-10-25 | 10144.9478 | 9303.9904 | 8749.8632 | 8401.3491 | 8276.9532 | 8371.5352 | 8752.9474 | 9227.9136 | 10153.1723 | 11408.4399 | 12438.5613 | 13194.1893 | 13841.8704 | 14438.1482 | 14882.2724 | 15203.0287 | 15210.2252 | 14824.7007 | 14122.5322 | 14026.9221 | 13384.3813 | 12600.9956 | 11751.8137 | 10670.2891 | 15210.2252
2018-10-26 | 9695.6833 | 8972.9534 | 8530.8853 | 8221.4377 | 8093.9576 | 8119.6593 | 8374.6194 | 8766.3123 | 9631.9432 | 10924.2212 | 12036.5878 | 12861.0961 | 13558.1244 | 14236.6474 | 14779.4659 | 15192.7481 | 15376.7718 | 15111.5309 | 14498.8041 | 14686.94 | 14025.894 | 12949.5097 | 11695.2702 | 10322.8031 | 15376.7718
2018-10-27 | 9191.9313 | 8469.2014 | 8048.7228 | 7858.5307 | 7925.3549 | 8567.8957 | 9833.444 | 10545.8932 | 10914.9686 | 11848.4519 | 12781.9351 | 13617.7521 | 14306.5559 | 15032.3699 | 15655.3774 | 16222.8695 | 16515.8681 | 16295.8621 | 15841.4573 | 16033.7055 | 15236.9549 | 14007.3889 | 12617.4447 | 11118.5256 | 16515.8681
2018-10-28 | 9940.3628 | 9171.37 | 8683.039 | 8434.2472 | 8447.6121 | 9093.237 | 10394.7676 | 11040.3926 | 11442.3661 | 12518.7504 | 13508.7772 | 14450.485 | 15219.4778 | 16160.1575 | 16835.5963 | 17318.787 | 17550.1017 | 17278.6925 | 16706.0601 | 16861.298 | 16035.7616 | 14920.3108 | 13503.6369 | 12037.6159 | 17550.1017
2018-10-29 | 10854.3128 | 10026.7203 | 9473.6212 | 9167.2577 | 9166.2297 | 9736.8059 | 11082.5433 | 11649.0072 | 12019.1107 | 13292.8835 | 14332.2575 | 15293.4985 | 16194.0836 | 16945.5993 | 17537.7649 | 18045.6291 | 18145.3515 | 17680.666 | 16946.6274 | 16948.6835 | 16173.5223 | 15035.4541 | 13618.7802 | 12101.3559 | 18145.3515
2018-10-30 | 10733.0011 | 9891.0157 | 9324.5517 | 9004.8234 | 8966.785 | 9531.1928 | 10807.0218 | 11427.9732 | 11792.9363 | 12938.201 | 14142.0654 | 15119.7555 | 15943.2357 | 16606.3378 | 16988.7781 | 17282.8047 | 17484.3055 | 17097.753 | 16571.3836 | 16679.3304 | 15917.5341 | 14909.0021 | 13586.9102 | 12158.9276 | 17484.3055
2018-10-31 | 10856.3689 | 9992.7941 | 9389.3198 | 9080.9002 | 9015.1041 | 9571.2874 | 10851.2286 | 11499.9378 | 11904.9955 | 13015.3059 | 14027.9502 | 14936.7598 | 15602.9461 | 16064.5474 | 16405.8651 | 16661.8533 | 16717.3688 | 16184.831 | 15217.4217 | 14686.94 | 13681.4922 | 12809.6929 | 11764.1505 | 10593.1842 | 16717.3688
2018-11-01 | 9421.1898 | 8620.327 | 8158.7257 | 7901.7094 | 7807.1274 | 7914.0462 | 8364.3388 | 8822.8559 | 9742.9743 | 10854.3128 | 11659.2879 | 12027.3352 | 12167.1521 | 12163.0398 | 12205.1905 | 12232.9483 | 12144.5347 | 11815.5538 | 11585.2672 | 11915.2761 | 11395.0751 | 10740.1975 | 9947.5592 | 9118.9387 | 12232.9483
2018-11-02 | 16242.4027 | 7621.0476 | 7531.6059 | 7524.4095 | 7643.665 | 7997.3195 | 8617.2428 | 9753.2549 | 10741.2256 | 11138.0588 | 11193.5743 | 11085.6275 | 10985.9051 | 10828.6112 | 10757.6747 | 10681.5978 | 10711.4117 | 11155.5359 | 12029.3914 | 11782.6557 | 11346.756 | 10602.4368 | 9651.4765 | 8796.1262 | 16242.4027
2018-11-03 | 8084.705 | 7859.5587 | 7733.1067 | 7781.4258 | 8056.9473 | 8991.4586 | 10519.1635 | 11121.6097 | 11276.8476 | 11474.2361 | 11711.7192 | 11889.5745 | 11910.1358 | 11942.0058 | 11875.1816 | 11772.375 | 11863.8728 | 12260.706 | 13093.4389 | 12819.9735 | 12285.3796 | 11368.3454 | 10281.6804 | 9224.8294 | 13093.4389
2018-11-04 | 8480.5102 | 8002.4598 | 7734.1348 | 7681.7035 | 7810.2116 | 8555.5589 | 9764.5636 | 10617.8578 | 11286.1002 | 11800.1328 | 12295.6602 | 12726.4196 | 12931.0046 | 13116.0563 | 13214.7506 | 13293.9116 | 13167.4596 | 13374.1007 | 14172.9074 | 13925.1437 | 13345.3149 | 12300.8006 | 11242.9214 | 10162.4249 | 14172.9074
2018-11-05 | 9275.2046 | 8663.5058 | 8345.8336 | 8191.6238 | 8294.4303 | 8981.1779 | 10204.5756 | 10615.8017 | 11644.895 | 12628.7534 | 13371.0165 | 13943.6488 | 14320.9488 | 14506.0005 | 14575.9089 | 14438.1482 | 14206.8335 | 14386.7449 | 15078.6328 | 14733.2029 | 14141.0374 | 13207.5541 | 11972.8478 | 10711.4117 | 15078.6328
2018-11-06 | 9699.7955 | 9020.2444 | 8580.2325 | 8346.8617 | 8382.844 | 9075.7599 | 10250.8385 | 11107.2168 | 11986.2126 | 12959.7904 | 13909.7227 | 14694.1365 | 15293.4985 | 15735.5665 | 15946.3199 | 15930.8989 | 15574.1603 | 15232.8426 | 15596.7777 | 15049.847 | 14168.7951 | 13016.334 | 11688.0737 | 10435.8902 | 15946.3199
2018-11-07 | 9368.7585 | 8672.7584 | 8234.8026 | 8064.1437 | 8105.2663 | 8721.0774 | 9961.9522 | 10744.3098 | 11589.3794 | 12526.9749 | 13357.6516 | 14092.7183 | 14678.7155 | 15152.6535 | 15355.1824 | 15312.0037 | 14896.6653 | 14559.4599 | 14783.5781 | 14056.736 | 13296.9958 | 12396.4106 | 11464.9835 | 10475.9848 | 15355.1824
2018-11-08 | 9520.9122 | 8820.7997 | 8336.581 | 8125.8276 | 8082.6489 | 8264.6165 | 8704.6284 | 9562.0348 | 11055.8136 | 12246.3131 | 13058.4847 | 13698.9693 | 14237.6755 | 14461.7937 | 14428.8956 | 14186.2722 | 13838.7862 | 13951.8733 | 14200.6651 | 13569.4331 | 12918.6678 | 12148.6469 | 11322.0825 | 10356.7292 | 14461.7937
2018-11-09 | 9522.9683 | 8817.7155 | 8402.3772 | 8184.4274 | 8094.9857 | 8220.4096 | 8527.8012 | 9171.37 | 10395.7957 | 11339.5596 | 11865.929 | 12174.3486 | 12212.387 | 12059.2052 | 11899.8551 | 11647.9791 | 11590.4075 | 12164.0679 | 12665.7637 | 12299.7725 | 11759.0102 | 10971.5122 | 10132.611 | 9131.2754 | 12665.7637
2018-11-10 | 8326.3004 | 7878.0639 | 7638.5247 | 7537.7743 | 7662.1702 | 8209.1009 | 9527.0806 | 10562.3423 | 11025.9997 | 11588.3514 | 12018.0826 | 12395.3826 | 12669.876 | 12910.4433 | 13028.6708 | 13123.2528 | 13016.334 | 13185.9647 | 13814.1126 | 13356.6236 | 12640.0621 | 11657.2317 | 10614.7736 | 9509.6035 | 13814.1126
2018-11-11 | 8516.4924 | 7934.6075 | 7618.9915 | 7501.792 | 7585.0653 | 8052.835 | 8978.0937 | 9920.8295 | 10745.3379 | 11475.2642 | 12020.1388 | 12410.8036 | 12771.6545 | 13104.7476 | 13259.9854 | 13402.8865 | 13278.4906 | 13345.3149 | 13950.8453 | 13526.2543 | 12808.6648 | 11830.9748 | 10729.9169 | 9525.0244 | 13950.8453
2018-11-12 | 8501.0715 | 7904.7936 | 7630.3002 | 7514.1288 | 7656.0018 | 8316.0197 | 9654.5607 | 10415.3289 | 10941.6983 | 11611.9969 | 12294.6322 | 12901.1907 | 13432.7004 | 13975.5188 | 14339.4539 | 14470.0182 | 14273.6578 | 14140.0093 | 14636.5648 | 14145.1496 | 13399.8023 | 12416.9719 | 11241.8934 | 10011.2993 | 14636.5648
2018-11-13 | 9004.8234 | 8401.3491 | 8032.2737 | 7918.1585 | 8009.6563 | 8650.1409 | 9945.5031 | 10741.2256 | 11446.4784 | 12327.5303 | 13108.8599 | 13683.5483 | 14240.7597 | 14730.1187 | 14948.0686 | 14977.8825 | 14706.4732 | 14557.4038 | 14981.9947 | 14482.355 | 13712.3341 | 12676.0444 | 11418.7206 | 10207.6598 | 14981.9947
2018-11-14 | 9176.5103 | 8490.7908 | 8111.4347 | 7913.0181 | 7960.3091 | 8541.166 | 9834.4721 | 10664.1207 | 11381.7103 | 12145.5627 | 12809.6929 | 13246.6206 | 13655.7906 | 13952.9014 | 14126.6444 | 14124.5883 | 13821.3091 | 13723.6429 | 14046.4554 | 13462.5143 | 12779.879 | 11932.7532 | 11083.5713 | 10118.2181 | 14126.6444
2018-11-15 | 9242.3065 | 8601.8218 | 8238.9148 | 8041.5263 | 8024.0492 | 8230.6903 | 8731.3581 | 9514.7438 | 10723.7485 | 11729.1963 | 12379.9616 | 12875.489 | 13203.4419 | 13490.2721 | 13596.1628 | 13536.535 | 13276.4345 | 13224.0032 | 13597.1908 | 13020.4462 | 12395.3826 | 11710.6911 | 10983.849 | 10176.8178 | 13597.1908
2018-11-16 | 9341.0008 | 8781.7333 | 8416.7701 | 8213.2132 | 8152.5573 | 8318.0758 | 8618.2709 | 9273.1484 | 10762.815 | 12104.4401 | 13065.6811 | 13764.7655 | 14347.6785 | 14712.6416 | 14866.8514 | 14857.5988 | 14567.6844 | 14513.197 | 14959.3773 | 14471.0463 | 13725.699 | 12840.5348 | 11893.6867 | 10810.106 | 14959.3773
2018-11-17 | 9903.3524 | 9350.2533 | 9034.6373 | 8896.8766 | 9075.7599 | 9797.4617 | 11118.5256 | 11893.6867 | 12794.2719 | 13997.1082 | 15133.1203 | 15990.5267 | 16601.1975 | 16936.3467 | 16980.5535 | 16836.6244 | 16532.3171 | 16541.5697 | 16848.9612 | 16210.5327 | 15258.5443 | 14015.6134 | 12746.9809 | 11358.0648 | 16980.5535
2018-11-18 | 10263.1753 | 9553.8103 | 9063.4231 | 8810.5191 | 8872.203 | 9436.6108 | 10823.4708 | 11611.9969 | 12248.3692 | 12960.8185 | 13436.8127 | 13526.2543 | 13298.0239 | 13049.2321 | 12714.0828 | 12378.9335 | 12394.3545 | 13062.5969 | 13733.9235 | 13525.2263 | 13015.3059 | 12224.7237 | 11171.9849 | 10171.6775 | 13733.9235
2018-11-19 | 9458.2002 | 9137.4438 | 9006.8796 | 9025.3847 | 9330.7201 | 10241.5859 | 12012.9423 | 12781.9351 | 13091.3827 | 13241.4803 | 13160.2631 | 12847.7313 | 12468.3752 | 12185.6573 | 11963.5952 | 11880.3219 | 12020.1388 | 12819.9735 | 13616.7241 | 13489.244 | 13095.495 | 12322.3899 | 11320.0263 | 10286.8208 | 13616.7241
2018-11-20 | 9539.4173 | 9164.1735 | 9071.6477 | 9110.7141 | 9430.4424 | 10329.9995 | 11914.248 | 12549.5924 | 12404.6352 | 12402.579 | 12349.1196 | 12283.3235 | 12179.4889 | 12073.5982 | 11900.8832 | 11816.5818 | 11854.6203 | 12594.8272 | 13396.7181 | 13276.4345 | 12835.3945 | 12078.7385 | 11098.9923 | 10063.7306 | 13396.7181
2018-11-21 | 9253.6152 | 8749.8632 | 8575.0922 | 8470.2295 | 8618.2709 | 9570.2593 | 10887.2109 | 11641.8108 | 11904.9955 | 12158.9276 | 12371.7371 | 12420.0561 | 12247.3412 | 12126.0295 | 11977.9881 | 11843.3115 | 11922.4726 | 12514.6381 | 12883.7136 | 12553.7046 | 12111.6366 | 11497.8816 | 10779.264 | 9946.5312 | 12883.7136
2018-11-22 | 9133.3316 | 8607.9902 | 8314.9916 | 8211.1571 | 8249.1955 | 8486.6785 | 9033.6092 | 9767.6478 | 10996.1858 | 12060.2333 | 12669.876 | 12997.8288 | 13015.3059 | 12994.7446 | 12891.9381 | 12716.1389 | 12684.2689 | 13185.9647 | 13571.4892 | 13312.4168 | 12933.0607 | 12367.6248 | 11721.9998 | 10834.7795 | 13571.4892
2018-11-23 | 9981.4854 | 9425.3021 | 8989.4024 | 8740.6107 | 8694.3477 | 8843.4172 | 9155.949 | 9869.4263 | 11497.8816 | 13098.5792 | 14136.9251 | 14806.1956 | 15228.7304 | 15535.0938 | 15590.6093 | 15486.7747 | 15091.9977 | 15250.3197 | 15742.763 | 15411.726 | 14826.7569 | 13959.0698 | 12993.7165 | 12027.3352 | 15742.763
2018-11-24 | 10800.8534 | 10053.45 | 9629.8871 | 9466.4247 | 9596.989 | 10253.9227 | 11453.6748 | 12290.5199 | 13375.1287 | 14570.7686 | 15649.2091 | 16760.5476 | 17611.7856 | 18042.5449 | 18245.0738 | 18168.997 | 17688.8905 | 17512.0633 | 17866.7458 | 17265.3276 | 16468.5771 | 15270.881 | 14177.0196 | 12801.4683 | 18245.0738
2018-11-25 | 11600.6881 | 10770.0114 | 10303.2698 | 10120.2742 | 10165.5091 | 10811.134 | 12002.6617 | 12806.6087 | 13873.7404 | 14986.107 | 15952.4883 | 16591.9449 | 16953.8238 | 17214.9524 | 17183.0824 | 17007.2832 | 16626.8991 | 16751.295 | 17097.753 | 16637.1798 | 15876.4115 | 14973.7702 | 13878.8807 | 12792.2158 | 17214.9524
2018-11-26 | 11725.084 | 10998.2419 | 10522.2477 | 10273.4559 | 10275.5121 | 10647.6717 | 11449.5626 | 12210.3308 | 13115.0282 | 13753.4568 | 13796.6355 | 13647.566 | 13415.2233 | 13051.2882 | 12612.3043 | 12182.5731 | 11949.2023 | 12428.2807 | 12954.6501 | 12652.3989 | 12151.7311 | 11628.4459 | 10932.4457 | 10046.2535 | 13796.6355
2018-11-27 | 9232.0258 | 8692.2916 | 8417.7982 | 8347.8897 | 8420.8824 | 8751.9194 | 9372.8708 | 10278.5963 | 11315.9141 | 11994.4371 | 12396.4106 | 12553.7046 | 12543.424 | 12328.5583 | 12082.8507 | 11698.3543 | 11193.5743 | 10984.8771 | 11134.9746 | 10738.1414 | 10465.7041 | 10219.9965 | 9832.4159 | 9268.0081 | 12553.7046
2018-11-28 | 8728.2739 | 8406.4895 | 8276.9532 | 8321.16 | 8553.5028 | 9040.8057 | 9818.023 | 10636.363 | 11411.5241 | 11848.4519 | 11907.0516 | 11712.7473 | 11472.18 | 11254.2302 | 11051.7013 | 10920.109 | 10930.3896 | 11599.6601 | 12361.4564 | 12145.5627 | 11812.4696 | 11607.8846 | 10918.0528 | 10134.6671 | 12361.4564
2018-11-29 | 9429.4144 | 9046.9741 | 8843.4172 | 8817.7155 | 8937.9992 | 9189.8752 | 9739.8901 | 10437.9464 | 11180.2095 | 11519.471 | 11562.6497 | 11534.892 | 11435.1696 | 11324.1386 | 11188.434 | 11053.7574 | 10934.5019 | 11398.1593 | 11995.4652 | 11727.1402 | 11309.7457 | 10833.7515 | 10191.2107 | 9407.825 | 11995.4652
2018-11-30 | 8632.6638 | 8128.9118 | 7874.9797 | 7778.3416 | 7825.6326 | 8027.1334 | 8414.714 | 9027.4409 | 10063.7306 | 10851.2286 | 11337.5034 | 11655.1756 | 11886.4903 | 12004.7178 | 12028.3633 | 11949.2023 | 11833.0309 | 12296.6883 | 13111.944 | 12829.2261 | 12357.3442 | 11638.7266 | 10770.0114 | 9669.9816 | 13111.944
2018-12-01 | 8814.6314 | 8255.3639 | 7976.7582 | 7888.3446 | 8038.4421 | 8771.4526 | 10121.3023 | 10866.6496 | 11503.022 | 12201.0782 | 12929.9765 | 13495.4124 | 13757.569 | 13856.2633 | 13732.8955 | 13508.7772 | 13299.0519 | 13777.1023 | 14555.3476 | 14315.8084 | 13752.4287 | 12841.5629 | 11759.0102 | 10495.518 | 14555.3476
2018-12-02 | 9421.1898 | 8749.8632 | 8322.1881 | 8153.5854 | 8269.7568 | 8935.9431 | 10325.8873 | 11037.3084 | 11547.2288 | 12280.2393 | 12980.3517 | 13406.9988 | 13652.7064 | 13805.8881 | 13753.4568 | 13574.5734 | 13330.9219 | 13853.1791 | 14613.9474 | 14338.4259 | 13782.2426 | 12910.4433 | 11777.5154 | 10506.8267 | 14613.9474
2018-12-03 | 9406.7969 | 8690.2355 | 8307.7952 | 8125.8276 | 8203.9606 | 8878.3714 | 10389.6273 | 11038.3365 | 11668.5405 | 12557.8169 | 13235.3119 | 13782.2426 | 14191.4125 | 14382.6327 | 14530.6741 | 14599.5544 | 14262.3491 | 14420.6711 | 15089.9416 | 14732.1749 | 14090.6622 | 13146.8983 | 11991.3529 | 10644.5875 | 15089.9416
2018-12-04 | 9528.1086 | 8842.3891 | 8447.6121 | 8277.9813 | 8376.6756 | 9070.6196 | 10424.5815 | 11164.7885 | 11775.4592 | 12642.1182 | 13330.9219 | 13903.5543 | 14345.6223 | 14540.9547 | 14670.491 | 14718.81 | 14354.8749 | 14528.6179 | 15233.8707 | 14933.6757 | 14342.5381 | 13473.823 | 12272.0147 | 10961.2316 | 15233.8707
2018-12-05 | 9827.2756 | 9048.0022 | 8624.4393 | 8450.6963 | 8518.5486 | 9188.8471 | 10546.9213 | 11293.2966 | 12032.4755 | 13057.4566 | 13816.1687 | 14325.061 | 14603.6667 | 14577.9651 | 14550.2073 | 14651.9858 | 14515.2531 | 14695.1645 | 15077.6048 | 14609.8351 | 14002.2485 | 13240.4522 | 12360.4284 | 11262.4547 | 15077.6048
2018-12-06 | 10167.5652 | 9392.404 | 8906.1292 | 8601.8218 | 8478.454 | 8615.1867 | 9044.918 | 9729.6094 | 11137.0307 | 12506.4136 | 13504.665 | 14160.5706 | 14601.6106 | 14873.0198 | 14994.3315 | 14896.6653 | 14453.5692 | 14263.3771 | 14564.6002 | 13866.5439 | 13184.9367 | 12470.4313 | 11571.9023 | 10510.939 | 14994.3315
2018-12-07 | 9417.0776 | 8729.3019 | 8275.9252 | 7980.8704 | 7898.6252 | 8014.7966 | 8317.0478 | 8867.0627 | 10170.6494 | 11459.8432 | 12281.2673 | 12812.7771 | 13090.3547 | 13242.5083 | 13287.7432 | 13090.3547 | 12819.9735 | 13137.6457 | 13949.8172 | 13417.2794 | 12843.619 | 12009.8581 | 10923.1932 | 9722.413 | 13949.8172
2018-12-08 | 8698.46 | 8075.4524 | 7762.9206 | 7653.9457 | 7779.3697 | 8471.2576 | 9805.6862 | 10541.781 | 11025.9997 | 11592.4636 | 12081.8227 | 12400.5229 | 12607.164 | 12773.7106 | 12850.8155 | 12943.3413 | 12907.3591 | 13357.6516 | 14226.3668 | 13980.6592 | 13294.9397 | 12332.6706 | 11190.4901 | 9846.8089 | 14226.3668
2018-12-09 | 8768.3684 | 8193.6799 | 7903.7656 | 7822.5484 | 7955.1688 | 8717.9932 | 10285.7927 | 11012.6348 | 11383.7664 | 11683.9614 | 11861.8167 | 11899.8551 | 11884.4342 | 11816.5818 | 11708.635 | 11550.313 | 11628.4459 | 12444.7297 | 13485.1317 | 13372.0446 | 12932.0326 | 12190.7976 | 11121.6097 | 9998.9625 | 13485.1317
2018-12-10 | 9132.3035 | 8752.9474 | 8575.0922 | 8679.9548 | 8979.1218 | 10107.9374 | 12010.8862 | 13060.5408 | 12965.9588 | 12643.1463 | 12388.1861 | 12076.6824 | 11810.4135 | 11627.4178 | 11402.2716 | 11315.9141 | 11438.2538 | 12394.3545 | 13679.4361 | 13678.408 | 13494.3843 | 12855.9558 | 11870.0412 | 10775.1518 | 13679.4361
2018-12-11 | 10051.3938 | 9708.02 | 9627.831 | 9654.5607 | 10011.2993 | 11121.6097 | 13098.5792 | 14012.5292 | 13625.9767 | 13231.1996 | 12740.8125 | 12412.8597 | 12086.963 | 11840.2273 | 11607.8846 | 11510.2184 | 11639.7546 | 12543.424 | 13613.6399 | 13530.3666 | 13272.3222 | 12626.6973 | 11549.2849 | 10468.7883 | 14012.5292
2018-12-12 | 9679.2342 | 9270.0643 | 9126.1351 | 9108.658 | 9466.4247 | 10534.5845 | 12297.7164 | 13146.8983 | 13206.5261 | 13195.2173 | 12989.6043 | 12725.3915 | 12405.6632 | 12134.254 | 11854.6203 | 11755.926 | 11911.1639 | 12885.7697 | 13795.6074 | 13629.0609 | 13426.532 | 12928.9484 | 12194.9099 | 11306.6615 | 13795.6074
2018-12-13 | 10496.5461 | 10142.8916 | 9975.317 | 9995.8783 | 10188.1265 | 10707.2995 | 11505.0781 | 12450.8981 | 13008.1095 | 12975.2114 | 12582.4905 | 12219.5834 | 11949.2023 | 11680.8772 | 11442.3661 | 11316.9421 | 11281.9879 | 11912.1919 | 12675.0163 | 12431.3649 | 12170.2363 | 11783.6838 | 11197.6866 | 10548.9774 | 13008.1095
2018-12-14 | 9882.7911 | 9465.3966 | 9321.4675 | 9333.8043 | 9478.7615 | 9894.0999 | 10649.7278 | 11585.2672 | 12434.4491 | 12530.0591 | 12189.7695 | 11930.6971 | 11729.1963 | 11562.6497 | 11450.5906 | 11350.8683 | 11354.9806 | 12016.0265 | 13102.6915 | 12969.043 | 12660.6234 | 12090.0472 | 11119.5536 | 10167.5652 | 13102.6915
2018-12-15 | 9449.9757 | 9086.0406 | 9058.2828 | 9136.4158 | 9557.9225 | 10632.2507 | 12544.452 | 13525.2263 | 13442.9811 | 12962.8746 | 12609.2201 | 12326.5022 | 12259.678 | 12152.7592 | 12024.251 | 12004.7178 | 12035.5597 | 12752.1212 | 13860.3755 | 13749.3445 | 13318.5852 | 12532.1153 | 11450.5906 | 10307.3821 | 13860.3755
2018-12-16 | 9437.6389 | 9024.3567 | 8873.2311 | 8927.7185 | 9228.9416 | 10237.4736 | 12083.8788 | 12931.0046 | 12842.591 | 12509.4978 | 12288.4638 | 12175.3766 | 12137.3382 | 12154.8153 | 12134.254 | 12160.9837 | 12176.4047 | 12722.3073 | 13714.3903 | 13532.4227 | 12998.8569 | 12095.1875 | 11018.8032 | 9834.4721 | 13714.3903
2018-12-17 | 8847.5294 | 8328.3565 | 8122.7434 | 8099.0979 | 8365.3668 | 9257.7275 | 10853.2847 | 11708.635 | 11793.9644 | 11893.6867 | 11983.1284 | 12035.5597 | 12140.4224 | 12268.9306 | 12403.6071 | 12539.3117 | 12472.4875 | 12961.8465 | 13825.4213 | 13552.984 | 12974.1833 | 12203.1344 | 11106.1888 | 9866.3421 | 13825.4213
2018-12-18 | 8894.8204 | 8361.2546 | 8142.2767 | 8130.968 | 8379.7598 | 9218.661 | 10834.7795 | 11723.0279 | 12031.4475 | 12213.415 | 12289.4919 | 12226.7799 | 12216.4992 | 12409.7755 | 12528.003 | 12557.8169 | 12497.161 | 12947.4536 | 13815.1407 | 13545.7876 | 13107.8318 | 12314.1654 | 11276.8476 | 10102.7971 | 13815.1407
2018-12-19 | 9162.1174 | 8650.1409 | 8401.3491 | 8362.2826 | 8585.3728 | 9395.4882 | 10856.3689 | 11801.1609 | 12127.0576 | 12312.1093 | 12474.5436 | 12538.2836 | 12531.0872 | 12589.6869 | 12588.6588 | 12565.0133 | 12446.7858 | 12798.3842 | 13536.535 | 13149.9825 | 12624.6411 | 11965.6513 | 11206.9392 | 10204.5756 | 13536.535
2018-12-20 | 9301.9343 | 8700.5161 | 8391.0685 | 8249.1955 | 8234.8026 | 8539.1099 | 9122.0229 | 9896.156 | 10904.688 | 11675.7369 | 12100.3279 | 12176.4047 | 12481.7401 | 12517.7223 | 12553.7046 | 12563.9853 | 12448.842 | 12760.3457 | 13417.2794 | 12929.9765 | 12388.1861 | 11770.3189 | 10997.2139 | 10042.1412 | 13417.2794
2018-12-21 | 9074.7319 | 8394.1527 | 7976.7582 | 7783.4819 | 7756.7522 | 7897.5972 | 8267.7006 | 8885.5679 | 10095.6006 | 11293.2966 | 12023.223 | 12401.551 | 12792.2158 | 12908.3871 | 12821.0016 | 12658.5673 | 12525.9469 | 13031.755 | 13810.0003 | 13496.4404 | 13054.3724 | 12403.6071 | 11494.7974 | 10325.8873 | 13810.0003
2018-12-22 | 9257.7275 | 8549.3905 | 8123.7715 | 7913.0181 | 7976.7582 | 8485.6505 | 9374.9269 | 10261.1191 | 11438.2538 | 12561.9291 | 13490.2721 | 14077.2973 | 14471.0463 | 14761.9888 | 14964.5176 | 14863.7672 | 14514.225 | 14718.81 | 15491.9151 | 15073.4925 | 14447.4008 | 13693.829 | 12669.876 | 11276.8476 | 15491.9151
2018-12-23 | 10067.8429 | 9219.6891 | 8678.9267 | 8407.5175 | 8444.5279 | 8949.3079 | 9809.7985 | 10679.5417 | 11926.5848 | 13184.9367 | 14112.2515 | 14768.1571 | 15241.0672 | 15428.175 | 15007.6963 | 14555.3476 | 14153.3741 | 14310.6681 | 15029.2857 | 14622.1719 | 14036.1747 | 13584.8541 | 12922.78 | 12062.2894 | 15428.175
2018-12-24 | 11012.6348 | 10199.4352 | 9669.9816 | 9436.6108 | 9383.1514 | 9699.7955 | 10289.905 | 11037.3084 | 12455.0104 | 14034.1186 | 15251.3478 | 16062.4913 | 16482.97 | 16555.9626 | 16610.4501 | 16413.0615 | 16199.224 | 16393.5283 | 16574.4678 | 15636.8723 | 14754.7923 | 14009.445 | 13283.6309 | 12245.2851 | 16610.4501
2018-12-25 | 11188.434 | 10371.1221 | 9640.1677 | 9077.8161 | 8691.2635 | 8622.3832 | 8782.7613 | 9228.9416 | 10285.7927 | 11362.177 | 12037.6159 | 12376.8774 | 12495.1049 | 12409.7755 | 12227.8079 | 11844.3396 | 11435.1696 | 11610.9688 | 12096.2156 | 11844.3396 | 11639.7546 | 11318.9983 | 10735.0572 | 9904.3805 | 12495.1049
2018-12-26 | 9041.8338 | 8441.4437 | 8166.9503 | 8021.9931 | 8089.8454 | 8456.8647 | 9083.9844 | 9811.8546 | 10725.8046 | 11576.0146 | 12227.8079 | 12496.133 | 12488.9365 | 12331.6425 | 12235.0044 | 12166.124 | 12226.7799 | 12919.6958 | 13656.8186 | 13391.5778 | 12896.0503 | 12282.2954 | 11541.0604 | 10546.9213 | 13656.8186
2018-12-27 | 9543.5296 | 8814.6314 | 8334.5249 | 8114.5189 | 8115.547 | 8277.9813 | 8704.6284 | 9179.5945 | 10291.9611 | 11623.3056 | 12652.3989 | 13314.4729 | 13725.699 | 13859.3475 | 13864.4878 | 13647.566 | 13383.3533 | 13688.6886 | 14370.2959 | 13941.5927 | 13323.7255 | 12659.5953 | 11785.7399 | 10680.5698 | 14370.2959
2018-12-28 | 9636.0555 | 8858.8382 | 8366.3949 | 8084.705 | 7945.9162 | 8009.6563 | 8326.3004 | 8738.5545 | 10115.1339 | 11603.7723 | 12693.5215 | 13505.693 | 14069.0728 | 14462.8218 | 14670.491 | 14663.2945 | 14438.1482 | 14372.352 | 15011.8086 | 14513.197 | 13828.5055 | 13041.0075 | 12030.4194 | 10764.8711 | 15011.8086
2018-12-29 | 9680.2623 | 8935.9431 | 8486.6785 | 8289.29 | 8310.8794 | 8704.6284 | 9522.9683 | 10292.9892 | 11540.0323 | 12947.4536 | 14061.8763 | 14782.5501 | 15157.7939 | 15325.3685 | 15448.7363 | 15511.4483 | 15264.7127 | 15194.8042 | 15903.1412 | 15365.4631 | 14635.5367 | 13645.5099 | 12562.9572 | 11211.0514 | 15903.1412
2018-12-30 | 9986.6257 | 9184.7348 | 8697.4319 | 8432.1911 | 8406.4895 | 8801.2665 | 9564.0909 | 10310.4663 | 11396.1032 | 12603.0518 | 13682.5203 | 14559.4599 | 15105.3625 | 15487.8028 | 15591.6374 | 15464.1573 | 15164.9903 | 15161.9061 | 15860.9905 | 15330.5088 | 14672.5471 | 13730.8393 | 12716.1389 | 11470.1239 | 15860.9905
2018-12-31 | 10311.4943 | 9477.7334 | 8968.8411 | 8694.3477 | 8670.7022 | 9016.1321 | 9722.413 | 10517.1074 | 11562.6497 | 12632.8656 | 13484.1037 | 13977.575 | 14094.7744 | 14170.8512 | 14147.2057 | 13999.1643 | 14041.315 | 14771.2413 | 15397.3331 | 14660.2103 | 13777.1023 | 12810.7209 | 11825.8344 | 11015.719 | 15397.3331
Max | 16242.4027 | 14411.4185 | 13627.0047 | 13144.8421 | 13275.4064 | 14614.9754 | 16884.9435 | 17981.8891 | 17358.8815 | 17386.6393 | 18892.7549 | 20261.1097 | 21349.8308 | 22286.3982 | 22809.6834 | 23339.137 | 23357.6422 | 23141.7485 | 22697.6243 | 21818.6286 | 21277.8662 | 20393.7301 | 18763.2187 | 17034.0129 | 6299675.3606
Note on C80: Jessica Shrader: Blank due to Daylight Savings Time. No "HR-2" occurred.
Note on B320: Jessica Shrader: Hour 1 and 2 combined due to the end of DST.

## Hourly Loads p.u of Peak
OPC 012928
FPL RC-16
Hourly Loads p.u. of Peak
(hourly load/peak)
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24 | Max
2018-01-01 | 0.40882 | 0.39395 | 0.37356 | 0.35965 | 0.35359 | 0.35656 | 0.36583 | 0.37348 | 0.40736 | 0.46088 | 0.51098 | 0.54528 | 0.56558 | 0.57356 | 0.57118 | 0.56387 | 0.55631 | 0.56278 | 0.59011 | 0.57386 | 0.54925 | 0.52184 | 0.48541 | 0.43953 | 0.59011
2018-01-02 | 0.39658 | 0.36905 | 0.35054 | 0.34168 | 0.33917 | 0.34945 | 0.38877 | 0.42069 | 0.46811 | 0.52389 | 0.56876 | 0.59951 | 0.62149 | 0.63678 | 0.64363 | 0.64016 | 0.62725 | 0.62178 | 0.64488 | 0.62032 | 0.58727 | 0.55042 | 0.50914 | 0.4608 | 0.64488
2018-01-03 | 0.41446 | 0.38133 | 0.36078 | 0.35079 | 0.34995 | 0.36153 | 0.3955 | 0.42742 | 0.46464 | 0.49623 | 0.51428 | 0.52013 | 0.52017 | 0.51536 | 0.51052 | 0.50751 | 0.50596 | 0.53015 | 0.56659 | 0.55668 | 0.53638 | 0.51181 | 0.47851 | 0.44003 | 0.56659
2018-01-04 | 0.40565 | 0.38263 | 0.36884 | 0.36286 | 0.36362 | 0.37264 | 0.3919 | 0.4173 | 0.45645 | 0.49105 | 0.51127 | 0.5157 | 0.51152 | 0.50484 | 0.49627 | 0.48829 | 0.48996 | 0.51465 | 0.53625 | 0.52167 | 0.50308 | 0.48027 | 0.45165 | 0.41785 | 0.53625
2018-01-05 | 0.3833 | 0.35852 | 0.34289 | 0.33391 | 0.33207 | 0.33984 | 0.35823 | 0.37945 | 0.42073 | 0.46092 | 0.5045 | 0.53141 | 0.54536 | 0.54975 | 0.54937 | 0.54423 | 0.53713 | 0.54311 | 0.57636 | 0.55944 | 0.53575 | 0.4999 | 0.45796 | 0.41292 | 0.57636
2018-01-06 | 0.36771 | 0.34281 | 0.32798 | 0.32267 | 0.32689 | 0.35133 | 0.40189 | 0.43381 | 0.46276 | 0.50166 | 0.54173 | 0.56713 | 0.5871 | 0.59776 | 0.59445 | 0.58179 | 0.5698 | 0.58777 | 0.61785 | 0.60055 | 0.56199 | 0.51453 | 0.47463 | 0.43055 | 0.61785
2018-01-07 | 0.39683 | 0.37816 | 0.37339 | 0.3772 | 0.39499 | 0.43523 | 0.51039 | 0.5637 | 0.58727 | 0.60122 | 0.59571 | 0.58021 | 0.56533 | 0.55058 | 0.53897 | 0.53822 | 0.55409 | 0.60486 | 0.66231 | 0.66623 | 0.65178 | 0.61447 | 0.56784 | 0.52176 | 0.66623
2018-01-08 | 0.48633 | 0.46778 | 0.46113 | 0.45817 | 0.46527 | 0.49711 | 0.55668 | 0.58547 | 0.58259 | 0.58259 | 0.579 | 0.56437 | 0.54436 | 0.52539 | 0.50905 | 0.50262 | 0.50734 | 0.53546 | 0.56822 | 0.55785 | 0.53375 | 0.49468 | 0.44935 | 0.40151 | 0.58547
2018-01-09 | 0.36261 | 0.34252 | 0.33303 | 0.32957 | 0.33642 | 0.36483 | 0.42269 | 0.46063 | 0.47254 | 0.49393 | 0.5086 | 0.51653 | 0.51724 | 0.51344 | 0.5086 | 0.50688 | 0.50993 | 0.53404 | 0.57031 | 0.56345 | 0.54131 | 0.50613 | 0.46397 | 0.41538 | 0.57031
2018-01-10 | 0.37235 | 0.34515 | 0.32952 | 0.32363 | 0.32714 | 0.3515 | 0.4064 | 0.44308 | 0.47083 | 0.50438 | 0.53095 | 0.54787 | 0.55727 | 0.56433 | 0.56458 | 0.56304 | 0.56086 | 0.56421 | 0.59391 | 0.57732 | 0.55096 | 0.51804 | 0.48382 | 0.44467 | 0.59391
2018-01-11 | 0.39892 | 0.37026 | 0.35087 | 0.34147 | 0.33951 | 0.3487 | 0.3693 | 0.39537 | 0.4537 | 0.51574 | 0.55877 | 0.58551 | 0.60536 | 0.61739 | 0.62228 | 0.61961 | 0.60628 | 0.59542 | 0.61317 | 0.59023 | 0.5604 | 0.5251 | 0.4885 | 0.44747 | 0.62228
2018-01-12 | 0.40331 | 0.37201 | 0.35246 | 0.3411 | 0.33541 | 0.33888 | 0.35263 | 0.37084 | 0.41534 | 0.46105 | 0.49347 | 0.51202 | 0.52836 | 0.53868 | 0.54156 | 0.53818 | 0.53028 | 0.52476 | 0.55551 | 0.54474 | 0.52004 | 0.48545 | 0.44613 | 0.40043 | 0.55551
2018-01-13 | 0.36261 | 0.34164 | 0.33186 | 0.33086 | 0.33993 | 0.3741 | 0.43836 | 0.4768 | 0.49201 | 0.51231 | 0.53024 | 0.54361 | 0.55581 | 0.56521 | 0.57122 | 0.57553 | 0.57302 | 0.57808 | 0.61392 | 0.60599 | 0.57457 | 0.53099 | 0.48328 | 0.42938 | 0.61392
2018-01-14 | 0.38267 | 0.35422 | 0.33905 | 0.33128 | 0.33437 | 0.36111 | 0.41902 | 0.45349 | 0.4811 | 0.51879 | 0.55013 | 0.56834 | 0.57766 | 0.57812 | 0.57415 | 0.56345 | 0.56053 | 0.57356 | 0.60799 | 0.59897 | 0.57093 | 0.53074 | 0.48077 | 0.42683 | 0.60799
2018-01-15 | 0.38054 | 0.35468 | 0.34014 | 0.33521 | 0.33859 | 0.36825 | 0.42996 | 0.46585 | 0.47856 | 0.49539 | 0.50412 | 0.50475 | 0.49782 | 0.49096 | 0.48332 | 0.47968 | 0.48349 | 0.51031 | 0.54536 | 0.53747 | 0.51628 | 0.48319 | 0.44095 | 0.39437 | 0.54536
2018-01-16 | 0.35973 | 0.34126 | 0.33579 | 0.33784 | 0.34983 | 0.39002 | 0.46485 | 0.51323 | 0.52146 | 0.52443 | 0.52435 | 0.51649 | 0.50446 | 0.49172 | 0.4806 | 0.47513 | 0.48073 | 0.51465 | 0.58677 | 0.60064 | 0.59746 | 0.57812 | 0.54691 | 0.51215 | 0.60064
2018-01-17 | 0.48758 | 0.47789 | 0.47931 | 0.48758 | 0.506 | 0.55272 | 0.63532 | 0.68524 | 0.67814 | 0.64275 | 0.60377 | 0.56379 | 0.53057 | 0.50371 | 0.48491 | 0.47454 | 0.47642 | 0.50575 | 0.55292 | 0.5495 | 0.53838 | 0.51641 | 0.49105 | 0.46034 | 0.68524
2018-01-18 | 0.43084 | 0.41772 | 0.41384 | 0.41551 | 0.42462 | 0.44542 | 0.4806 | 0.52552 | 0.55572 | 0.55907 | 0.54858 | 0.52706 | 0.50442 | 0.48407 | 0.46602 | 0.4562 | 0.45633 | 0.48227 | 0.53943 | 0.54946 | 0.54941 | 0.5449 | 0.53295 | 0.51587 | 0.55907
2018-01-19 | 0.50362 | 0.49945 | 0.50266 | 0.51223 | 0.52761 | 0.55246 | 0.59099 | 0.63745 | 0.66398 | 0.6433 | 0.59813 | 0.55409 | 0.51892 | 0.49301 | 0.47216 | 0.45537 | 0.45035 | 0.46485 | 0.51507 | 0.5119 | 0.49974 | 0.47509 | 0.44998 | 0.41463 | 0.66398
2018-01-20 | 0.38877 | 0.37653 | 0.37373 | 0.37728 | 0.39211 | 0.42157 | 0.46991 | 0.51545 | 0.53199 | 0.52456 | 0.51444 | 0.50471 | 0.49322 | 0.48436 | 0.47759 | 0.47383 | 0.4745 | 0.4905 | 0.53554 | 0.53195 | 0.50834 | 0.47375 | 0.43113 | 0.38543 | 0.53554
2018-01-21 | 0.351 | 0.33295 | 0.32551 | 0.32547 | 0.33391 | 0.36796 | 0.43381 | 0.47233 | 0.48064 | 0.48319 | 0.48578 | 0.4857 | 0.4847 | 0.48023 | 0.4763 | 0.47229 | 0.47383 | 0.49477 | 0.53596 | 0.53446 | 0.51223 | 0.47667 | 0.43456 | 0.39148 | 0.53596
2018-01-22 | 0.35747 | 0.34469 | 0.3426 | 0.34912 | 0.3685 | 0.4163 | 0.50128 | 0.55443 | 0.54653 | 0.55631 | 0.54941 | 0.53559 | 0.51979 | 0.50141 | 0.48846 | 0.48144 | 0.48624 | 0.51866 | 0.59019 | 0.60979 | 0.6092 | 0.59044 | 0.56111 | 0.52606 | 0.60979
2018-01-23 | 0.505 | 0.4999 | 0.50529 | 0.51729 | 0.53951 | 0.59395 | 0.6862 | 0.73078 | 0.70547 | 0.66323 | 0.62303 | 0.57849 | 0.54127 | 0.51022 | 0.48938 | 0.47868 | 0.47956 | 0.50471 | 0.56483 | 0.57578 | 0.56667 | 0.5411 | 0.50099 | 0.46101 | 0.73078
2018-01-24 | 0.43176 | 0.42144 | 0.42077 | 0.42645 | 0.44325 | 0.48942 | 0.57047 | 0.61292 | 0.6125 | 0.5988 | 0.58121 | 0.55568 | 0.533 | 0.51348 | 0.49744 | 0.48816 | 0.49059 | 0.51261 | 0.5617 | 0.56287 | 0.55017 | 0.52873 | 0.50179 | 0.46819 | 0.61292
2018-01-25 | 0.4402 | 0.42608 | 0.4204 | 0.42203 | 0.42967 | 0.44743 | 0.47856 | 0.51758 | 0.55401 | 0.55192 | 0.53091 | 0.50793 | 0.48954 | 0.475 | 0.46381 | 0.45533 | 0.45161 | 0.46264 | 0.5002 | 0.49631 | 0.47943 | 0.45875 | 0.43051 | 0.39825 | 0.55401
2018-01-26 | 0.37047 | 0.35213 | 0.34427 | 0.34093 | 0.34348 | 0.35534 | 0.37786 | 0.40882 | 0.45219 | 0.47446 | 0.48445 | 0.4834 | 0.48282 | 0.48227 | 0.47906 | 0.47563 | 0.47496 | 0.48695 | 0.52489 | 0.52364 | 0.50032 | 0.46723 | 0.42871 | 0.38371 | 0.52489
2018-01-27 | 0.34661 | 0.32459 | 0.31494 | 0.31235 | 0.32108 | 0.35196 | 0.41618 | 0.4519 | 0.46673 | 0.48407 | 0.50375 | 0.51666 | 0.52719 | 0.53584 | 0.53981 | 0.54482 | 0.54708 | 0.55121 | 0.58422 | 0.58042 | 0.55 | 0.50463 | 0.4542 | 0.39913 | 0.58422
2018-01-28 | 0.35288 | 0.32748 | 0.31507 | 0.31014 | 0.31624 | 0.3459 | 0.40653 | 0.44463 | 0.46155 | 0.48432 | 0.50776 | 0.52426 | 0.53955 | 0.55226 | 0.56157 | 0.56863 | 0.57106 | 0.57219 | 0.60051 | 0.5955 | 0.56784 | 0.5218 | 0.47379 | 0.42048 | 0.60051
2018-01-29 | 0.37381 | 0.34749 | 0.33466 | 0.33007 | 0.33633 | 0.36763 | 0.42863 | 0.46936 | 0.48691 | 0.51081 | 0.52848 | 0.54311 | 0.47592 | 0.54064 | 0.53492 | 0.53722 | 0.54565 | 0.56776 | 0.59554 | 0.58869 | 0.56968 | 0.534 | 0.49025 | 0.44024 | 0.59554
2018-01-30 | 0.40343 | 0.38133 | 0.37026 | 0.36784 | 0.3764 | 0.40962 | 0.47772 | 0.51896 | 0.53947 | 0.5589 | 0.56955 | 0.56817 | 0.56207 | 0.55489 | 0.54687 | 0.54223 | 0.54536 | 0.56404 | 0.597 | 0.59186 | 0.56838 | 0.53404 | 0.48616 | 0.43652 | 0.597
2018-01-31 | 0.39942 | 0.37791 | 0.36909 | 0.36533 | 0.37114 | 0.40256 | 0.4664 | 0.50458 | 0.51983 | 0.53935 | 0.55355 | 0.56141 | 0.56304 | 0.56095 | 0.55706 | 0.55932 | 0.5561 | 0.56124 | 0.58535 | 0.57603 | 0.55054 | 0.51812 | 0.48039 | 0.43665 | 0.58535
2018-02-01 | 0.39591 | 0.36825 | 0.35087 | 0.34172 | 0.34005 | 0.34812 | 0.36942 | 0.40026 | 0.45553 | 0.50738 | 0.54189 | 0.56078 | 0.57469 | 0.58305 | 0.58827 | 0.59011 | 0.5856 | 0.57448 | 0.58744 | 0.57586 | 0.54565 | 0.51156 | 0.47467 | 0.43235 | 0.59011
2018-02-02 | 0.39065 | 0.36249 | 0.34448 | 0.33437 | 0.33082 | 0.33412 | 0.34807 | 0.37235 | 0.43372 | 0.49009 | 0.52485 | 0.54678 | 0.57402 | 0.59324 | 0.60678 | 0.61301 | 0.61225 | 0.60022 | 0.60001 | 0.57193 | 0.54553 | 0.5294 | 0.50755 | 0.45424 | 0.61301
2018-02-03 | 0.40598 | 0.36587 | 0.35025 | 0.3436 | 0.34787 | 0.37561 | 0.43151 | 0.46564 | 0.49669 | 0.53613 | 0.57553 | 0.60281 | 0.62399 | 0.64041 | 0.65236 | 0.65721 | 0.64898 | 0.63782 | 0.65516 | 0.64664 | 0.61016 | 0.56809 | 0.5157 | 0.459 | 0.65721
2018-02-04 | 0.41062 | 0.38208 | 0.36491 | 0.35656 | 0.35839 | 0.38288 | 0.43882 | 0.47187 | 0.50082 | 0.54252 | 0.57991 | 0.60736 | 0.6288 | 0.64225 | 0.65128 | 0.65646 | 0.65165 | 0.63816 | 0.65579 | 0.65249 | 0.62061 | 0.5762 | 0.52685 | 0.47053 | 0.65646
2018-02-05 | 0.4229 | 0.39148 | 0.37456 | 0.36562 | 0.36717 | 0.39437 | 0.45307 | 0.48633 | 0.51557 | 0.55928 | 0.59738 | 0.62579 | 0.64359 | 0.65604 | 0.66368 | 0.66018 | 0.64622 | 0.63452 | 0.65052 | 0.64179 | 0.60983 | 0.56646 | 0.5139 | 0.4575 | 0.66368
2018-02-06 | 0.40958 | 0.37707 | 0.36007 | 0.35133 | 0.35384 | 0.37891 | 0.43703 | 0.47049 | 0.50087 | 0.53579 | 0.56617 | 0.58831 | 0.60628 | 0.62299 | 0.62997 | 0.63419 | 0.63018 | 0.62508 | 0.64292 | 0.63845 | 0.60707 | 0.56446 | 0.51298 | 0.45478 | 0.64292
2018-02-07 | 0.40565 | 0.37561 | 0.35501 | 0.34553 | 0.34699 | 0.37268 | 0.43017 | 0.46544 | 0.48783 | 0.5167 | 0.54403 | 0.56939 | 0.58439 | 0.58685 | 0.60615 | 0.61158 | 0.61004 | 0.60607 | 0.60803 | 0.59203 | 0.56863 | 0.52944 | 0.49293 | 0.4476 | 0.61158
2018-02-08 | 0.40607 | 0.37469 | 0.35597 | 0.34653 | 0.34582 | 0.35359 | 0.37511 | 0.40519 | 0.46101 | 0.51812 | 0.56074 | 0.58681 | 0.60419 | 0.61263 | 0.61798 | 0.61463 | 0.60716 | 0.59613 | 0.60306 | 0.5889 | 0.55944 | 0.52606 | 0.48942 | 0.44968 | 0.61798
2018-02-09 | 0.40782 | 0.37703 | 0.35835 | 0.34862 | 0.34644 | 0.35305 | 0.36859 | 0.39249 | 0.43619 | 0.47609 | 0.50245 | 0.51607 | 0.52865 | 0.53625 | 0.5396 | 0.5368 | 0.53011 | 0.52807 | 0.55234 | 0.55602 | 0.52873 | 0.49218 | 0.4529 | 0.40339 | 0.55602
2018-02-10 | 0.36236 | 0.33917 | 0.32957 | 0.32802 | 0.33583 | 0.36838 | 0.43239 | 0.46953 | 0.48545 | 0.50525 | 0.52715 | 0.54139 | 0.5546 | 0.56487 | 0.56914 | 0.57356 | 0.57436 | 0.57118 | 0.59379 | 0.59938 | 0.56972 | 0.52744 | 0.47743 | 0.42303 | 0.59938
2018-02-11 | 0.37941 | 0.35217 | 0.33897 | 0.33462 | 0.34026 | 0.37093 | 0.43489 | 0.47179 | 0.4905 | 0.51553 | 0.53801 | 0.55865 | 0.57599 | 0.59128 | 0.60051 | 0.61004 | 0.6128 | 0.60741 | 0.62374 | 0.62579 | 0.59938 | 0.54833 | 0.49418 | 0.4359 | 0.62579
2018-02-12 | 0.38538 | 0.35735 | 0.34018 | 0.33299 | 0.33679 | 0.36391 | 0.42416 | 0.45721 | 0.48273 | 0.51536 | 0.54377 | 0.56667 | 0.58368 | 0.59755 | 0.6011 | 0.59558 | 0.58815 | 0.58952 | 0.61677 | 0.61 | 0.58129 | 0.53864 | 0.47893 | 0.41831 | 0.61677
2018-02-13 | 0.37423 | 0.34636 | 0.33337 | 0.32831 | 0.33416 | 0.36387 | 0.42683 | 0.46564 | 0.48603 | 0.49903 | 0.51064 | 0.51474 | 0.51699 | 0.51632 | 0.51403 | 0.51043 | 0.50684 | 0.50692 | 0.53638 | 0.54779 | 0.53036 | 0.50028 | 0.45992 | 0.41375 | 0.54779
2018-02-14 | 0.37736 | 0.35935 | 0.3533 | 0.35534 | 0.36846 | 0.41058 | 0.49117 | 0.5424 | 0.54139 | 0.52869 | 0.51841 | 0.50112 | 0.48733 | 0.47789 | 0.47191 | 0.4717 | 0.47154 | 0.47596 | 0.50571 | 0.51152 | 0.49326 | 0.46849 | 0.44058 | 0.40724 | 0.5424
2018-02-15 | 0.37828 | 0.35986 | 0.35008 | 0.34649 | 0.34803 | 0.36015 | 0.38384 | 0.41722 | 0.4534 | 0.47651 | 0.48959 | 0.49092 | 0.48491 | 0.47881 | 0.47342 | 0.47141 | 0.47028 | 0.47329 | 0.49648 | 0.50191 | 0.48445 | 0.4613 | 0.43427 | 0.39926 | 0.50191
2018-02-16 | 0.36972 | 0.35296 | 0.35075 | 0.35275 | 0.35681 | 0.37448 | 0.40561 | 0.44776 | 0.48177 | 0.49167 | 0.48695 | 0.47596 | 0.46974 | 0.46519 | 0.4631 | 0.46385 | 0.4664 | 0.47116 | 0.49757 | 0.50676 | 0.48637 | 0.45892 | 0.4298 | 0.39086 | 0.50676
2018-02-17 | 0.3599 | 0.34314 | 0.33763 | 0.33938 | 0.35029 | 0.38016 | 0.42946 | 0.47425 | 0.49907 | 0.50855 | 0.51282 | 0.51382 | 0.51536 | 0.5182 | 0.52117 | 0.52547 | 0.52773 | 0.52898 | 0.54983 | 0.55673 | 0.52903 | 0.49013 | 0.44196 | 0.39433 | 0.55673
2018-02-18 | 0.35309 | 0.32923 | 0.32088 | 0.3187 | 0.32735 | 0.35986 | 0.42562 | 0.46644 | 0.48198 | 0.49715 | 0.51127 | 0.52284 | 0.53291 | 0.54361 | 0.55359 | 0.56308 | 0.56646 | 0.56132 | 0.57503 | 0.58167 | 0.55238 | 0.50734 | 0.45963 | 0.40389 | 0.58167
2018-02-19 | 0.35998 | 0.33362 | 0.32171 | 0.31686 | 0.32267 | 0.35229 | 0.41451 | 0.45006 | 0.47108 | 0.49502 | 0.51917 | 0.53976 | 0.55589 | 0.57139 | 0.58618 | 0.60026 | 0.60369 | 0.59529 | 0.60302 | 0.60649 | 0.57783 | 0.53391 | 0.48303 | 0.42691 | 0.60649
2018-02-20 | 0.37857 | 0.35058 | 0.335 | 0.32668 | 0.32902 | 0.35727 | 0.41722 | 0.45378 | 0.48415 | 0.51963 | 0.55297 | 0.57561 | 0.59638 | 0.61255 | 0.62391 | 0.63373 | 0.63507 | 0.62575 | 0.63649 | 0.64196 | 0.61522 | 0.57586 | 0.52489 | 0.47204 | 0.64196
2018-02-21 | 0.42324 | 0.38864 | 0.37047 | 0.3614 | 0.36195 | 0.38589 | 0.44375 | 0.48044 | 0.52464 | 0.57093 | 0.61008 | 0.63866 | 0.65825 | 0.67091 | 0.67246 | 0.66891 | 0.64806 | 0.63085 | 0.63837 | 0.6288 | 0.59826 | 0.55861 | 0.51971 | 0.47149 | 0.67246
2018-02-22 | 0.42528 | 0.38898 | 0.3693 | 0.35668 | 0.35338 | 0.3576 | 0.37649 | 0.40878 | 0.47647 | 0.53772 | 0.58154 | 0.61351 | 0.63841 | 0.65194 | 0.65721 | 0.65955 | 0.65103 | 0.62901 | 0.62529 | 0.61651 | 0.58242 | 0.54591 | 0.50617 | 0.4598 | 0.65955
2018-02-23 | 0.4153 | 0.38292 | 0.36211 | 0.34995 | 0.34444 | 0.34644 | 0.35864 | 0.38664 | 0.45182 | 0.5157 | 0.56508 | 0.60214 | 0.64484 | 0.65169 | 0.65754 | 0.66281 | 0.65784 | 0.64405 | 0.64388 | 0.64493 | 0.6143 | 0.56412 | 0.5172 | 0.4598 | 0.66281
2018-02-24 | 0.40782 | 0.37983 | 0.36144 | 0.35087 | 0.35217 | 0.37732 | 0.42788 | 0.46527 | 0.50153 | 0.54532 | 0.58547 | 0.61376 | 0.64137 | 0.66022 | 0.67179 | 0.68069 | 0.67275 | 0.66022 | 0.67225 | 0.67467 | 0.63507 | 0.58468 | 0.52614 | 0.46531 | 0.68069
2018-02-25 | 0.41225 | 0.37941 | 0.35965 | 0.34874 | 0.34958 | 0.37502 | 0.43189 | 0.46393 | 0.49702 | 0.53467 | 0.5683 | 0.59625 | 0.62278 | 0.64589 | 0.66389 | 0.67438 | 0.67129 | 0.65303 | 0.65671 | 0.65683 | 0.6214 | 0.57081 | 0.51653 | 0.45474 | 0.67438
2018-02-26 | 0.40226 | 0.36913 | 0.3487 | 0.33917 | 0.33989 | 0.36215 | 0.41701 | 0.45186 | 0.48069 | 0.51273 | 0.55501 | 0.58309 | 0.60812 | 0.62516 | 0.63603 | 0.63824 | 0.62859 | 0.6219 | 0.63933 | 0.63878 | 0.60891 | 0.56688 | 0.51482 | 0.4595 | 0.63933
2018-02-27 | 0.41137 | 0.38346 | 0.3685 | 0.36149 | 0.3637 | 0.3881 | 0.44509 | 0.47626 | 0.49477 | 0.5177 | 0.54269 | 0.53742 | 0.5622 | 0.56558 | 0.56433 | 0.56124 | 0.55451 | 0.5655 | 0.58576 | 0.58936 | 0.56458 | 0.52176 | 0.47137 | 0.42077 | 0.58936
2018-02-28 | 0.37774 | 0.35305 | 0.3416 | 0.33801 | 0.34331 | 0.37331 | 0.43682 | 0.47304 | 0.48436 | 0.4913 | 0.49677 | 0.49844 | 0.49878 | 0.50149 | 0.50446 | 0.5086 | 0.51119 | 0.5078 | 0.51963 | 0.52664 | 0.50404 | 0.47429 | 0.43891 | 0.39859 | 0.52664
2018-03-01 | 0.36249 | 0.33972 | 0.32727 | 0.32184 | 0.32397 | 0.33704 | 0.36224 | 0.39621 | 0.43882 | 0.46681 | 0.48445 | 0.49355 | 0.50224 | 0.51081 | 0.51716 | 0.52531 | 0.52631 | 0.51946 | 0.52004 | 0.52961 | 0.50367 | 0.47454 | 0.44108 | 0.40051 | 0.52961
2018-03-02 | 0.36466 | 0.34197 | 0.32911 | 0.31757 | 0.31586 | 0.32234 | 0.33817 | 0.36566 | 0.41906 | 0.46339 | 0.49121 | 0.51131 | 0.52669 | 0.54173 | 0.55221 | 0.56141 | 0.56437 | 0.55735 | 0.56019 | 0.57039 | 0.54131 | 0.50195 | 0.45683 | 0.40703 | 0.57039
2018-03-03 | 0.36993 | 0.33922 | 0.32246 | 0.3162 | 0.31979 | 0.34707 | 0.40239 | 0.43719 | 0.4684 | 0.50304 | 0.53513 | 0.55856 | 0.5815 | 0.60369 | 0.61777 | 0.63039 | 0.63415 | 0.62475 | 0.62462 | 0.63051 | 0.59408 | 0.54419 | 0.48933 | 0.42821 | 0.63415
2018-03-04 | 0.37862 | 0.3469 | 0.32957 | 0.32079 | 0.32271 | 0.34782 | 0.40331 | 0.43936 | 0.46886 | 0.50308 | 0.53379 | 0.55882 | 0.58138 | 0.60223 | 0.61994 | 0.63306 | 0.63624 | 0.62637 | 0.62738 | 0.63118 | 0.59938 | 0.55556 | 0.50141 | 0.44333 | 0.63624
2018-03-05 | 0.39295 | 0.36395 | 0.34711 | 0.34014 | 0.34298 | 0.36825 | 0.42733 | 0.4631 | 0.4908 | 0.52944 | 0.5627 | 0.59115 | 0.6148 | 0.63001 | 0.63607 | 0.63803 | 0.63026 | 0.62011 | 0.62713 | 0.63064 | 0.6031 | 0.56057 | 0.5088 | 0.45085 | 0.63803
2018-03-06 | 0.40231 | 0.37385 | 0.35601 | 0.34849 | 0.3497 | 0.37398 | 0.42955 | 0.46502 | 0.50346 | 0.54256 | 0.57135 | 0.59508 | 0.61083 | 0.60762 | 0.6003 | 0.55635 | 0.53488 | 0.53843 | 0.56274 | 0.56767 | 0.54482 | 0.50822 | 0.46548 | 0.41676 | 0.61083
2018-03-07 | 0.37444 | 0.3482 | 0.33725 | 0.3322 | 0.33688 | 0.36408 | 0.42211 | 0.45758 | 0.4895 | 0.51574 | 0.53717 | 0.54682 | 0.55184 | 0.5523 | 0.55188 | 0.55226 | 0.54862 | 0.53884 | 0.54382 | 0.54737 | 0.52677 | 0.49113 | 0.45319 | 0.40435 | 0.5523
2018-03-08 | 0.37126 | 0.34665 | 0.33529 | 0.33111 | 0.33429 | 0.34502 | 0.37214 | 0.40991 | 0.4491 | 0.47145 | 0.47784 | 0.47734 | 0.4763 | 0.47588 | 0.4791 | 0.48386 | 0.48641 | 0.48407 | 0.49121 | 0.50383 | 0.48211 | 0.45587 | 0.42357 | 0.39094 | 0.50383
2018-03-09 | 0.35397 | 0 | 0.33307 | 0.32175 | 0.31774 | 0.32296 | 0.33767 | 0.35894 | 0.3899 | 0.42792 | 0.45879 | 0.47233 | 0.49063 | 0.50074 | 0.50814 | 0.51887 | 0.52995 | 0.53525 | 0.52731 | 0.52961 | 0.54215 | 0.51098 | 0.47028 | 0.41212 | 0.54215
2018-03-10 | 0.36387 | 0.33182 | 0.31628 | 0.31143 | 0.31711 | 0.34268 | 0.39821 | 0.43911 | 0.45131 | 0.47521 | 0.50392 | 0.52113 | 0.54052 | 0.55338 | 0.57256 | 0.59111 | 0.6064 | 0.60745 | 0.59479 | 0.5914 | 0.5965 | 0.55288 | 0.50429 | 0.44317 | 0.60745
2018-03-11 | 0.38643 | 0.35121 | 0.3317 | 0.322 | 0.32196 | 0.34657 | 0.40155 | 0.44083 | 0.4514 | 0.47943 | 0.50433 | 0.52744 | 0.54749 | 0.56588 | 0.58313 | 0.60243 | 0.61869 | 0.62345 | 0.61238 | 0.60686 | 0.61246 | 0.57482 | 0.52372 | 0.45733 | 0.62345
2018-03-12 | 0.40531 | 0.36963 | 0.35112 | 0.34294 | 0.34477 | 0.36959 | 0.42691 | 0.42457 | 0.47475 | 0.50839 | 0.54933 | 0.58205 | 0.60736 | 0.62454 | 0.63377 | 0.65157 | 0.66226 | 0.65729 | 0.63954 | 0.63214 | 0.63532 | 0.59646 | 0.54737 | 0.48712 | 0.66226
2018-03-13 | 0.4313 | 0.39395 | 0.37168 | 0.35981 | 0.35672 | 0.37536 | 0.42441 | 0.4552 | 0.46418 | 0.49067 | 0.51039 | 0.52192 | 0.52832 | 0.53233 | 0.53508 | 0.53797 | 0.54357 | 0.54223 | 0.52685 | 0.52497 | 0.53538 | 0.50291 | 0.45934 | 0.40673 | 0.54357
2018-03-14 | 0.36253 | 0.33755 | 0.32363 | 0.32016 | 0.32714 | 0.35706 | 0.42391 | 0.47179 | 0.48248 | 0.49197 | 0.49919 | 0.50095 | 0.5002 | 0.50208 | 0.5045 | 0.50893 | 0.51528 | 0.5149 | 0.50509 | 0.50425 | 0.51336 | 0.48783 | 0.45232 | 0.41141 | 0.51528
2018-03-15 | 0.36621 | 0.33917 | 0.32267 | 0.31523 | 0.31666 | 0.32681 | 0.34803 | 0.38359 | 0.42353 | 0.46005 | 0.48783 | 0.50371 | 0.51511 | 0.52464 | 0.53579 | 0.54724 | 0.55961 | 0.56174 | 0.54799 | 0.53467 | 0.53772 | 0.50851 | 0.47509 | 0.42796 | 0.56174
2018-03-16 | 0.38614 | 0.35706 | 0.33842 | 0.32798 | 0.32376 | 0.32647 | 0.34026 | 0.36178 | 0.40494 | 0.46071 | 0.4999 | 0.52852 | 0.55117 | 0.56847 | 0.58522 | 0.59667 | 0.60197 | 0.60014 | 0.5853 | 0.57966 | 0.58969 | 0.55831 | 0.51871 | 0.46285 | 0.60197
2018-03-17 | 0.41375 | 0.38129 | 0.36307 | 0.35647 | 0.36007 | 0.38597 | 0.43928 | 0.4791 | 0.50049 | 0.5426 | 0.58823 | 0.61936 | 0.64175 | 0.65311 | 0.65905 | 0.66323 | 0.66448 | 0.65525 | 0.64472 | 0.65098 | 0.65052 | 0.61547 | 0.5739 | 0.5167 | 0.66448
2018-03-18 | 0.4659 | 0.4326 | 0.41563 | 0.40744 | 0.40615 | 0.42453 | 0.47124 | 0.49878 | 0.4941 | 0.50922 | 0.52397 | 0.53199 | 0.53884 | 0.54833 | 0.5607 | 0.57381 | 0.5876 | 0.59186 | 0.58008 | 0.57423 | 0.58129 | 0.54528 | 0.49585 | 0.43464 | 0.59186
2018-03-19 | 0.38079 | 0.34858 | 0.33132 | 0.32363 | 0.32568 | 0.35075 | 0.40586 | 0.44304 | 0.45833 | 0.48816 | 0.51754 | 0.53914 | 0.55338 | 0.57072 | 0.58777 | 0.60415 | 0.61438 | 0.61501 | 0.59847 | 0.58723 | 0.59504 | 0.56003 | 0.51294 | 0.45315 | 0.61501
2018-03-20 | 0.40205 | 0.36821 | 0.35029 | 0.34014 | 0.34076 | 0.36362 | 0.4168 | 0.45457 | 0.47091 | 0.49957 | 0.52949 | 0.5518 | 0.56922 | 0.58735 | 0.60377 | 0.61681 | 0.62533 | 0.62232 | 0.60757 | 0.59546 | 0.60185 | 0.56136 | 0.51135 | 0.45336 | 0.62533
2018-03-21 | 0.39754 | 0.36149 | 0.33922 | 0.32693 | 0.32664 | 0.34548 | 0.38998 | 0.42896 | 0.45336 | 0.48979 | 0.52648 | 0.55522 | 0.57803 | 0.60072 | 0.62224 | 0.6397 | 0.64651 | 0.63983 | 0.61597 | 0.5983 | 0.59976 | 0.56475 | 0.5266 | 0.47906 | 0.64651
2018-03-22 | 0.43067 | 0.39817 | 0.37586 | 0.36249 | 0.3571 | 0.36282 | 0.38041 | 0.40327 | 0.44179 | 0.5012 | 0.54536 | 0.56863 | 0.58894 | 0.60431 | 0.61484 | 0.62625 | 0.64087 | 0.64058 | 0.62195 | 0.59934 | 0.59671 | 0.56086 | 0.5177 | 0.4656 | 0.64087
2018-03-23 | 0.41664 | 0.37949 | 0.3571 | 0.34398 | 0.33771 | 0.34039 | 0.3525 | 0.37114 | 0.41217 | 0.47275 | 0.5251 | 0.56441 | 0.60168 | 0.6339 | 0.6557 | 0.67388 | 0.68173 | 0.68086 | 0.66523 | 0.64618 | 0.64927 | 0.60762 | 0.55911 | 0.49828 | 0.68173
2018-03-24 | 0.44417 | 0.40536 | 0.37937 | 0.3685 | 0.36708 | 0.38543 | 0.42487 | 0.45909 | 0.48311 | 0.51695 | 0.54348 | 0.56178 | 0.5688 | 0.56801 | 0.56057 | 0.55568 | 0.55618 | 0.55919 | 0.55869 | 0.5617 | 0.55727 | 0.52238 | 0.48206 | 0.42946 | 0.5688
2018-03-25 | 0.38492 | 0.35196 | 0.33111 | 0.32347 | 0.32568 | 0.34578 | 0.39228 | 0.42909 | 0.45119 | 0.48369 | 0.50642 | 0.52907 | 0.54674 | 0.55898 | 0.57031 | 0.57929 | 0.58702 | 0.58764 | 0.57586 | 0.5617 | 0.56692 | 0.52869 | 0.47697 | 0.41701 | 0.58764
2018-03-26 | 0.36391 | 0.33307 | 0.31569 | 0.30968 | 0.3144 | 0.33917 | 0.39336 | 0.43924 | 0.4656 | 0.47901 | 0.48963 | 0.48971 | 0.48466 | 0.47847 | 0.47446 | 0.4722 | 0.47626 | 0.47906 | 0.47764 | 0.49113 | 0.51102 | 0.48578 | 0.44597 | 0.40226 | 0.51102
2018-03-27 | 0.36257 | 0.33905 | 0.32689 | 0.32405 | 0.32961 | 0.35397 | 0.40536 | 0.44158 | 0.4595 | 0.48466 | 0.49698 | 0.50304 | 0.50584 | 0.50814 | 0.50784 | 0.5073 | 0.50822 | 0.50759 | 0.50442 | 0.51578 | 0.52627 | 0.50016 | 0.46205 | 0.41568 | 0.52627
2018-03-28 | 0.37352 | 0.34494 | 0.32998 | 0.322 | 0.32518 | 0.34624 | 0.39111 | 0.42817 | 0.45461 | 0.49042 | 0.5261 | 0.54712 | 0.56157 | 0.57001 | 0.57686 | 0.58113 | 0.58037 | 0.57135 | 0.55806 | 0.55819 | 0.5637 | 0.53884 | 0.50684 | 0.46406 | 0.58113
2018-03-29 | 0.42261 | 0.39382 | 0.37506 | 0.36533 | 0.36328 | 0.37013 | 0.38823 | 0.41451 | 0.45361 | 0.50676 | 0.55213 | 0.58322 | 0.59679 | 0.60402 | 0.60252 | 0.59521 | 0.5856 | 0.57553 | 0.55973 | 0.55522 | 0.54398 | 0.50947 | 0.47701 | 0.43502 | 0.60402
2018-03-30 | 0.39265 | 0.36257 | 0.34143 | 0.33094 | 0.3271 | 0.33111 | 0.34711 | 0.367 | 0.40339 | 0.45052 | 0.48303 | 0.49932 | 0.50672 | 0.51227 | 0.51754 | 0.52197 | 0.52644 | 0.52543 | 0.51478 | 0.50726 | 0.5213 | 0.489 | 0.44567 | 0.39224 | 0.52644
2018-03-31 | 0.34703 | 0.3228 | 0.30717 | 0.30212 | 0.30796 | 0.34089 | 0.39984 | 0.43715 | 0.44973 | 0.46715 | 0.48511 | 0.49945 | 0.50968 | 0.52184 | 0.53254 | 0.54143 | 0.54561 | 0.5411 | 0.53588 | 0.54231 | 0.55405 | 0.51804 | 0.47078 | 0.41288 | 0.55405
2018-04-01 | 0.36362 | 0.33437 | 0.31945 | 0.31335 | 0.31753 | 0.34486 | 0.40899 | 0.44793 | 0.46184 | 0.48073 | 0.49903 | 0.51478 | 0.5274 | 0.54369 | 0.56329 | 0.58526 | 0.60523 | 0.61238 | 0.60152 | 0.58217 | 0.58673 | 0.5482 | 0.49113 | 0.42867 | 0.61238
2018-04-02 | 0.37586 | 0.34323 | 0.32547 | 0.31632 | 0.3187 | 0.34611 | 0.40494 | 0.43778 | 0.45294 | 0.48123 | 0.50496 | 0.52639 | 0.54098 | 0.5589 | 0.58606 | 0.61033 | 0.62855 | 0.63615 | 0.62182 | 0.60227 | 0.60628 | 0.56759 | 0.50985 | 0.44684 | 0.63615
2018-04-03 | 0.39169 | 0.35676 | 0.33696 | 0.32877 | 0.33057 | 0.35819 | 0.41204 | 0.44404 | 0.46544 | 0.49757 | 0.52777 | 0.55272 | 0.57503 | 0.59629 | 0.62537 | 0.64447 | 0.65788 | 0.65253 | 0.63757 | 0.61568 | 0.62713 | 0.58706 | 0.52827 | 0.4641 | 0.65788
2018-04-04 | 0.40765 | 0.37252 | 0.35075 | 0.34005 | 0.33884 | 0.36274 | 0.42056 | 0.45102 | 0.47446 | 0.51144 | 0.54678 | 0.57569 | 0.59784 | 0.62048 | 0.64221 | 0.66109 | 0.6763 | 0.67488 | 0.65629 | 0.62391 | 0.61702 | 0.58217 | 0.53625 | 0.48232 | 0.6763
2018-04-05 | 0.43005 | 0.39257 | 0.36817 | 0.353 | 0.34686 | 0.34904 | 0.36688 | 0.38931 | 0.44254 | 0.50308 | 0.54933 | 0.58618 | 0.6161 | 0.64639 | 0.66715 | 0.68244 | 0.68821 | 0.68445 | 0.65909 | 0.6255 | 0.62178 | 0.58535 | 0.54148 | 0.49067 | 0.68821
2018-04-06 | 0.4379 | 0.399 | 0.37093 | 0.35409 | 0.34707 | 0.34812 | 0.36015 | 0.37703 | 0.43285 | 0.49769 | 0.54908 | 0.58589 | 0.61919 | 0.64823 | 0.67484 | 0.6918 | 0.70003 | 0.69945 | 0.67948 | 0.6524 | 0.65337 | 0.611 | 0.55806 | 0.4918 | 0.70003
2018-04-07 | 0.44037 | 0.4046 | 0.38492 | 0.37536 | 0.37799 | 0.40444 | 0.45929 | 0.49038 | 0.51795 | 0.56876 | 0.61881 | 0.6621 | 0.69769 | 0.7292 | 0.75393 | 0.77257 | 0.78397 | 0.77942 | 0.7569 | 0.73714 | 0.7312 | 0.68274 | 0.62257 | 0.5599 | 0.78397
2018-04-08 | 0.50667 | 0.46656 | 0.43703 | 0.42152 | 0.42178 | 0.44404 | 0.50049 | 0.53036 | 0.5548 | 0.58919 | 0.62901 | 0.66193 | 0.68119 | 0.69122 | 0.68921 | 0.6786 | 0.68432 | 0.66139 | 0.61731 | 0.59592 | 0.5988 | 0.55848 | 0.50204 | 0.44158 | 0.69122
2018-04-09 | 0.39474 | 0.36337 | 0.34515 | 0.33596 | 0.33533 | 0.35839 | 0.41329 | 0.43911 | 0.45228 | 0.47872 | 0.49924 | 0.51014 | 0.51662 | 0.52201 | 0.53074 | 0.54139 | 0.55155 | 0.55802 | 0.55104 | 0.54118 | 0.55623 | 0.52288 | 0.46907 | 0.41208 | 0.55802
2018-04-10 | 0.36449 | 0.33642 | 0.32008 | 0.31402 | 0.31695 | 0.34306 | 0.40155 | 0.43239 | 0.44697 | 0.47103 | 0.49318 | 0.50918 | 0.52 | 0.53241 | 0.54582 | 0.56036 | 0.57039 | 0.57014 | 0.56028 | 0.55334 | 0.56788 | 0.53224 | 0.48223 | 0.42403 | 0.57039
2018-04-11 | 0.37623 | 0.3439 | 0.32702 | 0.31983 | 0.32221 | 0.34586 | 0.40243 | 0.43414 | 0.45599 | 0.49134 | 0.52305 | 0.54461 | 0.55948 | 0.57427 | 0.58773 | 0.59266 | 0.5942 | 0.58664 | 0.57264 | 0.56187 | 0.56934 | 0.54306 | 0.50646 | 0.4598 | 0.5942
2018-04-12 | 0.4138 | 0.38125 | 0.3581 | 0.34482 | 0.33922 | 0.34352 | 0.36303 | 0.38726 | 0.44074 | 0.49903 | 0.54331 | 0.57728 | 0.60009 | 0.62036 | 0.63247 | 0.6435 | 0.6476 | 0.64305 | 0.61877 | 0.59061 | 0.5904 | 0.56241 | 0.51858 | 0.47337 | 0.6476
2018-04-13 | 0.42867 | 0.3937 | 0.37172 | 0.35689 | 0.35066 | 0.35296 | 0.36591 | 0.38426 | 0.43222 | 0.49004 | 0.53345 | 0.56433 | 0.5912 | 0.60891 | 0.61631 | 0.62224 | 0.62378 | 0.62086 | 0.60682 | 0.6026 | 0.61539 | 0.58363 | 0.53813 | 0.48085 | 0.62378
2018-04-14 | 0.43051 | 0.39763 | 0.37933 | 0.36884 | 0.3698 | 0.39295 | 0.44797 | 0.47914 | 0.51265 | 0.56337 | 0.60991 | 0.65002 | 0.68215 | 0.71353 | 0.73835 | 0.75932 | 0.77027 | 0.76667 | 0.74361 | 0.71449 | 0.71044 | 0.66628 | 0.60494 | 0.53533 | 0.77027
2018-04-15 | 0.47567 | 0.43723 | 0.41329 | 0.39675 | 0.39357 | 0.41409 | 0.46832 | 0.4969 | 0.53717 | 0.59341 | 0.64008 | 0.6824 | 0.71299 | 0.73475 | 0.74332 | 0.74992 | 0.74512 | 0.71595 | 0.701 | 0.68019 | 0.68173 | 0.64167 | 0.58067 | 0.51403 | 0.74992
2018-04-16 | 0.45867 | 0.42081 | 0.397 | 0.38467 | 0.38208 | 0.40164 | 0.45177 | 0.47642 | 0.49406 | 0.52117 | 0.54382 | 0.55932 | 0.5754 | 0.59391 | 0.60728 | 0.61727 | 0.62332 | 0.62111 | 0.61071 | 0.60824 | 0.61969 | 0.59358 | 0.54382 | 0.48336 | 0.62332
2018-04-17 | 0.43469 | 0.40277 | 0.38409 | 0.37431 | 0.37569 | 0.3993 | 0.45299 | 0.48353 | 0.51031 | 0.55021 | 0.58518 | 0.60766 | 0.61514 | 0.6209 | 0.62307 | 0.61977 | 0.61476 | 0.60427 | 0.5945 | 0.58856 | 0.596 | 0.57365 | 0.5335 | 0.48173 | 0.62307
2018-04-18 | 0.43494 | 0.40205 | 0.3807 | 0.36896 | 0.36713 | 0.38572 | 0.42378 | 0.4557 | 0.49786 | 0.55029 | 0.59283 | 0.62103 | 0.63841 | 0.65725 | 0.6664 | 0.66477 | 0.66114 | 0.65683 | 0.63866 | 0.61714 | 0.61831 | 0.59257 | 0.55572 | 0.51227 | 0.6664
2018-04-19 | 0.46489 | 0.43339 | 0.41137 | 0.397 | 0.39211 | 0.39667 | 0.4054 | 0.4186 | 0.45649 | 0.51912 | 0.57005 | 0.60494 | 0.63302 | 0.65353 | 0.66473 | 0.67229 | 0.67108 | 0.65583 | 0.62612 | 0.58969 | 0.58322 | 0.55013 | 0.51098 | 0.4562 | 0.67229
2018-04-20 | 0.40653 | 0.36938 | 0.34406 | 0.33086 | 0.3253 | 0.32823 | 0.3416 | 0.35739 | 0.40197 | 0.44818 | 0.47375 | 0.49464 | 0.50864 | 0.51871 | 0.52547 | 0.53078 | 0.53421 | 0.53061 | 0.52155 | 0.51637 | 0.5345 | 0.51424 | 0.47354 | 0.41981 | 0.5345
2018-04-21 | 0.37252 | 0.34151 | 0.32497 | 0.31691 | 0.31941 | 0.34423 | 0.39654 | 0.42457 | 0.4476 | 0.47701 | 0.50446 | 0.52531 | 0.54636 | 0.56333 | 0.58251 | 0.59767 | 0.60987 | 0.60879 | 0.59943 | 0.58643 | 0.59642 | 0.56103 | 0.5078 | 0.44977 | 0.60987
2018-04-22 | 0.39541 | 0.35906 | 0.34143 | 0.33061 | 0.33082 | 0.35773 | 0.41246 | 0.43627 | 0.46055 | 0.4903 | 0.52117 | 0.55167 | 0.57457 | 0.59316 | 0.61234 | 0.63552 | 0.65153 | 0.65453 | 0.64229 | 0.62366 | 0.63206 | 0.59475 | 0.53496 | 0.46865 | 0.65453
2018-04-23 | 0.41388 | 0.37908 | 0.35714 | 0.34385 | 0.34172 | 0.36383 | 0.4143 | 0.38597 | 0.46966 | 0.50367 | 0.53609 | 0.56011 | 0.58869 | 0.62299 | 0.65934 | 0.68654 | 0.70613 | 0.71106 | 0.69586 | 0.66673 | 0.66368 | 0.63172 | 0.57302 | 0.49389 | 0.71106
2018-04-24 | 0.43945 | 0.40289 | 0.36888 | 0.3543 | 0.35476 | 0.36825 | 0.41739 | 0.44634 | 0.47814 | 0.52326 | 0.56826 | 0.6059 | 0.6402 | 0.67062 | 0.69611 | 0.72097 | 0.73534 | 0.73346 | 0.71232 | 0.67919 | 0.67643 | 0.63786 | 0.57628 | 0.51022 | 0.73534
2018-04-25 | 0.45115 | 0.40841 | 0.38154 | 0.36596 | 0.36232 | 0.38233 | 0.43101 | 0.45846 | 0.49259 | 0.53918 | 0.5884 | 0.63122 | 0.66841 | 0.70254 | 0.73191 | 0.75669 | 0.77023 | 0.76655 | 0.73814 | 0.6964 | 0.68478 | 0.64697 | 0.59299 | 0.5335 | 0.77023
2018-04-26 | 0.47342 | 0.42817 | 0.3985 | 0.37924 | 0.36817 | 0.36892 | 0.38129 | 0.40548 | 0.4656 | 0.53195 | 0.5917 | 0.64275 | 0.68257 | 0.71261 | 0.73062 | 0.74662 | 0.75485 | 0.74996 | 0.72247 | 0.68031 | 0.66849 | 0.63364 | 0.58635 | 0.53408 | 0.75485
2018-04-27 | 0.48303 | 0.44279 | 0.4125 | 0.39433 | 0.38263 | 0.38058 | 0.38726 | 0.40611 | 0.47229 | 0.54703 | 0.60904 | 0.65888 | 0.6974 | 0.72853 | 0.74917 | 0.76676 | 0.77374 | 0.76906 | 0.74449 | 0.70939 | 0.7043 | 0.66619 | 0.60611 | 0.54545 | 0.77374
2018-04-28 | 0.49226 | 0.4557 | 0.43235 | 0.41772 | 0.41647 | 0.43953 | 0.48833 | 0.51691 | 0.5548 | 0.60699 | 0.66536 | 0.71391 | 0.7503 | 0.78126 | 0.80683 | 0.82642 | 0.8316 | 0.82955 | 0.80645 | 0.7714 | 0.76133 | 0.71478 | 0.64752 | 0.57958 | 0.8316
2018-04-29 | 0.52389 | 0.48449 | 0.45875 | 0.44384 | 0.44133 | 0.4618 | 0.50772 | 0.53571 | 0.58067 | 0.63669 | 0.69185 | 0.7381 | 0.77194 | 0.79905 | 0.81786 | 0.83118 | 0.82843 | 0.81877 | 0.7996 | 0.76809 | 0.75606 | 0.71215 | 0.64714 | 0.57929 | 0.83118
2018-04-30 | 0.52205 | 0.48603 | 0.46251 | 0.44935 | 0.44851 | 0.46869 | 0.51566 | 0.5434 | 0.58677 | 0.64271 | 0.69707 | 0.73973 | 0.77114 | 0.7983 | 0.81485 | 0.82621 | 0.82032 | 0.78798 | 0.76383 | 0.7378 | 0.73601 | 0.69661 | 0.63448 | 0.56964 | 0.82621
2018-05-01 | 0.51286 | 0.47555 | 0.45056 | 0.43715 | 0.43335 | 0.45553 | 0.50529 | 0.53442 | 0.5739 | 0.63039 | 0.68771 | 0.73062 | 0.76446 | 0.7932 | 0.81142 | 0.82053 | 0.81598 | 0.79178 | 0.75468 | 0.7259 | 0.72322 | 0.68036 | 0.62215 | 0.56024 | 0.82053
2018-05-02 | 0.50734 | 0.4702 | 0.44626 | 0.43159 | 0.42775 | 0.44877 | 0.49685 | 0.52677 | 0.56207 | 0.61301 | 0.65625 | 0.68854 | 0.70722 | 0.72874 | 0.74415 | 0.75222 | 0.7472 | 0.73204 | 0.70868 | 0.67689 | 0.67626 | 0.63085 | 0.58497 | 0.53538 | 0.75222
2018-05-03 | 0.48628 | 0.44885 | 0.4237 | 0.40841 | 0.40059 | 0.4049 | 0.41956 | 0.44246 | 0.48725 | 0.54189 | 0.58597 | 0.61589 | 0.62959 | 0.63615 | 0.63247 | 0.61564 | 0.5767 | 0.56157 | 0.54762 | 0.54377 | 0.5533 | 0.53575 | 0.50605 | 0.46836 | 0.63615
2018-05-04 | 0.42955 | 0.39896 | 0.37991 | 0.367 | 0.36295 | 0.36303 | 0.36792 | 0.37385 | 0.41722 | 0.46615 | 0.50425 | 0.53137 | 0.55882 | 0.5823 | 0.60256 | 0.62512 | 0.64263 | 0.65148 | 0.64384 | 0.61639 | 0.60707 | 0.57122 | 0.5246 | 0.45938 | 0.65148
2018-05-05 | 0.40757 | 0.36692 | 0.35112 | 0.33976 | 0.34009 | 0.36366 | 0.40995 | 0.43845 | 0.47183 | 0.51541 | 0.55986 | 0.59688 | 0.63176 | 0.66364 | 0.69289 | 0.71737 | 0.73876 | 0.74177 | 0.7246 | 0.66853 | 0.67012 | 0.62784 | 0.54728 | 0.4936 | 0.74177
2018-05-06 | 0.43443 | 0.39721 | 0.37218 | 0.35731 | 0.3538 | 0.3741 | 0.42102 | 0.4496 | 0.48386 | 0.53149 | 0.57874 | 0.62437 | 0.66703 | 0.69916 | 0.72949 | 0.7556 | 0.77219 | 0.7711 | 0.75055 | 0.69556 | 0.70233 | 0.66122 | 0.59855 | 0.5274 | 0.77219
2018-05-07 | 0.47078 | 0.43197 | 0.40941 | 0.39441 | 0.39115 | 0.41045 | 0.45675 | 0.48491 | 0.52497 | 0.57294 | 0.62491 | 0.66757 | 0.70526 | 0.73956 | 0.77043 | 0.78564 | 0.79684 | 0.79371 | 0.76906 | 0.73308 | 0.72435 | 0.68896 | 0.62483 | 0.55819 | 0.79684
2018-05-08 | 0.49869 | 0.46117 | 0.43728 | 0.41985 | 0.41576 | 0.43377 | 0.47864 | 0.50467 | 0.54695 | 0.59679 | 0.6466 | 0.68721 | 0.72143 | 0.75351 | 0.77821 | 0.79997 | 0.81313 | 0.8095 | 0.7884 | 0.74996 | 0.73521 | 0.69615 | 0.6364 | 0.57302 | 0.81313
2018-05-09 | 0.50726 | 0.46577 | 0.44229 | 0.42432 | 0.4199 | 0.43857 | 0.48323 | 0.50981 | 0.54987 | 0.60018 | 0.64835 | 0.68737 | 0.7208 | 0.75046 | 0.77699 | 0.79655 | 0.80632 | 0.79663 | 0.76642 | 0.72381 | 0.70593 | 0.6697 | 0.62245 | 0.56993 | 0.80632
2018-05-10 | 0.51737 | 0.47993 | 0.45474 | 0.43669 | 0.428 | 0.43021 | 0.43928 | 0.46293 | 0.52606 | 0.59032 | 0.63699 | 0.67242 | 0.70818 | 0.73141 | 0.74641 | 0.75744 | 0.75681 | 0.74871 | 0.72556 | 0.68449 | 0.68846 | 0.65771 | 0.61714 | 0.56792 | 0.75744
2018-05-11 | 0.51879 | 0.48265 | 0.45599 | 0.43882 | 0.43042 | 0.42825 | 0.43164 | 0.44634 | 0.4974 | 0.55898 | 0.60749 | 0.64467 | 0.67718 | 0.70459 | 0.72468 | 0.73463 | 0.73835 | 0.72811 | 0.70672 | 0.67576 | 0.67634 | 0.65516 | 0.60724 | 0.54632 | 0.73835
2018-05-12 | 0.48959 | 0.45253 | 0.42946 | 0.41735 | 0.4163 | 0.43744 | 0.48298 | 0.50972 | 0.54678 | 0.59938 | 0.65203 | 0.69389 | 0.72794 | 0.75447 | 0.77378 | 0.79057 | 0.7968 | 0.79162 | 0.77415 | 0.74775 | 0.74039 | 0.69824 | 0.63603 | 0.57277 | 0.7968
2018-05-13 | 0.51703 | 0.48135 | 0.45604 | 0.44049 | 0.43711 | 0.45716 | 0.50179 | 0.52723 | 0.56245 | 0.61422 | 0.66247 | 0.69878 | 0.73158 | 0.75314 | 0.76901 | 0.78217 | 0.78894 | 0.78142 | 0.75936 | 0.72928 | 0.7246 | 0.69172 | 0.63293 | 0.56721 | 0.78894
2018-05-14 | 0.51653 | 0.48106 | 0.45445 | 0.43895 | 0.43598 | 0.44417 | 0.50542 | 0.52589 | 0.56487 | 0.62165 | 0.66991 | 0.71441 | 0.74591 | 0.76575 | 0.77971 | 0.77929 | 0.77524 | 0.76647 | 0.74261 | 0.71428 | 0.71633 | 0.68207 | 0.62721 | 0.5627 | 0.77971
2018-05-15 | 0.5068 | 0.46995 | 0.44509 | 0.43143 | 0.43093 | 0.45073 | 0.49606 | 0.52105 | 0.55384 | 0.60778 | 0.65491 | 0.67939 | 0.68846 | 0.68666 | 0.67212 | 0.65516 | 0.65052 | 0.64986 | 0.64096 | 0.62633 | 0.62633 | 0.60298 | 0.55426 | 0.49999 | 0.68846
2018-05-16 | 0.45027 | 0.4186 | 0.39817 | 0.38522 | 0.38325 | 0.40594 | 0.45278 | 0.47329 | 0.48854 | 0.51603 | 0.53943 | 0.55593 | 0.56329 | 0.5683 | 0.57866 | 0.58459 | 0.59124 | 0.5843 | 0.56613 | 0.54248 | 0.53262 | 0.51123 | 0.47488 | 0.42842 | 0.59124
2018-05-17 | 0.38388 | 0.35442 | 0.33408 | 0.32259 | 0.31912 | 0.32305 | 0.33546 | 0.35898 | 0.40857 | 0.45996 | 0.50158 | 0.53325 | 0.55627 | 0.57728 | 0.59742 | 0.61326 | 0.6232 | 0.62132 | 0.60294 | 0.57135 | 0.56187 | 0.5434 | 0.504 | 0.45996 | 0.6232
2018-05-18 | 0.41701 | 0.38451 | 0.3619 | 0.34653 | 0.33959 | 0.34101 | 0.34523 | 0.36429 | 0.41722 | 0.4778 | 0.52589 | 0.56207 | 0.59195 | 0.61606 | 0.63778 | 0.65349 | 0.66477 | 0.66222 | 0.641 | 0.61079 | 0.60732 | 0.58484 | 0.53642 | 0.47851 | 0.66477
2018-05-19 | 0.42754 | 0.39232 | 0.37022 | 0.35931 | 0.35981 | 0.38112 | 0.42645 | 0.45294 | 0.49218 | 0.53838 | 0.58108 | 0.61714 | 0.64764 | 0.67776 | 0.69786 | 0.71721 | 0.72765 | 0.72598 | 0.70864 | 0.67488 | 0.66297 | 0.63176 | 0.57595 | 0.50931 | 0.72765
2018-05-20 | 0.4534 | 0.41505 | 0.39286 | 0.37933 | 0.37544 | 0.39345 | 0.43594 | 0.46723 | 0.50596 | 0.55309 | 0.59905 | 0.63644 | 0.66611 | 0.69068 | 0.70806 | 0.72197 | 0.73007 | 0.72648 | 0.71173 | 0.67705 | 0.6664 | 0.63185 | 0.57444 | 0.51031 | 0.73007
2018-05-21 | 0.45436 | 0.41551 | 0.39077 | 0.3749 | 0.37055 | 0.3886 | 0.43247 | 0.46285 | 0.49706 | 0.5401 | 0.58225 | 0.61902 | 0.64952 | 0.68198 | 0.71261 | 0.73333 | 0.74583 | 0.74069 | 0.71917 | 0.68307 | 0.66636 | 0.6359 | 0.57933 | 0.51315 | 0.74583
2018-05-22 | 0.45156 | 0.41137 | 0.38304 | 0.36842 | 0.36583 | 0.38518 | 0.4295 | 0.45796 | 0.49777 | 0.54482 | 0.59441 | 0.64117 | 0.68395 | 0.72489 | 0.75527 | 0.78075 | 0.79667 | 0.79178 | 0.76906 | 0.72878 | 0.70572 | 0.67551 | 0.61062 | 0.54052 | 0.79667
2018-05-23 | 0.47718 | 0.43439 | 0.40494 | 0.38756 | 0.38054 | 0.3965 | 0.43548 | 0.47162 | 0.51887 | 0.57515 | 0.63273 | 0.68888 | 0.73605 | 0.78314 | 0.81715 | 0.83933 | 0.84643 | 0.83682 | 0.80699 | 0.75502 | 0.73304 | 0.70175 | 0.64655 | 0.58627 | 0.84643
2018-05-24 | 0.52844 | 0.48474 | 0.45039 | 0.42675 | 0.41388 | 0.41037 | 0.41371 | 0.43941 | 0.5073 | 0.58146 | 0.64756 | 0.70781 | 0.75815 | 0.7927 | 0.81364 | 0.82475 | 0.82425 | 0.81481 | 0.78234 | 0.74002 | 0.72193 | 0.68967 | 0.64041 | 0.58614 | 0.82475
2018-05-25 | 0.53508 | 0.49176 | 0.45888 | 0.43707 | 0.42374 | 0.41868 | 0.42081 | 0.43707 | 0.49176 | 0.55919 | 0.63072 | 0.68675 | 0.73584 | 0.76818 | 0.78727 | 0.79818 | 0.80181 | 0.78677 | 0.75502 | 0.71825 | 0.70668 | 0.6776 | 0.62667 | 0.57515 | 0.80181
2018-05-26 | 0.52138 | 0.48323 | 0.45499 | 0.43644 | 0.42625 | 0.42641 | 0.43093 | 0.45207 | 0.51791 | 0.59529 | 0.66402 | 0.71299 | 0.75393 | 0.78201 | 0.79763 | 0.80574 | 0.80599 | 0.79346 | 0.7625 | 0.72556 | 0.71775 | 0.68432 | 0.62863 | 0.56437 | 0.80599
2018-05-27 | 0.51048 | 0.47145 | 0.4458 | 0.43009 | 0.42483 | 0.44442 | 0.48495 | 0.52025 | 0.56742 | 0.62512 | 0.68027 | 0.72916 | 0.76492 | 0.79224 | 0.80808 | 0.81552 | 0.80365 | 0.77252 | 0.74307 | 0.71424 | 0.7109 | 0.68006 | 0.62491 | 0.55735 | 0.81552
2018-05-28 | 0.50254 | 0.46477 | 0.44087 | 0.42587 | 0.42223 | 0.4415 | 0.48369 | 0.51465 | 0.55869 | 0.61117 | 0.66473 | 0.71875 | 0.75673 | 0.78773 | 0.80453 | 0.80929 | 0.80883 | 0.79266 | 0.76722 | 0.73889 | 0.72978 | 0.69673 | 0.64 | 0.57641 | 0.80929
2018-05-29 | 0.51871 | 0.47713 | 0.45223 | 0.43698 | 0.43159 | 0.4491 | 0.49004 | 0.52067 | 0.55794 | 0.60427 | 0.65207 | 0.6857 | 0.70588 | 0.71909 | 0.70989 | 0.69974 | 0.69327 | 0.68508 | 0.67756 | 0.65474 | 0.65253 | 0.63047 | 0.58468 | 0.52798 | 0.71909
2018-05-30 | 0.47149 | 0.43076 | 0.4107 | 0.39825 | 0.39595 | 0.41405 | 0.4539 | 0.48541 | 0.52894 | 0.59128 | 0.64597 | 0.69022 | 0.72477 | 0.75134 | 0.76692 | 0.77691 | 0.77411 | 0.75301 | 0.71512 | 0.68382 | 0.67446 | 0.64647 | 0.60277 | 0.55526 | 0.77691
2018-05-31 | 0.50797 | 0.46727 | 0.43891 | 0.42035 | 0.41321 | 0.41196 | 0.42035 | 0.44739 | 0.51415 | 0.58785 | 0.65236 | 0.70179 | 0.73337 | 0.75347 | 0.75681 | 0.75376 | 0.74261 | 0.71817 | 0.6898 | 0.65976 | 0.6557 | 0.63544 | 0.59872 | 0.55113 | 0.75681
2018-06-01 | 0.50768 | 0.46861 | 0.44296 | 0.42495 | 0.41509 | 0.41459 | 0.41843 | 0.43761 | 0.49447 | 0.56324 | 0.62525 | 0.67129 | 0.70893 | 0.73459 | 0.74771 | 0.74445 | 0.72861 | 0.70125 | 0.67075 | 0.64977 | 0.64935 | 0.63481 | 0.59487 | 0.54169 | 0.74771
2018-06-02 | 0.49343 | 0.45992 | 0.44058 | 0.42976 | 0.43109 | 0.45445 | 0.49585 | 0.52347 | 0.54896 | 0.57833 | 0.60632 | 0.62211 | 0.63753 | 0.64781 | 0.6547 | 0.65437 | 0.65278 | 0.64488 | 0.63678 | 0.62784 | 0.63068 | 0.61305 | 0.56742 | 0.51319 | 0.6547
2018-06-03 | 0.46339 | 0.42955 | 0.40857 | 0.39595 | 0.3952 | 0.41659 | 0.45946 | 0.48658 | 0.51236 | 0.54866 | 0.58489 | 0.61539 | 0.63745 | 0.65337 | 0.66001 | 0.66218 | 0.65408 | 0.6453 | 0.63026 | 0.61714 | 0.62144 | 0.59872 | 0.55422 | 0.49786 | 0.66218
2018-06-04 | 0.44622 | 0.4115 | 0.38973 | 0.37837 | 0.3782 | 0.39905 | 0.44062 | 0.4468 | 0.50128 | 0.55038 | 0.59078 | 0.62241 | 0.64396 | 0.66962 | 0.688 | 0.70037 | 0.70977 | 0.71165 | 0.69949 | 0.67108 | 0.65696 | 0.63306 | 0.58581 | 0.52502 | 0.71165
2018-06-05 | 0.46986 | 0.4326 | 0.40728 | 0.39161 | 0.3866 | 0.40389 | 0.44016 | 0.47814 | 0.52957 | 0.58556 | 0.6425 | 0.69264 | 0.73074 | 0.76555 | 0.7894 | 0.80645 | 0.81355 | 0.81042 | 0.79045 | 0.74954 | 0.72636 | 0.68951 | 0.63097 | 0.56149 | 0.81355
2018-06-06 | 0.50521 | 0.46113 | 0.43105 | 0.41196 | 0.40306 | 0.41655 | 0.44542 | 0.48378 | 0.54411 | 0.6095 | 0.67597 | 0.73609 | 0.7838 | 0.81953 | 0.84439 | 0.85817 | 0.86269 | 0.85441 | 0.82763 | 0.7846 | 0.75615 | 0.72402 | 0.66983 | 0.61326 | 0.86269
2018-06-07 | 0.55735 | 0.5134 | 0.48173 | 0.46168 | 0.4478 | 0.44292 | 0.44701 | 0.47434 | 0.54331 | 0.61601 | 0.68863 | 0.75113 | 0.79153 | 0.81948 | 0.83586 | 0.84025 | 0.82508 | 0.80181 | 0.7706 | 0.73843 | 0.71629 | 0.68608 | 0.6382 | 0.5853 | 0.84025
2018-06-08 | 0.53517 | 0.49376 | 0.46372 | 0.43744 | 0.42909 | 0.42587 | 0.42645 | 0.44438 | 0.50479 | 0.58451 | 0.65888 | 0.72101 | 0.75723 | 0.76546 | 0.75619 | 0.75038 | 0.73935 | 0.72753 | 0.70471 | 0.67697 | 0.66122 | 0.63665 | 0.58409 | 0.53241 | 0.76546
2018-06-09 | 0.47843 | 0.44045 | 0.41384 | 0.40009 | 0.39817 | 0.41559 | 0.44768 | 0.48261 | 0.53291 | 0.59362 | 0.65896 | 0.72418 | 0.77323 | 0.81334 | 0.83457 | 0.82822 | 0.81689 | 0.78798 | 0.75364 | 0.72285 | 0.70542 | 0.67522 | 0.61911 | 0.55702 | 0.83457
2018-06-10 | 0.50053 | 0.46076 | 0.43611 | 0.42048 | 0.41643 | 0.43343 | 0.46569 | 0.50676 | 0.56362 | 0.62307 | 0.67781 | 0.72673 | 0.76408 | 0.78456 | 0.78347 | 0.75652 | 0.73208 | 0.72051 | 0.71746 | 0.69548 | 0.68817 | 0.6552 | 0.59959 | 0.53972 | 0.78456
2018-06-11 | 0.48887 | 0.45152 | 0.42499 | 0.41058 | 0.40728 | 0.42228 | 0.45608 | 0.49272 | 0.54478 | 0.61025 | 0.66811 | 0.71591 | 0.74545 | 0.7635 | 0.74545 | 0.71357 | 0.69728 | 0.69218 | 0.68491 | 0.66285 | 0.65224 | 0.63009 | 0.58096 | 0.52502 | 0.7635
2018-06-12 | 0.47421 | 0.43673 | 0.41263 | 0.39763 | 0.39424 | 0.40861 | 0.44166 | 0.47024 | 0.50045 | 0.53997 | 0.58948 | 0.64234 | 0.69807 | 0.74704 | 0.77917 | 0.78619 | 0.76634 | 0.7348 | 0.7106 | 0.68554 | 0.67212 | 0.64313 | 0.58589 | 0.52723 | 0.78619
2018-06-13 | 0.47471 | 0.43694 | 0.41212 | 0.39595 | 0.3929 | 0.40707 | 0.43606 | 0.47492 | 0.53086 | 0.58835 | 0.64317 | 0.69531 | 0.7353 | 0.75544 | 0.75498 | 0.73296 | 0.71027 | 0.68595 | 0.66414 | 0.63218 | 0.61271 | 0.59303 | 0.55518 | 0.50726 | 0.75544
2018-06-14 | 0.46205 | 0.42704 | 0.40231 | 0.38743 | 0.38079 | 0.38346 | 0.3927 | 0.41885 | 0.47722 | 0.54599 | 0.61041 | 0.66707 | 0.70989 | 0.74445 | 0.76024 | 0.75903 | 0.73872 | 0.71825 | 0.686 | 0.65061 | 0.63703 | 0.61372 | 0.57398 | 0.5279 | 0.76024
2018-06-15 | 0.48349 | 0.45048 | 0.42403 | 0.40799 | 0.40335 | 0.40749 | 0.41492 | 0.43928 | 0.50145 | 0.57448 | 0.63845 | 0.69544 | 0.74094 | 0.76964 | 0.7861 | 0.77992 | 0.75807 | 0.73049 | 0.701 | 0.67004 | 0.66385 | 0.6491 | 0.60519 | 0.55572 | 0.7861
2018-06-16 | 0.50266 | 0.46727 | 0.44455 | 0.43026 | 0.42537 | 0.44083 | 0.47078 | 0.50162 | 0.54114 | 0.58982 | 0.65232 | 0.71127 | 0.75113 | 0.78598 | 0.80996 | 0.82404 | 0.83244 | 0.8265 | 0.79646 | 0.74449 | 0.71975 | 0.68825 | 0.63122 | 0.56968 | 0.83244
2018-06-17 | 0.5129 | 0.47396 | 0.44467 | 0.42746 | 0.42136 | 0.43464 | 0.46556 | 0.49919 | 0.54035 | 0.58418 | 0.626 | 0.66381 | 0.69602 | 0.72402 | 0.73346 | 0.73329 | 0.72606 | 0.7195 | 0.70609 | 0.68382 | 0.6705 | 0.65286 | 0.59567 | 0.53592 | 0.73346
2018-06-18 | 0.48044 | 0.444 | 0.42048 | 0.40548 | 0.40302 | 0.41856 | 0.45265 | 0.4872 | 0.53383 | 0.58522 | 0.64029 | 0.69139 | 0.71884 | 0.72853 | 0.72222 | 0.70505 | 0.68549 | 0.66874 | 0.65224 | 0.63569 | 0.62926 | 0.61271 | 0.56571 | 0.51089 | 0.72853
2018-06-19 | 0.4598 | 0.42641 | 0.40577 | 0.39353 | 0.39036 | 0.40619 | 0.43936 | 0.47333 | 0.52364 | 0.58088 | 0.64083 | 0.68763 | 0.72573 | 0.75314 | 0.75535 | 0.73162 | 0.70931 | 0.68637 | 0.66314 | 0.641 | 0.62922 | 0.60406 | 0.55982 | 0.50442 | 0.75535
2018-06-20 | 0.45386 | 0.4191 | 0.39637 | 0.38375 | 0.38054 | 0.39433 | 0.42499 | 0.46122 | 0.51419 | 0.57803 | 0.63736 | 0.69072 | 0.73104 | 0.75376 | 0.7472 | 0.7142 | 0.69318 | 0.67434 | 0.6583 | 0.63715 | 0.62458 | 0.60895 | 0.57085 | 0.52309 | 0.75376
2018-06-21 | 0.47388 | 0.43928 | 0.41451 | 0.39992 | 0.39349 | 0.39604 | 0.40235 | 0.43301 | 0.50559 | 0.58363 | 0.64601 | 0.7025 | 0.74658 | 0.77198 | 0.76438 | 0.73705 | 0.71336 | 0.69398 | 0.67037 | 0.64555 | 0.6331 | 0.61823 | 0.58138 | 0.53258 | 0.77198
2018-06-22 | 0.48415 | 0.45219 | 0.42633 | 0.41008 | 0.4008 | 0.40026 | 0.40272 | 0.4331 | 0.50224 | 0.58242 | 0.64844 | 0.6979 | 0.74344 | 0.77649 | 0.79747 | 0.80068 | 0.78706 | 0.75623 | 0.71696 | 0.68265 | 0.66866 | 0.64781 | 0.60369 | 0.54586 | 0.80068
2018-06-23 | 0.49163 | 0.45854 | 0.43498 | 0.42073 | 0.41764 | 0.43398 | 0.4656 | 0.50383 | 0.55898 | 0.61952 | 0.68332 | 0.73927 | 0.7879 | 0.82646 | 0.84827 | 0.8532 | 0.84459 | 0.82584 | 0.79834 | 0.75999 | 0.7345 | 0.70037 | 0.64559 | 0.5787 | 0.8532
2018-06-24 | 0.52167 | 0.48115 | 0.45428 | 0.43673 | 0.43088 | 0.44484 | 0.47559 | 0.51302 | 0.57093 | 0.63327 | 0.7007 | 0.75748 | 0.80582 | 0.84806 | 0.87284 | 0.88633 | 0.88876 | 0.87213 | 0.85015 | 0.81213 | 0.7912 | 0.75481 | 0.6949 | 0.62734 | 0.88876
2018-06-25 | 0.56788 | 0.52334 | 0.4905 | 0.46995 | 0.46218 | 0.47442 | 0.50346 | 0.54014 | 0.59792 | 0.66648 | 0.7368 | 0.78953 | 0.83632 | 0.87263 | 0.89498 | 0.8972 | 0.8786 | 0.85429 | 0.82354 | 0.78305 | 0.75803 | 0.72539 | 0.67388 | 0.60837 | 0.8972
2018-06-26 | 0.55096 | 0.50563 | 0.47484 | 0.45499 | 0.44726 | 0.45787 | 0.48791 | 0.52422 | 0.58372 | 0.65596 | 0.72494 | 0.77821 | 0.81882 | 0.84531 | 0.87121 | 0.87965 | 0.87986 | 0.86657 | 0.84242 | 0.80286 | 0.7744 | 0.73956 | 0.68232 | 0.61522 | 0.87986
2018-06-27 | 0.55539 | 0.51373 | 0.48365 | 0.46456 | 0.45825 | 0.47141 | 0.49623 | 0.53153 | 0.59015 | 0.65775 | 0.71833 | 0.77144 | 0.8044 | 0.83206 | 0.85571 | 0.85826 | 0.84923 | 0.82705 | 0.78677 | 0.74424 | 0.72046 | 0.68696 | 0.64426 | 0.58881 | 0.85826
2018-06-28 | 0.53053 | 0.48816 | 0.45946 | 0.43778 | 0.42457 | 0.41384 | 0.44317 | 0.46076 | 0.53166 | 0.61259 | 0.67605 | 0.73973 | 0.79015 | 0.8212 | 0.84008 | 0.85412 | 0.85245 | 0.84263 | 0.81343 | 0.77269 | 0.74954 | 0.72101 | 0.67342 | 0.61568 | 0.85412
2018-06-29 | 0.56166 | 0.52034 | 0.4895 | 0.46761 | 0.45495 | 0.45002 | 0.44843 | 0.46828 | 0.54081 | 0.62658 | 0.70363 | 0.7711 | 0.8222 | 0.84677 | 0.84785 | 0.83152 | 0.81865 | 0.79793 | 0.75656 | 0.71792 | 0.69469 | 0.67083 | 0.62458 | 0.56709 | 0.84785
2018-06-30 | 0.51628 | 0.47793 | 0.4519 | 0.43648 | 0.43456 | 0.45131 | 0.4819 | 0.51311 | 0.56462 | 0.63126 | 0.69243 | 0.74474 | 0.78627 | 0.82141 | 0.84271 | 0.85312 | 0.84388 | 0.8085 | 0.77357 | 0.7411 | 0.72306 | 0.69577 | 0.64952 | 0.58936 | 0.85312
2018-07-01 | 0.5345 | 0.49577 | 0.47174 | 0.45716 | 0.4537 | 0.47041 | 0.50379 | 0.53107 | 0.56538 | 0.61301 | 0.66118 | 0.70918 | 0.73897 | 0.75226 | 0.76517 | 0.77069 | 0.78025 | 0.77432 | 0.75836 | 0.74349 | 0.73559 | 0.70379 | 0.64944 | 0.58957 | 0.78025
2018-07-02 | 0.53095 | 0.49401 | 0.46945 | 0.45604 | 0.45173 | 0.46544 | 0.49619 | 0.52748 | 0.57874 | 0.64292 | 0.71077 | 0.75727 | 0.78497 | 0.78836 | 0.77227 | 0.75698 | 0.75289 | 0.74695 | 0.73538 | 0.71416 | 0.70634 | 0.6888 | 0.64534 | 0.58514 | 0.78836
2018-07-03 | 0.53751 | 0.49932 | 0.47672 | 0.46151 | 0.45904 | 0.47241 | 0.50279 | 0.53475 | 0.58643 | 0.65596 | 0.72824 | 0.78368 | 0.82237 | 0.8494 | 0.87138 | 0.88345 | 0.8786 | 0.84664 | 0.81163 | 0.77699 | 0.75552 | 0.73066 | 0.68399 | 0.62566 | 0.88345
2018-07-04 | 0.57244 | 0.52869 | 0.49619 | 0.47413 | 0.46239 | 0.46209 | 0.46694 | 0.48236 | 0.54403 | 0.63118 | 0.70956 | 0.76977 | 0.80566 | 0.82299 | 0.82889 | 0.82738 | 0.78522 | 0.73333 | 0.69577 | 0.66189 | 0.64033 | 0.61288 | 0.59759 | 0.56533 | 0.82889
2018-07-05 | 0.52084 | 0.48236 | 0.45654 | 0.43941 | 0.43109 | 0.43143 | 0.43661 | 0.45144 | 0.50337 | 0.56153 | 0.628 | 0.67426 | 0.71211 | 0.74787 | 0.7523 | 0.72611 | 0.70183 | 0.68491 | 0.66816 | 0.65052 | 0.63937 | 0.62203 | 0.58856 | 0.54373 | 0.7523
2018-07-06 | 0.50166 | 0.46727 | 0.44333 | 0.42687 | 0.42161 | 0.42249 | 0.42616 | 0.44246 | 0.50204 | 0.56145 | 0.61426 | 0.63465 | 0.65512 | 0.67355 | 0.69026 | 0.69289 | 0.68808 | 0.67526 | 0.65462 | 0.62261 | 0.61639 | 0.60327 | 0.56558 | 0.51624 | 0.69289
2018-07-07 | 0.47475 | 0.44438 | 0.4257 | 0.41639 | 0.41593 | 0.43352 | 0.46473 | 0.49815 | 0.54699 | 0.59679 | 0.64639 | 0.6786 | 0.69347 | 0.70492 | 0.70893 | 0.72046 | 0.72046 | 0.71858 | 0.71023 | 0.69932 | 0.69093 | 0.67095 | 0.62424 | 0.56763 | 0.72046
2018-07-08 | 0.51482 | 0.47609 | 0.44977 | 0.43448 | 0.43013 | 0.4435 | 0.47434 | 0.50951 | 0.56024 | 0.62821 | 0.69373 | 0.75134 | 0.796 | 0.81639 | 0.81242 | 0.78857 | 0.76371 | 0.74181 | 0.71884 | 0.68825 | 0.66277 | 0.63419 | 0.58794 | 0.53525 | 0.81639
2018-07-09 | 0.48549 | 0.45244 | 0.43088 | 0.4097 | 0.4115 | 0.43151 | 0.46439 | 0.49719 | 0.55071 | 0.6204 | 0.6819 | 0.74106 | 0.77883 | 0.78961 | 0.75652 | 0.72982 | 0.71691 | 0.69786 | 0.67472 | 0.66114 | 0.64915 | 0.65959 | 0.58422 | 0.53258 | 0.78961
2018-07-10 | 0.48044 | 0.44584 | 0.42487 | 0.41292 | 0.40937 | 0.42457 | 0.45762 | 0.49406 | 0.54745 | 0.61092 | 0.65938 | 0.69197 | 0.72163 | 0.74252 | 0.74169 | 0.72786 | 0.70684 | 0.68386 | 0.66469 | 0.64455 | 0.63895 | 0.62136 | 0.58075 | 0.52986 | 0.74252
2018-07-11 | 0.47947 | 0.44563 | 0.42395 | 0.4125 | 0.40978 | 0.4237 | 0.45232 | 0.48971 | 0.55109 | 0.61743 | 0.68065 | 0.73659 | 0.77825 | 0.8115 | 0.83089 | 0.83557 | 0.83152 | 0.8171 | 0.7935 | 0.75723 | 0.73571 | 0.71211 | 0.66661 | 0.6128 | 0.83557
2018-07-12 | 0.5612 | 0.52213 | 0.49226 | 0.47329 | 0.45842 | 0.45854 | 0.46243 | 0.48115 | 0.54001 | 0.61969 | 0.68307 | 0.73914 | 0.78368 | 0.80791 | 0.81497 | 0.81355 | 0.80712 | 0.78564 | 0.75564 | 0.71424 | 0.69318 | 0.66385 | 0.62161 | 0.57315 | 0.81497
2018-07-13 | 0.53337 | 0.50199 | 0.47918 | 0.46126 | 0.44939 | 0.44471 | 0.44567 | 0.46656 | 0.53358 | 0.60749 | 0.66874 | 0.72301 | 0.76208 | 0.78159 | 0.79751 | 0.80858 | 0.80653 | 0.79141 | 0.76655 | 0.73429 | 0.71654 | 0.69736 | 0.65236 | 0.59826 | 0.80858
2018-07-14 | 0.54783 | 0.50993 | 0.48135 | 0.46556 | 0.46134 | 0.47388 | 0.50295 | 0.53458 | 0.59082 | 0.65642 | 0.72034 | 0.77282 | 0.81042 | 0.82049 | 0.81293 | 0.80887 | 0.8072 | 0.80641 | 0.79592 | 0.76108 | 0.72957 | 0.69523 | 0.64254 | 0.58296 | 0.82049
2018-07-15 | 0.52949 | 0.4918 | 0.46594 | 0.44927 | 0.44534 | 0.45858 | 0.49025 | 0.52075 | 0.56684 | 0.63047 | 0.68361 | 0.7284 | 0.75531 | 0.75552 | 0.74403 | 0.72314 | 0.7086 | 0.69836 | 0.69393 | 0.67718 | 0.6715 | 0.65337 | 0.60795 | 0.55368 | 0.75552
2018-07-16 | 0.50555 | 0.46807 | 0.44225 | 0.42942 | 0.42758 | 0.44542 | 0.48549 | 0.51829 | 0.57419 | 0.63766 | 0.68963 | 0.72832 | 0.75209 | 0.73421 | 0.71345 | 0.69632 | 0.68094 | 0.66648 | 0.65692 | 0.64066 | 0.64292 | 0.63105 | 0.59115 | 0.54043 | 0.75209
2018-07-17 | 0.49318 | 0.46097 | 0.43569 | 0.4232 | 0.42198 | 0.43849 | 0.47246 | 0.50124 | 0.56312 | 0.62257 | 0.67994 | 0.7287 | 0.72987 | 0.72205 | 0.71232 | 0.72815 | 0.74938 | 0.75184 | 0.74712 | 0.72757 | 0.71157 | 0.68825 | 0.63427 | 0.5792 | 0.75184
2018-07-18 | 0.52117 | 0.48261 | 0.45687 | 0.43987 | 0.43339 | 0.44601 | 0.47367 | 0.50642 | 0.56617 | 0.63845 | 0.70409 | 0.76258 | 0.81 | 0.84476 | 0.86594 | 0.87752 | 0.87756 | 0.85546 | 0.81368 | 0.76947 | 0.74148 | 0.71119 | 0.66214 | 0.60912 | 0.87756
2018-07-19 | 0.55547 | 0.51298 | 0.48282 | 0.46347 | 0.45106 | 0.45027 | 0.45453 | 0.47546 | 0.54758 | 0.62842 | 0.69795 | 0.75656 | 0.80043 | 0.83185 | 0.84485 | 0.84927 | 0.85972 | 0.8517 | 0.81923 | 0.78401 | 0.76304 | 0.73032 | 0.68081 | 0.62913 | 0.85972
2018-07-20 | 0.57666 | 0.53584 | 0.50408 | 0.48169 | 0.46861 | 0.46301 | 0.46364 | 0.47688 | 0.54352 | 0.6278 | 0.69694 | 0.7635 | 0.81309 | 0.84576 | 0.86139 | 0.85241 | 0.84434 | 0.83148 | 0.80327 | 0.76809 | 0.75326 | 0.72686 | 0.68052 | 0.62057 | 0.86139
2018-07-21 | 0.5655 | 0.52564 | 0.49656 | 0.47856 | 0.47408 | 0.48658 | 0.51724 | 0.5454 | 0.59429 | 0.65846 | 0.72443 | 0.77883 | 0.8128 | 0.81861 | 0.79922 | 0.7795 | 0.75832 | 0.73918 | 0.71955 | 0.69765 | 0.69335 | 0.66226 | 0.61664 | 0.56312 | 0.81861
2018-07-22 | 0.5106 | 0.47392 | 0.45282 | 0.43769 | 0.43544 | 0.45436 | 0.48595 | 0.51745 | 0.57118 | 0.63156 | 0.68562 | 0.72598 | 0.75017 | 0.76367 | 0.78217 | 0.79295 | 0.78477 | 0.76032 | 0.73868 | 0.71445 | 0.70755 | 0.6814 | 0.63268 | 0.5792 | 0.79295
2018-07-23 | 0.5307 | 0.49443 | 0.46911 | 0.45307 | 0.44897 | 0.46243 | 0.49848 | 0.52664 | 0.57962 | 0.63377 | 0.68119 | 0.71888 | 0.74754 | 0.77461 | 0.80077 | 0.81414 | 0.81915 | 0.81493 | 0.81167 | 0.78222 | 0.76421 | 0.73688 | 0.68052 | 0.62199 | 0.81915
2018-07-24 | 0.56621 | 0.52272 | 0.49309 | 0.47471 | 0.46819 | 0.48002 | 0.50646 | 0.53663 | 0.59199 | 0.66168 | 0.72406 | 0.67004 | 0.81142 | 0.83194 | 0.84397 | 0.85542 | 0.87113 | 0.86206 | 0.8479 | 0.8133 | 0.78163 | 0.75042 | 0.68838 | 0.62462 | 0.87113
2018-07-25 | 0.57064 | 0.52556 | 0.49606 | 0.4758 | 0.46602 | 0.47772 | 0.50408 | 0.53579 | 0.59959 | 0.67012 | 0.73283 | 0.78936 | 0.8232 | 0.8415 | 0.85822 | 0.87384 | 0.87597 | 0.86022 | 0.82746 | 0.78702 | 0.76555 | 0.73237 | 0.68374 | 0.63034 | 0.87597
2018-07-26 | 0.58271 | 0.5426 | 0.5162 | 0.49372 | 0.47993 | 0.47764 | 0.48357 | 0.49945 | 0.5584 | 0.63661 | 0.70722 | 0.75364 | 0.77319 | 0.78393 | 0.78075 | 0.76893 | 0.76906 | 0.76024 | 0.74064 | 0.71332 | 0.70613 | 0.67764 | 0.63314 | 0.5912 | 0.78393
2018-07-27 | 0.54545 | 0.50914 | 0.4839 | 0.46535 | 0.45545 | 0.45261 | 0.45491 | 0.46936 | 0.5426 | 0.62541 | 0.6936 | 0.75372 | 0.80123 | 0.83753 | 0.86081 | 0.87626 | 0.88145 | 0.87555 | 0.84911 | 0.80988 | 0.79178 | 0.76145 | 0.70793 | 0.64986 | 0.88145
2018-07-28 | 0.59199 | 0.55267 | 0.52297 | 0.50433 | 0.49907 | 0.51244 | 0.54047 | 0.56801 | 0.62479 | 0.69665 | 0.75924 | 0.81706 | 0.85592 | 0.8916 | 0.92348 | 0.94119 | 0.94758 | 0.94048 | 0.92243 | 0.88671 | 0.86473 | 0.8288 | 0.76254 | 0.69226 | 0.94758
2018-07-29 | 0.62988 | 0.58568 | 0.5538 | 0.53421 | 0.52552 | 0.53521 | 0.56078 | 0.58514 | 0.64171 | 0.70659 | 0.7678 | 0.82187 | 0.85721 | 0.88111 | 0.89289 | 0.8837 | 0.87468 | 0.84388 | 0.80607 | 0.7724 | 0.75819 | 0.72865 | 0.6743 | 0.62124 | 0.89289
2018-07-30 | 0.56788 | 0.53216 | 0.50475 | 0.48879 | 0.48244 | 0.49539 | 0.52807 | 0.55368 | 0.60849 | 0.66916 | 0.71884 | 0.77603 | 0.82396 | 0.86561 | 0.88738 | 0.88913 | 0.86331 | 0.82061 | 0.78982 | 0.75949 | 0.74039 | 0.71173 | 0.65671 | 0.60093 | 0.88913
2018-07-31 | 0.54662 | 0.50793 | 0.48148 | 0.46573 | 0.46026 | 0.4722 | 0.50392 | 0.52815 | 0.57666 | 0.64601 | 0.71808 | 0.78167 | 0.82291 | 0.84998 | 0.85926 | 0.84881 | 0.8161 | 0.78527 | 0.75915 | 0.72974 | 0.72084 | 0.69515 | 0.64681 | 0.59124 | 0.85926
2018-08-01 | 0.54331 | 0.50713 | 0.47784 | 0.46473 | 0.4575 | 0.47074 | 0.49794 | 0.53166 | 0.58906 | 0.66139 | 0.72506 | 0.78013 | 0.82132 | 0.85015 | 0.87405 | 0.88684 | 0.885 | 0.85993 | 0.8227 | 0.78619 | 0.77106 | 0.73989 | 0.68554 | 0.63185 | 0.88684
2018-08-02 | 0.5805 | 0.53809 | 0.5083 | 0.48758 | 0.47601 | 0.47496 | 0.48177 | 0.49681 | 0.56111 | 0.63908 | 0.70676 | 0.75798 | 0.79734 | 0.81948 | 0.83925 | 0.83837 | 0.8316 | 0.81418 | 0.78297 | 0.75109 | 0.73881 | 0.71411 | 0.66707 | 0.61931 | 0.83925
2018-08-03 | 0.57072 | 0.533 | 0.50475 | 0.48591 | 0.47463 | 0.47325 | 0.47826 | 0.48574 | 0.53663 | 0.60055 | 0.64818 | 0.69866 | 0.72276 | 0.72991 | 0.7325 | 0.73889 | 0.7442 | 0.73759 | 0.72013 | 0.703 | 0.68783 | 0.6593 | 0.61062 | 0.5566 | 0.7442
2018-08-04 | 0.50546 | 0.47099 | 0.44856 | 0.43527 | 0.43435 | 0.45219 | 0.48654 | 0.51198 | 0.56074 | 0.62161 | 0.68119 | 0.73179 | 0.74557 | 0.73931 | 0.71716 | 0.6946 | 0.67217 | 0.64714 | 0.63118 | 0.61906 | 0.62721 | 0.60741 | 0.56905 | 0.52547 | 0.74557
2018-08-05 | 0.48265 | 0.45332 | 0.43611 | 0.42662 | 0.42612 | 0.442 | 0.47893 | 0.50889 | 0.56253 | 0.62947 | 0.68587 | 0.73826 | 0.77954 | 0.80415 | 0.79918 | 0.79538 | 0.79914 | 0.80261 | 0.78903 | 0.75874 | 0.74491 | 0.70939 | 0.65161 | 0.59387 | 0.80415
2018-08-06 | 0.53579 | 0.49761 | 0.47007 | 0.45269 | 0.44939 | 0.46201 | 0.49355 | 0.5238 | 0.58296 | 0.65445 | 0.71821 | 0.78485 | 0.83031 | 0.86812 | 0.89143 | 0.89331 | 0.87334 | 0.85149 | 0.82174 | 0.79203 | 0.7785 | 0.7457 | 0.68215 | 0.62324 | 0.89331
2018-08-07 | 0.56483 | 0.52422 | 0.49706 | 0.47901 | 0.47237 | 0.48495 | 0.5162 | 0.5434 | 0.60594 | 0.67923 | 0.74424 | 0.8054 | 0.85258 | 0.88483 | 0.89147 | 0.88759 | 0.88119 | 0.87004 | 0.84029 | 0.80607 | 0.77461 | 0.73074 | 0.66368 | 0.60181 | 0.89147
2018-08-08 | 0.54595 | 0.50354 | 0.47801 | 0.46255 | 0.45562 | 0.48064 | 0.50036 | 0.52702 | 0.56993 | 0.63277 | 0.69038 | 0.75159 | 0.80616 | 0.85095 | 0.87388 | 0.87526 | 0.86774 | 0.83536 | 0.79538 | 0.75794 | 0.74445 | 0.71282 | 0.66423 | 0.61894 | 0.87526
2018-08-09 | 0.56191 | 0.52242 | 0.4928 | 0.47371 | 0.46435 | 0.46435 | 0.47062 | 0.48959 | 0.56086 | 0.64459 | 0.71482 | 0.77545 | 0.82028 | 0.84986 | 0.87021 | 0.8822 | 0.88053 | 0.85496 | 0.81267 | 0.7714 | 0.75564 | 0.72184 | 0.6725 | 0.62658 | 0.8822
2018-08-10 | 0.57615 | 0.53767 | 0.50617 | 0.48591 | 0.47362 | 0.46924 | 0.47124 | 0.48261 | 0.55075 | 0.63461 | 0.70664 | 0.77582 | 0.8235 | 0.85909 | 0.8761 | 0.87944 | 0.87647 | 0.86473 | 0.83302 | 0.79212 | 0.77315 | 0.73287 | 0.67384 | 0.61296 | 0.87944
2018-08-11 | 0.55614 | 0.51465 | 0.48603 | 0.46857 | 0.46293 | 0.47814 | 0.50956 | 0.53287 | 0.58689 | 0.66193 | 0.73108 | 0.79951 | 0.85103 | 0.88353 | 0.89181 | 0.88951 | 0.89072 | 0.88287 | 0.85918 | 0.82253 | 0.80774 | 0.76062 | 0.70254 | 0.63507 | 0.89181
2018-08-12 | 0.57599 | 0.53538 | 0.50291 | 0.48298 | 0.47642 | 0.48913 | 0.5205 | 0.54586 | 0.6006 | 0.67137 | 0.73467 | 0.7917 | 0.83256 | 0.86398 | 0.87543 | 0.87455 | 0.88136 | 0.87681 | 0.86085 | 0.82588 | 0.80415 | 0.76041 | 0.6992 | 0.63845 | 0.88136
2018-08-13 | 0.57854 | 0.54081 | 0.51144 | 0.48712 | 0.48077 | 0.49414 | 0.52681 | 0.55292 | 0.61246 | 0.68424 | 0.74913 | 0.81589 | 0.86369 | 0.89665 | 0.91324 | 0.92181 | 0.92176 | 0.90167 | 0.87062 | 0.83014 | 0.81322 | 0.77365 | 0.71157 | 0.64981 | 0.92181
2018-08-14 | 0.59429 | 0.55602 | 0.52898 | 0.51135 | 0.50346 | 0.51357 | 0.54503 | 0.5688 | 0.62596 | 0.69945 | 0.76592 | 0.81781 | 0.86218 | 0.88558 | 0.88884 | 0.85888 | 0.8143 | 0.78 | 0.75122 | 0.72669 | 0.72168 | 0.68808 | 0.64221 | 0.58426 | 0.88884
2018-08-15 | 0.53408 | 0.4999 | 0.47333 | 0.46113 | 0.45792 | 0.47425 | 0.51031 | 0.54043 | 0.59913 | 0.66243 | 0.72272 | 0.76596 | 0.79859 | 0.79174 | 0.734 | 0.69698 | 0.67217 | 0.65499 | 0.63348 | 0.61284 | 0.61564 | 0.59395 | 0.56337 | 0.52414 | 0.79859
2018-08-16 | 0.48349 | 0.45645 | 0.43803 | 0.4257 | 0.41939 | 0.42169 | 0.43326 | 0.45215 | 0.51783 | 0.60924 | 0.68449 | 0.7391 | 0.78974 | 0.79868 | 0.8237 | 0.80478 | 0.77039 | 0.73454 | 0.70041 | 0.67125 | 0.66318 | 0.63962 | 0.60465 | 0.55702 | 0.8237
2018-08-17 | 0.51357 | 0.48127 | 0.45708 | 0.44012 | 0.43297 | 0.43331 | 0.44104 | 0.45578 | 0.51791 | 0.60502 | 0.68324 | 0.74557 | 0.79676 | 0.83929 | 0.84631 | 0.83837 | 0.84242 | 0.84088 | 0.82228 | 0.79166 | 0.78197 | 0.74687 | 0.687 | 0.61685 | 0.84631
2018-08-18 | 0.56395 | 0.52192 | 0.4936 | 0.47655 | 0.47283 | 0.49635 | 0.53655 | 0.55439 | 0.59713 | 0.67121 | 0.74115 | 0.80394 | 0.85061 | 0.88796 | 0.90476 | 0.91838 | 0.92055 | 0.91165 | 0.89235 | 0.85771 | 0.84397 | 0.793 | 0.71984 | 0.6555 | 0.92055
2018-08-19 | 0.59303 | 0.55109 | 0.52088 | 0.50158 | 0.49573 | 0.51495 | 0.55614 | 0.57223 | 0.61727 | 0.68859 | 0.75184 | 0.81347 | 0.86214 | 0.89494 | 0.91412 | 0.93706 | 0.94875 | 0.9368 | 0.91428 | 0.87489 | 0.85888 | 0.81109 | 0.7386 | 0.67095 | 0.94875
2018-08-20 | 0.60962 | 0.56709 | 0.53751 | 0.51524 | 0.50801 | 0.52493 | 0.56395 | 0.51988 | 0.62157 | 0.69335 | 0.75594 | 0.82116 | 0.86264 | 0.90246 | 0.91859 | 0.92176 | 0.92051 | 0.9081 | 0.88119 | 0.84785 | 0.83281 | 0.79074 | 0.72514 | 0.65738 | 0.92176
2018-08-21 | 0.60423 | 0.56224 | 0.53249 | 0.51336 | 0.50559 | 0.52359 | 0.56492 | 0.5833 | 0.62913 | 0.69473 | 0.7607 | 0.82341 | 0.86766 | 0.90572 | 0.92699 | 0.9485 | 0.94926 | 0.91779 | 0.88462 | 0.83879 | 0.8283 | 0.78184 | 0.71963 | 0.65215 | 0.94926
2018-08-22 | 0.59086 | 0.55096 | 0.52213 | 0.50387 | 0.49644 | 0.51344 | 0.55497 | 0.57273 | 0.61781 | 0.68971 | 0.75305 | 0.81301 | 0.85989 | 0.89331 | 0.90568 | 0.93213 | 0.93894 | 0.92018 | 0.88968 | 0.84376 | 0.81882 | 0.77027 | 0.71386 | 0.657 | 0.93894
2018-08-23 | 0.59989 | 0.55948 | 0.52677 | 0.50421 | 0.49021 | 0.48896 | 0.49543 | 0.50931 | 0.57361 | 0.66243 | 0.73651 | 0.80127 | 0.84986 | 0.88236 | 0.8969 | 0.90864 | 0.91533 | 0.90597 | 0.87622 | 0.83227 | 0.81121 | 0.77215 | 0.72393 | 0.66657 | 0.91533
2018-08-24 | 0.60841 | 0.56504 | 0.53116 | 0.50768 | 0.49335 | 0.48783 | 0.4885 | 0.49727 | 0.56613 | 0.65374 | 0.72418 | 0.7955 | 0.85086 | 0.88997 | 0.91341 | 0.92561 | 0.92686 | 0.92001 | 0.89243 | 0.85462 | 0.83812 | 0.78794 | 0.72326 | 0.65921 | 0.92686
2018-08-25 | 0.60858 | 0.56512 | 0.53989 | 0.52476 | 0.52389 | 0.54699 | 0.58982 | 0.60657 | 0.6377 | 0.69978 | 0.75953 | 0.8105 | 0.84209 | 0.85441 | 0.85713 | 0.85638 | 0.85884 | 0.84919 | 0.8204 | 0.79366 | 0.78685 | 0.74023 | 0.68265 | 0.6171 | 0.85884
2018-08-26 | 0.56968 | 0.53554 | 0.51152 | 0.49723 | 0.49464 | 0.51632 | 0.56003 | 0.5759 | 0.6105 | 0.67426 | 0.72974 | 0.77988 | 0.81481 | 0.84564 | 0.86628 | 0.88278 | 0.89122 | 0.88399 | 0.85922 | 0.82149 | 0.8077 | 0.76091 | 0.68951 | 0.62579 | 0.89122
2018-08-27 | 0.56404 | 0.52272 | 0.49259 | 0.47438 | 0.46761 | 0.48649 | 0.52928 | 0.54382 | 0.58393 | 0.65374 | 0.71382 | 0.77081 | 0.81602 | 0.85245 | 0.88032 | 0.90012 | 0.91174 | 0.90451 | 0.88019 | 0.83983 | 0.82663 | 0.77946 | 0.71102 | 0.64877 | 0.91174
2018-08-28 | 0.59107 | 0.55104 | 0.52121 | 0.50124 | 0.49297 | 0.5119 | 0.55639 | 0.57264 | 0.61138 | 0.66711 | 0.71056 | 0.74737 | 0.78924 | 0.83135 | 0.86916 | 0.89264 | 0.90288 | 0.88537 | 0.8494 | 0.8199 | 0.80181 | 0.75163 | 0.69034 | 0.6303 | 0.90288
2018-08-29 | 0.5716 | 0.53391 | 0.50818 | 0.49038 | 0.48562 | 0.505 | 0.54975 | 0.57143 | 0.61568 | 0.68792 | 0.75401 | 0.80302 | 0.83829 | 0.8715 | 0.89482 | 0.90793 | 0.90355 | 0.87459 | 0.83741 | 0.80018 | 0.78593 | 0.74227 | 0.69101 | 0.64271 | 0.90793
2018-08-30 | 0.59437 | 0.5566 | 0.52894 | 0.50876 | 0.49995 | 0.50834 | 0.51135 | 0.52184 | 0.57578 | 0.65863 | 0.72811 | 0.79249 | 0.83503 | 0.86762 | 0.89164 | 0.90196 | 0.90054 | 0.87572 | 0.83181 | 0.79392 | 0.77979 | 0.73818 | 0.6913 | 0.64584 | 0.90196
2018-08-31 | 0.59604 | 0.55522 | 0.52426 | 0.50542 | 0.49205 | 0.4862 | 0.48975 | 0.49949 | 0.56278 | 0.65245 | 0.71846 | 0.77624 | 0.82337 | 0.85521 | 0.86933 | 0.87388 | 0.86436 | 0.84568 | 0.80607 | 0.76851 | 0.75732 | 0.71804 | 0.67004 | 0.61915 | 0.87388
2018-09-01 | 0.57085 | 0.53738 | 0.51165 | 0.49238 | 0.48608 | 0.48984 | 0.50128 | 0.50646 | 0.56592 | 0.65445 | 0.72728 | 0.79588 | 0.83344 | 0.86193 | 0.88633 | 0.89465 | 0.88796 | 0.87113 | 0.8423 | 0.80657 | 0.7955 | 0.74892 | 0.68608 | 0.62738 | 0.89465
2018-09-02 | 0.57198 | 0.53291 | 0.50525 | 0.48887 | 0.48332 | 0.50266 | 0.54482 | 0.56153 | 0.59801 | 0.66469 | 0.72331 | 0.78276 | 0.82458 | 0.85011 | 0.87743 | 0.89319 | 0.89649 | 0.88211 | 0.8499 | 0.81401 | 0.79279 | 0.73438 | 0.66565 | 0.59826 | 0.89649
2018-09-03 | 0.54173 | 0.50325 | 0.47822 | 0.4618 | 0.45741 | 0.47701 | 0.52255 | 0.53922 | 0.57319 | 0.6316 | 0.67217 | 0.71445 | 0.75427 | 0.79584 | 0.82554 | 0.83544 | 0.84142 | 0.82746 | 0.80256 | 0.76997 | 0.75995 | 0.71537 | 0.65453 | 0.58835 | 0.84142
2018-09-04 | 0.53408 | 0.49594 | 0.47103 | 0.45566 | 0.45144 | 0.47087 | 0.51808 | 0.53408 | 0.55877 | 0.6105 | 0.66456 | 0.70889 | 0.74562 | 0.77992 | 0.79425 | 0.80027 | 0.80745 | 0.79659 | 0.77687 | 0.75874 | 0.75356 | 0.70881 | 0.64722 | 0.58865 | 0.80745
2018-09-05 | 0.53517 | 0.49882 | 0.47567 | 0.46117 | 0.45888 | 0.4791 | 0.5284 | 0.54561 | 0.58184 | 0.64793 | 0.71106 | 0.76701 | 0.8138 | 0.84894 | 0.86874 | 0.86996 | 0.85082 | 0.81221 | 0.77123 | 0.74328 | 0.72686 | 0.68537 | 0.63962 | 0.59445 | 0.86996
2018-09-06 | 0.54687 | 0.51545 | 0.49101 | 0.47413 | 0.46598 | 0.46585 | 0.47601 | 0.49255 | 0.54469 | 0.61275 | 0.66485 | 0.70413 | 0.72694 | 0.72397 | 0.71679 | 0.70735 | 0.689 | 0.67426 | 0.657 | 0.64806 | 0.64814 | 0.62295 | 0.59182 | 0.55648 | 0.72694
2018-09-07 | 0.51695 | 0.48152 | 0.45729 | 0.44045 | 0.43406 | 0.43519 | 0.44392 | 0.4552 | 0.50496 | 0.56918 | 0.6265 | 0.68307 | 0.72886 | 0.76003 | 0.77449 | 0.76463 | 0.74725 | 0.72314 | 0.68704 | 0.67522 | 0.67467 | 0.63979 | 0.59044 | 0.53813 | 0.77449
2018-09-08 | 0.49506 | 0.46573 | 0.44292 | 0.42917 | 0.42829 | 0.45286 | 0.49986 | 0.51729 | 0.54553 | 0.61171 | 0.67806 | 0.73559 | 0.78075 | 0.81476 | 0.83954 | 0.8499 | 0.84877 | 0.83946 | 0.80511 | 0.78552 | 0.77185 | 0.72218 | 0.66047 | 0.59863 | 0.8499
2018-09-09 | 0.54469 | 0.50571 | 0.4811 | 0.46539 | 0.45892 | 0.47776 | 0.52351 | 0.53989 | 0.56834 | 0.62784 | 0.68938 | 0.74395 | 0.78932 | 0.82851 | 0.84627 | 0.86498 | 0.86043 | 0.84058 | 0.80816 | 0.7818 | 0.76337 | 0.70831 | 0.64422 | 0.58309 | 0.86498
2018-09-10 | 0.53279 | 0.49957 | 0.47722 | 0.4613 | 0.45787 | 0.47952 | 0.52614 | 0.54135 | 0.56934 | 0.62207 | 0.68207 | 0.73028 | 0.7724 | 0.80845 | 0.82926 | 0.83887 | 0.83511 | 0.81786 | 0.78903 | 0.76722 | 0.7541 | 0.69983 | 0.63853 | 0.57636 | 0.83887
2018-09-11 | 0.52414 | 0.48996 | 0.46548 | 0.45006 | 0.44655 | 0.46707 | 0.51449 | 0.53145 | 0.55714 | 0.61413 | 0.66573 | 0.70956 | 0.74152 | 0.76413 | 0.77185 | 0.77424 | 0.75974 | 0.73104 | 0.70463 | 0.68967 | 0.68215 | 0.64238 | 0.59717 | 0.54269 | 0.77424
2018-09-12 | 0.48737 | 0.45925 | 0.43911 | 0.42884 | 0.42884 | 0.45202 | 0.50358 | 0.51837 | 0.54866 | 0.59859 | 0.64401 | 0.68186 | 0.71884 | 0.75364 | 0.76225 | 0.75894 | 0.76133 | 0.76417 | 0.73789 | 0.70814 | 0.69611 | 0.66026 | 0.61998 | 0.57068 | 0.76417
2018-09-13 | 0.5167 | 0.48064 | 0.45507 | 0.43439 | 0.42595 | 0.42516 | 0.43661 | 0.45215 | 0.49874 | 0.56517 | 0.63427 | 0.69535 | 0.74165 | 0.7701 | 0.78151 | 0.78021 | 0.764 | 0.74081 | 0.70145 | 0.68127 | 0.66857 | 0.62851 | 0.58063 | 0.53086 | 0.78151
2018-09-14 | 0.49059 | 0.45779 | 0.43414 | 0.41814 | 0.40861 | 0.40703 | 0.4135 | 0.42249 | 0.47893 | 0.55376 | 0.62291 | 0.68625 | 0.73287 | 0.76367 | 0.77917 | 0.78435 | 0.78514 | 0.765 | 0.72903 | 0.70781 | 0.6964 | 0.65387 | 0.60231 | 0.54298 | 0.78514
2018-09-15 | 0.49777 | 0.46439 | 0.44363 | 0.43193 | 0.43147 | 0.45399 | 0.50074 | 0.51921 | 0.5505 | 0.61434 | 0.69005 | 0.7462 | 0.7922 | 0.83181 | 0.85939 | 0.87769 | 0.88094 | 0.86891 | 0.83824 | 0.81481 | 0.79734 | 0.74202 | 0.67998 | 0.60607 | 0.88094
2018-09-16 | 0.54808 | 0.51139 | 0.48294 | 0.46481 | 0.45971 | 0.47805 | 0.52414 | 0.54064 | 0.57018 | 0.6288 | 0.69218 | 0.74946 | 0.79241 | 0.82404 | 0.81844 | 0.80114 | 0.78694 | 0.77027 | 0.75134 | 0.74386 | 0.72907 | 0.6801 | 0.62383 | 0.56446 | 0.82404
2018-09-17 | 0.50922 | 0.475 | 0.45077 | 0.43548 | 0.43423 | 0.45733 | 0.50722 | 0.52393 | 0.54896 | 0.59567 | 0.65408 | 0.69807 | 0.72966 | 0.74637 | 0.76467 | 0.76358 | 0.73764 | 0.70764 | 0.68687 | 0.69038 | 0.68445 | 0.64664 | 0.5922 | 0.53258 | 0.76467
2018-09-18 | 0.48658 | 0.45182 | 0.43347 | 0.42081 | 0.41973 | 0.44254 | 0.49297 | 0.50993 | 0.53592 | 0.58631 | 0.63431 | 0.68353 | 0.73007 | 0.77223 | 0.80181 | 0.81836 | 0.8128 | 0.81531 | 0.7795 | 0.75815 | 0.73918 | 0.69022 | 0.63043 | 0.56742 | 0.81836
2018-09-19 | 0.51545 | 0.47801 | 0.4552 | 0.44053 | 0.43786 | 0.45896 | 0.5083 | 0.52898 | 0.55506 | 0.60975 | 0.65491 | 0.68282 | 0.69109 | 0.67747 | 0.65428 | 0.64342 | 0.63348 | 0.62366 | 0.61196 | 0.61639 | 0.61133 | 0.58539 | 0.54816 | 0.50655 | 0.69109
2018-09-20 | 0.46443 | 0.43565 | 0.41655 | 0.40598 | 0.40059 | 0.40594 | 0.42215 | 0.44313 | 0.48232 | 0.54169 | 0.59408 | 0.63519 | 0.6654 | 0.68512 | 0.68737 | 0.65683 | 0.6313 | 0.61852 | 0.59834 | 0.60277 | 0.59834 | 0.56784 | 0.5307 | 0.49121 | 0.68737
2018-09-21 | 0.45361 | 0.4224 | 0.40193 | 0.38864 | 0.38292 | 0.38438 | 0.39499 | 0.40707 | 0.45319 | 0.52368 | 0.58777 | 0.64685 | 0.69402 | 0.72686 | 0.74892 | 0.75723 | 0.75606 | 0.74056 | 0.70567 | 0.68955 | 0.67179 | 0.62424 | 0.57294 | 0.51457 | 0.75723
2018-09-22 | 0.46757 | 0.43506 | 0.4135 | 0.40452 | 0.40673 | 0.43423 | 0.48349 | 0.5058 | 0.53446 | 0.58581 | 0.63707 | 0.68198 | 0.71558 | 0.72255 | 0.71374 | 0.7025 | 0.69611 | 0.68357 | 0.67576 | 0.68048 | 0.66444 | 0.61998 | 0.56525 | 0.50943 | 0.72255
2018-09-23 | 0.46226 | 0.42988 | 0.40815 | 0.39683 | 0.39804 | 0.42708 | 0.4824 | 0.50613 | 0.51804 | 0.55209 | 0.57657 | 0.60565 | 0.62667 | 0.63118 | 0.63348 | 0.63857 | 0.64547 | 0.65662 | 0.64931 | 0.65901 | 0.65052 | 0.61033 | 0.56011 | 0.50358 | 0.65901
2018-09-24 | 0.45578 | 0.42445 | 0.40895 | 0.39679 | 0.39554 | 0.42391 | 0.4781 | 0.50137 | 0.52008 | 0.55455 | 0.58739 | 0.6199 | 0.64162 | 0.66803 | 0.69782 | 0.72126 | 0.72343 | 0.71395 | 0.69728 | 0.69698 | 0.6875 | 0.64823 | 0.59136 | 0.53767 | 0.72343
2018-09-25 | 0.49126 | 0.45725 | 0.43506 | 0.42111 | 0.42027 | 0.43903 | 0.48023 | 0.50584 | 0.53625 | 0.59053 | 0.64359 | 0.67839 | 0.69698 | 0.7134 | 0.73526 | 0.75305 | 0.74027 | 0.70597 | 0.68253 | 0.67881 | 0.66594 | 0.62508 | 0.5734 | 0.52422 | 0.75305
2018-09-26 | 0.47901 | 0.44864 | 0.42884 | 0.41705 | 0.4168 | 0.44212 | 0.49264 | 0.51712 | 0.53726 | 0.57524 | 0.62383 | 0.67839 | 0.71934 | 0.7594 | 0.77328 | 0.77457 | 0.76049 | 0.73304 | 0.70446 | 0.70003 | 0.68345 | 0.64831 | 0.60235 | 0.58756 | 0.77457
2018-09-27 | 0.53287 | 0.4824 | 0.46201 | 0.4473 | 0.44158 | 0.44409 | 0.45683 | 0.47266 | 0.52359 | 0.59734 | 0.65926 | 0.71675 | 0.76166 | 0.79208 | 0.81322 | 0.81426 | 0.78773 | 0.75974 | 0.72184 | 0.71232 | 0.6898 | 0.65499 | 0.60983 | 0.55936 | 0.81426
2018-09-28 | 0.51449 | 0.48186 | 0.45783 | 0.44116 | 0.43343 | 0.43448 | 0.44313 | 0.45792 | 0.50412 | 0.57728 | 0.64292 | 0.70225 | 0.75188 | 0.7869 | 0.80871 | 0.81543 | 0.80616 | 0.77908 | 0.7381 | 0.73726 | 0.72122 | 0.6766 | 0.61915 | 0.55848 | 0.81543
2018-09-29 | 0.51269 | 0.47592 | 0.45466 | 0.44116 | 0.4412 | 0.46385 | 0.51256 | 0.53329 | 0.55915 | 0.61798 | 0.68036 | 0.74102 | 0.77804 | 0.80891 | 0.82433 | 0.82421 | 0.81372 | 0.78535 | 0.75364 | 0.7406 | 0.70145 | 0.65395 | 0.59462 | 0.53742 | 0.82433
2018-09-30 | 0.48775 | 0.45495 | 0.4346 | 0.42244 | 0.42232 | 0.44676 | 0.50216 | 0.52075 | 0.55104 | 0.6087 | 0.66519 | 0.71299 | 0.75101 | 0.76358 | 0.77503 | 0.75706 | 0.7546 | 0.74913 | 0.72853 | 0.73104 | 0.71474 | 0.67187 | 0.61409 | 0.55368 | 0.77503
2018-10-01 | 0.50492 | 0.47041 | 0.45065 | 0.43857 | 0.43657 | 0.46193 | 0.51574 | 0.53421 | 0.56529 | 0.62282 | 0.6758 | 0.7274 | 0.76843 | 0.79864 | 0.81159 | 0.83365 | 0.8466 | 0.83352 | 0.80202 | 0.78627 | 0.76488 | 0.71499 | 0.64839 | 0.61392 | 0.8466
2018-10-02 | 0.54269 | 0.49757 | 0.47337 | 0.45796 | 0.45399 | 0.47484 | 0.5241 | 0.54148 | 0.57352 | 0.63536 | 0.69744 | 0.74846 | 0.78982 | 0.83194 | 0.85466 | 0.87062 | 0.87994 | 0.86419 | 0.82813 | 0.80975 | 0.78568 | 0.73058 | 0.66899 | 0.60122 | 0.87994
2018-10-03 | 0.54728 | 0.50993 | 0.4811 | 0.46452 | 0.45804 | 0.47667 | 0.5241 | 0.54461 | 0.58025 | 0.6458 | 0.70956 | 0.76759 | 0.80678 | 0.84907 | 0.87046 | 0.88195 | 0.8814 | 0.8456 | 0.79396 | 0.76538 | 0.72782 | 0.68194 | 0.63001 | 0.57791 | 0.88195
2018-10-04 | 0.52882 | 0.49004 | 0.46531 | 0.44806 | 0.43966 | 0.44258 | 0.45558 | 0.47187 | 0.52627 | 0.5975 | 0.65161 | 0.69878 | 0.73856 | 0.76233 | 0.77102 | 0.76584 | 0.74771 | 0.72038 | 0.68487 | 0.67873 | 0.65863 | 0.62036 | 0.57348 | 0.52456 | 0.77102
2018-10-05 | 0.47408 | 0.4321 | 0.40059 | 0.37586 | 0.3622 | 0.35856 | 0.36479 | 0.37076 | 0.40189 | 0.4481 | 0.49326 | 0.52514 | 0.55944 | 0.58969 | 0.61484 | 0.63323 | 0.65103 | 0.64405 | 0.61677 | 0.61451 | 0.59905 | 0.55731 | 0.50676 | 0.45299 | 0.65103
2018-10-06 | 0.40974 | 0.37912 | 0.36044 | 0.35075 | 0.35305 | 0.38221 | 0.43281 | 0.45478 | 0.47622 | 0.51574 | 0.55572 | 0.5912 | 0.62821 | 0.65541 | 0.6827 | 0.69118 | 0.70054 | 0.68742 | 0.67409 | 0.68796 | 0.66644 | 0.62086 | 0.56976 | 0.51286 | 0.70054
2018-10-07 | 0.46272 | 0.43264 | 0.41317 | 0.40068 | 0.39788 | 0.42123 | 0.47434 | 0.49844 | 0.50939 | 0.54858 | 0.59069 | 0.62032 | 0.64447 | 0.66469 | 0.6748 | 0.6702 | 0.66962 | 0.6616 | 0.65545 | 0.67129 | 0.65328 | 0.62111 | 0.56512 | 0.50191 | 0.6748
2018-10-08 | 0.45516 | 0.42483 | 0.4031 | 0.39228 | 0.39353 | 0.42023 | 0.47392 | 0.49439 | 0.51541 | 0.56362 | 0.61748 | 0.66231 | 0.70396 | 0.73597 | 0.76199 | 0.77374 | 0.77273 | 0.7602 | 0.73739 | 0.73759 | 0.71633 | 0.66945 | 0.61188 | 0.55376 | 0.77374
2018-10-09 | 0.50066 | 0.46698 | 0.44354 | 0.42629 | 0.42357 | 0.41873 | 0.49222 | 0.51177 | 0.53663 | 0.59445 | 0.6494 | 0.6979 | 0.73417 | 0.76893 | 0.79262 | 0.80829 | 0.81105 | 0.796 | 0.7622 | 0.75477 | 0.72966 | 0.68052 | 0.62537 | 0.56116 | 0.81105
2018-10-10 | 0.50667 | 0.4674 | 0.44388 | 0.42696 | 0.42391 | 0.44455 | 0.49347 | 0.51541 | 0.5424 | 0.60085 | 0.65825 | 0.70258 | 0.74161 | 0.77386 | 0.79575 | 0.81054 | 0.81347 | 0.79287 | 0.75084 | 0.73601 | 0.70789 | 0.66531 | 0.61752 | 0.56646 | 0.81347
2018-10-11 | 0.51632 | 0.47964 | 0.4562 | 0.43861 | 0.42875 | 0.42925 | 0.44091 | 0.45307 | 0.50266 | 0.58046 | 0.64472 | 0.69861 | 0.74006 | 0.77144 | 0.79275 | 0.80628 | 0.80887 | 0.79116 | 0.74633 | 0.72615 | 0.69782 | 0.65458 | 0.61158 | 0.56024 | 0.80887
2018-10-12 | 0.51361 | 0.47584 | 0.44722 | 0.42925 | 0.42061 | 0.41898 | 0.42733 | 0.43364 | 0.48766 | 0.57072 | 0.63778 | 0.69381 | 0.74102 | 0.77148 | 0.79166 | 0.80252 | 0.80373 | 0.78807 | 0.75042 | 0.74716 | 0.72005 | 0.67313 | 0.6242 | 0.56751 | 0.80373
2018-10-13 | 0.51996 | 0.48578 | 0.46422 | 0.45144 | 0.45173 | 0.47505 | 0.52105 | 0.54022 | 0.56563 | 0.6194 | 0.6796 | 0.72736 | 0.76066 | 0.78744 | 0.80553 | 0.81735 | 0.81577 | 0.79897 | 0.76676 | 0.7653 | 0.73697 | 0.69076 | 0.63473 | 0.57453 | 0.81735
2018-10-14 | 0.52376 | 0.49159 | 0.47183 | 0.4585 | 0.45533 | 0.47939 | 0.53149 | 0.55142 | 0.57682 | 0.63231 | 0.68558 | 0.72999 | 0.76108 | 0.79429 | 0.81221 | 0.81706 | 0.80741 | 0.78243 | 0.75999 | 0.76559 | 0.73404 | 0.68499 | 0.62642 | 0.56383 | 0.81706
2018-10-15 | 0.5063 | 0.46911 | 0.44701 | 0.43318 | 0.43347 | 0.45654 | 0.50701 | 0.5299 | 0.55313 | 0.60168 | 0.6471 | 0.69005 | 0.64555 | 0.74399 | 0.75051 | 0.75523 | 0.74382 | 0.7256 | 0.70342 | 0.70877 | 0.67927 | 0.63444 | 0.57503 | 0.51649 | 0.75523
2018-10-16 | 0.46473 | 0.4303 | 0.40899 | 0.39445 | 0.38797 | 0.40586 | 0.45014 | 0.46552 | 0.48089 | 0.5185 | 0.55401 | 0.58159 | 0.61008 | 0.63899 | 0.66485 | 0.69042 | 0.70488 | 0.69757 | 0.66828 | 0.66552 | 0.63774 | 0.58919 | 0.53145 | 0.4702 | 0.70488
2018-10-17 | 0.41705 | 0.38079 | 0.36036 | 0.34841 | 0.34544 | 0.36679 | 0.41237 | 0.4326 | 0.45282 | 0.49042 | 0.52522 | 0.55664 | 0.58263 | 0.6125 | 0.64137 | 0.66728 | 0.67977 | 0.66841 | 0.63247 | 0.62011 | 0.58819 | 0.54403 | 0.50187 | 0.45361 | 0.67977
2018-10-18 | 0.41271 | 0.37619 | 0.35338 | 0.34039 | 0.3345 | 0.3398 | 0.35601 | 0.37281 | 0.41496 | 0.46978 | 0.51536 | 0.5528 | 0.58973 | 0.62186 | 0.6509 | 0.67313 | 0.68123 | 0.66857 | 0.63231 | 0.62245 | 0.59203 | 0.54975 | 0.50989 | 0.4623 | 0.68123
2018-10-19 | 0.42023 | 0.38726 | 0.36337 | 0.34895 | 0.34294 | 0.34319 | 0.35413 | 0.3647 | 0.40899 | 0.46824 | 0.51971 | 0.56316 | 0.6077 | 0.64162 | 0.66882 | 0.68495 | 0.69047 | 0.67802 | 0.65023 | 0.65257 | 0.62617 | 0.57883 | 0.52969 | 0.4763 | 0.69047
2018-10-20 | 0.42938 | 0.39533 | 0.37515 | 0.36462 | 0.36525 | 0.38902 | 0.43586 | 0.45992 | 0.48687 | 0.53918 | 0.58973 | 0.63222 | 0.66799 | 0.69581 | 0.72088 | 0.72819 | 0.72314 | 0.70601 | 0.68909 | 0.69519 | 0.66448 | 0.61651 | 0.56174 | 0.50458 | 0.72819
2018-10-21 | 0.45428 | 0.42382 | 0.40615 | 0.39504 | 0.39587 | 0.42056 | 0.47283 | 0.49899 | 0.50897 | 0.54148 | 0.57749 | 0.59922 | 0.61397 | 0.62111 | 0.62282 | 0.62433 | 0.62115 | 0.61497 | 0.61476 | 0.63268 | 0.60996 | 0.57361 | 0.52385 | 0.46598 | 0.63268
2018-10-22 | 0.42236 | 0.39282 | 0.37569 | 0.36725 | 0.36926 | 0.39219 | 0.44952 | 0.47713 | 0.48858 | 0.51875 | 0.55677 | 0.59437 | 0.62195 | 0.64551 | 0.66268 | 0.67242 | 0.66673 | 0.65249 | 0.64584 | 0.65687 | 0.63306 | 0.59274 | 0.53914 | 0.48186 | 0.67242
2018-10-23 | 0.43448 | 0.40694 | 0.38843 | 0.37724 | 0.37598 | 0.39988 | 0.45482 | 0.48202 | 0.48858 | 0.51432 | 0.54377 | 0.56822 | 0.58848 | 0.60139 | 0.6133 | 0.61877 | 0.6156 | 0.60674 | 0.60009 | 0.61209 | 0.6011 | 0.56596 | 0.5182 | 0.46715 | 0.61877
2018-10-24 | 0.42374 | 0.39437 | 0.37732 | 0.3698 | 0.37218 | 0.39474 | 0.44162 | 0.47049 | 0.48791 | 0.52105 | 0.54841 | 0.5678 | 0.57741 | 0.58773 | 0.59562 | 0.60273 | 0.60197 | 0.59253 | 0.58451 | 0.58894 | 0.5668 | 0.53809 | 0.50496 | 0.45971 | 0.60273
2018-10-25 | 0.41229 | 0.37811 | 0.35559 | 0.34143 | 0.33638 | 0.34022 | 0.35572 | 0.37502 | 0.41263 | 0.46364 | 0.5055 | 0.53621 | 0.56253 | 0.58677 | 0.60482 | 0.61785 | 0.61814 | 0.60248 | 0.57394 | 0.57005 | 0.54394 | 0.5121 | 0.47759 | 0.43364 | 0.61814
2018-10-26 | 0.39403 | 0.36466 | 0.3467 | 0.33412 | 0.32894 | 0.32998 | 0.34034 | 0.35626 | 0.39144 | 0.44396 | 0.48917 | 0.52268 | 0.551 | 0.57858 | 0.60064 | 0.61743 | 0.62491 | 0.61413 | 0.58923 | 0.59688 | 0.57001 | 0.52627 | 0.4753 | 0.41952 | 0.62491
2018-10-27 | 0.37356 | 0.34419 | 0.3271 | 0.31937 | 0.32209 | 0.3482 | 0.39963 | 0.42859 | 0.44358 | 0.48152 | 0.51946 | 0.55343 | 0.58142 | 0.61092 | 0.63624 | 0.6593 | 0.67121 | 0.66226 | 0.6438 | 0.65161 | 0.61923 | 0.56926 | 0.51277 | 0.45186 | 0.67121
2018-10-28 | 0.40398 | 0.37272 | 0.35288 | 0.34277 | 0.34331 | 0.36955 | 0.42244 | 0.44868 | 0.46502 | 0.50876 | 0.549 | 0.58727 | 0.61852 | 0.65675 | 0.6842 | 0.70384 | 0.71324 | 0.70221 | 0.67893 | 0.68524 | 0.65169 | 0.60636 | 0.54879 | 0.48921 | 0.71324
2018-10-29 | 0.44112 | 0.40749 | 0.38501 | 0.37256 | 0.37252 | 0.3957 | 0.45039 | 0.47342 | 0.48846 | 0.54022 | 0.58246 | 0.62153 | 0.65813 | 0.68867 | 0.71274 | 0.73337 | 0.73743 | 0.71854 | 0.68871 | 0.6888 | 0.65729 | 0.61104 | 0.55347 | 0.4918 | 0.73743
2018-10-30 | 0.43619 | 0.40197 | 0.37895 | 0.36596 | 0.36441 | 0.38735 | 0.4392 | 0.46443 | 0.47927 | 0.52581 | 0.57473 | 0.61447 | 0.64793 | 0.67488 | 0.69042 | 0.70237 | 0.71056 | 0.69485 | 0.67346 | 0.67785 | 0.64689 | 0.6059 | 0.55217 | 0.49414 | 0.71056
2018-10-31 | 0.4412 | 0.40611 | 0.38158 | 0.36905 | 0.36637 | 0.38898 | 0.44099 | 0.46736 | 0.48382 | 0.52894 | 0.5701 | 0.60703 | 0.6341 | 0.65286 | 0.66673 | 0.67714 | 0.67939 | 0.65775 | 0.61844 | 0.59688 | 0.55602 | 0.52059 | 0.4781 | 0.43051 | 0.67939
2018-11-01 | 0.38288 | 0.35033 | 0.33157 | 0.32113 | 0.31728 | 0.32163 | 0.33993 | 0.35856 | 0.39595 | 0.44112 | 0.47383 | 0.48879 | 0.49447 | 0.49431 | 0.49602 | 0.49715 | 0.49355 | 0.48018 | 0.47083 | 0.48424 | 0.4631 | 0.43648 | 0.40427 | 0.37059 | 0.49715
2018-11-02 | 0.66009 | 0.30972 | 0.30608 | 0.30579 | 0.31064 | 0.32501 | 0.35021 | 0.39637 | 0.43652 | 0.45265 | 0.45491 | 0.45052 | 0.44647 | 0.44008 | 0.43719 | 0.4341 | 0.43531 | 0.45336 | 0.48887 | 0.47885 | 0.46113 | 0.43088 | 0.39224 | 0.35747 | 0.66009
2018-11-03 | 0.32856 | 0.31941 | 0.31427 | 0.31624 | 0.32743 | 0.36541 | 0.4275 | 0.45198 | 0.45829 | 0.46631 | 0.47596 | 0.48319 | 0.48403 | 0.48532 | 0.48261 | 0.47843 | 0.48215 | 0.49828 | 0.53212 | 0.521 | 0.49928 | 0.46201 | 0.41785 | 0.3749 | 0.53212
2018-11-04 | 0.34465 | 0.32522 | 0.31432 | 0.31218 | 0.31741 | 0.3477 | 0.39683 | 0.43151 | 0.45867 | 0.47956 | 0.4997 | 0.5172 | 0.52552 | 0.53304 | 0.53705 | 0.54027 | 0.53513 | 0.54352 | 0.57599 | 0.56592 | 0.54235 | 0.4999 | 0.45691 | 0.413 | 0.57599
2018-11-05 | 0.37694 | 0.35209 | 0.33917 | 0.33291 | 0.33709 | 0.365 | 0.41471 | 0.43143 | 0.47325 | 0.51323 | 0.5434 | 0.56667 | 0.582 | 0.58952 | 0.59237 | 0.58677 | 0.57737 | 0.58468 | 0.6128 | 0.59876 | 0.57469 | 0.53676 | 0.48658 | 0.43531 | 0.6128
2018-11-06 | 0.3942 | 0.36658 | 0.3487 | 0.33922 | 0.34068 | 0.36884 | 0.41659 | 0.4514 | 0.48712 | 0.52669 | 0.56529 | 0.59717 | 0.62153 | 0.63949 | 0.64806 | 0.64743 | 0.63293 | 0.61906 | 0.63385 | 0.61163 | 0.57582 | 0.52898 | 0.475 | 0.42411 | 0.64806
2018-11-07 | 0.38075 | 0.35246 | 0.33466 | 0.32773 | 0.3294 | 0.35442 | 0.40485 | 0.43665 | 0.47099 | 0.5091 | 0.54286 | 0.57273 | 0.59654 | 0.6158 | 0.62404 | 0.62228 | 0.6054 | 0.5917 | 0.60081 | 0.57127 | 0.54039 | 0.50379 | 0.46594 | 0.42574 | 0.62404
2018-11-08 | 0.38693 | 0.35848 | 0.3388 | 0.33023 | 0.32848 | 0.33587 | 0.35376 | 0.3886 | 0.44931 | 0.49769 | 0.5307 | 0.55673 | 0.57862 | 0.58773 | 0.58639 | 0.57653 | 0.56241 | 0.567 | 0.57712 | 0.55146 | 0.52502 | 0.49372 | 0.46013 | 0.4209 | 0.58773
2018-11-09 | 0.38701 | 0.35835 | 0.34147 | 0.33262 | 0.32898 | 0.33408 | 0.34657 | 0.37272 | 0.42249 | 0.46084 | 0.48223 | 0.49477 | 0.49631 | 0.49009 | 0.48361 | 0.47337 | 0.47103 | 0.49435 | 0.51474 | 0.49986 | 0.47789 | 0.44588 | 0.41179 | 0.3711 | 0.51474
2018-11-10 | 0.33838 | 0.32016 | 0.31043 | 0.30634 | 0.31139 | 0.33362 | 0.38718 | 0.42925 | 0.4481 | 0.47095 | 0.48842 | 0.50375 | 0.5149 | 0.52468 | 0.52949 | 0.53333 | 0.52898 | 0.53588 | 0.56141 | 0.54281 | 0.51369 | 0.47375 | 0.43138 | 0.38647 | 0.56141
2018-11-11 | 0.34611 | 0.32246 | 0.30964 | 0.30487 | 0.30826 | 0.32727 | 0.36487 | 0.40318 | 0.43669 | 0.46636 | 0.4885 | 0.50438 | 0.51904 | 0.53258 | 0.53889 | 0.54469 | 0.53964 | 0.54235 | 0.56696 | 0.54971 | 0.52054 | 0.48081 | 0.43606 | 0.3871 | 0.56696
2018-11-12 | 0.34548 | 0.32125 | 0.3101 | 0.30537 | 0.31114 | 0.33796 | 0.39236 | 0.42328 | 0.44467 | 0.47191 | 0.49965 | 0.5243 | 0.54591 | 0.56797 | 0.58276 | 0.58806 | 0.58008 | 0.57465 | 0.59483 | 0.57486 | 0.54457 | 0.50463 | 0.45687 | 0.40686 | 0.59483
2018-11-13 | 0.36596 | 0.34143 | 0.32643 | 0.32179 | 0.32551 | 0.35154 | 0.40419 | 0.43652 | 0.46519 | 0.50099 | 0.53274 | 0.5561 | 0.57874 | 0.59863 | 0.60749 | 0.6087 | 0.59767 | 0.59161 | 0.60887 | 0.58856 | 0.55727 | 0.51515 | 0.46406 | 0.41484 | 0.60887
2018-11-14 | 0.37293 | 0.34507 | 0.32965 | 0.32159 | 0.32351 | 0.34711 | 0.39967 | 0.43339 | 0.46255 | 0.4936 | 0.52059 | 0.53834 | 0.55497 | 0.56705 | 0.57411 | 0.57402 | 0.5617 | 0.55773 | 0.57085 | 0.54712 | 0.51937 | 0.48495 | 0.45044 | 0.4112 | 0.57411
2018-11-15 | 0.37561 | 0.34958 | 0.33483 | 0.32681 | 0.3261 | 0.3345 | 0.35484 | 0.38668 | 0.43581 | 0.47667 | 0.50312 | 0.52326 | 0.53659 | 0.54825 | 0.55255 | 0.55013 | 0.53955 | 0.53742 | 0.55259 | 0.52915 | 0.50375 | 0.47592 | 0.44638 | 0.41359 | 0.55259
2018-11-16 | 0.37962 | 0.35689 | 0.34206 | 0.33379 | 0.33132 | 0.33805 | 0.35025 | 0.37686 | 0.4374 | 0.49192 | 0.53099 | 0.5594 | 0.58309 | 0.59792 | 0.60419 | 0.60381 | 0.59203 | 0.58982 | 0.60795 | 0.5881 | 0.55781 | 0.52184 | 0.48336 | 0.43932 | 0.60795
2018-11-17 | 0.40247 | 0.37999 | 0.36717 | 0.36157 | 0.36884 | 0.39817 | 0.45186 | 0.48336 | 0.51996 | 0.56884 | 0.61501 | 0.64986 | 0.67467 | 0.68829 | 0.69009 | 0.68424 | 0.67187 | 0.67225 | 0.68474 | 0.6588 | 0.62011 | 0.56959 | 0.51804 | 0.46159 | 0.69009
2018-11-18 | 0.4171 | 0.38827 | 0.36834 | 0.35806 | 0.36057 | 0.3835 | 0.43987 | 0.47191 | 0.49777 | 0.52673 | 0.54607 | 0.54971 | 0.54043 | 0.53032 | 0.5167 | 0.50308 | 0.50371 | 0.53086 | 0.55815 | 0.54967 | 0.52894 | 0.49681 | 0.45403 | 0.41338 | 0.55815
2018-11-19 | 0.38438 | 0.37135 | 0.36604 | 0.36679 | 0.3792 | 0.41622 | 0.48821 | 0.51946 | 0.53203 | 0.53813 | 0.53483 | 0.52213 | 0.50672 | 0.49523 | 0.4862 | 0.48282 | 0.4885 | 0.521 | 0.55338 | 0.5482 | 0.5322 | 0.50078 | 0.46005 | 0.41806 | 0.55338
2018-11-20 | 0.38768 | 0.37243 | 0.36867 | 0.37026 | 0.38325 | 0.41981 | 0.4842 | 0.51002 | 0.50412 | 0.50404 | 0.50187 | 0.49919 | 0.49497 | 0.49067 | 0.48365 | 0.48023 | 0.48177 | 0.51185 | 0.54444 | 0.53955 | 0.52163 | 0.49088 | 0.45106 | 0.40899 | 0.54444
2018-11-21 | 0.37607 | 0.35559 | 0.34849 | 0.34423 | 0.35025 | 0.38894 | 0.44246 | 0.47312 | 0.48382 | 0.49414 | 0.50279 | 0.50475 | 0.49773 | 0.4928 | 0.48679 | 0.48131 | 0.48453 | 0.5086 | 0.52359 | 0.51018 | 0.49222 | 0.46727 | 0.43807 | 0.40423 | 0.52359
2018-11-22 | 0.37118 | 0.34983 | 0.33792 | 0.3337 | 0.33525 | 0.3449 | 0.36713 | 0.39696 | 0.44689 | 0.49013 | 0.5149 | 0.52823 | 0.52894 | 0.52811 | 0.52393 | 0.51678 | 0.51549 | 0.53588 | 0.55155 | 0.54102 | 0.5256 | 0.50262 | 0.47638 | 0.44033 | 0.55155
2018-11-23 | 0.40565 | 0.38304 | 0.36533 | 0.35522 | 0.35334 | 0.3594 | 0.3721 | 0.40109 | 0.46727 | 0.53233 | 0.57453 | 0.60172 | 0.6189 | 0.63135 | 0.6336 | 0.62938 | 0.61334 | 0.61977 | 0.63979 | 0.62633 | 0.60256 | 0.5673 | 0.52807 | 0.48879 | 0.63979
2018-11-24 | 0.43895 | 0.40857 | 0.39136 | 0.38472 | 0.39002 | 0.41672 | 0.46548 | 0.49949 | 0.54357 | 0.59216 | 0.63598 | 0.68115 | 0.71574 | 0.73325 | 0.74148 | 0.73839 | 0.71888 | 0.71169 | 0.72611 | 0.70166 | 0.66928 | 0.62061 | 0.57615 | 0.52025 | 0.74148
2018-11-25 | 0.47145 | 0.43769 | 0.41873 | 0.41129 | 0.41313 | 0.43936 | 0.48779 | 0.52046 | 0.56383 | 0.60904 | 0.64831 | 0.6743 | 0.689 | 0.69962 | 0.69832 | 0.69118 | 0.67572 | 0.68077 | 0.69485 | 0.67614 | 0.64522 | 0.60853 | 0.56404 | 0.51988 | 0.69962
2018-11-26 | 0.47651 | 0.44697 | 0.42762 | 0.41751 | 0.4176 | 0.43272 | 0.46531 | 0.49623 | 0.533 | 0.55894 | 0.5607 | 0.55464 | 0.5452 | 0.5304 | 0.51256 | 0.4951 | 0.48562 | 0.50509 | 0.52648 | 0.51419 | 0.49385 | 0.47258 | 0.44429 | 0.40828 | 0.5607
2018-11-27 | 0.37519 | 0.35326 | 0.3421 | 0.33926 | 0.34222 | 0.35568 | 0.38091 | 0.41772 | 0.45988 | 0.48745 | 0.50379 | 0.51018 | 0.50977 | 0.50103 | 0.49105 | 0.47542 | 0.45491 | 0.44643 | 0.45253 | 0.4364 | 0.42533 | 0.41534 | 0.39959 | 0.37665 | 0.51018
2018-11-28 | 0.35472 | 0.34164 | 0.33638 | 0.33817 | 0.34761 | 0.36742 | 0.399 | 0.43226 | 0.46376 | 0.48152 | 0.4839 | 0.47601 | 0.46623 | 0.45737 | 0.44914 | 0.44379 | 0.44421 | 0.47141 | 0.50237 | 0.4936 | 0.48006 | 0.47174 | 0.44371 | 0.41187 | 0.50237
2018-11-29 | 0.38321 | 0.36767 | 0.3594 | 0.35835 | 0.36324 | 0.37348 | 0.39583 | 0.4242 | 0.45436 | 0.46815 | 0.46991 | 0.46878 | 0.46473 | 0.46021 | 0.4547 | 0.44923 | 0.44438 | 0.46322 | 0.4875 | 0.47659 | 0.45963 | 0.44028 | 0.41417 | 0.38233 | 0.4875
2018-11-30 | 0.35083 | 0.33036 | 0.32004 | 0.31611 | 0.31803 | 0.32622 | 0.34197 | 0.36688 | 0.40899 | 0.44099 | 0.46076 | 0.47367 | 0.48307 | 0.48787 | 0.48883 | 0.48562 | 0.48089 | 0.49974 | 0.53287 | 0.52138 | 0.5022 | 0.473 | 0.43769 | 0.39299 | 0.53287
2018-12-01 | 0.35823 | 0.3355 | 0.32418 | 0.32058 | 0.32668 | 0.35647 | 0.41133 | 0.44162 | 0.46748 | 0.49585 | 0.52547 | 0.54845 | 0.55911 | 0.56312 | 0.55811 | 0.549 | 0.54047 | 0.5599 | 0.59153 | 0.58179 | 0.5589 | 0.52188 | 0.47789 | 0.42654 | 0.59153
2018-12-02 | 0.38288 | 0.35559 | 0.33821 | 0.33136 | 0.33608 | 0.36316 | 0.41964 | 0.44856 | 0.46928 | 0.49907 | 0.52752 | 0.54486 | 0.55485 | 0.56107 | 0.55894 | 0.55167 | 0.54177 | 0.56299 | 0.59391 | 0.58271 | 0.56011 | 0.52468 | 0.47864 | 0.427 | 0.59391
2018-12-03 | 0.38229 | 0.35317 | 0.33763 | 0.33023 | 0.33341 | 0.36082 | 0.42223 | 0.4486 | 0.47421 | 0.51035 | 0.53788 | 0.56011 | 0.57674 | 0.58451 | 0.59053 | 0.59333 | 0.57962 | 0.58606 | 0.61326 | 0.59872 | 0.57264 | 0.53429 | 0.48733 | 0.4326 | 0.61326
2018-12-04 | 0.38722 | 0.35935 | 0.34331 | 0.33642 | 0.34043 | 0.36863 | 0.42366 | 0.45374 | 0.47856 | 0.51378 | 0.54177 | 0.56504 | 0.58301 | 0.59094 | 0.59621 | 0.59817 | 0.58338 | 0.59044 | 0.61911 | 0.60691 | 0.58288 | 0.54758 | 0.49874 | 0.44546 | 0.61911
2018-12-05 | 0.39938 | 0.36771 | 0.3505 | 0.34344 | 0.34619 | 0.37344 | 0.42863 | 0.45896 | 0.489 | 0.53066 | 0.56149 | 0.58217 | 0.59349 | 0.59245 | 0.59132 | 0.59546 | 0.5899 | 0.59721 | 0.61275 | 0.59374 | 0.56905 | 0.53809 | 0.50233 | 0.45771 | 0.61275
2018-12-06 | 0.41321 | 0.38171 | 0.36195 | 0.34958 | 0.34456 | 0.35012 | 0.36759 | 0.39541 | 0.45261 | 0.50826 | 0.54883 | 0.57549 | 0.59341 | 0.60444 | 0.60937 | 0.6054 | 0.58739 | 0.57966 | 0.59191 | 0.56354 | 0.53584 | 0.5068 | 0.47028 | 0.42716 | 0.60937
2018-12-07 | 0.38271 | 0.35476 | 0.33633 | 0.32434 | 0.321 | 0.32572 | 0.33801 | 0.36036 | 0.41334 | 0.46573 | 0.49911 | 0.52071 | 0.53199 | 0.53818 | 0.54001 | 0.53199 | 0.521 | 0.53391 | 0.56692 | 0.54528 | 0.52197 | 0.48808 | 0.44392 | 0.39512 | 0.56692
2018-12-08 | 0.35351 | 0.32819 | 0.31549 | 0.31106 | 0.31615 | 0.34427 | 0.3985 | 0.42842 | 0.4481 | 0.47112 | 0.49101 | 0.50396 | 0.51236 | 0.51912 | 0.52226 | 0.52602 | 0.52456 | 0.54286 | 0.57816 | 0.56817 | 0.54031 | 0.5012 | 0.45478 | 0.40017 | 0.57816
2018-12-09 | 0.35635 | 0.33299 | 0.32121 | 0.31791 | 0.3233 | 0.3543 | 0.41801 | 0.44755 | 0.46264 | 0.47484 | 0.48206 | 0.48361 | 0.48298 | 0.48023 | 0.47584 | 0.46941 | 0.47258 | 0.50575 | 0.54804 | 0.54344 | 0.52556 | 0.49543 | 0.45198 | 0.40636 | 0.54804
2018-12-10 | 0.37114 | 0.35572 | 0.34849 | 0.35275 | 0.36491 | 0.41079 | 0.48812 | 0.53078 | 0.52694 | 0.51382 | 0.50346 | 0.4908 | 0.47998 | 0.47254 | 0.46339 | 0.45988 | 0.46485 | 0.50371 | 0.55593 | 0.55589 | 0.54841 | 0.52247 | 0.4824 | 0.4379 | 0.55593
2018-12-11 | 0.40849 | 0.39453 | 0.39128 | 0.39236 | 0.40686 | 0.45198 | 0.53233 | 0.56947 | 0.55376 | 0.53772 | 0.51779 | 0.50446 | 0.49121 | 0.48119 | 0.47174 | 0.46778 | 0.47304 | 0.50977 | 0.55326 | 0.54987 | 0.53939 | 0.51315 | 0.46936 | 0.42545 | 0.56947
2018-12-12 | 0.39336 | 0.37674 | 0.37089 | 0.37018 | 0.38472 | 0.42813 | 0.49978 | 0.53429 | 0.53671 | 0.53625 | 0.5279 | 0.51716 | 0.50417 | 0.49314 | 0.48177 | 0.47776 | 0.48407 | 0.52368 | 0.56065 | 0.55389 | 0.54565 | 0.52543 | 0.4956 | 0.4595 | 0.56065
2018-12-13 | 0.42658 | 0.41221 | 0.4054 | 0.40623 | 0.41405 | 0.43515 | 0.46757 | 0.506 | 0.52865 | 0.52731 | 0.51135 | 0.4966 | 0.48562 | 0.47471 | 0.46502 | 0.45992 | 0.4585 | 0.48411 | 0.51511 | 0.50521 | 0.4946 | 0.47889 | 0.45507 | 0.42871 | 0.52865
2018-12-14 | 0.40164 | 0.38467 | 0.37882 | 0.37933 | 0.38522 | 0.4021 | 0.43281 | 0.47083 | 0.50534 | 0.50922 | 0.49539 | 0.48486 | 0.47667 | 0.46991 | 0.46535 | 0.4613 | 0.46147 | 0.48833 | 0.53249 | 0.52706 | 0.51453 | 0.49134 | 0.4519 | 0.41321 | 0.53249
2018-12-15 | 0.38405 | 0.36926 | 0.36813 | 0.3713 | 0.38843 | 0.4321 | 0.50981 | 0.54967 | 0.54632 | 0.52681 | 0.51244 | 0.50095 | 0.49823 | 0.49389 | 0.48867 | 0.48787 | 0.48913 | 0.51825 | 0.56329 | 0.55877 | 0.54127 | 0.50931 | 0.46535 | 0.41889 | 0.56329
2018-12-16 | 0.38355 | 0.36675 | 0.36061 | 0.36282 | 0.37506 | 0.41605 | 0.49109 | 0.52552 | 0.52192 | 0.50839 | 0.4994 | 0.49481 | 0.49326 | 0.49397 | 0.49314 | 0.49422 | 0.49485 | 0.51703 | 0.55735 | 0.54996 | 0.52827 | 0.49155 | 0.4478 | 0.39967 | 0.55735
2018-12-17 | 0.35956 | 0.33846 | 0.33011 | 0.32915 | 0.33997 | 0.37623 | 0.44108 | 0.47584 | 0.47931 | 0.48336 | 0.48699 | 0.48913 | 0.49339 | 0.49861 | 0.50408 | 0.5096 | 0.50688 | 0.52677 | 0.56187 | 0.55079 | 0.52727 | 0.49594 | 0.45136 | 0.40097 | 0.56187
2018-12-18 | 0.36149 | 0.3398 | 0.3309 | 0.33044 | 0.34055 | 0.37465 | 0.44033 | 0.47642 | 0.48896 | 0.49635 | 0.49945 | 0.4969 | 0.49648 | 0.50433 | 0.50914 | 0.51035 | 0.50789 | 0.52618 | 0.56145 | 0.5505 | 0.5327 | 0.50045 | 0.45829 | 0.41058 | 0.56145
2018-12-19 | 0.37235 | 0.35154 | 0.34143 | 0.33984 | 0.34891 | 0.38183 | 0.4412 | 0.4796 | 0.49284 | 0.50036 | 0.50697 | 0.50956 | 0.50926 | 0.51165 | 0.5116 | 0.51064 | 0.50584 | 0.52013 | 0.55013 | 0.53442 | 0.51307 | 0.48628 | 0.45545 | 0.41471 | 0.55013
2018-12-20 | 0.37803 | 0.35359 | 0.34101 | 0.33525 | 0.33466 | 0.34703 | 0.37072 | 0.40218 | 0.44317 | 0.4745 | 0.49176 | 0.49485 | 0.50726 | 0.50872 | 0.51018 | 0.5106 | 0.50592 | 0.51858 | 0.54528 | 0.52547 | 0.50346 | 0.47835 | 0.44693 | 0.40811 | 0.54528
2018-12-21 | 0.3688 | 0.34114 | 0.32418 | 0.31632 | 0.31523 | 0.32096 | 0.336 | 0.36111 | 0.41029 | 0.45896 | 0.48862 | 0.504 | 0.51988 | 0.5246 | 0.52105 | 0.51444 | 0.50905 | 0.52961 | 0.56124 | 0.5485 | 0.53053 | 0.50408 | 0.46715 | 0.41964 | 0.56124
2018-12-22 | 0.37623 | 0.34745 | 0.33015 | 0.32159 | 0.32418 | 0.34486 | 0.381 | 0.41701 | 0.46485 | 0.51052 | 0.54825 | 0.5721 | 0.5881 | 0.59993 | 0.60816 | 0.60406 | 0.58986 | 0.59817 | 0.62959 | 0.61259 | 0.58714 | 0.55652 | 0.5149 | 0.45829 | 0.62959
2018-12-23 | 0.40916 | 0.37469 | 0.35271 | 0.34168 | 0.34319 | 0.3637 | 0.39867 | 0.43402 | 0.4847 | 0.53584 | 0.57352 | 0.60018 | 0.6194 | 0.627 | 0.60991 | 0.59153 | 0.57519 | 0.58159 | 0.61079 | 0.59425 | 0.57043 | 0.55209 | 0.52518 | 0.49021 | 0.627
2018-12-24 | 0.44755 | 0.41451 | 0.39299 | 0.3835 | 0.38133 | 0.3942 | 0.41818 | 0.44856 | 0.50617 | 0.57035 | 0.61982 | 0.65278 | 0.66987 | 0.67283 | 0.67505 | 0.66703 | 0.65834 | 0.66623 | 0.67359 | 0.63548 | 0.59964 | 0.56934 | 0.53985 | 0.49765 | 0.67505
2018-12-25 | 0.4547 | 0.42148 | 0.39178 | 0.36892 | 0.35321 | 0.35041 | 0.35693 | 0.37506 | 0.41801 | 0.46176 | 0.48921 | 0.503 | 0.5078 | 0.50433 | 0.49694 | 0.48135 | 0.46473 | 0.47187 | 0.49159 | 0.48135 | 0.47304 | 0.46 | 0.43627 | 0.40251 | 0.5078
2018-12-26 | 0.36746 | 0.34306 | 0.33191 | 0.32601 | 0.32877 | 0.34369 | 0.36917 | 0.39875 | 0.4359 | 0.47045 | 0.49694 | 0.50784 | 0.50755 | 0.50116 | 0.49723 | 0.49443 | 0.4969 | 0.52506 | 0.55501 | 0.54423 | 0.5241 | 0.49915 | 0.46903 | 0.42863 | 0.55501
2018-12-27 | 0.38785 | 0.35823 | 0.33872 | 0.32977 | 0.32982 | 0.33642 | 0.35376 | 0.37306 | 0.41827 | 0.47237 | 0.51419 | 0.5411 | 0.55781 | 0.56324 | 0.56345 | 0.55464 | 0.5439 | 0.55631 | 0.58401 | 0.56659 | 0.54148 | 0.51449 | 0.47897 | 0.43406 | 0.58401
2018-12-28 | 0.39161 | 0.36002 | 0.34001 | 0.32856 | 0.32292 | 0.32551 | 0.33838 | 0.35514 | 0.41108 | 0.47158 | 0.51587 | 0.54887 | 0.57177 | 0.58777 | 0.59621 | 0.59592 | 0.58677 | 0.58409 | 0.61008 | 0.58982 | 0.56199 | 0.52999 | 0.48892 | 0.43748 | 0.61008
2018-12-29 | 0.39341 | 0.36316 | 0.3449 | 0.33688 | 0.33775 | 0.35376 | 0.38701 | 0.41831 | 0.46899 | 0.52618 | 0.57148 | 0.60076 | 0.61601 | 0.62282 | 0.62784 | 0.63039 | 0.62036 | 0.61752 | 0.6463 | 0.62445 | 0.59479 | 0.55455 | 0.51056 | 0.45562 | 0.6463
2018-12-30 | 0.40586 | 0.37327 | 0.35346 | 0.34268 | 0.34164 | 0.35768 | 0.38868 | 0.41902 | 0.46314 | 0.51219 | 0.55606 | 0.5917 | 0.61388 | 0.62942 | 0.63364 | 0.62846 | 0.61631 | 0.61618 | 0.64459 | 0.62303 | 0.59629 | 0.55802 | 0.51678 | 0.46615 | 0.64459
2018-12-31 | 0.41906 | 0.38518 | 0.36449 | 0.35334 | 0.35238 | 0.36642 | 0.39512 | 0.42742 | 0.46991 | 0.5134 | 0.54799 | 0.56805 | 0.57281 | 0.5759 | 0.57494 | 0.56893 | 0.57064 | 0.6003 | 0.62575 | 0.59579 | 0.5599 | 0.52063 | 0.4806 | 0.44768 | 0.62575
Max | 0.66009 | 0.58568 | 0.5538 | 0.53421 | 0.53951 | 0.59395 | 0.6862 | 0.73078 | 0.70547 | 0.70659 | 0.7678 | 0.82341 | 0.86766 | 0.90572 | 0.92699 | 0.9485 | 0.94926 | 0.94048 | 0.92243 | 0.88671 | 0.86473 | 0.8288 | 0.76254 | 0.69226

## CLEF
OPC 012929
FPL RC-16
CLEF = (Hourly Loads p.u of Peak) **2
Date | HR-1 | HR-2 | HR-3 | HR-4 | HR-5 | HR-6 | HR-7 | HR-8 | HR-9 | HR-10 | HR-11 | HR-12 | HR-13 | HR-14 | HR-15 | HR-16 | HR-17 | HR-18 | HR-19 | HR-20 | HR-21 | HR-22 | HR-23 | HR-24
2018-01-01 | 0.16714 | 0.1552 | 0.13955 | 0.12935 | 0.12503 | 0.12713 | 0.13383 | 0.13948 | 0.16594 | 0.21241 | 0.2611 | 0.29733 | 0.31989 | 0.32898 | 0.32625 | 0.31795 | 0.30948 | 0.31673 | 0.34823 | 0.32931 | 0.30167 | 0.27232 | 0.23562 | 0.19319
2018-01-02 | 0.15728 | 0.1362 | 0.12288 | 0.11675 | 0.11504 | 0.12212 | 0.15114 | 0.17698 | 0.21913 | 0.27446 | 0.32349 | 0.35941 | 0.38625 | 0.40549 | 0.41426 | 0.40981 | 0.39345 | 0.38661 | 0.41587 | 0.38479 | 0.34488 | 0.30296 | 0.25922 | 0.21234
2018-01-03 | 0.17178 | 0.14541 | 0.13016 | 0.12305 | 0.12247 | 0.1307 | 0.15642 | 0.18268 | 0.21589 | 0.24624 | 0.26448 | 0.27053 | 0.27058 | 0.2656 | 0.26063 | 0.25757 | 0.256 | 0.28106 | 0.32102 | 0.3099 | 0.2877 | 0.26195 | 0.22897 | 0.19363
2018-01-04 | 0.16455 | 0.1464 | 0.13604 | 0.13167 | 0.13222 | 0.13886 | 0.15359 | 0.17414 | 0.20835 | 0.24113 | 0.2614 | 0.26594 | 0.26165 | 0.25486 | 0.24628 | 0.23843 | 0.24006 | 0.26487 | 0.28757 | 0.27214 | 0.25309 | 0.23066 | 0.20399 | 0.1746
2018-01-05 | 0.14692 | 0.12854 | 0.11758 | 0.1115 | 0.11027 | 0.11549 | 0.12833 | 0.14398 | 0.17701 | 0.21245 | 0.25452 | 0.28239 | 0.29742 | 0.30222 | 0.30181 | 0.29619 | 0.28851 | 0.29496 | 0.33219 | 0.31298 | 0.28703 | 0.2499 | 0.20972 | 0.1705
2018-01-06 | 0.13521 | 0.11752 | 0.10757 | 0.10412 | 0.10686 | 0.12343 | 0.16151 | 0.18819 | 0.21415 | 0.25166 | 0.29347 | 0.32164 | 0.34469 | 0.35731 | 0.35338 | 0.33849 | 0.32468 | 0.34547 | 0.38174 | 0.36067 | 0.31583 | 0.26474 | 0.22527 | 0.18537
2018-01-07 | 0.15748 | 0.143 | 0.13942 | 0.14228 | 0.15602 | 0.18942 | 0.2605 | 0.31776 | 0.34488 | 0.36147 | 0.35487 | 0.33664 | 0.3196 | 0.30314 | 0.29049 | 0.28968 | 0.30702 | 0.36585 | 0.43865 | 0.44387 | 0.42481 | 0.37757 | 0.32244 | 0.27223
2018-01-08 | 0.23651 | 0.21881 | 0.21264 | 0.20992 | 0.21648 | 0.24711 | 0.3099 | 0.34278 | 0.33941 | 0.33941 | 0.33524 | 0.31852 | 0.29633 | 0.27604 | 0.25914 | 0.25263 | 0.2574 | 0.28672 | 0.32287 | 0.3112 | 0.28489 | 0.24471 | 0.20192 | 0.16121
2018-01-09 | 0.13149 | 0.11732 | 0.11091 | 0.10861 | 0.11318 | 0.1331 | 0.17867 | 0.21218 | 0.22329 | 0.24397 | 0.25867 | 0.26681 | 0.26754 | 0.26362 | 0.25867 | 0.25693 | 0.26003 | 0.2852 | 0.32525 | 0.31748 | 0.29302 | 0.25617 | 0.21527 | 0.17254
2018-01-10 | 0.13864 | 0.11913 | 0.10859 | 0.10474 | 0.10702 | 0.12355 | 0.16516 | 0.19632 | 0.22168 | 0.25439 | 0.28191 | 0.30016 | 0.31055 | 0.31847 | 0.31875 | 0.31701 | 0.31457 | 0.31833 | 0.35273 | 0.3333 | 0.30356 | 0.26836 | 0.23408 | 0.19773
2018-01-11 | 0.15914 | 0.13709 | 0.12311 | 0.1166 | 0.11527 | 0.12159 | 0.13638 | 0.15632 | 0.20584 | 0.26599 | 0.31223 | 0.34283 | 0.36646 | 0.38117 | 0.38723 | 0.38391 | 0.36757 | 0.35452 | 0.37598 | 0.34838 | 0.31405 | 0.27573 | 0.23863 | 0.20023
2018-01-12 | 0.16266 | 0.13839 | 0.12423 | 0.11635 | 0.1125 | 0.11484 | 0.12435 | 0.13753 | 0.17251 | 0.21257 | 0.24351 | 0.26217 | 0.27916 | 0.29017 | 0.29329 | 0.28963 | 0.2812 | 0.27538 | 0.3086 | 0.29674 | 0.27044 | 0.23566 | 0.19903 | 0.16034
2018-01-13 | 0.13149 | 0.11672 | 0.11013 | 0.10947 | 0.11555 | 0.13995 | 0.19216 | 0.22734 | 0.24207 | 0.26247 | 0.28115 | 0.29551 | 0.30892 | 0.31946 | 0.3263 | 0.33123 | 0.32835 | 0.33417 | 0.3769 | 0.36722 | 0.33013 | 0.28195 | 0.23356 | 0.18437
2018-01-14 | 0.14644 | 0.12547 | 0.11495 | 0.10975 | 0.1118 | 0.1304 | 0.17558 | 0.20565 | 0.23146 | 0.26914 | 0.30264 | 0.32301 | 0.33369 | 0.33422 | 0.32965 | 0.31748 | 0.31419 | 0.32898 | 0.36965 | 0.35876 | 0.32596 | 0.28168 | 0.23114 | 0.18218
2018-01-15 | 0.14481 | 0.12579 | 0.11569 | 0.11236 | 0.11464 | 0.13561 | 0.18487 | 0.21702 | 0.22901 | 0.24541 | 0.25414 | 0.25477 | 0.24782 | 0.24105 | 0.2336 | 0.2301 | 0.23376 | 0.26041 | 0.29742 | 0.28887 | 0.26655 | 0.23348 | 0.19444 | 0.15553
2018-01-16 | 0.12941 | 0.11646 | 0.11276 | 0.11413 | 0.12238 | 0.15212 | 0.21609 | 0.26341 | 0.27192 | 0.27503 | 0.27494 | 0.26676 | 0.25448 | 0.24178 | 0.23098 | 0.22575 | 0.2311 | 0.26487 | 0.3443 | 0.36077 | 0.35696 | 0.33422 | 0.29911 | 0.26229
2018-01-17 | 0.23773 | 0.22838 | 0.22974 | 0.23773 | 0.25604 | 0.30549 | 0.40363 | 0.46956 | 0.45988 | 0.41313 | 0.36454 | 0.31786 | 0.28151 | 0.25372 | 0.23513 | 0.22519 | 0.22698 | 0.25579 | 0.30573 | 0.30195 | 0.28986 | 0.26668 | 0.24113 | 0.21191
2018-01-18 | 0.18562 | 0.17449 | 0.17126 | 0.17265 | 0.1803 | 0.1984 | 0.23098 | 0.27617 | 0.30883 | 0.31256 | 0.30094 | 0.27779 | 0.25444 | 0.23432 | 0.21718 | 0.20812 | 0.20824 | 0.23259 | 0.29098 | 0.3019 | 0.30186 | 0.29692 | 0.28404 | 0.26612
2018-01-19 | 0.25364 | 0.24945 | 0.25267 | 0.26238 | 0.27837 | 0.30522 | 0.34927 | 0.40634 | 0.44087 | 0.41383 | 0.35776 | 0.30702 | 0.26927 | 0.24306 | 0.22294 | 0.20736 | 0.20282 | 0.21609 | 0.2653 | 0.26204 | 0.24974 | 0.22571 | 0.20248 | 0.17192
2018-01-20 | 0.15114 | 0.14177 | 0.13967 | 0.14234 | 0.15375 | 0.17772 | 0.22081 | 0.26569 | 0.28302 | 0.27516 | 0.26465 | 0.25473 | 0.24327 | 0.23461 | 0.2281 | 0.22452 | 0.22515 | 0.24059 | 0.28681 | 0.28297 | 0.25841 | 0.22444 | 0.18588 | 0.14855
2018-01-21 | 0.1232 | 0.11086 | 0.10596 | 0.10593 | 0.1115 | 0.1354 | 0.18819 | 0.2231 | 0.23102 | 0.23348 | 0.23599 | 0.2359 | 0.23493 | 0.23062 | 0.22686 | 0.22306 | 0.22452 | 0.24479 | 0.28725 | 0.28564 | 0.26238 | 0.22722 | 0.18884 | 0.15326
2018-01-22 | 0.12779 | 0.11881 | 0.11738 | 0.12188 | 0.1358 | 0.17331 | 0.25129 | 0.30739 | 0.2987 | 0.30948 | 0.30186 | 0.28685 | 0.27018 | 0.25141 | 0.23859 | 0.23178 | 0.23643 | 0.26901 | 0.34833 | 0.37184 | 0.37113 | 0.34862 | 0.31485 | 0.27674
2018-01-23 | 0.25503 | 0.2499 | 0.25532 | 0.26758 | 0.29107 | 0.35278 | 0.47088 | 0.53405 | 0.49768 | 0.43987 | 0.38817 | 0.33466 | 0.29297 | 0.26033 | 0.23949 | 0.22913 | 0.22998 | 0.25473 | 0.31904 | 0.33152 | 0.32112 | 0.29279 | 0.25099 | 0.21253
2018-01-24 | 0.18642 | 0.17761 | 0.17705 | 0.18186 | 0.19647 | 0.23953 | 0.32544 | 0.37567 | 0.37516 | 0.35856 | 0.33781 | 0.30878 | 0.28408 | 0.26367 | 0.24745 | 0.2383 | 0.24068 | 0.26277 | 0.31551 | 0.31682 | 0.30268 | 0.27956 | 0.25179 | 0.21921
2018-01-25 | 0.19378 | 0.18154 | 0.17673 | 0.17811 | 0.18462 | 0.20019 | 0.22901 | 0.26789 | 0.30693 | 0.30462 | 0.28186 | 0.25799 | 0.23965 | 0.22563 | 0.21512 | 0.20732 | 0.20395 | 0.21403 | 0.2502 | 0.24633 | 0.22986 | 0.21045 | 0.18534 | 0.15861
2018-01-26 | 0.13725 | 0.12399 | 0.11852 | 0.11623 | 0.11798 | 0.12627 | 0.14278 | 0.16714 | 0.20448 | 0.22511 | 0.23469 | 0.23368 | 0.23311 | 0.23259 | 0.2295 | 0.22622 | 0.22559 | 0.23712 | 0.27551 | 0.2742 | 0.25032 | 0.21831 | 0.18379 | 0.14724
2018-01-27 | 0.12014 | 0.10536 | 0.099189 | 0.097564 | 0.10309 | 0.12388 | 0.1732 | 0.20421 | 0.21784 | 0.23432 | 0.25376 | 0.26694 | 0.27793 | 0.28712 | 0.29139 | 0.29683 | 0.29929 | 0.30383 | 0.34131 | 0.33688 | 0.3025 | 0.25465 | 0.20629 | 0.1593
2018-01-28 | 0.12452 | 0.10724 | 0.099268 | 0.096185 | 0.10001 | 0.11965 | 0.16526 | 0.1977 | 0.21303 | 0.23457 | 0.25782 | 0.27485 | 0.29112 | 0.30499 | 0.31536 | 0.32334 | 0.32611 | 0.3274 | 0.36062 | 0.35462 | 0.32244 | 0.27227 | 0.22448 | 0.1768
2018-01-29 | 0.13973 | 0.12075 | 0.112 | 0.10894 | 0.11312 | 0.13515 | 0.18372 | 0.2203 | 0.23708 | 0.26093 | 0.27929 | 0.29496 | 0.2265 | 0.29229 | 0.28614 | 0.2886 | 0.29774 | 0.32235 | 0.35467 | 0.34655 | 0.32453 | 0.28515 | 0.24035 | 0.19381
2018-01-30 | 0.16276 | 0.14541 | 0.13709 | 0.1353 | 0.14168 | 0.16779 | 0.22822 | 0.26932 | 0.29103 | 0.31237 | 0.32439 | 0.32282 | 0.31593 | 0.3079 | 0.29906 | 0.29401 | 0.29742 | 0.31814 | 0.35641 | 0.3503 | 0.32306 | 0.2852 | 0.23635 | 0.19055
2018-01-31 | 0.15954 | 0.14281 | 0.13623 | 0.13347 | 0.13774 | 0.16205 | 0.21753 | 0.25461 | 0.27023 | 0.29089 | 0.30642 | 0.31518 | 0.31701 | 0.31466 | 0.31032 | 0.31284 | 0.30925 | 0.31499 | 0.34263 | 0.33181 | 0.3031 | 0.26845 | 0.23078 | 0.19066
2018-02-01 | 0.15675 | 0.13561 | 0.12311 | 0.11678 | 0.11564 | 0.12118 | 0.13647 | 0.16021 | 0.20751 | 0.25744 | 0.29365 | 0.31447 | 0.33027 | 0.33995 | 0.34606 | 0.34823 | 0.34292 | 0.33003 | 0.34508 | 0.33162 | 0.29774 | 0.2617 | 0.22531 | 0.18692
2018-02-02 | 0.15261 | 0.1314 | 0.11867 | 0.1118 | 0.10944 | 0.11164 | 0.12116 | 0.13864 | 0.18812 | 0.24018 | 0.27547 | 0.29897 | 0.3295 | 0.35194 | 0.36818 | 0.37578 | 0.37485 | 0.36026 | 0.36001 | 0.32711 | 0.2976 | 0.28027 | 0.25761 | 0.20633
2018-02-03 | 0.16482 | 0.13386 | 0.12267 | 0.11806 | 0.12101 | 0.14108 | 0.1862 | 0.21683 | 0.2467 | 0.28743 | 0.33123 | 0.36338 | 0.38937 | 0.41013 | 0.42558 | 0.43192 | 0.42117 | 0.40682 | 0.42924 | 0.41814 | 0.3723 | 0.32273 | 0.26594 | 0.21068
2018-02-04 | 0.16861 | 0.14599 | 0.13316 | 0.12713 | 0.12845 | 0.1466 | 0.19256 | 0.22266 | 0.25082 | 0.29433 | 0.3363 | 0.36889 | 0.39539 | 0.41249 | 0.42416 | 0.43094 | 0.42465 | 0.40724 | 0.43006 | 0.42574 | 0.38516 | 0.332 | 0.27757 | 0.2214
2018-02-05 | 0.17885 | 0.15326 | 0.1403 | 0.13368 | 0.13481 | 0.15553 | 0.20527 | 0.23651 | 0.26582 | 0.31279 | 0.35686 | 0.39161 | 0.41421 | 0.43039 | 0.44048 | 0.43583 | 0.4176 | 0.40262 | 0.42318 | 0.4119 | 0.37189 | 0.32088 | 0.26409 | 0.2093
2018-02-06 | 0.16775 | 0.14218 | 0.12965 | 0.12343 | 0.1252 | 0.14357 | 0.19099 | 0.22136 | 0.25087 | 0.28708 | 0.32055 | 0.34611 | 0.36757 | 0.38812 | 0.39686 | 0.40219 | 0.39712 | 0.39072 | 0.41335 | 0.40762 | 0.36854 | 0.31861 | 0.26315 | 0.20683
2018-02-07 | 0.16455 | 0.14108 | 0.12603 | 0.11939 | 0.1204 | 0.13889 | 0.18505 | 0.21663 | 0.23798 | 0.26698 | 0.29596 | 0.3242 | 0.34151 | 0.34439 | 0.36742 | 0.37404 | 0.37215 | 0.36732 | 0.3697 | 0.3505 | 0.32334 | 0.28031 | 0.24298 | 0.20034
2018-02-08 | 0.16489 | 0.14039 | 0.12672 | 0.12008 | 0.11959 | 0.12503 | 0.1407 | 0.16418 | 0.21253 | 0.26845 | 0.31443 | 0.34434 | 0.36504 | 0.37531 | 0.3819 | 0.37778 | 0.36864 | 0.35537 | 0.36368 | 0.3468 | 0.31298 | 0.27674 | 0.23953 | 0.20222
2018-02-09 | 0.16632 | 0.14215 | 0.12842 | 0.12153 | 0.12002 | 0.12464 | 0.13586 | 0.15405 | 0.19026 | 0.22666 | 0.25246 | 0.26633 | 0.27947 | 0.28757 | 0.29116 | 0.28815 | 0.28102 | 0.27885 | 0.30508 | 0.30915 | 0.27956 | 0.24224 | 0.20512 | 0.16272
2018-02-10 | 0.13131 | 0.11504 | 0.10861 | 0.1076 | 0.11278 | 0.1357 | 0.18696 | 0.22046 | 0.23566 | 0.25528 | 0.27788 | 0.29311 | 0.30758 | 0.31908 | 0.32392 | 0.32898 | 0.32989 | 0.32625 | 0.35258 | 0.35926 | 0.32458 | 0.27819 | 0.22794 | 0.17895
2018-02-11 | 0.14395 | 0.12402 | 0.1149 | 0.11197 | 0.11578 | 0.13759 | 0.18913 | 0.22258 | 0.24059 | 0.26577 | 0.28945 | 0.31209 | 0.33176 | 0.34961 | 0.36062 | 0.37215 | 0.37552 | 0.36894 | 0.38905 | 0.39161 | 0.35926 | 0.30066 | 0.24421 | 0.19001
2018-02-12 | 0.14852 | 0.1277 | 0.11572 | 0.11088 | 0.11343 | 0.13243 | 0.17991 | 0.20904 | 0.23303 | 0.2656 | 0.29569 | 0.32112 | 0.34068 | 0.35706 | 0.36132 | 0.35472 | 0.34592 | 0.34754 | 0.3804 | 0.3721 | 0.3379 | 0.29013 | 0.22937 | 0.17498
2018-02-13 | 0.14005 | 0.11997 | 0.11113 | 0.10779 | 0.11166 | 0.1324 | 0.18218 | 0.21683 | 0.23623 | 0.24903 | 0.26076 | 0.26495 | 0.26728 | 0.26659 | 0.26422 | 0.26054 | 0.25689 | 0.25697 | 0.2877 | 0.30007 | 0.28128 | 0.25028 | 0.21153 | 0.17119
2018-02-14 | 0.1424 | 0.12914 | 0.12482 | 0.12627 | 0.13577 | 0.16857 | 0.24125 | 0.29419 | 0.29311 | 0.27952 | 0.26875 | 0.25112 | 0.23749 | 0.22838 | 0.2227 | 0.2225 | 0.22235 | 0.22654 | 0.25575 | 0.26165 | 0.24331 | 0.21948 | 0.19411 | 0.16584
2018-02-15 | 0.1431 | 0.1295 | 0.12256 | 0.12005 | 0.12113 | 0.12971 | 0.14733 | 0.17407 | 0.20557 | 0.22706 | 0.23969 | 0.241 | 0.23513 | 0.22925 | 0.22412 | 0.22223 | 0.22117 | 0.224 | 0.24649 | 0.25191 | 0.23469 | 0.2128 | 0.18859 | 0.1594
2018-02-16 | 0.13669 | 0.12458 | 0.12302 | 0.12444 | 0.12731 | 0.14023 | 0.16452 | 0.20049 | 0.2321 | 0.24174 | 0.23712 | 0.22654 | 0.22066 | 0.2164 | 0.21446 | 0.21516 | 0.21753 | 0.22199 | 0.24757 | 0.2568 | 0.23655 | 0.21061 | 0.18473 | 0.15277
2018-02-17 | 0.12953 | 0.11775 | 0.11399 | 0.11518 | 0.1227 | 0.14452 | 0.18444 | 0.22491 | 0.24907 | 0.25863 | 0.26298 | 0.26401 | 0.2656 | 0.26854 | 0.27162 | 0.27612 | 0.2785 | 0.27982 | 0.30232 | 0.30994 | 0.27987 | 0.24023 | 0.19532 | 0.15549
2018-02-18 | 0.12467 | 0.10839 | 0.10296 | 0.10157 | 0.10716 | 0.1295 | 0.18115 | 0.21757 | 0.23231 | 0.24716 | 0.2614 | 0.27336 | 0.28399 | 0.29551 | 0.30647 | 0.31706 | 0.32088 | 0.31508 | 0.33066 | 0.33834 | 0.30513 | 0.2574 | 0.21126 | 0.16313
2018-02-19 | 0.12959 | 0.1113 | 0.1035 | 0.1004 | 0.10412 | 0.12411 | 0.17181 | 0.20255 | 0.22191 | 0.24504 | 0.26953 | 0.29134 | 0.30901 | 0.32649 | 0.34361 | 0.36031 | 0.36444 | 0.35437 | 0.36363 | 0.36783 | 0.33388 | 0.28506 | 0.23331 | 0.18226
2018-02-20 | 0.14332 | 0.12291 | 0.11222 | 0.10672 | 0.10826 | 0.12764 | 0.17407 | 0.20592 | 0.2344 | 0.27001 | 0.30577 | 0.33133 | 0.35566 | 0.37521 | 0.38926 | 0.40161 | 0.40331 | 0.39156 | 0.40511 | 0.41211 | 0.37849 | 0.33162 | 0.27551 | 0.22282
2018-02-21 | 0.17913 | 0.15104 | 0.13725 | 0.13061 | 0.131 | 0.14891 | 0.19692 | 0.23082 | 0.27525 | 0.32596 | 0.3722 | 0.40788 | 0.4333 | 0.45012 | 0.4522 | 0.44744 | 0.41998 | 0.39797 | 0.40751 | 0.39539 | 0.35791 | 0.31204 | 0.2701 | 0.22231
2018-02-22 | 0.18087 | 0.1513 | 0.13638 | 0.12722 | 0.12488 | 0.12788 | 0.14174 | 0.1671 | 0.22702 | 0.28914 | 0.33819 | 0.37639 | 0.40756 | 0.42503 | 0.43192 | 0.435 | 0.42383 | 0.39565 | 0.39099 | 0.38009 | 0.33921 | 0.29801 | 0.25621 | 0.21141
2018-02-23 | 0.17247 | 0.14663 | 0.13113 | 0.12247 | 0.11864 | 0.12002 | 0.12863 | 0.14949 | 0.20414 | 0.26594 | 0.31932 | 0.36258 | 0.41582 | 0.4247 | 0.43236 | 0.43931 | 0.43275 | 0.4148 | 0.41458 | 0.41593 | 0.37736 | 0.31823 | 0.2675 | 0.21141
2018-02-24 | 0.16632 | 0.14427 | 0.13064 | 0.12311 | 0.12402 | 0.14237 | 0.18308 | 0.21648 | 0.25154 | 0.29737 | 0.34278 | 0.3767 | 0.41136 | 0.43589 | 0.4513 | 0.46334 | 0.45259 | 0.43589 | 0.45192 | 0.45518 | 0.40331 | 0.34185 | 0.27683 | 0.21651
2018-02-25 | 0.16995 | 0.14395 | 0.12935 | 0.12162 | 0.12221 | 0.14064 | 0.18653 | 0.21523 | 0.24703 | 0.28587 | 0.32296 | 0.35552 | 0.38786 | 0.41717 | 0.44076 | 0.45479 | 0.45063 | 0.42645 | 0.43126 | 0.43143 | 0.38614 | 0.32582 | 0.26681 | 0.20679
2018-02-26 | 0.16182 | 0.13626 | 0.12159 | 0.11504 | 0.11552 | 0.13116 | 0.1739 | 0.20417 | 0.23106 | 0.26289 | 0.30804 | 0.33999 | 0.36981 | 0.39083 | 0.40453 | 0.40735 | 0.39512 | 0.38676 | 0.40874 | 0.40804 | 0.37077 | 0.32135 | 0.26504 | 0.21114
2018-02-27 | 0.16923 | 0.14704 | 0.1358 | 0.13067 | 0.13228 | 0.15062 | 0.1981 | 0.22682 | 0.24479 | 0.26802 | 0.29451 | 0.28882 | 0.31607 | 0.31989 | 0.31847 | 0.31499 | 0.30748 | 0.31979 | 0.34312 | 0.34734 | 0.31875 | 0.27223 | 0.22219 | 0.17705
2018-02-28 | 0.14269 | 0.12464 | 0.11669 | 0.11425 | 0.11786 | 0.13936 | 0.19081 | 0.22377 | 0.23461 | 0.24137 | 0.24678 | 0.24845 | 0.24878 | 0.25149 | 0.25448 | 0.25867 | 0.26131 | 0.25786 | 0.27001 | 0.27735 | 0.25406 | 0.22495 | 0.19264 | 0.15887
2018-03-01 | 0.1314 | 0.11541 | 0.1071 | 0.10358 | 0.10495 | 0.1136 | 0.13122 | 0.15698 | 0.19256 | 0.21792 | 0.23469 | 0.2436 | 0.25225 | 0.26093 | 0.26745 | 0.27595 | 0.277 | 0.26984 | 0.27044 | 0.28049 | 0.25368 | 0.22519 | 0.19455 | 0.16041
2018-03-02 | 0.13298 | 0.11695 | 0.10831 | 0.10085 | 0.099768 | 0.1039 | 0.11436 | 0.13371 | 0.17561 | 0.21473 | 0.24129 | 0.26144 | 0.2774 | 0.29347 | 0.30494 | 0.31518 | 0.31852 | 0.31064 | 0.31382 | 0.32534 | 0.29302 | 0.25196 | 0.20869 | 0.16567
2018-03-03 | 0.13684 | 0.11507 | 0.10398 | 0.09998 | 0.10226 | 0.12046 | 0.16192 | 0.19114 | 0.2194 | 0.25305 | 0.28636 | 0.31199 | 0.33815 | 0.36444 | 0.38164 | 0.39739 | 0.40214 | 0.39031 | 0.39015 | 0.39754 | 0.35293 | 0.29615 | 0.23945 | 0.18336
2018-03-04 | 0.14335 | 0.12034 | 0.10861 | 0.10291 | 0.10414 | 0.12098 | 0.16266 | 0.19304 | 0.21983 | 0.25309 | 0.28493 | 0.31227 | 0.338 | 0.36268 | 0.38433 | 0.40076 | 0.4048 | 0.39235 | 0.3936 | 0.39839 | 0.35926 | 0.30864 | 0.25141 | 0.19655
2018-03-05 | 0.15441 | 0.13246 | 0.12049 | 0.11569 | 0.11763 | 0.13561 | 0.18261 | 0.21446 | 0.24088 | 0.28031 | 0.31663 | 0.34946 | 0.37798 | 0.39691 | 0.40458 | 0.40708 | 0.39723 | 0.38453 | 0.39329 | 0.3977 | 0.36373 | 0.31424 | 0.25888 | 0.20327
2018-03-06 | 0.16185 | 0.13977 | 0.12674 | 0.12145 | 0.12229 | 0.13986 | 0.18451 | 0.21624 | 0.25347 | 0.29437 | 0.32644 | 0.35412 | 0.37312 | 0.3692 | 0.36036 | 0.30953 | 0.28609 | 0.2899 | 0.31668 | 0.32225 | 0.29683 | 0.25829 | 0.21667 | 0.17369
2018-03-07 | 0.1402 | 0.12124 | 0.11374 | 0.11036 | 0.11349 | 0.13255 | 0.17818 | 0.20938 | 0.23961 | 0.26599 | 0.28856 | 0.29902 | 0.30453 | 0.30503 | 0.30457 | 0.30499 | 0.30099 | 0.29035 | 0.29574 | 0.29961 | 0.27749 | 0.24121 | 0.20539 | 0.1635
2018-03-08 | 0.13784 | 0.12017 | 0.11242 | 0.10963 | 0.11175 | 0.11904 | 0.13849 | 0.16803 | 0.20169 | 0.22227 | 0.22834 | 0.22786 | 0.22686 | 0.22646 | 0.22954 | 0.23412 | 0.23659 | 0.23432 | 0.24129 | 0.25385 | 0.23243 | 0.20782 | 0.17941 | 0.15283
2018-03-09 | 0.12529 | 0 | 0.11094 | 0.10352 | 0.10096 | 0.10431 | 0.11402 | 0.12884 | 0.15202 | 0.18311 | 0.21049 | 0.2231 | 0.24072 | 0.25074 | 0.2582 | 0.26923 | 0.28084 | 0.28649 | 0.27806 | 0.28049 | 0.29392 | 0.2611 | 0.22117 | 0.16985
2018-03-10 | 0.1324 | 0.11011 | 0.10003 | 0.09699 | 0.10056 | 0.11743 | 0.15857 | 0.19282 | 0.20368 | 0.22583 | 0.25393 | 0.27158 | 0.29216 | 0.30623 | 0.32783 | 0.34941 | 0.36773 | 0.36899 | 0.35377 | 0.34976 | 0.35581 | 0.30568 | 0.25431 | 0.1964
2018-03-11 | 0.14933 | 0.12335 | 0.11002 | 0.10369 | 0.10366 | 0.12011 | 0.16125 | 0.19433 | 0.20376 | 0.22986 | 0.25435 | 0.27819 | 0.29975 | 0.32022 | 0.34004 | 0.36293 | 0.38277 | 0.38869 | 0.37501 | 0.36828 | 0.37511 | 0.33042 | 0.27428 | 0.20915
2018-03-12 | 0.16428 | 0.13663 | 0.12329 | 0.1176 | 0.11887 | 0.1366 | 0.18226 | 0.18026 | 0.22539 | 0.25846 | 0.30176 | 0.33878 | 0.36889 | 0.39005 | 0.40166 | 0.42454 | 0.43859 | 0.43203 | 0.40901 | 0.3996 | 0.40363 | 0.35576 | 0.29961 | 0.23729
2018-03-13 | 0.18602 | 0.1552 | 0.13815 | 0.12947 | 0.12725 | 0.14089 | 0.18012 | 0.20721 | 0.21547 | 0.24076 | 0.2605 | 0.2724 | 0.27912 | 0.28337 | 0.28632 | 0.28941 | 0.29546 | 0.29401 | 0.27757 | 0.2756 | 0.28663 | 0.25292 | 0.21099 | 0.16543
2018-03-14 | 0.13143 | 0.11394 | 0.10474 | 0.10251 | 0.10702 | 0.12749 | 0.1797 | 0.22258 | 0.23279 | 0.24203 | 0.2492 | 0.25095 | 0.2502 | 0.25208 | 0.25452 | 0.25901 | 0.26551 | 0.26513 | 0.25511 | 0.25427 | 0.26354 | 0.23798 | 0.20459 | 0.16926
2018-03-15 | 0.13411 | 0.11504 | 0.10412 | 0.099373 | 0.10027 | 0.1068 | 0.12113 | 0.14714 | 0.17938 | 0.21164 | 0.23798 | 0.25372 | 0.26534 | 0.27525 | 0.28708 | 0.29947 | 0.31316 | 0.31555 | 0.3003 | 0.28587 | 0.28914 | 0.25858 | 0.22571 | 0.18315
2018-03-16 | 0.1491 | 0.12749 | 0.11453 | 0.10757 | 0.10482 | 0.10659 | 0.11578 | 0.13088 | 0.16397 | 0.21226 | 0.2499 | 0.27934 | 0.30379 | 0.32315 | 0.34248 | 0.35601 | 0.36237 | 0.36016 | 0.34258 | 0.33601 | 0.34774 | 0.31171 | 0.26906 | 0.21423
2018-03-17 | 0.17119 | 0.14538 | 0.13182 | 0.12707 | 0.12965 | 0.14897 | 0.19297 | 0.22954 | 0.25049 | 0.29442 | 0.34601 | 0.3836 | 0.41184 | 0.42656 | 0.43434 | 0.43987 | 0.44153 | 0.42935 | 0.41566 | 0.42378 | 0.42318 | 0.3788 | 0.32936 | 0.26698
2018-03-18 | 0.21706 | 0.18714 | 0.17275 | 0.16601 | 0.16496 | 0.18023 | 0.22207 | 0.24878 | 0.24413 | 0.25931 | 0.27455 | 0.28302 | 0.29035 | 0.30066 | 0.31438 | 0.32926 | 0.34528 | 0.3503 | 0.3365 | 0.32974 | 0.3379 | 0.29733 | 0.24587 | 0.18892
2018-03-19 | 0.145 | 0.1215 | 0.10977 | 0.10474 | 0.10607 | 0.12302 | 0.16472 | 0.19629 | 0.21007 | 0.2383 | 0.26784 | 0.29067 | 0.30623 | 0.32572 | 0.34547 | 0.36499 | 0.37747 | 0.37824 | 0.35816 | 0.34483 | 0.35407 | 0.31363 | 0.26311 | 0.20535
2018-03-20 | 0.16165 | 0.13558 | 0.1227 | 0.11569 | 0.11612 | 0.13222 | 0.17373 | 0.20664 | 0.22176 | 0.24957 | 0.28036 | 0.30448 | 0.32401 | 0.34498 | 0.36454 | 0.38045 | 0.39104 | 0.38728 | 0.36915 | 0.35457 | 0.36222 | 0.31513 | 0.26148 | 0.20554
2018-03-21 | 0.15804 | 0.13067 | 0.11507 | 0.10689 | 0.10669 | 0.11936 | 0.15208 | 0.18401 | 0.20554 | 0.2399 | 0.27718 | 0.30827 | 0.33412 | 0.36087 | 0.38718 | 0.40922 | 0.41798 | 0.40938 | 0.37942 | 0.35796 | 0.35971 | 0.31894 | 0.27731 | 0.2295
2018-03-22 | 0.18548 | 0.15854 | 0.14127 | 0.1314 | 0.12752 | 0.13164 | 0.14471 | 0.16262 | 0.19518 | 0.2512 | 0.29742 | 0.32334 | 0.34685 | 0.3652 | 0.37803 | 0.39219 | 0.41072 | 0.41034 | 0.38682 | 0.35921 | 0.35606 | 0.31457 | 0.26802 | 0.21679
2018-03-23 | 0.17359 | 0.14402 | 0.12752 | 0.11832 | 0.11405 | 0.11586 | 0.12426 | 0.13774 | 0.16988 | 0.22349 | 0.27573 | 0.31856 | 0.36202 | 0.40182 | 0.42995 | 0.45411 | 0.46476 | 0.46357 | 0.44253 | 0.41755 | 0.42155 | 0.3692 | 0.3126 | 0.24828
2018-03-24 | 0.19729 | 0.16431 | 0.14392 | 0.1358 | 0.13475 | 0.14855 | 0.18051 | 0.21076 | 0.23339 | 0.26724 | 0.29537 | 0.3156 | 0.32353 | 0.32263 | 0.31424 | 0.30878 | 0.30934 | 0.3127 | 0.31213 | 0.31551 | 0.31055 | 0.27288 | 0.23239 | 0.18444
2018-03-25 | 0.14817 | 0.12388 | 0.10963 | 0.10463 | 0.10607 | 0.11956 | 0.15388 | 0.18412 | 0.20357 | 0.23396 | 0.25646 | 0.27991 | 0.29893 | 0.31246 | 0.32525 | 0.33557 | 0.34459 | 0.34533 | 0.33162 | 0.31551 | 0.3214 | 0.27952 | 0.2275 | 0.1739
2018-03-26 | 0.13243 | 0.11094 | 0.099663 | 0.0959 | 0.098847 | 0.11504 | 0.15474 | 0.19293 | 0.21679 | 0.22946 | 0.23973 | 0.23982 | 0.23489 | 0.22893 | 0.22511 | 0.22298 | 0.22682 | 0.2295 | 0.22814 | 0.24121 | 0.26114 | 0.23599 | 0.19889 | 0.16182
2018-03-27 | 0.13146 | 0.11495 | 0.10686 | 0.10501 | 0.10864 | 0.12529 | 0.16431 | 0.19499 | 0.21114 | 0.23489 | 0.24699 | 0.25305 | 0.25587 | 0.2582 | 0.2579 | 0.25735 | 0.25829 | 0.25765 | 0.25444 | 0.26603 | 0.27696 | 0.25016 | 0.21349 | 0.17279
2018-03-28 | 0.13952 | 0.11898 | 0.10889 | 0.10369 | 0.10574 | 0.11988 | 0.15297 | 0.18333 | 0.20667 | 0.24051 | 0.27678 | 0.29934 | 0.31536 | 0.32491 | 0.33277 | 0.33771 | 0.33683 | 0.32644 | 0.31143 | 0.31157 | 0.31776 | 0.29035 | 0.25689 | 0.21535
2018-03-29 | 0.1786 | 0.1551 | 0.14067 | 0.13347 | 0.13197 | 0.137 | 0.15072 | 0.17181 | 0.20576 | 0.2568 | 0.30485 | 0.34014 | 0.35616 | 0.36484 | 0.36303 | 0.35427 | 0.34292 | 0.33123 | 0.3133 | 0.30827 | 0.29592 | 0.25956 | 0.22754 | 0.18924
2018-03-30 | 0.15418 | 0.13146 | 0.11658 | 0.10952 | 0.10699 | 0.10963 | 0.12049 | 0.13469 | 0.16272 | 0.20297 | 0.23331 | 0.24932 | 0.25676 | 0.26242 | 0.26784 | 0.27245 | 0.27713 | 0.27608 | 0.265 | 0.25731 | 0.27175 | 0.23912 | 0.19863 | 0.15385
2018-03-31 | 0.12043 | 0.1042 | 0.094354 | 0.091274 | 0.094842 | 0.1162 | 0.15987 | 0.1911 | 0.20225 | 0.21823 | 0.23534 | 0.24945 | 0.25978 | 0.27232 | 0.28359 | 0.29315 | 0.29769 | 0.29279 | 0.28717 | 0.2941 | 0.30697 | 0.26836 | 0.22164 | 0.17047
2018-04-01 | 0.13222 | 0.1118 | 0.10205 | 0.098191 | 0.10083 | 0.11893 | 0.16727 | 0.20064 | 0.2133 | 0.2311 | 0.24903 | 0.265 | 0.27815 | 0.2956 | 0.31729 | 0.34253 | 0.36631 | 0.37501 | 0.36182 | 0.33892 | 0.34425 | 0.30053 | 0.24121 | 0.18376
2018-04-02 | 0.14127 | 0.11781 | 0.10593 | 0.10006 | 0.10157 | 0.11979 | 0.16397 | 0.19165 | 0.20516 | 0.23158 | 0.25499 | 0.27709 | 0.29265 | 0.31237 | 0.34346 | 0.3725 | 0.39507 | 0.40469 | 0.38666 | 0.36273 | 0.36757 | 0.32216 | 0.25995 | 0.19967
2018-04-03 | 0.15342 | 0.12728 | 0.11354 | 0.10809 | 0.10928 | 0.1283 | 0.16978 | 0.19718 | 0.21663 | 0.24757 | 0.27854 | 0.30549 | 0.33066 | 0.35557 | 0.39109 | 0.41534 | 0.4328 | 0.42579 | 0.4065 | 0.37906 | 0.39329 | 0.34464 | 0.27907 | 0.21539
2018-04-04 | 0.16618 | 0.13877 | 0.12302 | 0.11564 | 0.11481 | 0.13158 | 0.17687 | 0.20342 | 0.22511 | 0.26157 | 0.29897 | 0.33142 | 0.35741 | 0.385 | 0.41243 | 0.43705 | 0.45739 | 0.45547 | 0.43072 | 0.38926 | 0.38071 | 0.33892 | 0.28757 | 0.23263
2018-04-05 | 0.18494 | 0.15411 | 0.13555 | 0.12461 | 0.12031 | 0.12183 | 0.1346 | 0.15156 | 0.19584 | 0.25309 | 0.30176 | 0.34361 | 0.37958 | 0.41782 | 0.44509 | 0.46573 | 0.47363 | 0.46847 | 0.4344 | 0.39125 | 0.38661 | 0.34263 | 0.2932 | 0.24076
2018-04-06 | 0.19176 | 0.1592 | 0.13759 | 0.12538 | 0.12046 | 0.12118 | 0.12971 | 0.14215 | 0.18736 | 0.2477 | 0.30149 | 0.34327 | 0.38339 | 0.4202 | 0.45541 | 0.47859 | 0.49005 | 0.48923 | 0.46169 | 0.42563 | 0.42689 | 0.37332 | 0.31143 | 0.24187
2018-04-07 | 0.19392 | 0.1637 | 0.14817 | 0.14089 | 0.14288 | 0.16357 | 0.21095 | 0.24047 | 0.26828 | 0.32349 | 0.38293 | 0.43837 | 0.48678 | 0.53173 | 0.56841 | 0.59686 | 0.61461 | 0.60749 | 0.57289 | 0.54337 | 0.53466 | 0.46613 | 0.3876 | 0.31349
2018-04-08 | 0.25672 | 0.21768 | 0.19099 | 0.17768 | 0.17789 | 0.19718 | 0.25049 | 0.28128 | 0.30781 | 0.34714 | 0.39565 | 0.43815 | 0.46402 | 0.47778 | 0.47501 | 0.4605 | 0.4683 | 0.43743 | 0.38107 | 0.35512 | 0.35856 | 0.3119 | 0.25204 | 0.19499
2018-04-09 | 0.15582 | 0.13203 | 0.11913 | 0.11287 | 0.11245 | 0.12845 | 0.17081 | 0.19282 | 0.20455 | 0.22917 | 0.24924 | 0.26024 | 0.26689 | 0.27249 | 0.28168 | 0.29311 | 0.3042 | 0.31139 | 0.30365 | 0.29288 | 0.30939 | 0.27341 | 0.22003 | 0.16981
2018-04-10 | 0.13286 | 0.11318 | 0.10245 | 0.09861 | 0.10046 | 0.11769 | 0.16125 | 0.18696 | 0.19978 | 0.22187 | 0.24322 | 0.25926 | 0.2704 | 0.28346 | 0.29792 | 0.314 | 0.32534 | 0.32506 | 0.31391 | 0.30619 | 0.32249 | 0.28328 | 0.23255 | 0.1798
2018-04-11 | 0.14155 | 0.11826 | 0.10694 | 0.10229 | 0.10382 | 0.11962 | 0.16195 | 0.18848 | 0.20793 | 0.24141 | 0.27358 | 0.2966 | 0.31302 | 0.32979 | 0.34542 | 0.35124 | 0.35308 | 0.34415 | 0.32792 | 0.31569 | 0.32415 | 0.29492 | 0.25651 | 0.21141
2018-04-12 | 0.17123 | 0.14535 | 0.12824 | 0.1189 | 0.11507 | 0.11801 | 0.13179 | 0.14997 | 0.19425 | 0.24903 | 0.29519 | 0.33326 | 0.36011 | 0.38484 | 0.40002 | 0.4141 | 0.41938 | 0.41351 | 0.38288 | 0.34882 | 0.34857 | 0.3163 | 0.26893 | 0.22408
2018-04-13 | 0.18376 | 0.155 | 0.13818 | 0.12737 | 0.12297 | 0.12458 | 0.13389 | 0.14765 | 0.18681 | 0.24014 | 0.28457 | 0.31847 | 0.34951 | 0.37077 | 0.37983 | 0.38718 | 0.38911 | 0.38547 | 0.36823 | 0.36313 | 0.3787 | 0.34063 | 0.28959 | 0.23122
2018-04-14 | 0.18534 | 0.15811 | 0.14389 | 0.13604 | 0.13675 | 0.15441 | 0.20068 | 0.22958 | 0.26281 | 0.31739 | 0.37199 | 0.42253 | 0.46533 | 0.50912 | 0.54516 | 0.57657 | 0.59331 | 0.58779 | 0.55296 | 0.5105 | 0.50472 | 0.44392 | 0.36595 | 0.28658
2018-04-15 | 0.22626 | 0.19117 | 0.17081 | 0.15741 | 0.1549 | 0.17147 | 0.21932 | 0.24691 | 0.28856 | 0.35214 | 0.4097 | 0.46567 | 0.50835 | 0.53986 | 0.55252 | 0.56238 | 0.5552 | 0.51259 | 0.49139 | 0.46266 | 0.46476 | 0.41174 | 0.33717 | 0.26422
2018-04-16 | 0.21038 | 0.17708 | 0.15761 | 0.14797 | 0.14599 | 0.16131 | 0.2041 | 0.22698 | 0.24409 | 0.27162 | 0.29574 | 0.31284 | 0.33109 | 0.35273 | 0.36879 | 0.38102 | 0.38853 | 0.38578 | 0.37296 | 0.36996 | 0.38402 | 0.35233 | 0.29574 | 0.23364
2018-04-17 | 0.18895 | 0.16222 | 0.14752 | 0.14011 | 0.14114 | 0.15944 | 0.2052 | 0.2338 | 0.26041 | 0.30273 | 0.34243 | 0.36925 | 0.37839 | 0.38552 | 0.38822 | 0.38412 | 0.37793 | 0.36515 | 0.35343 | 0.34641 | 0.35522 | 0.32907 | 0.28462 | 0.23206
2018-04-18 | 0.18917 | 0.16165 | 0.14494 | 0.13613 | 0.13478 | 0.14878 | 0.17959 | 0.20766 | 0.24786 | 0.30282 | 0.35144 | 0.38567 | 0.40756 | 0.43198 | 0.44409 | 0.44192 | 0.4371 | 0.43143 | 0.40788 | 0.38086 | 0.38231 | 0.35114 | 0.30883 | 0.26242
2018-04-19 | 0.21613 | 0.18783 | 0.16923 | 0.15761 | 0.15375 | 0.15734 | 0.16435 | 0.17523 | 0.20839 | 0.26949 | 0.32496 | 0.36595 | 0.40071 | 0.4271 | 0.44187 | 0.45198 | 0.45035 | 0.43011 | 0.39203 | 0.34774 | 0.34014 | 0.30264 | 0.2611 | 0.20812
2018-04-20 | 0.16526 | 0.13644 | 0.11838 | 0.10947 | 0.10582 | 0.10773 | 0.11669 | 0.12773 | 0.16158 | 0.20087 | 0.22444 | 0.24467 | 0.25871 | 0.26906 | 0.27612 | 0.28173 | 0.28538 | 0.28155 | 0.27201 | 0.26663 | 0.28569 | 0.26444 | 0.22424 | 0.17624
2018-04-21 | 0.13877 | 0.11663 | 0.10561 | 0.10043 | 0.10202 | 0.11849 | 0.15724 | 0.18026 | 0.20034 | 0.22754 | 0.25448 | 0.27595 | 0.29851 | 0.31734 | 0.33931 | 0.35721 | 0.37194 | 0.37062 | 0.35931 | 0.3439 | 0.35571 | 0.31475 | 0.25786 | 0.20229
2018-04-22 | 0.15635 | 0.12893 | 0.11658 | 0.1093 | 0.10944 | 0.12797 | 0.17012 | 0.19033 | 0.2121 | 0.24039 | 0.27162 | 0.30434 | 0.33013 | 0.35184 | 0.37496 | 0.40389 | 0.42449 | 0.42842 | 0.41254 | 0.38895 | 0.3995 | 0.35372 | 0.28618 | 0.21964
2018-04-23 | 0.1713 | 0.1437 | 0.12755 | 0.11824 | 0.11678 | 0.13237 | 0.17164 | 0.14897 | 0.22058 | 0.25368 | 0.28739 | 0.31372 | 0.34655 | 0.38812 | 0.43473 | 0.47134 | 0.49863 | 0.50561 | 0.48422 | 0.44454 | 0.44048 | 0.39907 | 0.32835 | 0.24393
2018-04-24 | 0.19311 | 0.16232 | 0.13607 | 0.12553 | 0.12585 | 0.13561 | 0.17421 | 0.19922 | 0.22862 | 0.2738 | 0.32292 | 0.36712 | 0.40986 | 0.44973 | 0.48456 | 0.51979 | 0.54072 | 0.53796 | 0.5074 | 0.46129 | 0.45755 | 0.40687 | 0.3321 | 0.26033
2018-04-25 | 0.20353 | 0.16679 | 0.14557 | 0.13392 | 0.13128 | 0.14618 | 0.18577 | 0.21018 | 0.24265 | 0.29071 | 0.34621 | 0.39844 | 0.44677 | 0.49356 | 0.5357 | 0.57258 | 0.59325 | 0.5876 | 0.54485 | 0.48497 | 0.46893 | 0.41857 | 0.35164 | 0.28462
2018-04-26 | 0.22412 | 0.18333 | 0.1588 | 0.14382 | 0.13555 | 0.1361 | 0.14538 | 0.16441 | 0.21679 | 0.28297 | 0.35011 | 0.41313 | 0.4659 | 0.50781 | 0.5338 | 0.55744 | 0.5698 | 0.56244 | 0.52196 | 0.46283 | 0.44688 | 0.40151 | 0.34381 | 0.28524
2018-04-27 | 0.23331 | 0.19606 | 0.17016 | 0.15549 | 0.1464 | 0.14484 | 0.14997 | 0.16492 | 0.22306 | 0.29925 | 0.37092 | 0.43412 | 0.48637 | 0.53075 | 0.56125 | 0.58792 | 0.59867 | 0.59145 | 0.55426 | 0.50324 | 0.49603 | 0.44381 | 0.36737 | 0.29751
2018-04-28 | 0.24232 | 0.20766 | 0.18692 | 0.17449 | 0.17345 | 0.19319 | 0.23847 | 0.2672 | 0.30781 | 0.36844 | 0.4427 | 0.50966 | 0.56294 | 0.61036 | 0.65097 | 0.68297 | 0.69156 | 0.68816 | 0.65036 | 0.59505 | 0.57962 | 0.51091 | 0.41928 | 0.33591
2018-04-29 | 0.27446 | 0.23473 | 0.21045 | 0.19699 | 0.19477 | 0.21326 | 0.25778 | 0.28699 | 0.33717 | 0.40538 | 0.47865 | 0.54479 | 0.59589 | 0.63849 | 0.66889 | 0.69087 | 0.68629 | 0.67039 | 0.63936 | 0.58997 | 0.57163 | 0.50716 | 0.41879 | 0.33557
2018-04-30 | 0.27253 | 0.23623 | 0.21392 | 0.20192 | 0.20117 | 0.21967 | 0.2659 | 0.29528 | 0.3443 | 0.41308 | 0.4859 | 0.54719 | 0.59466 | 0.63729 | 0.66398 | 0.68263 | 0.67293 | 0.62092 | 0.58344 | 0.54435 | 0.54171 | 0.48526 | 0.40257 | 0.32449
2018-05-01 | 0.26302 | 0.22614 | 0.20301 | 0.1911 | 0.18779 | 0.20751 | 0.25532 | 0.2856 | 0.32936 | 0.39739 | 0.47294 | 0.5338 | 0.5844 | 0.62917 | 0.6584 | 0.67327 | 0.66582 | 0.62692 | 0.56955 | 0.52693 | 0.52305 | 0.46288 | 0.38708 | 0.31386
2018-05-02 | 0.2574 | 0.22109 | 0.19915 | 0.18627 | 0.18297 | 0.20139 | 0.24686 | 0.27749 | 0.31593 | 0.37578 | 0.43066 | 0.47409 | 0.50016 | 0.53106 | 0.55377 | 0.56583 | 0.55831 | 0.53588 | 0.50223 | 0.45818 | 0.45733 | 0.39797 | 0.34219 | 0.28663
2018-05-03 | 0.23647 | 0.20147 | 0.17952 | 0.16679 | 0.16047 | 0.16394 | 0.17603 | 0.19577 | 0.23741 | 0.29365 | 0.34336 | 0.37932 | 0.39639 | 0.40469 | 0.40002 | 0.37901 | 0.33258 | 0.31536 | 0.29989 | 0.29569 | 0.30614 | 0.28703 | 0.25608 | 0.21936
2018-05-04 | 0.18451 | 0.15917 | 0.14433 | 0.13469 | 0.13173 | 0.13179 | 0.13537 | 0.13977 | 0.17407 | 0.21729 | 0.25427 | 0.28235 | 0.31227 | 0.33907 | 0.36308 | 0.39078 | 0.41297 | 0.42443 | 0.41453 | 0.37994 | 0.36854 | 0.3263 | 0.2752 | 0.21103
2018-05-05 | 0.16611 | 0.13463 | 0.12329 | 0.11544 | 0.11566 | 0.13225 | 0.16806 | 0.19223 | 0.22262 | 0.26564 | 0.31344 | 0.35626 | 0.39913 | 0.44042 | 0.4801 | 0.51462 | 0.54577 | 0.55023 | 0.52505 | 0.44693 | 0.44906 | 0.39418 | 0.29952 | 0.24364
2018-05-06 | 0.18873 | 0.15777 | 0.13852 | 0.12767 | 0.12517 | 0.13995 | 0.17726 | 0.20214 | 0.23412 | 0.28248 | 0.33495 | 0.38984 | 0.44493 | 0.48882 | 0.53215 | 0.57093 | 0.59628 | 0.5946 | 0.56332 | 0.48381 | 0.49327 | 0.43721 | 0.35826 | 0.27815
2018-05-07 | 0.22164 | 0.1866 | 0.16762 | 0.15556 | 0.153 | 0.16847 | 0.20862 | 0.23513 | 0.2756 | 0.32826 | 0.39052 | 0.44565 | 0.49739 | 0.54695 | 0.59357 | 0.61723 | 0.63495 | 0.62997 | 0.59145 | 0.53741 | 0.52468 | 0.47467 | 0.39041 | 0.31157
2018-05-08 | 0.2487 | 0.21268 | 0.19121 | 0.17628 | 0.17286 | 0.18815 | 0.22909 | 0.25469 | 0.29915 | 0.35616 | 0.41809 | 0.47225 | 0.52046 | 0.56778 | 0.6056 | 0.63996 | 0.66119 | 0.65529 | 0.62157 | 0.56244 | 0.54054 | 0.48462 | 0.40501 | 0.32835
2018-05-09 | 0.25731 | 0.21694 | 0.19562 | 0.18005 | 0.17631 | 0.19234 | 0.23352 | 0.2599 | 0.30236 | 0.36021 | 0.42036 | 0.47248 | 0.51955 | 0.5632 | 0.60372 | 0.63449 | 0.65016 | 0.63462 | 0.5874 | 0.5239 | 0.49833 | 0.4485 | 0.38744 | 0.32482
2018-05-10 | 0.26767 | 0.23034 | 0.20679 | 0.1907 | 0.18318 | 0.18508 | 0.19297 | 0.2143 | 0.27674 | 0.34848 | 0.40575 | 0.45214 | 0.50152 | 0.53496 | 0.55713 | 0.57372 | 0.57277 | 0.56056 | 0.52644 | 0.46853 | 0.47398 | 0.43258 | 0.38086 | 0.32254
2018-05-11 | 0.26914 | 0.23295 | 0.20793 | 0.19256 | 0.18526 | 0.1834 | 0.18631 | 0.19922 | 0.2474 | 0.31246 | 0.36904 | 0.41561 | 0.45857 | 0.49644 | 0.52517 | 0.53968 | 0.54516 | 0.53015 | 0.49945 | 0.45665 | 0.45744 | 0.42924 | 0.36874 | 0.29847
2018-05-12 | 0.23969 | 0.20478 | 0.18444 | 0.17418 | 0.17331 | 0.19136 | 0.23327 | 0.25982 | 0.29897 | 0.35926 | 0.42514 | 0.48149 | 0.5299 | 0.56923 | 0.59873 | 0.62501 | 0.63489 | 0.62666 | 0.59931 | 0.55913 | 0.54818 | 0.48754 | 0.40453 | 0.32807
2018-05-13 | 0.26733 | 0.2317 | 0.20797 | 0.19403 | 0.19106 | 0.209 | 0.25179 | 0.27797 | 0.31635 | 0.37726 | 0.43887 | 0.48829 | 0.53521 | 0.56722 | 0.59138 | 0.6118 | 0.62243 | 0.61062 | 0.57663 | 0.53185 | 0.52505 | 0.47848 | 0.40061 | 0.32173
2018-05-14 | 0.26681 | 0.23142 | 0.20652 | 0.19267 | 0.19008 | 0.19729 | 0.25545 | 0.27656 | 0.31908 | 0.38645 | 0.44878 | 0.51038 | 0.55638 | 0.58638 | 0.60795 | 0.6073 | 0.601 | 0.58747 | 0.55147 | 0.5102 | 0.51313 | 0.46522 | 0.39339 | 0.31663
2018-05-15 | 0.25684 | 0.22085 | 0.1981 | 0.18613 | 0.1857 | 0.20316 | 0.24608 | 0.27149 | 0.30674 | 0.3694 | 0.42891 | 0.46158 | 0.47398 | 0.47151 | 0.45175 | 0.42924 | 0.42318 | 0.42231 | 0.41082 | 0.39229 | 0.39229 | 0.36358 | 0.30721 | 0.24999
2018-05-16 | 0.20274 | 0.17523 | 0.15854 | 0.14839 | 0.14688 | 0.16479 | 0.20501 | 0.224 | 0.23867 | 0.26629 | 0.29098 | 0.30906 | 0.31729 | 0.32296 | 0.33485 | 0.34175 | 0.34956 | 0.34141 | 0.3205 | 0.29428 | 0.28368 | 0.26135 | 0.22551 | 0.18354
2018-05-17 | 0.14736 | 0.12562 | 0.11161 | 0.10406 | 0.10184 | 0.10436 | 0.11253 | 0.12887 | 0.16693 | 0.21157 | 0.25158 | 0.28435 | 0.30943 | 0.33326 | 0.35691 | 0.37608 | 0.38838 | 0.38604 | 0.36353 | 0.32644 | 0.31569 | 0.29528 | 0.25402 | 0.21157
2018-05-18 | 0.1739 | 0.14785 | 0.13097 | 0.12008 | 0.11532 | 0.11629 | 0.11919 | 0.1327 | 0.17407 | 0.2283 | 0.27656 | 0.31593 | 0.3504 | 0.37952 | 0.40676 | 0.42705 | 0.44192 | 0.43854 | 0.41088 | 0.37307 | 0.36884 | 0.34204 | 0.28775 | 0.22897
2018-05-19 | 0.18279 | 0.15391 | 0.13706 | 0.12911 | 0.12947 | 0.14525 | 0.18186 | 0.20516 | 0.24224 | 0.28986 | 0.33766 | 0.38086 | 0.41944 | 0.45937 | 0.48701 | 0.51438 | 0.52948 | 0.52705 | 0.50217 | 0.45547 | 0.43954 | 0.39913 | 0.33171 | 0.25939
2018-05-20 | 0.20557 | 0.17227 | 0.15434 | 0.14389 | 0.14096 | 0.1548 | 0.19004 | 0.21831 | 0.256 | 0.30591 | 0.35886 | 0.40506 | 0.4437 | 0.47703 | 0.50134 | 0.52124 | 0.53301 | 0.52777 | 0.50656 | 0.4584 | 0.44409 | 0.39923 | 0.32998 | 0.26041
2018-05-21 | 0.20645 | 0.17265 | 0.1527 | 0.14055 | 0.13731 | 0.15101 | 0.18703 | 0.21423 | 0.24707 | 0.29171 | 0.33902 | 0.38319 | 0.42188 | 0.4651 | 0.50781 | 0.53778 | 0.55626 | 0.54862 | 0.5172 | 0.46659 | 0.44403 | 0.40437 | 0.33562 | 0.26332
2018-05-22 | 0.20391 | 0.16923 | 0.14672 | 0.13573 | 0.13383 | 0.14836 | 0.18447 | 0.20972 | 0.24778 | 0.29683 | 0.35333 | 0.41109 | 0.46779 | 0.52547 | 0.57043 | 0.60958 | 0.63469 | 0.62692 | 0.59145 | 0.53112 | 0.49804 | 0.45631 | 0.37286 | 0.29216
2018-05-23 | 0.2277 | 0.1887 | 0.16397 | 0.1502 | 0.14481 | 0.15721 | 0.18964 | 0.22242 | 0.26923 | 0.3308 | 0.40034 | 0.47455 | 0.54177 | 0.6133 | 0.66773 | 0.70448 | 0.71645 | 0.70027 | 0.65124 | 0.57005 | 0.53735 | 0.49245 | 0.41803 | 0.34371
2018-05-24 | 0.27925 | 0.23497 | 0.20286 | 0.18211 | 0.1713 | 0.1684 | 0.17116 | 0.19308 | 0.25735 | 0.3381 | 0.41933 | 0.50099 | 0.57479 | 0.62838 | 0.662 | 0.68021 | 0.67938 | 0.66391 | 0.61206 | 0.54763 | 0.52118 | 0.47565 | 0.41013 | 0.34356
2018-05-25 | 0.28632 | 0.24183 | 0.21057 | 0.19103 | 0.17955 | 0.1753 | 0.17708 | 0.19103 | 0.24183 | 0.3127 | 0.39781 | 0.47162 | 0.54146 | 0.5901 | 0.6198 | 0.63709 | 0.6429 | 0.61901 | 0.57005 | 0.51588 | 0.49939 | 0.45914 | 0.39271 | 0.3308
2018-05-26 | 0.27184 | 0.23352 | 0.20702 | 0.19048 | 0.18169 | 0.18183 | 0.1857 | 0.20436 | 0.26823 | 0.35437 | 0.44092 | 0.50835 | 0.56841 | 0.61154 | 0.63622 | 0.64922 | 0.64962 | 0.62957 | 0.5814 | 0.52644 | 0.51516 | 0.4683 | 0.39518 | 0.31852
2018-05-27 | 0.26059 | 0.22227 | 0.19874 | 0.18498 | 0.18048 | 0.19751 | 0.23517 | 0.27066 | 0.32197 | 0.39078 | 0.46277 | 0.53167 | 0.5851 | 0.62765 | 0.65299 | 0.66507 | 0.64585 | 0.59679 | 0.55215 | 0.51014 | 0.50537 | 0.46249 | 0.39052 | 0.31064
2018-05-28 | 0.25254 | 0.21601 | 0.19437 | 0.18137 | 0.17828 | 0.19492 | 0.23396 | 0.26487 | 0.31213 | 0.37352 | 0.44187 | 0.5166 | 0.57264 | 0.62052 | 0.64726 | 0.65495 | 0.65421 | 0.62831 | 0.58862 | 0.54596 | 0.53258 | 0.48544 | 0.40959 | 0.33224
2018-05-29 | 0.26906 | 0.22766 | 0.20451 | 0.19095 | 0.18627 | 0.20169 | 0.24014 | 0.2711 | 0.3113 | 0.36515 | 0.4252 | 0.47019 | 0.49827 | 0.51708 | 0.50395 | 0.48964 | 0.48062 | 0.46933 | 0.45908 | 0.42869 | 0.42579 | 0.39749 | 0.34185 | 0.27876
2018-05-30 | 0.22231 | 0.18555 | 0.16868 | 0.15861 | 0.15678 | 0.17143 | 0.20603 | 0.23562 | 0.27978 | 0.34961 | 0.41728 | 0.4764 | 0.52529 | 0.56451 | 0.58817 | 0.60359 | 0.59925 | 0.56703 | 0.51139 | 0.46761 | 0.4549 | 0.41793 | 0.36333 | 0.30832
2018-05-31 | 0.25803 | 0.21835 | 0.19264 | 0.1767 | 0.17074 | 0.16971 | 0.1767 | 0.20015 | 0.26435 | 0.34557 | 0.42558 | 0.49251 | 0.53784 | 0.56772 | 0.57277 | 0.56816 | 0.55147 | 0.51576 | 0.47582 | 0.43528 | 0.42995 | 0.40379 | 0.35846 | 0.30374
2018-06-01 | 0.25774 | 0.2196 | 0.19621 | 0.18058 | 0.1723 | 0.17188 | 0.17509 | 0.1915 | 0.2445 | 0.31724 | 0.39093 | 0.45063 | 0.50259 | 0.53962 | 0.55906 | 0.5542 | 0.53088 | 0.49175 | 0.4499 | 0.4222 | 0.42166 | 0.40299 | 0.35387 | 0.29342
2018-06-02 | 0.24347 | 0.21153 | 0.19411 | 0.18469 | 0.18584 | 0.20652 | 0.24587 | 0.27402 | 0.30135 | 0.33446 | 0.36762 | 0.38702 | 0.40644 | 0.41966 | 0.42863 | 0.4282 | 0.42612 | 0.41587 | 0.40549 | 0.39418 | 0.39776 | 0.37583 | 0.32197 | 0.26337
2018-06-03 | 0.21473 | 0.18451 | 0.16693 | 0.15678 | 0.15619 | 0.17355 | 0.2111 | 0.23676 | 0.26251 | 0.30103 | 0.34209 | 0.3787 | 0.40634 | 0.42689 | 0.43561 | 0.43848 | 0.42781 | 0.41641 | 0.39723 | 0.38086 | 0.38619 | 0.35846 | 0.30716 | 0.24786
2018-06-04 | 0.19911 | 0.16933 | 0.15189 | 0.14316 | 0.14303 | 0.15924 | 0.19414 | 0.19963 | 0.25129 | 0.30291 | 0.34902 | 0.38739 | 0.41469 | 0.44839 | 0.47335 | 0.49052 | 0.50377 | 0.50644 | 0.48929 | 0.45035 | 0.43159 | 0.40076 | 0.34317 | 0.27564
2018-06-05 | 0.22077 | 0.18714 | 0.16587 | 0.15336 | 0.14946 | 0.16313 | 0.19374 | 0.22862 | 0.28044 | 0.34287 | 0.41281 | 0.47975 | 0.53399 | 0.58606 | 0.62316 | 0.65036 | 0.66187 | 0.65678 | 0.62481 | 0.56182 | 0.52759 | 0.47542 | 0.39812 | 0.31527
2018-06-06 | 0.25524 | 0.21264 | 0.1858 | 0.16971 | 0.16246 | 0.17352 | 0.1984 | 0.23404 | 0.29605 | 0.37148 | 0.45693 | 0.54183 | 0.61435 | 0.67162 | 0.71299 | 0.73646 | 0.74423 | 0.73002 | 0.68497 | 0.61559 | 0.57176 | 0.5242 | 0.44867 | 0.37608
2018-06-07 | 0.31064 | 0.26358 | 0.23206 | 0.21314 | 0.20053 | 0.19617 | 0.19982 | 0.22499 | 0.29519 | 0.37947 | 0.47421 | 0.5642 | 0.62653 | 0.67156 | 0.69867 | 0.70602 | 0.68076 | 0.6429 | 0.59383 | 0.54528 | 0.51307 | 0.4707 | 0.4073 | 0.34258
2018-06-08 | 0.2864 | 0.2438 | 0.21504 | 0.19136 | 0.18412 | 0.18137 | 0.18186 | 0.19747 | 0.25482 | 0.34165 | 0.43412 | 0.51985 | 0.5734 | 0.58593 | 0.57182 | 0.56307 | 0.54664 | 0.52929 | 0.49662 | 0.45829 | 0.43721 | 0.40533 | 0.34116 | 0.28346
2018-06-09 | 0.22889 | 0.194 | 0.17126 | 0.16007 | 0.15854 | 0.17272 | 0.20042 | 0.23291 | 0.28399 | 0.35238 | 0.43423 | 0.52444 | 0.59789 | 0.66153 | 0.6965 | 0.68594 | 0.66732 | 0.62092 | 0.56797 | 0.52251 | 0.49762 | 0.45592 | 0.38329 | 0.31027
2018-06-10 | 0.25053 | 0.2123 | 0.19019 | 0.1768 | 0.17341 | 0.18786 | 0.21686 | 0.2568 | 0.31767 | 0.38822 | 0.45942 | 0.52814 | 0.58382 | 0.61553 | 0.61383 | 0.57232 | 0.53594 | 0.51913 | 0.51474 | 0.48369 | 0.47358 | 0.42929 | 0.35951 | 0.2913
2018-06-11 | 0.239 | 0.20387 | 0.18062 | 0.16857 | 0.16587 | 0.17832 | 0.20801 | 0.24277 | 0.29678 | 0.3724 | 0.44638 | 0.51253 | 0.5557 | 0.58293 | 0.5557 | 0.50918 | 0.48619 | 0.47911 | 0.4691 | 0.43937 | 0.42541 | 0.39702 | 0.33751 | 0.27564
2018-06-12 | 0.22488 | 0.19074 | 0.17026 | 0.15811 | 0.15543 | 0.16697 | 0.19507 | 0.22113 | 0.25045 | 0.29157 | 0.34749 | 0.41259 | 0.4873 | 0.55806 | 0.6071 | 0.61809 | 0.58728 | 0.53992 | 0.50496 | 0.46996 | 0.45175 | 0.41361 | 0.34327 | 0.27797
2018-06-13 | 0.22535 | 0.19092 | 0.16985 | 0.15678 | 0.15437 | 0.1657 | 0.19015 | 0.22555 | 0.28182 | 0.34616 | 0.41367 | 0.48346 | 0.54066 | 0.57068 | 0.56999 | 0.53723 | 0.50448 | 0.47053 | 0.44109 | 0.39965 | 0.37542 | 0.35169 | 0.30823 | 0.25731
2018-06-14 | 0.21349 | 0.18236 | 0.16185 | 0.1501 | 0.145 | 0.14704 | 0.15421 | 0.17544 | 0.22774 | 0.2981 | 0.37261 | 0.44498 | 0.50395 | 0.5542 | 0.57796 | 0.57612 | 0.54571 | 0.51588 | 0.47059 | 0.42329 | 0.40581 | 0.37665 | 0.32946 | 0.27868
2018-06-15 | 0.23376 | 0.20293 | 0.1798 | 0.16645 | 0.16269 | 0.16605 | 0.17216 | 0.19297 | 0.25145 | 0.33003 | 0.40762 | 0.48363 | 0.54899 | 0.59235 | 0.61796 | 0.60827 | 0.57467 | 0.53362 | 0.49139 | 0.44895 | 0.4407 | 0.42134 | 0.36626 | 0.30883
2018-06-16 | 0.25267 | 0.21835 | 0.19762 | 0.18512 | 0.18094 | 0.19433 | 0.22164 | 0.25162 | 0.29284 | 0.34788 | 0.42552 | 0.50591 | 0.5642 | 0.61776 | 0.65603 | 0.67904 | 0.69295 | 0.68311 | 0.63435 | 0.55426 | 0.51805 | 0.47369 | 0.39844 | 0.32453
2018-06-17 | 0.26307 | 0.22464 | 0.19773 | 0.18272 | 0.17754 | 0.18892 | 0.21675 | 0.2492 | 0.29198 | 0.34126 | 0.39187 | 0.44064 | 0.48445 | 0.5242 | 0.53796 | 0.53772 | 0.52717 | 0.51769 | 0.49857 | 0.46761 | 0.44956 | 0.42623 | 0.35482 | 0.28721
2018-06-18 | 0.23082 | 0.19714 | 0.1768 | 0.16441 | 0.16242 | 0.17519 | 0.20489 | 0.23737 | 0.28498 | 0.34248 | 0.40997 | 0.47801 | 0.51672 | 0.53075 | 0.5216 | 0.49709 | 0.4699 | 0.44721 | 0.42541 | 0.4041 | 0.39597 | 0.37542 | 0.32003 | 0.26101
2018-06-19 | 0.21141 | 0.18183 | 0.16465 | 0.15487 | 0.15238 | 0.16499 | 0.19304 | 0.22404 | 0.2742 | 0.33742 | 0.41066 | 0.47283 | 0.52668 | 0.56722 | 0.57056 | 0.53527 | 0.50312 | 0.47111 | 0.43976 | 0.41088 | 0.39591 | 0.36489 | 0.3134 | 0.25444
2018-06-20 | 0.20599 | 0.17565 | 0.15711 | 0.14727 | 0.14481 | 0.15549 | 0.18062 | 0.21272 | 0.2644 | 0.33412 | 0.40623 | 0.47709 | 0.53441 | 0.56816 | 0.55831 | 0.51008 | 0.4805 | 0.45473 | 0.43335 | 0.40597 | 0.3901 | 0.37082 | 0.32587 | 0.27363
2018-06-21 | 0.22456 | 0.19297 | 0.17181 | 0.15994 | 0.15483 | 0.15685 | 0.16188 | 0.1875 | 0.25562 | 0.34063 | 0.41733 | 0.4935 | 0.55738 | 0.59595 | 0.58427 | 0.54325 | 0.50889 | 0.4816 | 0.4494 | 0.41674 | 0.40082 | 0.38221 | 0.338 | 0.28364
2018-06-22 | 0.2344 | 0.20448 | 0.18176 | 0.16816 | 0.16064 | 0.16021 | 0.16219 | 0.18757 | 0.25225 | 0.33921 | 0.42047 | 0.48707 | 0.55271 | 0.60294 | 0.63595 | 0.64109 | 0.61947 | 0.57188 | 0.51402 | 0.46602 | 0.4471 | 0.41966 | 0.36444 | 0.29797
2018-06-23 | 0.2417 | 0.21026 | 0.18921 | 0.17701 | 0.17442 | 0.18833 | 0.21679 | 0.25385 | 0.31246 | 0.38381 | 0.46693 | 0.54651 | 0.62078 | 0.68304 | 0.71956 | 0.72795 | 0.71334 | 0.682 | 0.63735 | 0.57758 | 0.53949 | 0.49052 | 0.41679 | 0.3349
2018-06-24 | 0.27214 | 0.2315 | 0.20637 | 0.19074 | 0.18566 | 0.19788 | 0.22618 | 0.26319 | 0.32596 | 0.40103 | 0.49098 | 0.57378 | 0.64935 | 0.71921 | 0.76185 | 0.78559 | 0.78989 | 0.76061 | 0.72276 | 0.65956 | 0.626 | 0.56974 | 0.48288 | 0.39355
2018-06-25 | 0.32249 | 0.27389 | 0.24059 | 0.22085 | 0.21361 | 0.22507 | 0.25347 | 0.29175 | 0.35751 | 0.4442 | 0.54288 | 0.62335 | 0.69944 | 0.76148 | 0.80099 | 0.80496 | 0.77195 | 0.72981 | 0.67821 | 0.61317 | 0.5746 | 0.5262 | 0.45411 | 0.37011
2018-06-26 | 0.30356 | 0.25566 | 0.22547 | 0.20702 | 0.20004 | 0.20965 | 0.23806 | 0.27481 | 0.34073 | 0.43028 | 0.52553 | 0.6056 | 0.67046 | 0.71454 | 0.75901 | 0.77378 | 0.77415 | 0.75095 | 0.70968 | 0.64458 | 0.5997 | 0.54695 | 0.46556 | 0.37849
2018-06-27 | 0.30846 | 0.26392 | 0.23392 | 0.21581 | 0.20999 | 0.22223 | 0.24624 | 0.28253 | 0.34828 | 0.43264 | 0.516 | 0.59512 | 0.64706 | 0.69233 | 0.73224 | 0.73661 | 0.7212 | 0.68401 | 0.61901 | 0.55389 | 0.51907 | 0.47191 | 0.41507 | 0.3467
2018-06-28 | 0.28146 | 0.2383 | 0.2111 | 0.19165 | 0.18026 | 0.17126 | 0.1964 | 0.2123 | 0.28266 | 0.37526 | 0.45705 | 0.54719 | 0.62434 | 0.67437 | 0.70574 | 0.72952 | 0.72667 | 0.71003 | 0.66166 | 0.59705 | 0.56182 | 0.51985 | 0.45349 | 0.37906
2018-06-29 | 0.31546 | 0.27075 | 0.23961 | 0.21866 | 0.20698 | 0.20252 | 0.20109 | 0.21928 | 0.29247 | 0.39261 | 0.49509 | 0.5946 | 0.67601 | 0.71702 | 0.71886 | 0.69142 | 0.67019 | 0.63669 | 0.57239 | 0.5154 | 0.48259 | 0.45001 | 0.3901 | 0.32159
2018-06-30 | 0.26655 | 0.22842 | 0.20421 | 0.19052 | 0.18884 | 0.20368 | 0.23223 | 0.26328 | 0.3188 | 0.39849 | 0.47946 | 0.55464 | 0.61822 | 0.67471 | 0.71017 | 0.72781 | 0.71214 | 0.65367 | 0.59841 | 0.54924 | 0.52281 | 0.4841 | 0.42188 | 0.34734
2018-07-01 | 0.28569 | 0.24579 | 0.22254 | 0.209 | 0.20584 | 0.22128 | 0.2538 | 0.28204 | 0.31965 | 0.37578 | 0.43716 | 0.50294 | 0.54608 | 0.56589 | 0.58549 | 0.59396 | 0.60879 | 0.59957 | 0.57511 | 0.55277 | 0.54109 | 0.49533 | 0.42177 | 0.34759
2018-07-02 | 0.28191 | 0.24405 | 0.22038 | 0.20797 | 0.20406 | 0.21663 | 0.2462 | 0.27824 | 0.33495 | 0.41335 | 0.5052 | 0.57346 | 0.61618 | 0.62151 | 0.59641 | 0.57302 | 0.56684 | 0.55794 | 0.54078 | 0.51002 | 0.49892 | 0.47444 | 0.41647 | 0.34239
2018-07-03 | 0.28891 | 0.24932 | 0.22726 | 0.21299 | 0.21072 | 0.22317 | 0.2528 | 0.28596 | 0.3439 | 0.43028 | 0.53033 | 0.61415 | 0.67629 | 0.72148 | 0.7593 | 0.78049 | 0.77195 | 0.7168 | 0.65874 | 0.60372 | 0.57081 | 0.53386 | 0.46784 | 0.39146
2018-07-04 | 0.32768 | 0.27952 | 0.2462 | 0.2248 | 0.2138 | 0.21353 | 0.21803 | 0.23267 | 0.29596 | 0.39839 | 0.50348 | 0.59254 | 0.64908 | 0.67732 | 0.68705 | 0.68456 | 0.61658 | 0.53778 | 0.4841 | 0.4381 | 0.41002 | 0.37562 | 0.35711 | 0.3196
2018-07-05 | 0.27127 | 0.23267 | 0.20843 | 0.19308 | 0.18584 | 0.18613 | 0.19063 | 0.2038 | 0.25338 | 0.31532 | 0.39439 | 0.45462 | 0.5071 | 0.55931 | 0.56596 | 0.52723 | 0.49257 | 0.4691 | 0.44643 | 0.42318 | 0.40879 | 0.38692 | 0.34641 | 0.29565
2018-07-06 | 0.25166 | 0.21835 | 0.19655 | 0.18222 | 0.17775 | 0.17849 | 0.18161 | 0.19577 | 0.25204 | 0.31522 | 0.37731 | 0.40278 | 0.42918 | 0.45366 | 0.47646 | 0.4801 | 0.47346 | 0.45597 | 0.42853 | 0.38765 | 0.37994 | 0.36393 | 0.31989 | 0.2665
2018-07-07 | 0.22539 | 0.19747 | 0.18122 | 0.17338 | 0.17299 | 0.18794 | 0.21597 | 0.24815 | 0.2992 | 0.35616 | 0.41782 | 0.4605 | 0.48091 | 0.49692 | 0.50259 | 0.51907 | 0.51907 | 0.51636 | 0.50442 | 0.48905 | 0.47738 | 0.45018 | 0.38968 | 0.32221
2018-07-08 | 0.26504 | 0.22666 | 0.20229 | 0.18877 | 0.18501 | 0.19669 | 0.22499 | 0.25961 | 0.31386 | 0.39465 | 0.48125 | 0.56451 | 0.63362 | 0.6665 | 0.66003 | 0.62184 | 0.58325 | 0.55029 | 0.51672 | 0.47369 | 0.43926 | 0.40219 | 0.34567 | 0.28649
2018-07-09 | 0.2357 | 0.2047 | 0.18566 | 0.16785 | 0.16933 | 0.1862 | 0.21566 | 0.2472 | 0.30328 | 0.3849 | 0.46499 | 0.54917 | 0.60658 | 0.62349 | 0.57232 | 0.53264 | 0.51396 | 0.48701 | 0.45524 | 0.4371 | 0.42139 | 0.43506 | 0.34131 | 0.28364
2018-07-10 | 0.23082 | 0.19877 | 0.18051 | 0.1705 | 0.16758 | 0.18026 | 0.20942 | 0.24409 | 0.2997 | 0.37322 | 0.43478 | 0.47882 | 0.52076 | 0.55134 | 0.5501 | 0.52978 | 0.49963 | 0.46767 | 0.44181 | 0.41544 | 0.40826 | 0.38609 | 0.33727 | 0.28075
2018-07-11 | 0.2299 | 0.19859 | 0.17973 | 0.17016 | 0.16792 | 0.17952 | 0.20459 | 0.23982 | 0.3037 | 0.38122 | 0.46328 | 0.54257 | 0.60567 | 0.65854 | 0.69038 | 0.69818 | 0.69142 | 0.66766 | 0.62964 | 0.5734 | 0.54128 | 0.5071 | 0.44437 | 0.37552
2018-07-12 | 0.31494 | 0.27262 | 0.24232 | 0.224 | 0.21015 | 0.21026 | 0.21384 | 0.2315 | 0.29162 | 0.38402 | 0.46659 | 0.54633 | 0.61415 | 0.65272 | 0.66418 | 0.66187 | 0.65144 | 0.61723 | 0.571 | 0.51014 | 0.4805 | 0.4407 | 0.3864 | 0.3285
2018-07-13 | 0.28448 | 0.252 | 0.22962 | 0.21276 | 0.20195 | 0.19777 | 0.19863 | 0.21768 | 0.28471 | 0.36904 | 0.44721 | 0.52275 | 0.58076 | 0.61088 | 0.63602 | 0.6538 | 0.6505 | 0.62633 | 0.5876 | 0.53919 | 0.51343 | 0.48631 | 0.42558 | 0.35791
2018-07-14 | 0.30011 | 0.26003 | 0.2317 | 0.21675 | 0.21284 | 0.22456 | 0.25296 | 0.28578 | 0.34907 | 0.43088 | 0.51889 | 0.59724 | 0.65678 | 0.6732 | 0.66085 | 0.65427 | 0.65157 | 0.65029 | 0.63349 | 0.57924 | 0.53228 | 0.48334 | 0.41286 | 0.33985
2018-07-15 | 0.28036 | 0.24187 | 0.2171 | 0.20184 | 0.19833 | 0.2103 | 0.24035 | 0.27118 | 0.3213 | 0.39749 | 0.46733 | 0.53057 | 0.57049 | 0.57081 | 0.55358 | 0.52293 | 0.50211 | 0.48771 | 0.48154 | 0.45857 | 0.45091 | 0.42689 | 0.3696 | 0.30656
2018-07-16 | 0.25558 | 0.21909 | 0.19558 | 0.1844 | 0.18283 | 0.1984 | 0.2357 | 0.26862 | 0.3297 | 0.4066 | 0.47559 | 0.53045 | 0.56564 | 0.53907 | 0.509 | 0.48486 | 0.46368 | 0.4442 | 0.43154 | 0.41045 | 0.41335 | 0.39823 | 0.34946 | 0.29207
2018-07-17 | 0.24322 | 0.21249 | 0.18982 | 0.17909 | 0.17807 | 0.19227 | 0.22321 | 0.25124 | 0.3171 | 0.3876 | 0.46232 | 0.531 | 0.5327 | 0.52136 | 0.5074 | 0.53021 | 0.56157 | 0.56527 | 0.55819 | 0.52935 | 0.50633 | 0.47369 | 0.4023 | 0.33548
2018-07-18 | 0.27162 | 0.23291 | 0.20873 | 0.19348 | 0.18783 | 0.19892 | 0.22436 | 0.25646 | 0.32055 | 0.40762 | 0.49574 | 0.58153 | 0.6561 | 0.71362 | 0.74986 | 0.77004 | 0.77011 | 0.73181 | 0.66207 | 0.59209 | 0.54979 | 0.50579 | 0.43843 | 0.37103
2018-07-19 | 0.30855 | 0.26315 | 0.23311 | 0.21481 | 0.20346 | 0.20274 | 0.2066 | 0.22607 | 0.29984 | 0.39491 | 0.48713 | 0.57239 | 0.64069 | 0.69198 | 0.71376 | 0.72127 | 0.73912 | 0.72539 | 0.67114 | 0.61468 | 0.58223 | 0.53337 | 0.46351 | 0.39581
2018-07-20 | 0.33253 | 0.28712 | 0.2541 | 0.23202 | 0.2196 | 0.21438 | 0.21496 | 0.22742 | 0.29542 | 0.39413 | 0.48573 | 0.58293 | 0.66112 | 0.71532 | 0.74199 | 0.7266 | 0.71292 | 0.69135 | 0.64525 | 0.58997 | 0.5674 | 0.52832 | 0.46311 | 0.3851
2018-07-21 | 0.31979 | 0.2763 | 0.24657 | 0.22901 | 0.22476 | 0.23676 | 0.26754 | 0.29747 | 0.35318 | 0.43357 | 0.5248 | 0.60658 | 0.66064 | 0.67012 | 0.63875 | 0.60762 | 0.57505 | 0.54639 | 0.51775 | 0.48672 | 0.48073 | 0.43859 | 0.38024 | 0.3171
2018-07-22 | 0.26071 | 0.2246 | 0.20504 | 0.19158 | 0.18961 | 0.20645 | 0.23615 | 0.26776 | 0.32625 | 0.39886 | 0.47007 | 0.52705 | 0.56276 | 0.58319 | 0.6118 | 0.62878 | 0.61586 | 0.57809 | 0.54565 | 0.51044 | 0.50063 | 0.46431 | 0.40029 | 0.33548
2018-07-23 | 0.28164 | 0.24446 | 0.22007 | 0.20527 | 0.20158 | 0.21384 | 0.24849 | 0.27735 | 0.33596 | 0.40166 | 0.46402 | 0.51678 | 0.55881 | 0.60002 | 0.64123 | 0.66282 | 0.67101 | 0.66411 | 0.65881 | 0.61186 | 0.58402 | 0.543 | 0.46311 | 0.38687
2018-07-24 | 0.32059 | 0.27323 | 0.24314 | 0.22535 | 0.21921 | 0.23042 | 0.25651 | 0.28797 | 0.35045 | 0.43782 | 0.52426 | 0.44895 | 0.6584 | 0.69212 | 0.71228 | 0.73174 | 0.75886 | 0.74315 | 0.71893 | 0.66146 | 0.61095 | 0.56313 | 0.47386 | 0.39015
2018-07-25 | 0.32563 | 0.27621 | 0.24608 | 0.22638 | 0.21718 | 0.22822 | 0.2541 | 0.28708 | 0.35951 | 0.44906 | 0.53704 | 0.62309 | 0.67766 | 0.70813 | 0.73653 | 0.7636 | 0.76733 | 0.73998 | 0.6847 | 0.6194 | 0.58606 | 0.53637 | 0.4675 | 0.39733
2018-07-26 | 0.33956 | 0.29442 | 0.26646 | 0.24376 | 0.23034 | 0.22814 | 0.23384 | 0.24945 | 0.31181 | 0.40527 | 0.50016 | 0.56797 | 0.59783 | 0.61455 | 0.60958 | 0.59125 | 0.59145 | 0.57796 | 0.54855 | 0.50883 | 0.49863 | 0.4592 | 0.40087 | 0.34951
2018-07-27 | 0.29751 | 0.25922 | 0.23416 | 0.21655 | 0.20744 | 0.20486 | 0.20694 | 0.2203 | 0.29442 | 0.39114 | 0.48108 | 0.5681 | 0.64196 | 0.70146 | 0.74099 | 0.76784 | 0.77695 | 0.7666 | 0.72098 | 0.6559 | 0.62692 | 0.57981 | 0.50117 | 0.42231
2018-07-28 | 0.35045 | 0.30545 | 0.2735 | 0.25435 | 0.24907 | 0.26259 | 0.29211 | 0.32263 | 0.39036 | 0.48532 | 0.57644 | 0.66759 | 0.73259 | 0.79495 | 0.85281 | 0.88584 | 0.89792 | 0.88451 | 0.85088 | 0.78625 | 0.74776 | 0.68691 | 0.58146 | 0.47923
2018-07-29 | 0.39675 | 0.34302 | 0.3067 | 0.28538 | 0.27617 | 0.28645 | 0.31447 | 0.34239 | 0.41179 | 0.49927 | 0.58952 | 0.67546 | 0.73481 | 0.77636 | 0.79726 | 0.78093 | 0.76506 | 0.71214 | 0.64975 | 0.5966 | 0.57486 | 0.53094 | 0.45468 | 0.38593
2018-07-30 | 0.32249 | 0.28319 | 0.25477 | 0.23892 | 0.23275 | 0.24541 | 0.27885 | 0.30656 | 0.37026 | 0.44777 | 0.51672 | 0.60223 | 0.6789 | 0.74928 | 0.78744 | 0.79056 | 0.74531 | 0.67341 | 0.62382 | 0.57682 | 0.54818 | 0.50656 | 0.43126 | 0.36112
2018-07-31 | 0.29879 | 0.25799 | 0.23182 | 0.2169 | 0.21183 | 0.22298 | 0.25393 | 0.27894 | 0.33253 | 0.41733 | 0.51564 | 0.61101 | 0.67718 | 0.72247 | 0.73833 | 0.72049 | 0.66602 | 0.61664 | 0.57631 | 0.53252 | 0.51961 | 0.48323 | 0.41836 | 0.34956
2018-08-01 | 0.29519 | 0.25718 | 0.22834 | 0.21597 | 0.2093 | 0.2216 | 0.24795 | 0.28266 | 0.347 | 0.43743 | 0.52571 | 0.6086 | 0.67457 | 0.72276 | 0.76396 | 0.78648 | 0.78322 | 0.73948 | 0.67684 | 0.61809 | 0.59454 | 0.54744 | 0.46996 | 0.39923
2018-08-02 | 0.33698 | 0.28954 | 0.25837 | 0.23773 | 0.22658 | 0.22559 | 0.2321 | 0.24682 | 0.31485 | 0.40842 | 0.49951 | 0.57454 | 0.63575 | 0.67156 | 0.70434 | 0.70286 | 0.69156 | 0.66289 | 0.61304 | 0.56414 | 0.54583 | 0.50996 | 0.44498 | 0.38355
2018-08-03 | 0.32572 | 0.28408 | 0.25477 | 0.23611 | 0.22527 | 0.22396 | 0.22874 | 0.23594 | 0.28797 | 0.36067 | 0.42014 | 0.48812 | 0.52239 | 0.53276 | 0.53655 | 0.54596 | 0.55383 | 0.54405 | 0.51859 | 0.49421 | 0.47312 | 0.43467 | 0.37286 | 0.3098
2018-08-04 | 0.25549 | 0.22183 | 0.2012 | 0.18946 | 0.18866 | 0.20448 | 0.23672 | 0.26212 | 0.31443 | 0.3864 | 0.46402 | 0.53551 | 0.55588 | 0.54658 | 0.51432 | 0.48247 | 0.45181 | 0.41879 | 0.39839 | 0.38324 | 0.39339 | 0.36894 | 0.32382 | 0.27612
2018-08-05 | 0.23295 | 0.2055 | 0.19019 | 0.18201 | 0.18158 | 0.19536 | 0.22937 | 0.25897 | 0.31644 | 0.39623 | 0.47042 | 0.54503 | 0.60769 | 0.64666 | 0.63869 | 0.63263 | 0.63862 | 0.64418 | 0.62256 | 0.57568 | 0.55489 | 0.50324 | 0.4246 | 0.35268
2018-08-06 | 0.28708 | 0.24761 | 0.22097 | 0.20493 | 0.20195 | 0.21345 | 0.2436 | 0.27437 | 0.33985 | 0.42831 | 0.51582 | 0.61599 | 0.68941 | 0.75363 | 0.79465 | 0.798 | 0.76272 | 0.72503 | 0.67526 | 0.62732 | 0.60606 | 0.55607 | 0.46533 | 0.38843
2018-08-07 | 0.31904 | 0.27481 | 0.24707 | 0.22946 | 0.22313 | 0.23517 | 0.26646 | 0.29528 | 0.36717 | 0.46135 | 0.55389 | 0.64868 | 0.72688 | 0.78292 | 0.79472 | 0.78781 | 0.7765 | 0.75697 | 0.70609 | 0.64975 | 0.60002 | 0.53399 | 0.44048 | 0.36217
2018-08-08 | 0.29806 | 0.25355 | 0.2285 | 0.21396 | 0.20759 | 0.23102 | 0.25036 | 0.27775 | 0.32482 | 0.40039 | 0.47663 | 0.56489 | 0.64989 | 0.72411 | 0.76367 | 0.76608 | 0.75298 | 0.69783 | 0.63263 | 0.57448 | 0.5542 | 0.50811 | 0.4412 | 0.38308
2018-08-09 | 0.31574 | 0.27293 | 0.24285 | 0.2244 | 0.21562 | 0.21562 | 0.22148 | 0.23969 | 0.31457 | 0.4155 | 0.51097 | 0.60132 | 0.67286 | 0.72226 | 0.75726 | 0.77827 | 0.77533 | 0.73095 | 0.66044 | 0.59505 | 0.571 | 0.52106 | 0.45226 | 0.39261
2018-08-10 | 0.33195 | 0.28909 | 0.25621 | 0.23611 | 0.22432 | 0.22018 | 0.22207 | 0.23291 | 0.30333 | 0.40272 | 0.49933 | 0.6019 | 0.67815 | 0.73804 | 0.76755 | 0.77341 | 0.76821 | 0.74776 | 0.69393 | 0.62745 | 0.59776 | 0.5371 | 0.45406 | 0.37572
2018-08-11 | 0.30929 | 0.26487 | 0.23623 | 0.21956 | 0.2143 | 0.22862 | 0.25965 | 0.28395 | 0.34444 | 0.43815 | 0.53447 | 0.63922 | 0.72425 | 0.78063 | 0.79532 | 0.79123 | 0.79338 | 0.77945 | 0.73818 | 0.67656 | 0.65245 | 0.57854 | 0.49356 | 0.40331
2018-08-12 | 0.33176 | 0.28663 | 0.25292 | 0.23327 | 0.22698 | 0.23924 | 0.27092 | 0.29797 | 0.36072 | 0.45074 | 0.53974 | 0.62679 | 0.69316 | 0.74646 | 0.76638 | 0.76484 | 0.7768 | 0.76879 | 0.74106 | 0.68207 | 0.64666 | 0.57822 | 0.48888 | 0.40762
2018-08-13 | 0.3347 | 0.29247 | 0.26157 | 0.23729 | 0.23114 | 0.24417 | 0.27753 | 0.30573 | 0.37511 | 0.46819 | 0.56119 | 0.66568 | 0.74596 | 0.80399 | 0.83401 | 0.84973 | 0.84965 | 0.813 | 0.75799 | 0.68913 | 0.66132 | 0.59854 | 0.50633 | 0.42226
2018-08-14 | 0.35318 | 0.30915 | 0.27982 | 0.26148 | 0.25347 | 0.26375 | 0.29706 | 0.32353 | 0.39182 | 0.48923 | 0.58664 | 0.66882 | 0.74336 | 0.78425 | 0.79004 | 0.73768 | 0.66309 | 0.6084 | 0.56432 | 0.52808 | 0.52082 | 0.47346 | 0.41243 | 0.34136
2018-08-15 | 0.28524 | 0.2499 | 0.22404 | 0.21264 | 0.20969 | 0.22491 | 0.26041 | 0.29207 | 0.35896 | 0.43882 | 0.52233 | 0.5867 | 0.63775 | 0.62686 | 0.53876 | 0.48579 | 0.45181 | 0.42902 | 0.40129 | 0.37557 | 0.37901 | 0.35278 | 0.31739 | 0.27472
2018-08-16 | 0.23376 | 0.20835 | 0.19187 | 0.18122 | 0.17589 | 0.17782 | 0.18772 | 0.20444 | 0.26815 | 0.37118 | 0.46853 | 0.54627 | 0.62368 | 0.63789 | 0.67849 | 0.64767 | 0.5935 | 0.53956 | 0.49057 | 0.45057 | 0.43981 | 0.40911 | 0.3656 | 0.31027
2018-08-17 | 0.26375 | 0.23162 | 0.20892 | 0.1937 | 0.18747 | 0.18775 | 0.19451 | 0.20774 | 0.26823 | 0.36606 | 0.46681 | 0.55588 | 0.63482 | 0.70441 | 0.71624 | 0.70286 | 0.70968 | 0.70707 | 0.67615 | 0.62672 | 0.61147 | 0.55781 | 0.47197 | 0.3805
2018-08-18 | 0.31804 | 0.2724 | 0.24364 | 0.2271 | 0.22357 | 0.24637 | 0.28788 | 0.30734 | 0.35656 | 0.45052 | 0.5493 | 0.64632 | 0.72354 | 0.78848 | 0.81859 | 0.84342 | 0.84742 | 0.83111 | 0.79629 | 0.73567 | 0.71228 | 0.62884 | 0.51817 | 0.42967
2018-08-19 | 0.35169 | 0.3037 | 0.27131 | 0.25158 | 0.24575 | 0.26517 | 0.30929 | 0.32744 | 0.38102 | 0.47415 | 0.56527 | 0.66173 | 0.74329 | 0.80092 | 0.83561 | 0.87807 | 0.90013 | 0.8776 | 0.83592 | 0.76543 | 0.73768 | 0.65786 | 0.54553 | 0.45018
2018-08-20 | 0.37164 | 0.32159 | 0.28891 | 0.26547 | 0.25807 | 0.27555 | 0.31804 | 0.27027 | 0.38635 | 0.48073 | 0.57144 | 0.6743 | 0.74415 | 0.81444 | 0.8438 | 0.84965 | 0.84734 | 0.82465 | 0.7765 | 0.71886 | 0.69358 | 0.62527 | 0.52583 | 0.43214
2018-08-21 | 0.3651 | 0.31612 | 0.28355 | 0.26354 | 0.25562 | 0.27415 | 0.31913 | 0.34024 | 0.39581 | 0.48265 | 0.57866 | 0.67801 | 0.75283 | 0.82033 | 0.8593 | 0.89966 | 0.90109 | 0.84235 | 0.78255 | 0.70356 | 0.68608 | 0.61127 | 0.51787 | 0.4253
2018-08-22 | 0.34912 | 0.30356 | 0.27262 | 0.25389 | 0.24645 | 0.26362 | 0.30799 | 0.32802 | 0.38169 | 0.47571 | 0.56709 | 0.66098 | 0.73941 | 0.798 | 0.82025 | 0.86886 | 0.8816 | 0.84672 | 0.79152 | 0.71193 | 0.67046 | 0.59331 | 0.5096 | 0.43165
2018-08-23 | 0.35986 | 0.31302 | 0.27749 | 0.25423 | 0.24031 | 0.23908 | 0.24546 | 0.25939 | 0.32902 | 0.43882 | 0.54244 | 0.64203 | 0.72226 | 0.77857 | 0.80444 | 0.82564 | 0.83783 | 0.82078 | 0.76777 | 0.69267 | 0.65807 | 0.59621 | 0.52408 | 0.44431
2018-08-24 | 0.37016 | 0.31927 | 0.28213 | 0.25774 | 0.24339 | 0.23798 | 0.23863 | 0.24728 | 0.3205 | 0.42738 | 0.52444 | 0.63282 | 0.72397 | 0.79204 | 0.83431 | 0.85675 | 0.85907 | 0.84642 | 0.79644 | 0.73038 | 0.70244 | 0.62085 | 0.52311 | 0.43456
2018-08-25 | 0.37037 | 0.31937 | 0.29148 | 0.27538 | 0.27446 | 0.2992 | 0.34788 | 0.36793 | 0.40666 | 0.4897 | 0.57689 | 0.65691 | 0.70911 | 0.73002 | 0.73467 | 0.73338 | 0.73761 | 0.72113 | 0.67306 | 0.6299 | 0.61914 | 0.54794 | 0.46602 | 0.38081
2018-08-26 | 0.32453 | 0.28681 | 0.26165 | 0.24724 | 0.24467 | 0.26659 | 0.31363 | 0.33167 | 0.37271 | 0.45462 | 0.53252 | 0.60821 | 0.66391 | 0.71511 | 0.75044 | 0.7793 | 0.79428 | 0.78145 | 0.73826 | 0.67485 | 0.65238 | 0.57898 | 0.47542 | 0.39161
2018-08-27 | 0.31814 | 0.27323 | 0.24265 | 0.22503 | 0.21866 | 0.23668 | 0.28013 | 0.29574 | 0.34097 | 0.42738 | 0.50954 | 0.59415 | 0.66588 | 0.72667 | 0.77496 | 0.81022 | 0.83126 | 0.81814 | 0.77474 | 0.70532 | 0.68332 | 0.60756 | 0.50555 | 0.4209
2018-08-28 | 0.34936 | 0.30365 | 0.27166 | 0.25124 | 0.24302 | 0.26204 | 0.30957 | 0.32792 | 0.37378 | 0.44504 | 0.5049 | 0.55856 | 0.62289 | 0.69114 | 0.75544 | 0.79681 | 0.81519 | 0.78389 | 0.72148 | 0.67224 | 0.6429 | 0.56495 | 0.47657 | 0.39728
2018-08-29 | 0.32673 | 0.28506 | 0.25824 | 0.24047 | 0.23582 | 0.25503 | 0.30222 | 0.32654 | 0.37906 | 0.47323 | 0.56854 | 0.64485 | 0.70272 | 0.75952 | 0.80069 | 0.82434 | 0.8164 | 0.76491 | 0.70125 | 0.64029 | 0.61769 | 0.55097 | 0.47749 | 0.41308
2018-08-30 | 0.35328 | 0.3098 | 0.27978 | 0.25884 | 0.24995 | 0.25841 | 0.26148 | 0.27232 | 0.33152 | 0.43379 | 0.53015 | 0.62805 | 0.69727 | 0.75276 | 0.79502 | 0.81353 | 0.81097 | 0.76689 | 0.69191 | 0.6303 | 0.60808 | 0.54491 | 0.4779 | 0.41712
2018-08-31 | 0.35527 | 0.30827 | 0.27485 | 0.25545 | 0.24211 | 0.23639 | 0.23986 | 0.24949 | 0.31673 | 0.42569 | 0.51618 | 0.60255 | 0.67794 | 0.73138 | 0.75573 | 0.76367 | 0.74711 | 0.71518 | 0.64975 | 0.59061 | 0.57353 | 0.51558 | 0.44895 | 0.38334
2018-09-01 | 0.32587 | 0.28878 | 0.26178 | 0.24244 | 0.23627 | 0.23994 | 0.25129 | 0.25651 | 0.32026 | 0.42831 | 0.52893 | 0.63342 | 0.69462 | 0.74293 | 0.78559 | 0.8004 | 0.78848 | 0.75886 | 0.70946 | 0.65056 | 0.63282 | 0.56088 | 0.4707 | 0.3936
2018-09-02 | 0.32716 | 0.28399 | 0.25528 | 0.239 | 0.2336 | 0.25267 | 0.29683 | 0.31532 | 0.35761 | 0.44181 | 0.52317 | 0.61271 | 0.67994 | 0.72269 | 0.76989 | 0.79778 | 0.80369 | 0.77812 | 0.72233 | 0.66261 | 0.62851 | 0.53931 | 0.44309 | 0.35791
2018-09-03 | 0.29347 | 0.25326 | 0.2287 | 0.21326 | 0.20923 | 0.22754 | 0.27306 | 0.29076 | 0.32854 | 0.39892 | 0.45181 | 0.51044 | 0.56892 | 0.63336 | 0.68152 | 0.69797 | 0.70799 | 0.6847 | 0.64411 | 0.59286 | 0.57752 | 0.51175 | 0.42842 | 0.34616
2018-09-04 | 0.28524 | 0.24595 | 0.22187 | 0.20763 | 0.2038 | 0.22172 | 0.26841 | 0.28524 | 0.31223 | 0.37271 | 0.44164 | 0.50253 | 0.55594 | 0.60827 | 0.63083 | 0.64043 | 0.65198 | 0.63455 | 0.60352 | 0.57568 | 0.56785 | 0.50241 | 0.4189 | 0.34651
2018-09-05 | 0.2864 | 0.24882 | 0.22626 | 0.21268 | 0.21057 | 0.22954 | 0.27921 | 0.29769 | 0.33853 | 0.41982 | 0.50561 | 0.5883 | 0.66227 | 0.7207 | 0.75472 | 0.75682 | 0.7239 | 0.65969 | 0.59479 | 0.55246 | 0.52832 | 0.46973 | 0.40911 | 0.35338
2018-09-06 | 0.29906 | 0.26569 | 0.24109 | 0.2248 | 0.21714 | 0.21702 | 0.22658 | 0.24261 | 0.29669 | 0.37547 | 0.44203 | 0.4958 | 0.52844 | 0.52414 | 0.51379 | 0.50034 | 0.47473 | 0.45462 | 0.43165 | 0.41998 | 0.42009 | 0.38807 | 0.35025 | 0.30967
2018-09-07 | 0.26724 | 0.23186 | 0.20911 | 0.194 | 0.18841 | 0.18939 | 0.19706 | 0.20721 | 0.25499 | 0.32396 | 0.3925 | 0.46659 | 0.53124 | 0.57765 | 0.59983 | 0.58465 | 0.55838 | 0.52293 | 0.47202 | 0.45592 | 0.45518 | 0.40933 | 0.34862 | 0.28959
2018-09-08 | 0.24508 | 0.2169 | 0.19617 | 0.18419 | 0.18343 | 0.20508 | 0.24986 | 0.26758 | 0.2976 | 0.37419 | 0.45976 | 0.54109 | 0.60958 | 0.66384 | 0.70483 | 0.72233 | 0.72042 | 0.70469 | 0.64821 | 0.61704 | 0.59576 | 0.52154 | 0.43622 | 0.35836
2018-09-09 | 0.29669 | 0.25575 | 0.23146 | 0.21659 | 0.21061 | 0.22826 | 0.27406 | 0.29148 | 0.32301 | 0.39418 | 0.47524 | 0.55345 | 0.62302 | 0.68643 | 0.71617 | 0.7482 | 0.74034 | 0.70658 | 0.65313 | 0.61121 | 0.58274 | 0.5017 | 0.41501 | 0.33999
2018-09-10 | 0.28386 | 0.24957 | 0.22774 | 0.2128 | 0.20965 | 0.22994 | 0.27683 | 0.29306 | 0.32415 | 0.38697 | 0.46522 | 0.53331 | 0.5966 | 0.6536 | 0.68767 | 0.7037 | 0.69741 | 0.66889 | 0.62256 | 0.58862 | 0.56866 | 0.48976 | 0.40772 | 0.33219
2018-09-11 | 0.27472 | 0.24006 | 0.21667 | 0.20255 | 0.19941 | 0.21815 | 0.2647 | 0.28244 | 0.31041 | 0.37716 | 0.4432 | 0.50348 | 0.54986 | 0.58389 | 0.59576 | 0.59944 | 0.5772 | 0.53441 | 0.4965 | 0.47565 | 0.46533 | 0.41265 | 0.35661 | 0.29451
2018-09-12 | 0.23753 | 0.21091 | 0.19282 | 0.1839 | 0.1839 | 0.20433 | 0.25359 | 0.26871 | 0.30103 | 0.35831 | 0.41474 | 0.46493 | 0.51672 | 0.56797 | 0.58102 | 0.576 | 0.57962 | 0.58395 | 0.54448 | 0.50146 | 0.48456 | 0.43594 | 0.38438 | 0.32568
2018-09-13 | 0.26698 | 0.23102 | 0.20709 | 0.1887 | 0.18144 | 0.18076 | 0.19063 | 0.20444 | 0.24874 | 0.31941 | 0.4023 | 0.48352 | 0.55004 | 0.59305 | 0.61075 | 0.60873 | 0.5837 | 0.5488 | 0.49204 | 0.46414 | 0.44699 | 0.39502 | 0.33713 | 0.28182
2018-09-14 | 0.24068 | 0.20957 | 0.18848 | 0.17484 | 0.16697 | 0.16567 | 0.17098 | 0.17849 | 0.22937 | 0.30665 | 0.38801 | 0.47093 | 0.5371 | 0.58319 | 0.6071 | 0.6152 | 0.61645 | 0.58523 | 0.53148 | 0.50099 | 0.48497 | 0.42754 | 0.36278 | 0.29483
2018-09-15 | 0.24778 | 0.21566 | 0.1968 | 0.18656 | 0.18616 | 0.20611 | 0.25074 | 0.26958 | 0.30305 | 0.37742 | 0.47617 | 0.55682 | 0.62758 | 0.69191 | 0.73854 | 0.77033 | 0.77606 | 0.75501 | 0.70265 | 0.66391 | 0.63575 | 0.5506 | 0.46237 | 0.36732
2018-09-16 | 0.30039 | 0.26152 | 0.23323 | 0.21605 | 0.21134 | 0.22854 | 0.27472 | 0.29229 | 0.32511 | 0.39539 | 0.47911 | 0.56169 | 0.62792 | 0.67904 | 0.66984 | 0.64183 | 0.61927 | 0.59331 | 0.56451 | 0.55333 | 0.53155 | 0.46254 | 0.38916 | 0.31861
2018-09-17 | 0.25931 | 0.22563 | 0.20319 | 0.18964 | 0.18855 | 0.20915 | 0.25727 | 0.2745 | 0.30135 | 0.35482 | 0.42781 | 0.4873 | 0.5324 | 0.55707 | 0.58472 | 0.58306 | 0.54411 | 0.50075 | 0.47179 | 0.47663 | 0.46847 | 0.41814 | 0.3507 | 0.28364
2018-09-18 | 0.23676 | 0.20414 | 0.1879 | 0.17708 | 0.17617 | 0.19584 | 0.24302 | 0.26003 | 0.28721 | 0.34376 | 0.40235 | 0.46721 | 0.53301 | 0.59634 | 0.6429 | 0.66971 | 0.66064 | 0.66473 | 0.60762 | 0.57479 | 0.54639 | 0.4764 | 0.39744 | 0.32197
2018-09-19 | 0.26569 | 0.2285 | 0.20721 | 0.19407 | 0.19172 | 0.21064 | 0.25837 | 0.27982 | 0.30809 | 0.37179 | 0.42891 | 0.46624 | 0.47761 | 0.45897 | 0.42809 | 0.41399 | 0.40129 | 0.38895 | 0.3745 | 0.37994 | 0.37373 | 0.34268 | 0.30048 | 0.25659
2018-09-20 | 0.2157 | 0.18979 | 0.17352 | 0.16482 | 0.16047 | 0.16479 | 0.17821 | 0.19636 | 0.23263 | 0.29342 | 0.35293 | 0.40347 | 0.44275 | 0.46939 | 0.47248 | 0.43143 | 0.39855 | 0.38257 | 0.35801 | 0.36333 | 0.35801 | 0.32244 | 0.28164 | 0.24129
2018-09-21 | 0.20576 | 0.17842 | 0.16155 | 0.15104 | 0.14663 | 0.14775 | 0.15602 | 0.1657 | 0.20539 | 0.27424 | 0.34547 | 0.41841 | 0.48166 | 0.52832 | 0.56088 | 0.5734 | 0.57163 | 0.54843 | 0.49798 | 0.47548 | 0.4513 | 0.38968 | 0.32826 | 0.26478
2018-09-22 | 0.21862 | 0.18928 | 0.17098 | 0.16364 | 0.16543 | 0.18855 | 0.23376 | 0.25583 | 0.28564 | 0.34317 | 0.40586 | 0.4651 | 0.51205 | 0.52208 | 0.50942 | 0.4935 | 0.48456 | 0.46727 | 0.45665 | 0.46305 | 0.44148 | 0.38438 | 0.31951 | 0.25952
2018-09-23 | 0.21368 | 0.1848 | 0.16659 | 0.15748 | 0.15844 | 0.1824 | 0.23271 | 0.25617 | 0.26836 | 0.3048 | 0.33244 | 0.36681 | 0.39271 | 0.39839 | 0.40129 | 0.40778 | 0.41663 | 0.43116 | 0.42161 | 0.43429 | 0.42318 | 0.3725 | 0.31372 | 0.25359
2018-09-24 | 0.20774 | 0.18016 | 0.16724 | 0.15744 | 0.15645 | 0.1797 | 0.22858 | 0.25137 | 0.27049 | 0.30753 | 0.34503 | 0.38427 | 0.41168 | 0.44626 | 0.48695 | 0.52021 | 0.52335 | 0.50972 | 0.48619 | 0.48579 | 0.47266 | 0.4202 | 0.34971 | 0.28909
2018-09-25 | 0.24133 | 0.20907 | 0.18928 | 0.17733 | 0.17663 | 0.19275 | 0.23062 | 0.25587 | 0.28757 | 0.34872 | 0.41421 | 0.46022 | 0.48579 | 0.50895 | 0.5406 | 0.56709 | 0.548 | 0.49839 | 0.46584 | 0.46078 | 0.44348 | 0.39072 | 0.32878 | 0.27481
2018-09-26 | 0.22946 | 0.20128 | 0.1839 | 0.17393 | 0.17373 | 0.19547 | 0.24269 | 0.26741 | 0.28864 | 0.3309 | 0.38916 | 0.46022 | 0.51745 | 0.57669 | 0.59795 | 0.59996 | 0.57835 | 0.53735 | 0.49627 | 0.49005 | 0.4671 | 0.42031 | 0.36283 | 0.34523
2018-09-27 | 0.28395 | 0.23271 | 0.21345 | 0.20008 | 0.19499 | 0.19721 | 0.20869 | 0.22341 | 0.27415 | 0.35681 | 0.43462 | 0.51373 | 0.58013 | 0.62739 | 0.66132 | 0.66302 | 0.62052 | 0.5772 | 0.52106 | 0.5074 | 0.47582 | 0.42902 | 0.37189 | 0.31288
2018-09-28 | 0.2647 | 0.23218 | 0.20961 | 0.19462 | 0.18786 | 0.18877 | 0.19636 | 0.20969 | 0.25414 | 0.33326 | 0.41335 | 0.49315 | 0.56533 | 0.61921 | 0.654 | 0.66493 | 0.64989 | 0.60697 | 0.54479 | 0.54355 | 0.52015 | 0.45778 | 0.38334 | 0.3119
2018-09-29 | 0.26285 | 0.2265 | 0.20671 | 0.19462 | 0.19466 | 0.21516 | 0.26272 | 0.2844 | 0.31265 | 0.3819 | 0.46288 | 0.54911 | 0.60534 | 0.65434 | 0.67952 | 0.67932 | 0.66214 | 0.61677 | 0.56797 | 0.54849 | 0.49204 | 0.42765 | 0.35357 | 0.28882
2018-09-30 | 0.2379 | 0.20698 | 0.18888 | 0.17846 | 0.17835 | 0.19959 | 0.25217 | 0.27118 | 0.30365 | 0.37052 | 0.44248 | 0.50835 | 0.56401 | 0.58306 | 0.60067 | 0.57315 | 0.56942 | 0.56119 | 0.53075 | 0.53441 | 0.51085 | 0.45141 | 0.37711 | 0.30656
2018-10-01 | 0.25494 | 0.22128 | 0.20308 | 0.19234 | 0.19059 | 0.21338 | 0.26599 | 0.28538 | 0.31955 | 0.38791 | 0.45671 | 0.52911 | 0.59048 | 0.63782 | 0.65868 | 0.69497 | 0.71673 | 0.69476 | 0.64324 | 0.61822 | 0.58504 | 0.51121 | 0.42041 | 0.3769
2018-10-02 | 0.29451 | 0.24757 | 0.22408 | 0.20972 | 0.20611 | 0.22547 | 0.27468 | 0.2932 | 0.32893 | 0.40368 | 0.48643 | 0.56019 | 0.62382 | 0.69212 | 0.73045 | 0.75799 | 0.7743 | 0.74682 | 0.6858 | 0.65569 | 0.6173 | 0.53374 | 0.44755 | 0.36147
2018-10-03 | 0.29952 | 0.26003 | 0.23146 | 0.21578 | 0.2098 | 0.22722 | 0.27468 | 0.2966 | 0.33669 | 0.41706 | 0.50348 | 0.5892 | 0.6509 | 0.72091 | 0.7577 | 0.77783 | 0.77687 | 0.71504 | 0.63037 | 0.5858 | 0.52972 | 0.46505 | 0.39691 | 0.33398
2018-10-04 | 0.27965 | 0.24014 | 0.21651 | 0.20075 | 0.1933 | 0.19588 | 0.20755 | 0.22266 | 0.27696 | 0.35701 | 0.4246 | 0.48829 | 0.54546 | 0.58115 | 0.59447 | 0.58651 | 0.55906 | 0.51895 | 0.46904 | 0.46067 | 0.43379 | 0.38484 | 0.32888 | 0.27516
2018-10-05 | 0.22476 | 0.18671 | 0.16047 | 0.14127 | 0.13119 | 0.12857 | 0.13307 | 0.13746 | 0.16151 | 0.20079 | 0.24331 | 0.27577 | 0.31298 | 0.34774 | 0.37803 | 0.40098 | 0.42383 | 0.4148 | 0.3804 | 0.37762 | 0.35886 | 0.3106 | 0.2568 | 0.2052
2018-10-06 | 0.16789 | 0.14373 | 0.12992 | 0.12302 | 0.12464 | 0.14608 | 0.18732 | 0.20683 | 0.22678 | 0.26599 | 0.30883 | 0.34951 | 0.39465 | 0.42957 | 0.46607 | 0.47773 | 0.49075 | 0.47254 | 0.4544 | 0.47329 | 0.44415 | 0.38547 | 0.32463 | 0.26302
2018-10-07 | 0.21411 | 0.18718 | 0.17071 | 0.16054 | 0.15831 | 0.17744 | 0.22499 | 0.24845 | 0.25948 | 0.30094 | 0.34892 | 0.38479 | 0.41534 | 0.44181 | 0.45535 | 0.44917 | 0.44839 | 0.43771 | 0.42962 | 0.45063 | 0.42678 | 0.38578 | 0.31937 | 0.25191
2018-10-08 | 0.20717 | 0.18048 | 0.16249 | 0.15388 | 0.15487 | 0.17659 | 0.2246 | 0.24442 | 0.26564 | 0.31767 | 0.38128 | 0.43865 | 0.49556 | 0.54165 | 0.58064 | 0.59867 | 0.59712 | 0.5779 | 0.54374 | 0.54405 | 0.51313 | 0.44816 | 0.37439 | 0.30665
2018-10-09 | 0.25066 | 0.21807 | 0.19673 | 0.18172 | 0.17941 | 0.17533 | 0.24228 | 0.26191 | 0.28797 | 0.35338 | 0.42172 | 0.48707 | 0.539 | 0.59125 | 0.62825 | 0.65333 | 0.65779 | 0.63362 | 0.58095 | 0.56967 | 0.5324 | 0.46311 | 0.39109 | 0.3149
2018-10-10 | 0.25672 | 0.21846 | 0.19703 | 0.18229 | 0.1797 | 0.19762 | 0.24351 | 0.26564 | 0.29419 | 0.36102 | 0.4333 | 0.49362 | 0.54998 | 0.59886 | 0.63322 | 0.65698 | 0.66173 | 0.62864 | 0.56376 | 0.54171 | 0.50111 | 0.44264 | 0.38133 | 0.32088
2018-10-11 | 0.26659 | 0.23006 | 0.20812 | 0.19238 | 0.18383 | 0.18426 | 0.1944 | 0.20527 | 0.25267 | 0.33693 | 0.41566 | 0.48806 | 0.54769 | 0.59512 | 0.62844 | 0.65009 | 0.65427 | 0.62593 | 0.557 | 0.52729 | 0.48695 | 0.42847 | 0.37404 | 0.31386
2018-10-12 | 0.26379 | 0.22642 | 0.20001 | 0.18426 | 0.17691 | 0.17554 | 0.18261 | 0.18804 | 0.23782 | 0.32572 | 0.40676 | 0.48137 | 0.54911 | 0.59518 | 0.62672 | 0.64404 | 0.64599 | 0.62105 | 0.56313 | 0.55825 | 0.51847 | 0.4531 | 0.38963 | 0.32206
2018-10-13 | 0.27036 | 0.23599 | 0.2155 | 0.2038 | 0.20406 | 0.22567 | 0.27149 | 0.29184 | 0.31993 | 0.38365 | 0.46186 | 0.52905 | 0.5786 | 0.62006 | 0.64888 | 0.66807 | 0.66547 | 0.63835 | 0.58792 | 0.58568 | 0.54312 | 0.47715 | 0.40288 | 0.33008
2018-10-14 | 0.27433 | 0.24166 | 0.22262 | 0.21022 | 0.20732 | 0.22982 | 0.28248 | 0.30406 | 0.33272 | 0.39981 | 0.47002 | 0.53289 | 0.57924 | 0.6309 | 0.65969 | 0.66759 | 0.65191 | 0.61219 | 0.57758 | 0.58612 | 0.53882 | 0.46922 | 0.3924 | 0.3179
2018-10-15 | 0.25634 | 0.22007 | 0.19982 | 0.18765 | 0.1879 | 0.20843 | 0.25706 | 0.2808 | 0.30596 | 0.36202 | 0.41874 | 0.47617 | 0.41674 | 0.55352 | 0.56326 | 0.57037 | 0.55327 | 0.5265 | 0.4948 | 0.50235 | 0.46141 | 0.40251 | 0.33066 | 0.26676
2018-10-16 | 0.21597 | 0.18516 | 0.16727 | 0.15559 | 0.15052 | 0.16472 | 0.20263 | 0.21671 | 0.23126 | 0.26884 | 0.30693 | 0.33824 | 0.3722 | 0.40831 | 0.44203 | 0.47669 | 0.49686 | 0.4866 | 0.4466 | 0.44292 | 0.40671 | 0.34714 | 0.28244 | 0.22109
2018-10-17 | 0.17393 | 0.145 | 0.12986 | 0.12139 | 0.11933 | 0.13454 | 0.17005 | 0.18714 | 0.20504 | 0.24051 | 0.27586 | 0.30985 | 0.33946 | 0.37516 | 0.41136 | 0.44526 | 0.46209 | 0.44677 | 0.40002 | 0.38453 | 0.34596 | 0.29596 | 0.25187 | 0.20576
2018-10-18 | 0.17033 | 0.14152 | 0.12488 | 0.11586 | 0.11189 | 0.11547 | 0.12674 | 0.13899 | 0.1722 | 0.22069 | 0.2656 | 0.30559 | 0.34779 | 0.38671 | 0.42367 | 0.4531 | 0.46408 | 0.44699 | 0.39981 | 0.38744 | 0.3505 | 0.30222 | 0.25999 | 0.21372
2018-10-19 | 0.17659 | 0.14997 | 0.13203 | 0.12177 | 0.1176 | 0.11778 | 0.12541 | 0.13301 | 0.16727 | 0.21924 | 0.2701 | 0.31715 | 0.3693 | 0.41168 | 0.44733 | 0.46916 | 0.47674 | 0.45971 | 0.4228 | 0.42585 | 0.39208 | 0.33504 | 0.28058 | 0.22686
2018-10-20 | 0.18437 | 0.15628 | 0.14074 | 0.13295 | 0.1334 | 0.15134 | 0.18997 | 0.21153 | 0.23704 | 0.29071 | 0.34779 | 0.39971 | 0.44621 | 0.48416 | 0.51967 | 0.53027 | 0.52293 | 0.49845 | 0.47484 | 0.48329 | 0.44153 | 0.38009 | 0.31555 | 0.25461
2018-10-21 | 0.20637 | 0.17963 | 0.16496 | 0.15605 | 0.15671 | 0.17687 | 0.22357 | 0.24899 | 0.25905 | 0.2932 | 0.3335 | 0.35906 | 0.37695 | 0.38578 | 0.38791 | 0.38978 | 0.38583 | 0.37819 | 0.37793 | 0.40029 | 0.37205 | 0.32902 | 0.27441 | 0.21714
2018-10-22 | 0.17839 | 0.15431 | 0.14114 | 0.13487 | 0.13635 | 0.15382 | 0.20207 | 0.22766 | 0.23871 | 0.2691 | 0.30999 | 0.35328 | 0.38682 | 0.41668 | 0.43915 | 0.45214 | 0.44454 | 0.42574 | 0.41712 | 0.43148 | 0.40076 | 0.35134 | 0.29067 | 0.23218
2018-10-23 | 0.18877 | 0.1656 | 0.15088 | 0.14231 | 0.14136 | 0.15991 | 0.20686 | 0.23235 | 0.23871 | 0.26452 | 0.29569 | 0.32287 | 0.34631 | 0.36167 | 0.37613 | 0.38288 | 0.37896 | 0.36813 | 0.36011 | 0.37465 | 0.36132 | 0.32031 | 0.26854 | 0.21823
2018-10-24 | 0.17955 | 0.15553 | 0.14237 | 0.13675 | 0.13852 | 0.15582 | 0.19503 | 0.22136 | 0.23806 | 0.27149 | 0.30076 | 0.3224 | 0.3334 | 0.34542 | 0.35477 | 0.36328 | 0.36237 | 0.35109 | 0.34165 | 0.34685 | 0.32126 | 0.28954 | 0.25499 | 0.21134
2018-10-25 | 0.16998 | 0.14297 | 0.12645 | 0.11658 | 0.11315 | 0.11575 | 0.12654 | 0.14064 | 0.17026 | 0.21496 | 0.25553 | 0.28752 | 0.31644 | 0.3443 | 0.3658 | 0.38174 | 0.3821 | 0.36298 | 0.32941 | 0.32496 | 0.29587 | 0.26225 | 0.2281 | 0.18804
2018-10-26 | 0.15526 | 0.13298 | 0.1202 | 0.11164 | 0.1082 | 0.10889 | 0.11583 | 0.12692 | 0.15323 | 0.1971 | 0.23928 | 0.27319 | 0.3036 | 0.33475 | 0.36077 | 0.38122 | 0.39052 | 0.37716 | 0.34719 | 0.35626 | 0.32491 | 0.27696 | 0.22591 | 0.176
2018-10-27 | 0.13955 | 0.11847 | 0.10699 | 0.102 | 0.10374 | 0.12124 | 0.15971 | 0.18369 | 0.19677 | 0.23186 | 0.26984 | 0.30628 | 0.33805 | 0.37322 | 0.4048 | 0.43467 | 0.45052 | 0.43859 | 0.41448 | 0.4246 | 0.38345 | 0.32406 | 0.26294 | 0.20417
2018-10-28 | 0.1632 | 0.13892 | 0.12452 | 0.11749 | 0.11786 | 0.13657 | 0.17846 | 0.20132 | 0.21624 | 0.25884 | 0.3014 | 0.34488 | 0.38257 | 0.43132 | 0.46813 | 0.49539 | 0.50871 | 0.49309 | 0.46095 | 0.46956 | 0.4247 | 0.36767 | 0.30117 | 0.23933
2018-10-29 | 0.19459 | 0.16605 | 0.14823 | 0.1388 | 0.13877 | 0.15658 | 0.20286 | 0.22412 | 0.23859 | 0.29184 | 0.33926 | 0.3863 | 0.43313 | 0.47427 | 0.50799 | 0.53784 | 0.5438 | 0.5163 | 0.47432 | 0.47444 | 0.43203 | 0.37337 | 0.30633 | 0.24187
2018-10-30 | 0.19026 | 0.16158 | 0.1436 | 0.13392 | 0.13279 | 0.15004 | 0.19289 | 0.2157 | 0.2297 | 0.27648 | 0.33032 | 0.37757 | 0.41982 | 0.45547 | 0.47669 | 0.49333 | 0.5049 | 0.48282 | 0.45355 | 0.45948 | 0.41847 | 0.36712 | 0.30489 | 0.24417
2018-10-31 | 0.19466 | 0.16492 | 0.14561 | 0.1362 | 0.13423 | 0.1513 | 0.19448 | 0.21842 | 0.23408 | 0.27978 | 0.32501 | 0.36849 | 0.40209 | 0.42623 | 0.44454 | 0.45852 | 0.46158 | 0.43264 | 0.38246 | 0.35626 | 0.30915 | 0.27101 | 0.22858 | 0.18534
2018-11-01 | 0.1466 | 0.12273 | 0.10994 | 0.10312 | 0.10067 | 0.10344 | 0.11555 | 0.12857 | 0.15678 | 0.19459 | 0.22452 | 0.23892 | 0.2445 | 0.24434 | 0.24604 | 0.24716 | 0.2436 | 0.23058 | 0.22168 | 0.23449 | 0.21446 | 0.19052 | 0.16343 | 0.13734
2018-11-02 | 0.43572 | 0.095926 | 0.093688 | 0.093509 | 0.096496 | 0.10563 | 0.12264 | 0.15711 | 0.19055 | 0.20489 | 0.20694 | 0.20297 | 0.19933 | 0.19367 | 0.19114 | 0.18844 | 0.1895 | 0.20554 | 0.239 | 0.22929 | 0.21264 | 0.18566 | 0.15385 | 0.12779
2018-11-03 | 0.10795 | 0.10202 | 0.098768 | 0.10001 | 0.10721 | 0.13353 | 0.18276 | 0.20429 | 0.21003 | 0.21745 | 0.22654 | 0.23348 | 0.23428 | 0.23554 | 0.23291 | 0.22889 | 0.23247 | 0.24828 | 0.28315 | 0.27145 | 0.24928 | 0.21345 | 0.1746 | 0.14055
2018-11-04 | 0.11878 | 0.10577 | 0.098794 | 0.097459 | 0.10075 | 0.12089 | 0.15748 | 0.1862 | 0.21038 | 0.22998 | 0.2497 | 0.2675 | 0.27617 | 0.28413 | 0.28842 | 0.29189 | 0.28636 | 0.29542 | 0.33176 | 0.32026 | 0.29415 | 0.2499 | 0.20877 | 0.17057
2018-11-05 | 0.14209 | 0.12396 | 0.11504 | 0.11083 | 0.11363 | 0.13322 | 0.17199 | 0.18613 | 0.22396 | 0.26341 | 0.29528 | 0.32112 | 0.33873 | 0.34754 | 0.3509 | 0.3443 | 0.33335 | 0.34185 | 0.37552 | 0.35851 | 0.33027 | 0.28811 | 0.23676 | 0.1895
2018-11-06 | 0.15539 | 0.13438 | 0.12159 | 0.11507 | 0.11606 | 0.13604 | 0.17355 | 0.20376 | 0.23729 | 0.2774 | 0.31955 | 0.35661 | 0.3863 | 0.40895 | 0.41998 | 0.41917 | 0.40061 | 0.38324 | 0.40177 | 0.37409 | 0.33157 | 0.27982 | 0.22563 | 0.17987
2018-11-07 | 0.14497 | 0.12423 | 0.112 | 0.10741 | 0.1085 | 0.12562 | 0.16391 | 0.19066 | 0.22183 | 0.25918 | 0.29469 | 0.32802 | 0.35586 | 0.37921 | 0.38942 | 0.38723 | 0.36651 | 0.35011 | 0.36097 | 0.32635 | 0.29202 | 0.2538 | 0.2171 | 0.18126
2018-11-08 | 0.14971 | 0.12851 | 0.11478 | 0.10905 | 0.1079 | 0.11281 | 0.12514 | 0.15101 | 0.20188 | 0.2477 | 0.28164 | 0.30994 | 0.3348 | 0.34542 | 0.34385 | 0.33239 | 0.3163 | 0.32149 | 0.33306 | 0.30411 | 0.27564 | 0.24376 | 0.21172 | 0.17715
2018-11-09 | 0.14978 | 0.12842 | 0.1166 | 0.11063 | 0.10823 | 0.11161 | 0.12011 | 0.13892 | 0.17849 | 0.21237 | 0.23255 | 0.24479 | 0.24633 | 0.24018 | 0.23388 | 0.22408 | 0.22187 | 0.24438 | 0.26495 | 0.24986 | 0.22838 | 0.19881 | 0.16957 | 0.13771
2018-11-10 | 0.1145 | 0.10251 | 0.096367 | 0.093841 | 0.096964 | 0.1113 | 0.14991 | 0.18426 | 0.20079 | 0.22179 | 0.23855 | 0.25376 | 0.26513 | 0.27529 | 0.28036 | 0.28444 | 0.27982 | 0.28717 | 0.31518 | 0.29465 | 0.26388 | 0.22444 | 0.18609 | 0.14936
2018-11-11 | 0.11979 | 0.10398 | 0.095874 | 0.092948 | 0.095023 | 0.1071 | 0.13313 | 0.16256 | 0.1907 | 0.21749 | 0.23863 | 0.25439 | 0.2694 | 0.28364 | 0.2904 | 0.29669 | 0.29121 | 0.29415 | 0.32145 | 0.30218 | 0.27097 | 0.23118 | 0.19015 | 0.14984
2018-11-12 | 0.11936 | 0.1032 | 0.096159 | 0.093254 | 0.096808 | 0.11422 | 0.15395 | 0.17917 | 0.19773 | 0.2227 | 0.24965 | 0.2749 | 0.29801 | 0.32258 | 0.3396 | 0.34582 | 0.3365 | 0.33022 | 0.35382 | 0.33046 | 0.29655 | 0.25465 | 0.20873 | 0.16553
2018-11-13 | 0.13392 | 0.11658 | 0.10656 | 0.10355 | 0.10596 | 0.12358 | 0.16337 | 0.19055 | 0.2164 | 0.25099 | 0.28382 | 0.30925 | 0.33495 | 0.35836 | 0.36904 | 0.37052 | 0.35721 | 0.35001 | 0.37072 | 0.34641 | 0.31055 | 0.26538 | 0.21535 | 0.17209
2018-11-14 | 0.13908 | 0.11907 | 0.10867 | 0.10342 | 0.10466 | 0.12049 | 0.15974 | 0.18783 | 0.21396 | 0.24364 | 0.27101 | 0.28981 | 0.30799 | 0.32154 | 0.3296 | 0.3295 | 0.31551 | 0.31106 | 0.32587 | 0.29934 | 0.26975 | 0.23517 | 0.20289 | 0.16909
2018-11-15 | 0.14108 | 0.12221 | 0.11211 | 0.1068 | 0.10634 | 0.11189 | 0.12591 | 0.14952 | 0.18993 | 0.22722 | 0.25313 | 0.2738 | 0.28793 | 0.30057 | 0.30531 | 0.30264 | 0.29112 | 0.28882 | 0.30536 | 0.28 | 0.25376 | 0.2265 | 0.19926 | 0.17105
2018-11-16 | 0.14411 | 0.12737 | 0.117 | 0.11141 | 0.10977 | 0.11428 | 0.12267 | 0.14202 | 0.19132 | 0.24199 | 0.28195 | 0.31293 | 0.33999 | 0.35751 | 0.36504 | 0.36459 | 0.3505 | 0.34788 | 0.3696 | 0.34587 | 0.31116 | 0.27232 | 0.23364 | 0.193
2018-11-17 | 0.16198 | 0.1444 | 0.13481 | 0.13073 | 0.13604 | 0.15854 | 0.20417 | 0.23364 | 0.27036 | 0.32358 | 0.37824 | 0.42231 | 0.45518 | 0.47375 | 0.47622 | 0.46819 | 0.45141 | 0.45192 | 0.46887 | 0.43401 | 0.38453 | 0.32444 | 0.26836 | 0.21307
2018-11-18 | 0.17397 | 0.15075 | 0.13567 | 0.12821 | 0.13001 | 0.14708 | 0.19348 | 0.2227 | 0.24778 | 0.27744 | 0.2982 | 0.30218 | 0.29207 | 0.28124 | 0.26698 | 0.25309 | 0.25372 | 0.28182 | 0.31153 | 0.30213 | 0.27978 | 0.24682 | 0.20614 | 0.17088
2018-11-19 | 0.14775 | 0.1379 | 0.13399 | 0.13454 | 0.14379 | 0.17324 | 0.23835 | 0.26984 | 0.28306 | 0.28959 | 0.28605 | 0.27262 | 0.25676 | 0.24525 | 0.23639 | 0.23311 | 0.23863 | 0.27145 | 0.30623 | 0.30053 | 0.28324 | 0.25078 | 0.21164 | 0.17477
2018-11-20 | 0.1503 | 0.13871 | 0.13592 | 0.13709 | 0.14688 | 0.17624 | 0.23445 | 0.26012 | 0.25414 | 0.25406 | 0.25187 | 0.2492 | 0.245 | 0.24076 | 0.23392 | 0.23062 | 0.2321 | 0.26199 | 0.29642 | 0.29112 | 0.2721 | 0.24096 | 0.20346 | 0.16727
2018-11-21 | 0.14143 | 0.12645 | 0.12145 | 0.11849 | 0.12267 | 0.15127 | 0.19577 | 0.22385 | 0.23408 | 0.24417 | 0.2528 | 0.25477 | 0.24774 | 0.24285 | 0.23696 | 0.23166 | 0.23477 | 0.25867 | 0.27415 | 0.26029 | 0.24228 | 0.21835 | 0.19191 | 0.1634
2018-11-22 | 0.13777 | 0.12238 | 0.11419 | 0.11136 | 0.11239 | 0.11896 | 0.13478 | 0.15758 | 0.19971 | 0.24023 | 0.26513 | 0.27903 | 0.27978 | 0.2789 | 0.2745 | 0.26707 | 0.26573 | 0.28717 | 0.3042 | 0.2927 | 0.27626 | 0.25263 | 0.22694 | 0.19389
2018-11-23 | 0.16455 | 0.14672 | 0.13347 | 0.12618 | 0.12485 | 0.12917 | 0.13846 | 0.16088 | 0.21835 | 0.28337 | 0.33008 | 0.36207 | 0.38303 | 0.3986 | 0.40145 | 0.39612 | 0.37619 | 0.38412 | 0.40933 | 0.39229 | 0.36308 | 0.32183 | 0.27885 | 0.23892
2018-11-24 | 0.19267 | 0.16693 | 0.15316 | 0.14801 | 0.15212 | 0.17366 | 0.21667 | 0.24949 | 0.29546 | 0.35065 | 0.40448 | 0.46396 | 0.51229 | 0.53766 | 0.54979 | 0.54522 | 0.51678 | 0.5065 | 0.52723 | 0.49233 | 0.44794 | 0.38516 | 0.33195 | 0.27066
2018-11-25 | 0.22227 | 0.19158 | 0.17533 | 0.16916 | 0.17067 | 0.19304 | 0.23794 | 0.27088 | 0.3179 | 0.37092 | 0.42031 | 0.45468 | 0.47473 | 0.48946 | 0.48765 | 0.47773 | 0.45659 | 0.46345 | 0.48282 | 0.45716 | 0.41631 | 0.37031 | 0.31814 | 0.27027
2018-11-26 | 0.22706 | 0.19978 | 0.18286 | 0.17432 | 0.17439 | 0.18725 | 0.21651 | 0.24624 | 0.28408 | 0.31241 | 0.31438 | 0.30762 | 0.29724 | 0.28133 | 0.26272 | 0.24512 | 0.23582 | 0.25511 | 0.27718 | 0.2644 | 0.24388 | 0.22333 | 0.1974 | 0.16669
2018-11-27 | 0.14077 | 0.12479 | 0.11703 | 0.1151 | 0.11712 | 0.12651 | 0.1451 | 0.17449 | 0.21149 | 0.23761 | 0.2538 | 0.26029 | 0.25986 | 0.25103 | 0.24113 | 0.22603 | 0.20694 | 0.1993 | 0.20478 | 0.19044 | 0.1809 | 0.17251 | 0.15967 | 0.14187
2018-11-28 | 0.12582 | 0.11672 | 0.11315 | 0.11436 | 0.12084 | 0.135 | 0.1592 | 0.18685 | 0.21508 | 0.23186 | 0.23416 | 0.22658 | 0.21737 | 0.20919 | 0.20173 | 0.19695 | 0.19732 | 0.22223 | 0.25238 | 0.24364 | 0.23046 | 0.22254 | 0.19688 | 0.16964
2018-11-29 | 0.14685 | 0.13518 | 0.12917 | 0.12842 | 0.13194 | 0.13948 | 0.15668 | 0.17994 | 0.20645 | 0.21917 | 0.22081 | 0.21975 | 0.21597 | 0.2118 | 0.20675 | 0.2018 | 0.19747 | 0.21457 | 0.23765 | 0.22714 | 0.21126 | 0.19385 | 0.17154 | 0.14618
2018-11-30 | 0.12308 | 0.10914 | 0.10243 | 0.099927 | 0.10115 | 0.10642 | 0.11695 | 0.1346 | 0.16727 | 0.19448 | 0.2123 | 0.22436 | 0.23335 | 0.23802 | 0.23896 | 0.23582 | 0.23126 | 0.24974 | 0.28395 | 0.27184 | 0.25221 | 0.22373 | 0.19158 | 0.15444
2018-12-01 | 0.12833 | 0.11256 | 0.10509 | 0.10277 | 0.10672 | 0.12707 | 0.16919 | 0.19503 | 0.21854 | 0.24587 | 0.27612 | 0.3008 | 0.3126 | 0.3171 | 0.31148 | 0.3014 | 0.29211 | 0.31349 | 0.34991 | 0.33849 | 0.31237 | 0.27236 | 0.22838 | 0.18193
2018-12-02 | 0.1466 | 0.12645 | 0.11439 | 0.1098 | 0.11295 | 0.13188 | 0.1761 | 0.2012 | 0.22022 | 0.24907 | 0.27828 | 0.29687 | 0.30785 | 0.3148 | 0.31241 | 0.30434 | 0.29351 | 0.31696 | 0.35273 | 0.33956 | 0.31372 | 0.27529 | 0.22909 | 0.18233
2018-12-03 | 0.14615 | 0.12473 | 0.11399 | 0.10905 | 0.11116 | 0.13019 | 0.17828 | 0.20124 | 0.22488 | 0.26046 | 0.28932 | 0.31372 | 0.33263 | 0.34165 | 0.34872 | 0.35204 | 0.33596 | 0.34346 | 0.37608 | 0.35846 | 0.32792 | 0.28547 | 0.23749 | 0.18714
2018-12-04 | 0.14994 | 0.12914 | 0.11786 | 0.11318 | 0.11589 | 0.13589 | 0.17948 | 0.20588 | 0.22901 | 0.26397 | 0.29351 | 0.31927 | 0.3399 | 0.34922 | 0.35547 | 0.35781 | 0.34034 | 0.34862 | 0.38329 | 0.36833 | 0.33975 | 0.29984 | 0.24874 | 0.19844
2018-12-05 | 0.15951 | 0.13521 | 0.12285 | 0.11795 | 0.11985 | 0.13945 | 0.18372 | 0.21064 | 0.23912 | 0.2816 | 0.31527 | 0.33892 | 0.35223 | 0.351 | 0.34966 | 0.35457 | 0.34798 | 0.35666 | 0.37547 | 0.35253 | 0.32382 | 0.28954 | 0.25233 | 0.2095
2018-12-06 | 0.17074 | 0.1457 | 0.131 | 0.12221 | 0.11872 | 0.12259 | 0.13512 | 0.15635 | 0.20486 | 0.25833 | 0.30121 | 0.33118 | 0.35214 | 0.36535 | 0.37133 | 0.36651 | 0.34503 | 0.33601 | 0.35035 | 0.31757 | 0.28712 | 0.25684 | 0.22117 | 0.18247
2018-12-07 | 0.14647 | 0.12585 | 0.11312 | 0.1052 | 0.10304 | 0.10609 | 0.11425 | 0.12986 | 0.17085 | 0.2169 | 0.24911 | 0.27114 | 0.28302 | 0.28963 | 0.29162 | 0.28302 | 0.27145 | 0.28506 | 0.3214 | 0.29733 | 0.27245 | 0.23822 | 0.19706 | 0.15612
2018-12-08 | 0.12497 | 0.10771 | 0.099531 | 0.096756 | 0.099953 | 0.11852 | 0.1588 | 0.18354 | 0.20079 | 0.22195 | 0.24109 | 0.25397 | 0.26251 | 0.26949 | 0.27275 | 0.27669 | 0.27516 | 0.29469 | 0.33427 | 0.32282 | 0.29193 | 0.2512 | 0.20683 | 0.16014
2018-12-09 | 0.12698 | 0.11088 | 0.10318 | 0.10107 | 0.10452 | 0.12553 | 0.17474 | 0.2003 | 0.21403 | 0.22547 | 0.23239 | 0.23388 | 0.23327 | 0.23062 | 0.22642 | 0.22034 | 0.22333 | 0.25579 | 0.30034 | 0.29533 | 0.27621 | 0.24546 | 0.20429 | 0.16513
2018-12-10 | 0.13774 | 0.12654 | 0.12145 | 0.12444 | 0.13316 | 0.16875 | 0.23826 | 0.28173 | 0.27766 | 0.26401 | 0.25347 | 0.24088 | 0.23038 | 0.22329 | 0.21473 | 0.21149 | 0.21609 | 0.25372 | 0.30906 | 0.30901 | 0.30076 | 0.27297 | 0.23271 | 0.19176
2018-12-11 | 0.16686 | 0.15566 | 0.1531 | 0.15395 | 0.16553 | 0.20429 | 0.28337 | 0.3243 | 0.30665 | 0.28914 | 0.2681 | 0.25448 | 0.24129 | 0.23154 | 0.22254 | 0.21881 | 0.22377 | 0.25986 | 0.3061 | 0.30236 | 0.29094 | 0.26332 | 0.2203 | 0.18101
2018-12-12 | 0.15474 | 0.14193 | 0.13756 | 0.13703 | 0.14801 | 0.18329 | 0.24978 | 0.28547 | 0.28806 | 0.28757 | 0.27868 | 0.26745 | 0.25418 | 0.24318 | 0.2321 | 0.22826 | 0.23432 | 0.27424 | 0.31433 | 0.30679 | 0.29774 | 0.27608 | 0.24562 | 0.21114
2018-12-13 | 0.18197 | 0.16991 | 0.16435 | 0.16503 | 0.17143 | 0.18935 | 0.21862 | 0.25604 | 0.27947 | 0.27806 | 0.26148 | 0.24662 | 0.23582 | 0.22535 | 0.21624 | 0.21153 | 0.21022 | 0.23436 | 0.26534 | 0.25524 | 0.24463 | 0.22933 | 0.20709 | 0.18379
2018-12-14 | 0.16131 | 0.14797 | 0.14351 | 0.14389 | 0.14839 | 0.16168 | 0.18732 | 0.22168 | 0.25536 | 0.25931 | 0.24541 | 0.23509 | 0.22722 | 0.22081 | 0.21655 | 0.2128 | 0.21295 | 0.23847 | 0.28355 | 0.27779 | 0.26474 | 0.24141 | 0.20421 | 0.17074
2018-12-15 | 0.14749 | 0.13635 | 0.13552 | 0.13787 | 0.15088 | 0.18671 | 0.2599 | 0.30213 | 0.29847 | 0.27753 | 0.26259 | 0.25095 | 0.24824 | 0.24393 | 0.23879 | 0.23802 | 0.23924 | 0.26858 | 0.31729 | 0.31223 | 0.29297 | 0.25939 | 0.21655 | 0.17547
2018-12-16 | 0.14711 | 0.13451 | 0.13004 | 0.13164 | 0.14067 | 0.1731 | 0.24117 | 0.27617 | 0.2724 | 0.25846 | 0.2494 | 0.24483 | 0.24331 | 0.24401 | 0.24318 | 0.24426 | 0.24488 | 0.26733 | 0.31064 | 0.30245 | 0.27907 | 0.24162 | 0.20053 | 0.15974
2018-12-17 | 0.12929 | 0.11456 | 0.10897 | 0.10834 | 0.11558 | 0.14155 | 0.19455 | 0.22642 | 0.22974 | 0.23364 | 0.23716 | 0.23924 | 0.24343 | 0.24861 | 0.2541 | 0.25969 | 0.25693 | 0.27749 | 0.31569 | 0.30337 | 0.27801 | 0.24595 | 0.20372 | 0.16078
2018-12-18 | 0.13067 | 0.11547 | 0.1095 | 0.10919 | 0.11598 | 0.14036 | 0.19389 | 0.22698 | 0.23908 | 0.24637 | 0.24945 | 0.24691 | 0.24649 | 0.25435 | 0.25922 | 0.26046 | 0.25795 | 0.27687 | 0.31522 | 0.30305 | 0.28377 | 0.25045 | 0.21003 | 0.16857
2018-12-19 | 0.13864 | 0.12358 | 0.11658 | 0.11549 | 0.12174 | 0.1458 | 0.19466 | 0.23002 | 0.2429 | 0.25036 | 0.25701 | 0.25965 | 0.25935 | 0.26178 | 0.26174 | 0.26076 | 0.25587 | 0.27053 | 0.30264 | 0.2856 | 0.26324 | 0.23647 | 0.20744 | 0.17199
2018-12-20 | 0.14291 | 0.12503 | 0.11629 | 0.11239 | 0.112 | 0.12043 | 0.13743 | 0.16175 | 0.1964 | 0.22515 | 0.24183 | 0.24488 | 0.25731 | 0.2588 | 0.26029 | 0.26071 | 0.25596 | 0.26893 | 0.29733 | 0.27612 | 0.25347 | 0.22882 | 0.19974 | 0.16656
2018-12-21 | 0.13601 | 0.11638 | 0.10509 | 0.10006 | 0.099373 | 0.10301 | 0.1129 | 0.1304 | 0.16833 | 0.21064 | 0.23875 | 0.25402 | 0.27027 | 0.2752 | 0.27149 | 0.26465 | 0.25914 | 0.28049 | 0.31499 | 0.30085 | 0.28146 | 0.2541 | 0.21823 | 0.1761
2018-12-22 | 0.14155 | 0.12072 | 0.109 | 0.10342 | 0.10509 | 0.11893 | 0.14516 | 0.1739 | 0.21609 | 0.26063 | 0.30057 | 0.3273 | 0.34587 | 0.35991 | 0.36986 | 0.36489 | 0.34793 | 0.35781 | 0.39639 | 0.37526 | 0.34474 | 0.30971 | 0.26513 | 0.21003
2018-12-23 | 0.16741 | 0.14039 | 0.12441 | 0.11675 | 0.11778 | 0.13228 | 0.15894 | 0.18837 | 0.23493 | 0.28712 | 0.32893 | 0.36021 | 0.38365 | 0.39313 | 0.37199 | 0.34991 | 0.33085 | 0.33824 | 0.37307 | 0.35313 | 0.32539 | 0.3048 | 0.27582 | 0.24031
2018-12-24 | 0.2003 | 0.17181 | 0.15444 | 0.14708 | 0.14541 | 0.15539 | 0.17488 | 0.2012 | 0.25621 | 0.3253 | 0.38417 | 0.42612 | 0.44872 | 0.45271 | 0.45569 | 0.44493 | 0.43341 | 0.44387 | 0.45372 | 0.40384 | 0.35956 | 0.32415 | 0.29144 | 0.24765
2018-12-25 | 0.20675 | 0.17765 | 0.15349 | 0.1361 | 0.12476 | 0.12279 | 0.1274 | 0.14067 | 0.17474 | 0.21322 | 0.23933 | 0.25301 | 0.25786 | 0.25435 | 0.24695 | 0.2317 | 0.21597 | 0.22266 | 0.24166 | 0.2317 | 0.22377 | 0.2116 | 0.19033 | 0.16202
2018-12-26 | 0.13503 | 0.11769 | 0.11016 | 0.10629 | 0.10809 | 0.11812 | 0.13629 | 0.159 | 0.19001 | 0.22132 | 0.24695 | 0.2579 | 0.25761 | 0.25116 | 0.24724 | 0.24446 | 0.24691 | 0.27568 | 0.30804 | 0.29619 | 0.27468 | 0.24915 | 0.21999 | 0.18372
2018-12-27 | 0.15043 | 0.12833 | 0.11473 | 0.10875 | 0.10878 | 0.11318 | 0.12514 | 0.13917 | 0.17495 | 0.22313 | 0.2644 | 0.29279 | 0.31116 | 0.31724 | 0.31748 | 0.30762 | 0.29583 | 0.30948 | 0.34107 | 0.32102 | 0.2932 | 0.2647 | 0.22942 | 0.18841
2018-12-28 | 0.15336 | 0.12962 | 0.11561 | 0.10795 | 0.10428 | 0.10596 | 0.1145 | 0.12612 | 0.16899 | 0.22239 | 0.26612 | 0.30126 | 0.32692 | 0.34547 | 0.35547 | 0.35512 | 0.3443 | 0.34116 | 0.3722 | 0.34788 | 0.31583 | 0.28089 | 0.23904 | 0.19139
2018-12-29 | 0.15477 | 0.13188 | 0.11896 | 0.11349 | 0.11408 | 0.12514 | 0.14978 | 0.17498 | 0.21995 | 0.27687 | 0.32658 | 0.36092 | 0.37947 | 0.38791 | 0.39418 | 0.39739 | 0.38484 | 0.38133 | 0.41771 | 0.38994 | 0.35377 | 0.30753 | 0.26067 | 0.20759
2018-12-30 | 0.16472 | 0.13933 | 0.12494 | 0.11743 | 0.11672 | 0.12794 | 0.15108 | 0.17558 | 0.2145 | 0.26234 | 0.3092 | 0.35011 | 0.37685 | 0.39618 | 0.40151 | 0.39497 | 0.37983 | 0.37968 | 0.4155 | 0.38817 | 0.35557 | 0.31139 | 0.26707 | 0.21729
2018-12-31 | 0.17561 | 0.14836 | 0.13286 | 0.12485 | 0.12417 | 0.13426 | 0.15612 | 0.18268 | 0.22081 | 0.26358 | 0.3003 | 0.32268 | 0.32811 | 0.33167 | 0.33056 | 0.32368 | 0.32563 | 0.36036 | 0.39156 | 0.35497 | 0.31349 | 0.27105 | 0.23098 | 0.20042

## Conductor Losses
OPC 012930
FPL RC-16
Conductor Losses - From Handwritten PDF
Dated 10/26/2010
Losses = I2R
I = current/amps
R = resistance of conductor
OH FEEDERS 568.3 kcmil ACAR
22500 | current/amps2
0.03287 | ohm/kft at 40º C
739.575 | w/kft
1000000
0.00073958 | mW/kft
48206 | kft
35.652 | mW/kft
3 | conductors
106.9559 | mW in losses
OH FEEDERS 3/0 AAAC
10000 | current/amps2
0.11378 | ohm/kft at 50º C
1137.8 | w/kft
1000000
0.0011378 | mW/kft
6051 | kft
6.8848 | mW/kft
3 | conductors
20.6545 | mW in losses
OH FEEDERS 1/0 AAAC
5625 | current/amps2
0.18049 | ohm/kft at 50º C
1015.2563 | w/kft
1000000
0.0010153 | mW/kft
3707 | kft
3.7636 | mW/kft
3 | conductors
11.2907 | mW in losses
OH LATERALS 1/0 AAAC
625 | current/amps2
0.18049 | ohm/kft at 50º C
112.8063 | w/kft
1000000
0.00011281 | mW/kft
119563 | kft
13.4875 | mW/kft
1 | conductors
13.4875 | mW in losses
UG FEEDERS 25kV, 1000 kcmil AL
22500 | current/amps2
0.0209 | ohm/kft at 58º C
470.25 | w/kft
1000000
0.00047025 | mW/kft
21268 | kft
10.0013 | mW/kft
3 | conductors
30.0038 | mW in losses
UG FEEDERS 25kV, 1/0 AL
625 | current/amps2
0.1886 | ohm/kft at 58º C
117.875 | w/kft
1000000
0.00011788 | mW/kft
1144 | kft
0.13485 | mW/kft
3 | conductors
0.40455 | mW in losses
UG LATERALS 25kV, 1/0 AL
625 | current/amps2
0.1886 | ohm/kft at 58º C
117.875 | w/kft
1000000
0.00011788 | mW/kft
114546 | kft
13.5021 | mW/kft
1 | conductors
13.5021 | mW in losses
196.2989 | mW in total cable losses