## 2014 Loss Exp Factors - Energy
OPC 012951
FPL RC-16
LINE NO. | FLOW OF ENERGY | FLOW MWH | LOSS % | LOSS MULTIPLIER | EXPANSION FACTOR | CUMULATIVE LOSS %
1 | Net Energy to Transmission | 123388587 | 0% | 0 | 0 | 0%
2
3 | Generation Step-up Transformer Losses | -228183 | 0.1849% | 1.0019 | 0 | 0%
4
5 | Flow to Transmission | 123160404 | 0% | 0 | 0 | 0%
6
7 | Transmission Line & Substation Losses | -2134065 | 0% | 0 | 0 | 0%
8
9 | Remove JEA/Southern Loss Payback & NF Wheeling Losses (a) | 151224 | 0% | 0 | 0 | 0%
10
11 | Adjusted Transmission Line & Substation Losses | -1982841 | 1.61% | 1.0164 | 0 | 0%
12
13 | Flow on Transmission | 121177563 | 0% | 0 | 0 | 0%
14
15 | Delivered Sales at Transmission | -7185763.9384 | 0% | 0 | 1.0182 | 1.792%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153 | 0% | 0 | 0 | 0%
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (a) | -151224 | 0% | 0 | 0 | 0%
20
21 | Flow to Distribution | 106479422.0616 | 0% | 0 | 0 | 0%
22
23 | Distribution Substation Losses | -449574 | 0.4222% | 1.0042 | 0 | 0%
24
25 | Flow to Primary Lines | 106029848.0616 | 0% | 0 | 0 | 0%
26
27 | Primary Line Losses | -623574 | 0.5881% | 1.0059 | 0 | 0%
28
29 | Flow on Primary | 105406274.0616 | 0% | 0 | 0 | 0%
30
31 | Delivered Sales at Primary | -2494087.7276 | 0% | 0 | 1.0286 | 2.782%
32
33 | Flow to Secondary | 102912186.334 | 0% | 0 | 0 | 0%
34
35 | Transformer Losses | -2029976 | 1.973% | 1.0201 | 0 | 0%
36
37 | Flow on Secondary | 100882210.334 | 0% | 0 | 0 | 0%
38
39 | Secondary Line & Service Losses | -408253 | 0.4047% | 1.0041 | 0 | 0%
40
41 | Balance For Use | 100473957.334 | 0% | 0 | 0 | 0%
42
43 | Company Use | -123235 | 0% | 0 | 0 | 0%
44
45 | Delivered Sales at Secondary | -100350722.419 | 0% | 0 | 1.0536 | 5.085%
46
47 | NET | -0.085001 | 0% | 0 | 0 | 0%
(a) | JEA/Southern loss payback and the non firm and short term wheeling losses are excluded from the transmission loss percentage calculation
because the flows that create these losses are not in the flow to transmission. However, because these are real losses they are included
in the flow to distribution.

## Data Summary
OPC 012952
FPL RC-16
LINE NO.
|  |  | EXPANSION FACTORS |  | ENERGY
1 |  |  | ENERGY | DEMAND | LOSS %
2 | Transmission | 0 | 1.0182 | 1.0231 | 1.792%
3
4 | Primary | 0 | 1.0286 | 1.0368 | 2.782%
5
6 | Secondary | 0 | 1.0536 | 1.07 | 5.085%
7
8
9 | COMPANY USE - DEMAND: |  | 0 | 0 | 0%
10 | (GSD-1) 12CP - MW | 3826.2243 | 0 | 0 | 0%
11 | (GSD-1) MWH | 25147188.6404 |  | 0 | 0%
12 | Load Factor (line 11 / line10 / 8760) | 0.75027 |  | 0 | 0%
13 | COMPANY USE 12CP DEMAND (rounded) - MW | 18.7506 |  | 0 | 0%
14
15
16 | CALCUATION OF NET ENERGY TO TRANSMISSION LESS SOUTHERN JEA/LP (MWH): |  |  | 0 | 0%
17 | NET ENERGY FOR LOAD |  | 116027434 | 0 | 0%
18
19 | Seminole Load Received | 2282100 | 0 | 0 | 0%
20 | St. Lucie Entitlement Received | 586976 | 0 | 0 | 0%
21 | Power wheeled for others | 4643301 | 0 | 0 | 0%
22 | Southern JEA / Transfers Loss Payback | -19451 | 0 | 0 | 0%
23 | Non-Firm Wheeling Losses | -77259 | 0 | 0 | 0%
24 | Short Term Firm Wheeling Losses | -54514 | 0 | 0 | 0%
25 | TOTAL FIRM POWER WHEELED FOR OTHERS |  | 7361153 | 0 | 0%
26
27 | NET ENERGY TO TRANSMISSION LESS SOUTHERN JEA/LP |  | 123388587 | 0 | 0%
28
29
30 | USING UNBILLED SALES (MWH): |  | 0 | 0 | 0%
31 | NEL | 116027434 | 0 | 0 | 0%
32 | PRIOR MONTH UNBILLED | 4167624 | 0 | 0 | 0%
33 | SUBTOTAL | 120195058 | 0 | 0 | 0%
34 | BILLED SALES | -109763891 | 0 | 0 | 0%
35 | COMPANY USE | -123235 | 0 | 0 | 0%
36 | CURRENT MONTH UNBILLED | -4434307 | 0 | 0 | 0%
37 | ENERGY LOST OR UNACCOUNTED FOR | 5873625 | 0 | 0 | 0%
38 | % LOST OR UNACCOUNTED FOR |  | 5.062% | 0 | 0%
39
40
41 | OVERALL UNBILLED FACTOR: |  | 0 | 0 | 0%
42 | TOTAL DELIVERED MWH | 110030574.085 | 0 | 0 | 0%
43 | TOTAL BILLED MWH | 109763891.085 | 0 | 0 | 0%
44 | TOTAL UNBILLED FACTOR | 1.0024 | 0 | 0 | 0%