## 2014 Loss Exp Factors - Energy
OPC 012955
FPL RC-16
LINE NO. | FLOW OF ENERGY | FLOW MWH | LOSS % | LOSS MULTIPLIER | EXPANSION FACTOR | CUMULATIVE LOSS %
1 | Net Energy to Transmission | 123388587 | 0% | 0 | 0 | 0%
2
3 | Generation Step-up Transformer Losses | -228183 | 0.1849% | 1.0019 | 0 | 0%
4
5 | Flow to Transmission | 123160404 | 0% | 0 | 0 | 0%
6
7 | Transmission Line & Substation Losses | -2134065 | 0% | 0 | 0 | 0%
8
9 | Remove JEA/Southern Loss Payback & NF Wheeling Losses (a) | 151224 | 0% | 0 | 0 | 0%
10
11 | Adjusted Transmission Line & Substation Losses | -1982841 | 1.61% | 1.0164 | 0 | 0%
12
13 | Flow on Transmission | 121177563 | 0% | 0 | 0 | 0%
14
15 | Delivered Sales at Transmission | -7185763.9384 | 0% | 0 | 1.0182 | 1.792%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153 | 0% | 0 | 0 | 0%
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (a) | -151224 | 0% | 0 | 0 | 0%
20
21 | Flow to Distribution | 106479422.0616 | 0% | 0 | 0 | 0%
22
23 | Distribution Substation Losses | -449574 | 0.4222% | 1.0042 | 0 | 0%
24
25 | Flow to Primary Lines | 106029848.0616 | 0% | 0 | 0 | 0%
26
27 | Primary Line Losses | -623574 | 0.5881% | 1.0059 | 0 | 0%
28
29 | Flow on Primary | 105406274.0616 | 0% | 0 | 0 | 0%
30
31 | Delivered Sales at Primary | -2494087.7276 | 0% | 0 | 1.0286 | 2.782%
32
33 | Flow to Secondary | 102912186.334 | 0% | 0 | 0 | 0%
34
35 | Transformer Losses | -2029976 | 1.973% | 1.0201 | 0 | 0%
36
37 | Flow on Secondary | 100882210.334 | 0% | 0 | 0 | 0%
38
39 | Secondary Line & Service Losses | -408253 | 0.4047% | 1.0041 | 0 | 0%
40
41 | Balance For Use | 100473957.334 | 0% | 0 | 0 | 0%
42
43 | Company Use | -123235 | 0% | 0 | 0 | 0%
44
45 | Delivered Sales at Secondary | -100350722.419 | 0% | 0 | 1.0536 | 5.085%
46
47 | NET | -0.085001 | 0% | 0 | 0 | 0%
(a) | JEA/Southern loss payback and the non firm and short term wheeling losses are excluded from the transmission loss percentage calculation
because the flows that create these losses are not in the flow to transmission. However, because these are real losses they are included
in the flow to distribution.

## Data Summary
OPC 012956
FPL RC-16
LINE NO.
|  |  | EXPANSION FACTORS |  | ENERGY
1 |  |  | ENERGY | DEMAND | LOSS %
2 | Transmission | 0 | 1.0182 | 1.0231 | 1.792%
3
4 | Primary | 0 | 1.0286 | 1.0368 | 2.782%
5
6 | Secondary | 0 | 1.0536 | 1.07 | 5.085%
7
8
9 | COMPANY USE - DEMAND: |  | 0 | 0 | 0%
10 | (GSD-1) 12CP - MW | 3826.2243 | 0 | 0 | 0%
11 | (GSD-1) MWH | 25147188.6404 |  | 0 | 0%
12 | Load Factor (line 11 / line10 / 8760) | 0.75027 |  | 0 | 0%
13 | COMPANY USE 12CP DEMAND (rounded) - MW | 18.7506 |  | 0 | 0%
14
15
16 | CALCUATION OF NET ENERGY TO TRANSMISSION LESS SOUTHERN JEA/LP (MWH): |  |  | 0 | 0%
17 | NET ENERGY FOR LOAD |  | 116027434 | 0 | 0%
18
19 | Seminole Load Received | 2282100 | 0 | 0 | 0%
20 | St. Lucie Entitlement Received | 586976 | 0 | 0 | 0%
21 | Power wheeled for others | 4643301 | 0 | 0 | 0%
22 | Southern JEA / Transfers Loss Payback | -19451 | 0 | 0 | 0%
23 | Non-Firm Wheeling Losses | -77259 | 0 | 0 | 0%
24 | Short Term Firm Wheeling Losses | -54514 | 0 | 0 | 0%
25 | TOTAL FIRM POWER WHEELED FOR OTHERS |  | 7361153 | 0 | 0%
26
27 | NET ENERGY TO TRANSMISSION LESS SOUTHERN JEA/LP |  | 123388587 | 0 | 0%
28
29
30 | USING UNBILLED SALES (MWH): |  | 0 | 0 | 0%
31 | NEL | 116027434 | 0 | 0 | 0%
32 | PRIOR MONTH UNBILLED | 4167624 | 0 | 0 | 0%
33 | SUBTOTAL | 120195058 | 0 | 0 | 0%
34 | BILLED SALES | -109763891 | 0 | 0 | 0%
35 | COMPANY USE | -123235 | 0 | 0 | 0%
36 | CURRENT MONTH UNBILLED | -4434307 | 0 | 0 | 0%
37 | ENERGY LOST OR UNACCOUNTED FOR | 5873625 | 0 | 0 | 0%
38 | % LOST OR UNACCOUNTED FOR |  | 5.062% | 0 | 0%
39
40
41 | OVERALL UNBILLED FACTOR: |  | 0 | 0 | 0%
42 | TOTAL DELIVERED MWH | 110030574.085 | 0 | 0 | 0%
43 | TOTAL BILLED MWH | 109763891.085 | 0 | 0 | 0%
44 | TOTAL UNBILLED FACTOR | 1.0024 | 0 | 0 | 0%

## Line Loss-KWH Anlys-Deli RC2016
OPC 012957
FPL RC-16
[6 empty] | RC2016 | RC2016 | RC2016
| RC2016 - Base Scenario_12CP and 1/13th | Year 2012 | Year 2013 | Year 2014 | Year 2015 | Year 2016 | Year 2017 | Year 2018
CILC-1T
CILC-1TE:[] | E:[]
CILC-1T_ G:[Delivered to Billed Sales Factor - Retail] | G:[Delivered to Billed Sales Factor - Retail] | 0.99905 | 1.0027 | 1.0004 | 0.99939 | 0.99947 | 1.0001 | 1.0003
CILC-1T_ I:[Delivered to Billed Sales Factor - Wholesale] | I:[Delivered to Billed Sales Factor - Wholesale] | 0 | 0 | 0 | 0 | 0 | 0 | 0
CILC-1T_K:[Delivered to Billed Sales Factor - to use] | K:[Delivered to Billed Sales Factor - to use] | 0.99905 | 1.0027 | 1.0004 | 0.99939 | 0.99947 | 1.0001 | 1.0003
CILC-1T_L:[] | L:[]
CILC-1T_M:[Billed Sales - KWH - Monthly] | M:[Billed Sales - KWH - Monthly] | 1352431246 | 1317537584 | 1366653995 | 1401306707 | 1478278060 | 1508335314 | 1532421391
CILC-1T_N:[Billed Sales - KWH - Latest 12] | N:[Billed Sales - KWH - Latest 12] | 16256711597 | 16011350469 | 16063658778 | 16525689129 | 17420730670 | 17939775613 | 18261160976
CILC-1T_O:[Delivered Sales - KWH] | O:[Delivered Sales - KWH] | 1351139758.8111 | 1321059230.5645 | 1367204458.223 | 1400455593.9699 | 1477500538.2043 | 1508543543.8624 | 1532833581.6575
CILC-1T_P:[] | P:[]
CILC-1T_Q:[Voltage Level % - Transmission - KWH] | Q:[Voltage Level % - Transmission - KWH] | 100% | 100% | 100% | 100% | 100% | 100% | 100%
CILC-1T_R:[Voltage Level % - Primary - KWH] | R:[Voltage Level % - Primary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
CILC-1T_S:[Voltage Level % - Secondary - KWH] | S:[Voltage Level % - Secondary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
CILC-1T_T:[] | T:[]
CILC-1T_U:[Delivered Sales - Transmission - KWH] | U:[Delivered Sales - Transmission - KWH] | 1351139758.8111 | 1321059230.5645 | 1367204458.223 | 1400455593.9699 | 1477500538.2043 | 1508543543.8624 | 1532833581.6575
CILC-1T_V:[Delivered Sales - Primary - KWH] | V:[Delivered Sales - Primary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
CILC-1T_W:[Delivered Sales - Secondary - KWH] | W:[Delivered Sales - Secondary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
CILC-1T_X:[] | X:[]
CILC-1T_Y:[Delivered Sales - Transmission - MWH] | Y:[Delivered Sales - Transmission - MWH] | 1351139.7588 | 1321059.2306 | 1367204.4582 | 1400455.594 | 1477500.5382 | 1508543.5439 | 1532833.5817
CILC-1T_Z:[Delivered Sales - Primary - MWH] | Z:[Delivered Sales - Primary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
CILC-1T_AA:[Delivered Sales - Secondary - MWH] | AA:[Delivered Sales - Secondary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
CILC-1T_AB:[] | AB:[]
CILC-1T_AC:[] | AC:[] | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSLD(T)-3
GSLD(T)-3_E:[] | E:[]
GSLD(T)-3_ G:[Delivered to Billed Sales Factor - Retail] | G:[Delivered to Billed Sales Factor - Retail] | 0.99905 | 1.0027 | 1.0004 | 0.99939 | 0.99947 | 1.0001 | 1.0003
GSLD(T)-3_ I:[Delivered to Billed Sales Factor - Wholesale] | I:[Delivered to Billed Sales Factor - Wholesale] | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSLD(T)-3_K:[Delivered to Billed Sales Factor - to use] | K:[Delivered to Billed Sales Factor - to use] | 0.99905 | 1.0027 | 1.0004 | 0.99939 | 0.99947 | 1.0001 | 1.0003
GSLD(T)-3_L:[] | L:[]
GSLD(T)-3_M:[Billed Sales - KWH - Monthly] | M:[Billed Sales - KWH - Monthly] | 167369098 | 158652735 | 161314413 | 182603864 | 169850435 | 172992260 | 175782528
GSLD(T)-3_N:[Billed Sales - KWH - Latest 12] | N:[Billed Sales - KWH - Latest 12] | 2193964476 | 1969873300 | 1887054866 | 2127937051 | 2079010746 | 2060865657 | 2095685593
GSLD(T)-3_O:[Delivered Sales - KWH] | O:[Delivered Sales - KWH] | 167209270.9873 | 159076797.9383 | 161379387.4939 | 182492955.7119 | 169761099.6992 | 173016142.06 | 175829809.9788
GSLD(T)-3_P:[] | P:[]
GSLD(T)-3_Q:[Voltage Level % - Transmission - KWH] | Q:[Voltage Level % - Transmission - KWH] | 100% | 100% | 100% | 100% | 100% | 100% | 100%
GSLD(T)-3_R:[Voltage Level % - Primary - KWH] | R:[Voltage Level % - Primary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
GSLD(T)-3_S:[Voltage Level % - Secondary - KWH] | S:[Voltage Level % - Secondary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
GSLD(T)-3_T:[] | T:[]
GSLD(T)-3_U:[Delivered Sales - Transmission - KWH] | U:[Delivered Sales - Transmission - KWH] | 167209270.9873 | 159076797.9383 | 161379387.4939 | 182492955.7119 | 169761099.6992 | 173016142.06 | 175829809.9788
GSLD(T)-3_V:[Delivered Sales - Primary - KWH] | V:[Delivered Sales - Primary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSLD(T)-3_W:[Delivered Sales - Secondary - KWH] | W:[Delivered Sales - Secondary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSLD(T)-3_X:[] | X:[]
GSLD(T)-3_Y:[Delivered Sales - Transmission - MWH] | Y:[Delivered Sales - Transmission - MWH] | 167209.271 | 159076.7979 | 161379.3875 | 182492.9557 | 169761.0997 | 173016.1421 | 175829.81
GSLD(T)-3_Z:[Delivered Sales - Primary - MWH] | Z:[Delivered Sales - Primary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSLD(T)-3_AA:[Delivered Sales - Secondary - MWH] | AA:[Delivered Sales - Secondary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
GSLD(T)-3_AB:[] | AB:[]
GSLD(T)-3_AC:[] | AC:[] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SST-TST
SST-TST_E:[] | E:[]
SST-TST_ G:[Delivered to Billed Sales Factor - Retail] | G:[Delivered to Billed Sales Factor - Retail] | 0.99905 | 1.0027 | 1.0004 | 0.99939 | 0.99947 | 1.0001 | 1.0003
SST-TST_ I:[Delivered to Billed Sales Factor - Wholesale] | I:[Delivered to Billed Sales Factor - Wholesale] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SST-TST_K:[Delivered to Billed Sales Factor - to use] | K:[Delivered to Billed Sales Factor - to use] | 0.99905 | 1.0027 | 1.0004 | 0.99939 | 0.99947 | 1.0001 | 1.0003
SST-TST_L:[] | L:[]
SST-TST_M:[Billed Sales - KWH - Monthly] | M:[Billed Sales - KWH - Monthly] | 78308634 | 89698634 | 57680521 | 100049295 | 89667754 | 89667754 | 89667754
SST-TST_N:[Billed Sales - KWH - Latest 12] | N:[Billed Sales - KWH - Latest 12] | 1049311627 | 1015856357 | 917807638 | 947442677 | 1130788390 | 1076013048 | 1076013048
SST-TST_O:[Delivered Sales - KWH] | O:[Delivered Sales - KWH] | 78233854.156 | 89938389.5031 | 57703753.6585 | 99988527.9615 | 89620591.9437 | 89680132.8815 | 89691872.8296
SST-TST_P:[] | P:[]
SST-TST_Q:[Voltage Level % - Transmission - KWH] | Q:[Voltage Level % - Transmission - KWH] | 100% | 100% | 100% | 100% | 100% | 100% | 100%
SST-TST_R:[Voltage Level % - Primary - KWH] | R:[Voltage Level % - Primary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
SST-TST_S:[Voltage Level % - Secondary - KWH] | S:[Voltage Level % - Secondary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
SST-TST_T:[] | T:[]
SST-TST_U:[Delivered Sales - Transmission - KWH] | U:[Delivered Sales - Transmission - KWH] | 78233854.156 | 89938389.5031 | 57703753.6585 | 99988527.9615 | 89620591.9437 | 89680132.8815 | 89691872.8296
SST-TST_V:[Delivered Sales - Primary - KWH] | V:[Delivered Sales - Primary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SST-TST_W:[Delivered Sales - Secondary - KWH] | W:[Delivered Sales - Secondary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SST-TST_X:[] | X:[]
SST-TST_Y:[Delivered Sales - Transmission - MWH] | Y:[Delivered Sales - Transmission - MWH] | 78233.8542 | 89938.3895 | 57703.7537 | 99988.528 | 89620.5919 | 89680.1329 | 89691.8728
SST-TST_Z:[Delivered Sales - Primary - MWH] | Z:[Delivered Sales - Primary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SST-TST_AA:[Delivered Sales - Secondary - MWH] | AA:[Delivered Sales - Secondary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
SST-TST_AB:[] | AB:[]
SST-TST_AC:[] | AC:[] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate Class Total
Rate Case Total_E:[] | E:[]
Rate Case Total_ G:[Delivered to Billed Sales Factor - Retail] | G:[Delivered to Billed Sales Factor - Retail] | 2.9971 | 3.008 | 3.0012 | 2.9982 | 2.9984 | 3.0004 | 3.0008
Rate Case Total_ I:[Delivered to Billed Sales Factor - Wholesale] | I:[Delivered to Billed Sales Factor - Wholesale] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate Case Total_K:[Delivered to Billed Sales Factor - to use] | K:[Delivered to Billed Sales Factor - to use] | 2.9971 | 3.008 | 3.0012 | 2.9982 | 2.9984 | 3.0004 | 3.0008
Rate Case Total_L:[] | L:[]
Rate Case Total_M:[Billed Sales - KWH - Monthly] | M:[Billed Sales - KWH - Monthly] | 1598108978 | 1565888953 | 1585648929 | 1683959866 | 1737796249 | 1770995328 | 1797871673
Rate Case Total_N:[Billed Sales - KWH - Latest 12] | N:[Billed Sales - KWH - Latest 12] | 19499987700 | 18997080126 | 18868521282 | 19601068857 | 20630529806 | 21076654318 | 21432859617
Rate Case Total_O:[Delivered Sales - KWH] | O:[Delivered Sales - KWH] | 1596582883.9544 | 1570074418.0059 | 1586287599.3754 | 1682937077.6433 | 1736882229.8472 | 1771239818.8039 | 1798355264.466
Rate Case Total_P:[] | P:[]
Rate Case Total_Q:[Voltage Level % - Transmission - KWH] | Q:[Voltage Level % - Transmission - KWH] | 300% | 300% | 300% | 300% | 300% | 300% | 300%
Rate Case Total_R:[Voltage Level % - Primary - KWH] | R:[Voltage Level % - Primary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Rate Case Total_S:[Voltage Level % - Secondary - KWH] | S:[Voltage Level % - Secondary - KWH] | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Rate Case Total_T:[] | T:[]
Rate Case Total_U:[Delivered Sales - Transmission - KWH] | U:[Delivered Sales - Transmission - KWH] | 1596582883.9544 | 1570074418.0059 | 1586287599.3754 | 1682937077.6433 | 1736882229.8472 | 1771239818.8039 | 1798355264.466
Rate Case Total_V:[Delivered Sales - Primary - KWH] | V:[Delivered Sales - Primary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate Case Total_W:[Delivered Sales - Secondary - KWH] | W:[Delivered Sales - Secondary - KWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate Case Total_X:[] | X:[]
Rate Case Total_Y:[Delivered Sales - Transmission - MWH] | Y:[Delivered Sales - Transmission - MWH] | 1596582.884 | 1570074.418 | 1586287.5994 | 1682937.0776 | 1736882.2298 | 1771239.8188 | 1798355.2645
Rate Case Total_Z:[Delivered Sales - Primary - MWH] | Z:[Delivered Sales - Primary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate Case Total_AA:[Delivered Sales - Secondary - MWH] | AA:[Delivered Sales - Secondary - MWH] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate Case Total_AB:[] | AB:[]
Rate Case Total_AC:[] | AC:[] | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Summary_Delivered_Sales
OPC 012958
FPL RC-16
Wholesale Delivered Sales
Year | Period | Florida Keys | Key West | Lee County | Metro Dade | Seminole Agreement | New Smyrna Beach | Wauchula | Blountstown | Winter Park | Homestead | Quincy | Total Wholesale
2008 | 1 | 51438.02 | 18675 |  | 619.117 | [7 empty] | 70732.137
2008 | 2 | 53909.591 | 21230 |  | 295.189 | [7 empty] | 75434.78
2008 | 3 | 58070.208 | 25200 |  | 659.911 | [7 empty] | 83930.119
2008 | 4 | 57682.352 | 24595 |  | 642.321 | [7 empty] | 82919.673
2008 | 5 | 67919.681 | 25695 |  | 601.435 | [7 empty] | 94216.116
2008 | 6 | 71794.6 | 23085 |  | 615.667 | [7 empty] | 95495.267
2008 | 7 | 73957.002 | 23040 |  | 643.124 | [7 empty] | 97640.126
2008 | 8 | 73492.165 | 23130 |  | 597.289 | [7 empty] | 97219.454
2008 | 9 | 62794.548 | 21330 |  | 589.969 | [7 empty] | 84714.517
2008 | 10 | 57611.893 | 19440 |  | 506.467 | [7 empty] | 77558.36
2008 | 11 | 45201.201 | 16605 |  | 531.902 | [7 empty] | 62338.103
2008 | 12 | 47513.018 | 16200 |  | 656.681 | 4500 | [6 empty] | 68869.699
2009 | 1 | 48532.176 | 16245 |  | 611.02 | 4650 | [6 empty] | 70038.196
2009 | 2 | 44843.899 | 15795 |  | 417.039 | 4200 | [6 empty] | 65255.938
2009 | 3 | 51885.582 | 17100 |  | 611.953 | 4650 | [6 empty] | 74247.535
2009 | 4 | 57070.319 | 17465 |  | 553.962 | 4650 | [6 empty] | 79739.281
2009 | 5 | 64566.029 | 20115 |  | 608.645 | 13500 | [6 empty] | 98789.674
2009 | 6 | 67422.286 | 21060 |  | 503.778 | 20925 | [6 empty] | 109911.064
2009 | 7 | 75359.653 | 22185 |  | 593.649 | 20250 | [6 empty] | 118388.302
2009 | 8 | 74640.708 | 22770 |  | 525.669 | 20925 | [6 empty] | 118861.377
2009 | 9 | 65199.352 | 21060 |  | 539.79 | 20925 | [6 empty] | 107724.142
2009 | 10 | 63729.235 | 19440 |  | 500.001 | 6750 | [6 empty] | 90419.236
2009 | 11 | 49920.963 | 16583 |  | 347.554 | 4650 | [6 empty] | 71501.517
2009 | 12 | 52145.927 | 16110 |  | 430.147 | 4500 | [6 empty] | 73186.074
2010 | 1 | 56593.035 | 16200 | 109394.3 | 436.297 | 0 | [6 empty] | 182623.632
2010 | 2 | 46078.829 | 15480 | 85973.099 | 253.868 | 0 | [6 empty] | 147785.796
2010 | 3 | 49500.831 | 17055 | 88619.247 | 615.59 | 0 | [6 empty] | 155790.668
2010 | 4 | 51444.13 | 17235 | 86660.504 | 593.885 | 0 | [6 empty] | 155933.519
2010 | 5 | 65770.982 | 20250 | 111143.427 | 668.799 | 0 | [6 empty] | 197833.208
2010 | 6 | 71167.412 | 21060 | 115273.648 | 467.716 | 0 | [6 empty] | 207968.776
2010 | 7 | 71875.767 | 22275 | 113803.861 | 593.039 | 0 | [6 empty] | 208547.667
2010 | 8 | 70637.158 | 22815 | 113071.015 | 586.661 | 0 | [6 empty] | 207109.834
2010 | 9 | 63646.966 | 21060 | 106584.899 | 556.12 | 0 | [6 empty] | 191847.985
2010 | 10 | 56271.941 | 19395 | 95246.997 | 597.324 | 0 | [6 empty] | 171511.262
2010 | 11 | 47470.025 | 16560 | 83461.894 | 530.991 | 0 | [6 empty] | 148022.91
2010 | 12 | 50114.637 | 18045 | 101294.148 | 692.068 | 0 | [6 empty] | 170145.853
2011 | 1 | 46905.73 | 16110 | 88944.758 | 618.849 | 0 | [6 empty] | 152579.337
2011 | 2 | 46600.297 | 15435 | 80799.967 | 355.997 | 0 | [6 empty] | 143191.261
2011 | 3 | 54307.979 | 17100 | 92072.526 | 723.969 | 0 | [6 empty] | 164204.474
2011 | 4 | 63704.388 | 17325 | 104888.657 | 688.893 | 0 | [6 empty] | 186606.938
2011 | 5 | 68847.198 | 20115 | 107074.308 | 765.342 | 0 | [6 empty] | 196801.848
2011 | 6 | 72436.462 | 21060 | 108087.621 | 633.727 | 0 | [6 empty] | 202217.81
2011 | 7 | 80409.621 | 22140 | 112792.205 | 622.54 | 0 | [6 empty] | 215964.366
2011 | 8 | 76752.611 | 22770 | 114067.916 | 581.344 | 0 | [6 empty] | 214171.871
2011 | 9 | 69116.777 | 21060 | 107230.475 | 614.328 | 0 | [6 empty] | 198021.58
2011 | 10 | 56226.877 | 20970 | 91884.466 | 488.707 | 0 |  | 4846.848 |  |  |  |  | 174416.898
2011 | 11 | 51407.406 | 16560 | 84513.238 | 622.828 | 0 |  | 4334.544 |  |  |  |  | 157438.016
2011 | 12 | 51239.465 | 16110 | 85559.115 | 442.481 | 0 |  | 4447.383 |  |  |  |  | 157798.444
2012 | 1 | 50699.967 | 16110 | 89991.825 | 573.01 | 0 |  | 4696.802 |  |  |  |  | 162071.604
2012 | 2 | 52001.394 | 15975 | 86884.248 | 365.38 | 0 |  | 4387.837 |  |  |  |  | 159613.859
2012 | 3 | 59426.751 | 17100 | 97530.348 | 568.669 | 0 |  | 4923.181 |  |  |  |  | 179548.949
2012 | 4 | 56813.245 | 17235 | 95089.7683 | 500.344 | 0 |  | 4983.3242 |  |  |  |  | 174621.6815
2012 | 5 | 65762.341 | 20115 | 109264.1547 | 520.575 | 0 |  | 6121.0439 | 3589.85 |  |  |  | 205372.9646
2012 | 6 | 69687.192 | 21060 | 105197.076 | 532.691 | 0 |  | 5728.745 | 3674.217 |  |  |  | 205879.921
2012 | 7 | 77143.0749 | 22140 | 113099.6235 | 551.085 | 0 |  | 6238.9201 | 4116.039 |  |  |  | 223288.7425
2012 | 8 | 77510.92 | 22815 | 115345.071 | 497.992 | 0 |  | 6415.799 | 3897.069 |  |  |  | 226481.851
2012 | 9 | 67200.521 | 21060 | 104983.1701 | 479.164 | 0 |  | 5749.07 | 3490.969 |  |  |  | 202962.8941
2012 | 10 | 62224.5033 | 19395 | 100007.6358 | 437.069 | 0 |  | 5337.9446 | 3039.8842 |  |  |  | 190442.0369
2012 | 11 | 45517.8114 | 16560 | 79468.1517 | 487.799 | 0 |  | 4122.5101 | 2761.0591 |  |  |  | 148917.3313
2012 | 12 | 52972.1518 | 16110 | 87506.6419 | 594.618 | 0 |  | 4579.383 | 3043.7551 |  |  |  | 164806.5498
2013 | 1 | 55278.1365 | 16110 | 89786.4264 | 495.657 | 0 |  | 4430.53 | 2945.2308 |  |  |  | 169045.9807
2013 | 2 | 50969.7119 | 15615 | 84958.6751 | 262.108 | 0 |  | 4216.1532 | 2657.6967 |  |  |  | 158679.345
2013 | 3 | 53074.2783 | 17100 | 92662.2037 | 399.068 | 0 |  | 4511.5509 | 2948.5339 |  |  |  | 170695.6349
2013 | 4 | 61920.6237 | 17235 | 101520.4839 | 563.317 | 0 |  | 5015.6158 | 2772.426 |  |  |  | 189027.4663
2013 | 5 | 64215.7624 | 20115 | 102931.9738 | 547.913 | 0 |  | 5416.7007 | 3201.0166 |  |  |  | 196428.3666
2013 | 6 | 71685.3782 | 0 | 107378.4151 | 531.087 | 0 |  | 5723.4525 | 3746.2912 |  |  |  | 189064.6241
2013 | 7 | 75399.9786 | 0 | 108944.6269 | 540.6187 | 0 |  | 5654.0407 | 3766.6253 |  |  |  | 194305.8902
2013 | 8 | 77641.0751 | 0 | 116066.3982 | 502.0119 | 0 |  | 6416.3103 | 3922.9659 |  |  |  | 204548.7614
2013 | 9 | 68405.674 | 0 | 104907.7248 | 500.2868 | 0 |  | 5734.3012 | 3620.5109 |  |  |  | 183168.4976
2013 | 10 | 66036.6954 | 0 | 106317.4068 | 455.3222 | 0 |  | 5499.3548 | 2964.0969 |  |  |  | 181272.8761
2013 | 11 | 55916.6054 | 0 | 93649.2246 | 453.7933 | 0 |  | 4493.9387 | 2661.8907 |  |  |  | 157175.4527
2013 | 12 | 58140.1811 | 0 | 93356.3934 | 0 | 0 |  | 4642.2964 | 2936.5062 |  |  |  | 159075.377
2014 | 1 | 53789.6831 | 0 | 302663.9818 | 0 | 0 | 0 | 5124.5694 | 3598.7402 | 16537 |  |  | 381713.9744
2014 | 2 | 55279.3615 | 0 | 247855.3863 | 0 | 0 | 18635 | 4132.2357 | 2923.0439 | 15456 |  |  | 344281.0275
2014 | 3 | 60007.1158 | 0 | 277647.8152 | 0 | 0 | 14868 | 4021.6145 | 2594.3847 | 16997 |  |  | 376135.9303
2014 | 4 | 62174.597 | 0 | 311518.4058 | 0 | 0 | 7200 | 5396.7404 | 2558.4093 | 15387 |  |  | 404235.1524
2014 | 5 | 69701.235 | 0 | 346316.9007 | 0 | 0 | 14775 | 5912.6414 | 2856.3084 | 16790 |  |  | 456352.0855
2014 | 6 | 74290.361 | 0 | 361951.7123 | 0 | 81900 | 23090 | 5789.238 | 4003.365 | 16560 |  |  | 567584.6763
2014 | 7 | 83182.857 | 0 | 342204.5554 | 0 | 90850 | 24575 | 6401.7082 | 3991.8651 | 17112 |  |  | 568317.9858
2014 | 8 | 85591.367 | 0 | 364790.1174 | 0 | 67200 | 26040 | 6416.0547 | 3910.0174 | 16386.4512 |  |  | 570334.0077
2014 | 9 | 78163.7078 | 0 | 343543.475 | 0 | 70400 | 18000 | 5741.6856 | 3555.7399 | 15857.856 |  |  | 535262.4643
2014 | 10 | 67326.9081 | 0 | 310293.8695 | 0 | 73600 | 14880 | 5418.6497 | 3001.9905 | 16386.4512 |  |  | 490907.8691
2014 | 11 | 61597.8055 | 0 | 269140.0141 | 0 | 64000 | 7200 | 4308.2244 | 2711.4749 | 15857.856 |  |  | 424815.3749
2014 | 12 | 49859.1556 | 0 | 273410.8433 | 0 | 73600 | 14880 | 4610.8397 | 2990.1306 | 16386.4512 |  |  | 435737.4204
TOTALS |  | 800964.1544 | 0 | 3751337.0767 | 0 | 521550 | 184143 | 63274.2018 | 38695.4701 | 195714.0656 |  |  | 5555677.9685
2015 | 1 | 55893.768 | 0 | 270576.5393 | 0 | 73250 | 23405 | 4758.6502 | 2854.7034 | 12284.608 | 0 |  | 443023.2689
2015 | 2 | 48914.218 | 0 | 301035.6946 | 0 | 85800 | 21900 | 1891.0991 | 3125.6857 | 14177.11 | 0 |  | 476843.8074
2015 | 3 | 66651.542 | 0 | 304886.0538 | 0 | 111860 | 14690 | 7271.0262 | 3177.2141 | 13087.406 | 0 |  | 521623.2421 | IN KWH
2015 | 4 | 71298.913 | 0 | 335684.3721 | 0 | 125830 | 14400 | 5562.313 | 2118.942 | 16697.979 | 0 |  | 571592.5191 | TOTAL DELIVERED SALES:
2015 | 5 | 72522.713 | 0 | 363433.2005 | 0 | 113525 | 18285 | 6014.8991 | 3481.6743 | 20002.003 | 0 |  | 597264.4899 | 114266537980.5932
2015 | 6 | 76756.25 | 0 | 363754.5206 | 0 | 115975 | 26070 | 6068.0906 | 3690.9137 | 21595.621 | 0 |  | 613910.3958
2015 | 7 | 87703.695 | 0 | 389609.5664 | 0 | 144250 | 29660 | 6157.5821 | 3999.268 | 22495.289 | 0 |  | 683875.4005 | TOTAL RETAIL DELIVERED SALES:
2015 | 8 | 84789.6144 | 0 | 366364.2557 | 0 | 96050 | 33480 | 6306.8821 | 3873.1525 | 28556.6907 | 2803 |  | 622223.5955 | 107852754056.9047
2015 | 9 | 72614.356 | 0 | 345994.3864 | 0 | 91130 | 21600 | 6269.895 | 3703.0505 | 27811.957 | 978 |  | 570101.6449
2015 | 10 | 67065.214 | 0 | 313843.1527 | 0 | 87075 | 14880 | 5407.5176 | 3090.8653 | 23220.036 | 149 |  | 514730.7856 | TOTAL WHOLESALE DELIVERED SALES:
2015 | 11 | 55372.932 | 0 | 273964.6786 | 0 | 44020 | 10800 | 4086.6144 | 2536.4217 | 17586.6026 | 0 |  | 408367.2493 | 6413783923.6885
2015 | 12 | 56986.2915 | 0 | 278690.8611 | 0 | 13575 | 14880 | 4533.4603 | 2930.2514 | 18631.6603 | 0 |  | 390227.5245
TOTALS |  | 816569.5069 | 0 | 3907837.2817 | 0 | 1102340 | 244050 | 64328.0298 | 38582.1427 | 236146.9626 | 3930 | 0 | 6413783.9237
2016 | 1 | 56207.6374 | 0 | 279779.942 | 0 | 73250 | 29760 | 4941.6098 | 3226.7218 | 19158.0707 | 72 | 76 | 466471.9817
2016 | 2 | 53000.332 | 0 | 271689.087 | 0 | 85800 | 27840 | 3011.6674 | 3024.3648 | 18016.1691 | 0 | 0 | 462381.6203
2016 | 3 | 60565.6633 | 0 | 322430.747 | 0 | 111860 | 18600 | 5646.3204 | 2885.7994 | 18348.2085 | 0 | 0 | 540336.7385 | IN KWH
2016 | 4 | 63590.7575 | 0 | 352644.26 | 0 | 125830 | 14400 | 5479.5267 | 2338.6756 | 18832.6094 | 0 | 0 | 583115.8292 | TOTAL DELIVERED SALES:
2016 | 5 | 71967.5552 | 0 | 357421.431 | 0 | 113525 | 22320 | 5963.7703 | 3168.9914 | 24239.1127 | 0 | 0 | 598605.8605 | 113964410734.8379
2016 | 6 | 78323.0795 | 0 | 369136.08 | 0 | 115975 | 28800 | 5928.6643 | 3847.1393 | 27847.3885 | 0 | 0 | 629857.3516
2016 | 7 | 85649.1979 | 0 | 347333.561 | 0 | 144250 | 33480 | 6279.6452 | 3995.5666 | 27951.8249 | 0 | 0 | 648939.7955 | TOTAL RETAIL DELIVERED SALES:
2016 | 8 | 84916.972 | 0 | 372588.691 | 0 | 96050 | 33480 | 6252.168 | 3848.2458 | 28556.6907 | 72 | 76 | 625840.7675 | 107428768095.8608
2016 | 9 | 72248.716 | 0 | 367780.053 | 0 | 91130 | 25200 | 6537.6919 | 3744.3203 | 27811.957 | 0 | 0 | 594452.7382
2016 | 10 | 66802.2276 | 0 | 336292.253 | 0 | 87075 | 18600 | 5361.5991 | 3154.2495 | 23220.036 | 0 | 0 | 540505.3652 | TOTAL WHOLESALE DELIVERED SALES:
2016 | 11 | 54976.1993 | 0 | 306122.189 | 0 | 44020 | 14400 | 3882.9522 | 2473.6873 | 17586.6026 | 0 | 0 | 443461.6304 | 6535642638.9771
2016 | 12 | 56726.0997 | 0 | 286734.034 | 0 | 13575 | 18600 | 4479.0423 | 2927.124 | 18631.6603 | 0 | 0 | 401672.9602
TOTALS |  | 804974.4374 | 0 | 3969952.328 | 0 | 1102340 | 285480 | 63764.6575 | 38634.8858 | 270200.3303 | 144 | 152 | 6535642.639
2017 | 1 | 56898.6801 | 0 | 283976.641 | 0 | 73250 | 180 |  | 0 | 240 | 84 | 76 | 414705.3211
2017 | 2 | 53651.9426 | 0 | 275764.422 | 0 | 85800 | 0 |  | 0 | 0 | 0 | 0 | 415216.3646
2017 | 3 | 61310.2856 | 0 | 327267.208 | 0 | 111860 | 0 |  | 0 | 0 | 0 | 0 | 500437.4936 | IN KWH
2017 | 4 | 64372.5716 | 0 | 357933.924 | 0 | 125830 | 0 |  | 0 | 0 | 0 | 0 | 548136.4956 | TOTAL DELIVERED SALES:
2017 | 5 | 72852.3576 | 0 | 362782.752 | 0 | 113525 | 0 |  |  | 0 | 0 | 0 | 549160.1096 | 113209155635.992
2017 | 6 | 79286.0197 | 0 | 374673.121 | 0 | 115975 | 0 |  |  | 0 | 0 | 0 | 569934.1407
2017 | 7 | 86702.2087 | 0 | 352543.565 | 0 | 144250 | 0 |  |  | 0 | 0 | 0 | 583495.7737 | TOTAL RETAIL DELIVERED SALES:
2017 | 8 | 85960.9805 | 0 | 378177.521 | 0 | 96050 | 180 |  |  | 240 | 84 | 76 | 560768.5015 | 107261282858.8345
2017 | 9 | 73136.9751 | 0 | 373296.754 | 0 | 91130 | 0 |  |  | 0 | 0 | 0 | 537563.7291
2017 | 10 | 67623.5251 | 0 | 341336.638 | 0 | 87075 | 0 |  |  | 0 | 0 | 0 | 496035.1631 | TOTAL WHOLESALE DELIVERED SALES:
2017 | 11 | 55652.1021 | 0 | 310714.022 | 0 | 44020 | 0 |  |  | 0 | 0 | 0 | 410386.1241 | 5947872777.1574
2017 | 12 | 57423.5166 | 0 | 291035.044 | 0 | 13575 | 0 |  |  | 0 | 0 | 0 | 362033.5606
TOTALS |  | 814871.1652 | 0 | 4029501.612 | 0 | 1102340 | 360 | 0 | 0 | 480 | 168 | 152 | 5947872.7772
2018 | 1 | 58448.4997 | 0 | 319300.7354 | 0 | 73600 |  |  |  | 0 |  |  | 451349.2351
2018 | 2 | 55359.6811 | 0 | 292265.9155 | 0 | 64000 |  |  |  | 0 |  |  | 411625.5966
2018 | 3 | 62338.0839 | 0 | 296979.1804 | 0 | 70400 |  |  |  | 0 |  |  | 429717.2643 | IN KWH
2018 | 4 | 65349.1859 | 0 | 304862.5715 | 0 | 67200 |  |  |  | 0 |  |  | 437411.7574 | TOTAL DELIVERED SALES:
2018 | 5 | 74742.4423 | 0 | 343128.5429 | 0 | 73600 |  |  |  | 0 |  |  | 491470.9853 | 113905885760.0118
2018 | 6 | 81381.5877 | 0 | 360845.9794 | 0 | 67200 |  |  |  | 0 |  |  | 509427.5672
2018 | 7 | 88718.6066 | 0 | 374441.1247 | 0 | 70400 |  |  |  | 0 |  |  | 533559.7313 | TOTAL RETAIL DELIVERED SALES:
2018 | 8 | 88037.5132 | 0 | 374453.2543 | 0 | 73600 |  |  |  | 0 |  |  | 536090.7675 | 108293475514.8958
2018 | 9 | 75395.8767 | 0 | 355859.2542 | 0 | 64000 |  |  |  | 0 |  |  | 495255.1309
2018 | 10 | 69634.1727 | 0 | 327480.1573 | 0 | 73600 |  |  |  | 0 |  |  | 470714.3301 | TOTAL WHOLESALE DELIVERED SALES:
2018 | 11 | 57494.0134 | 0 | 292567.1312 | 0 | 70400 |  |  |  | 0 |  |  | 420461.1446 | 5612410245.116
2018 | 12 | 59169.1732 | 0 | 298957.5617 | 0 | 67200 |  |  |  | 0 |  |  | 425326.7349
TOTALS |  | 836068.8366 | 0 | 3941141.4085 | 0 | 835200 | 0 | 0 | 0 | 0 | 0 | 0 | 5612410.2451
2019 | 1 | 59185.4658 | 0 | 325075.0773 | 0 | 73600 |  |  |  | 0 |  |  | 457860.543
2019 | 2 | 56057.7009 | 0 | 297965.4519 | 0 | 64000 |  |  |  | 0 |  |  | 418023.1528
2019 | 3 | 63124.093 | 0 | 302195.181 | 0 | 67200 |  |  |  | 0 |  |  | 432519.2741 | IN KWH
2019 | 4 | 66173.1614 | 0 | 309398.6572 | 0 | 70400 |  |  |  | 0 |  |  | 445971.8186 | TOTAL DELIVERED SALES:
2019 | 5 | 75684.8556 | 0 | 346308.5108 | 0 | 73600 |  |  |  | 0 |  |  | 495593.3665 | 114586123556.2541
2019 | 6 | 82407.7128 | 0 | 363110.0993 | 0 | 64000 |  |  |  | 0 |  |  | 509517.8121
2019 | 7 | 89837.2427 | 0 | 376188.6675 | 0 | 73600 |  |  |  | 0 |  |  | 539625.9102 | TOTAL RETAIL DELIVERED SALES:
2019 | 8 | 89147.5615 | 0 | 376161.0424 | 0 | 70400 |  |  |  | 0 |  |  | 535708.6039 | 108918850855.1101
2019 | 9 | 76346.5291 | 0 | 358108.4901 | 0 | 67200 |  |  |  | 0 |  |  | 501655.0192
2019 | 10 | 70512.1769 | 0 | 330680.6063 | 0 | 73600 |  |  |  | 0 |  |  | 474792.7832 | TOTAL WHOLESALE DELIVERED SALES:
2019 | 11 | 58218.9446 | 0 | 296895.8828 | 0 | 67200 |  |  |  | 0 |  |  | 422314.8274 | 5667272701.144
2019 | 12 | 59915.2261 | 0 | 303374.364 | 0 | 70400 |  |  |  | 0 |  |  | 433689.5901
TOTALS |  | 846610.6704 | 0 | 3985462.0307 | 0 | 835200 | 0 | 0 | 0 | 0 |  |  | 5667272.7011
2020 | 1 | 59931.7241 | 0 | 329308.6347 | 0 | 73600 | [6 empty] | 462840.3588
2020 | 2 | 56764.5218 | 0 | 302148.9586 | 0 | 64000 | [6 empty] | 422913.4804
2020 | 3 | 63920.0128 | 0 | 305786.6939 | 0 | 70400 | [6 empty] | 440106.7067
2020 | 4 | 67007.5263 | 0 | 312423.5932 | 0 | 70400 | [6 empty] | 449831.1195
2020 | 5 | 76639.1517 | 0 | 348016.4511 | 0 | 67200 | [6 empty] | 491855.6027
2020 | 6 | 83446.7761 | 0 | 363884.4485 | 0 | 70400 | [6 empty] | 517731.2245
2020 | 7 | 90969.9835 | 0 | 376295.4166 | 0 | 73600 | [6 empty] | 540865.4002
2020 | 8 | 90271.6063 | 0 | 376147.0467 | 0 | 67200 | [6 empty] | 533618.6529
2020 | 9 | 77309.168 | 0 | 358631.4861 | 0 | 70400 | [6 empty] | 506340.6542
2020 | 10 | 71401.2516 | 0 | 332335.6605 | 0 | 70400 | [6 empty] | 474136.912
2020 | 11 | 58953.0162 | 0 | 300143.0664 | 0 | 67200 | [6 empty] | 426296.0827
2020 | 12 | 60670.6859 | 0 | 307254.7707 | 0 | 73600 | [6 empty] | 441525.4566
2021 | 1 | 60687.3919 | 0 | 333530.6868 | 0 | 67200 | [6 empty] | 461418.0787
2021 | 2 | 57480.255 | 0 | 306019.5692 | 0 | 64000 | [6 empty] | 427499.8242
2021 | 3 | 64725.9682 | 0 | 309440.9849 | 0 | 73600 | [6 empty] | 447766.953
2021 | 4 | 67852.4115 | 0 | 315564.3607 | 0 | 70400 | [6 empty] | 453816.7722
2021 | 5 | 77605.4802 | 0 | 350313.9626 | 0 | 67200 | [6 empty] | 495119.4429
2021 | 6 | 84498.9407 | 0 | 365389.8595 | 0 | 0 | [6 empty] | 449888.8002
2021 | 7 | 92117.0068 | 0 | 377429.9966 | 0 | 0 | [6 empty] | 469547.0035
2021 | 8 | 91409.8239 | 0 | 377221.5434 | 0 | 0 | [6 empty] | 468631.3672
2021 | 9 | 78283.9447 | 0 | 359971.661 | 0 | 0 | [6 empty] | 438255.6057
2021 | 10 | 72301.5364 | 0 | 334409.4988 | 0 | 0 | [6 empty] | 406711.0353
2021 | 11 | 59696.3437 | 0 | 303314.4041 | 0 | 0 | [6 empty] | 363010.7478
2021 | 12 | 61435.6711 | 0 | 310911.9945 | 0 | 0 | [6 empty] | 372347.6656
2022 | 1 | 61452.5877 | 0 | 337431.8869 | 0 | 0 | [6 empty] | 398884.4746
2022 | 2 | 58205.0126 | 0 | 309879.5258 | 0 | 0 | [6 empty] | 368084.5384
2022 | 3 | 65542.0856 | 0 | 313024.4782 | 0 | 0 | [6 empty] | 378566.5639
2022 | 4 | 68707.9497 | 0 | 318790.071 | 0 | 0 | [6 empty] | 387498.0207
2022 | 5 | 78583.9931 | 0 | 352844.2263 | 0 | 0 | [6 empty] | 431428.2193
2022 | 6 | 85564.3718 | 0 | 367741.6452 | 0 | 0 | [6 empty] | 453306.0171
2022 | 7 | 93278.4928 | 0 | 379557.3349 | 0 | 0 | [6 empty] | 472835.8277
2022 | 8 | 92562.393 | 0 | 379336.4718 | 0 | 0 | [6 empty] | 471898.8649
2022 | 9 | 79271.0122 | 0 | 362366.015 | 0 | 0 | [6 empty] | 441637.0272
2022 | 10 | 73213.1728 | 0 | 337389.05 | 0 | 0 | [6 empty] | 410602.2229
2022 | 11 | 60449.0436 | 0 | 307125.3622 | 0 | 0 | [6 empty] | 367574.4057
2022 | 12 | 62210.3019 | 0 | 315045.1666 | 0 | 0 | [6 empty] | 377255.4685
2023 | 1 | 62227.4318 | 0 | 341801.9919 | 0 | 0 | [6 empty] | 404029.4237
2023 | 2 | 58938.9086 | 0 | 314249.5645 | 0 | 0 | [6 empty] | 373188.4731
2023 | 3 | 66368.4934 | 0 | 317300.7761 | 0 | 0 | [6 empty] | 383669.2695
2023 | 4 | 69574.2753 | 0 | 322925.9642 | 0 | 0 | [6 empty] | 392500.2395
2023 | 5 | 79574.8438 | 0 | 356666.3185 | 0 | 0 | [6 empty] | 436241.1622
2023 | 6 | 86643.2368 | 0 | 371370.542 | 0 | 0 | [6 empty] | 458013.7788
2023 | 7 | 94454.6236 | 0 | 383041.9644 | 0 | 0 | [6 empty] | 477496.5881
2023 | 8 | 93729.4948 | 0 | 382771.2071 | 0 | 0 | [6 empty] | 476500.7019
2023 | 9 | 80270.5254 | 0 | 365927.7706 | 0 | 0 | [6 empty] | 446198.296
2023 | 10 | 74136.3039 | 0 | 341241.3865 | 0 | 0 | [6 empty] | 415377.6904
2023 | 11 | 61211.2341 | 0 | 311434.2573 | 0 | 0 | [6 empty] | 372645.4914
2023 | 12 | 62994.6998 | 0 | 319546.4731 | 0 | 0 | [6 empty] | 382541.1729
2024 | 1 | 63012.0457 | 0 | 346426.1861 | 0 | 0 | [6 empty] | 409438.2318
2024 | 2 | 59682.0582 | 0 | 318996.547 | 0 | 0 | [6 empty] | 378678.6052
2024 | 3 | 67205.3212 | 0 | 321658.2274 | 0 | 0 | [6 empty] | 388863.5486
2024 | 4 | 70451.5242 | 0 | 327086.6425 | 0 | 0 | [6 empty] | 397538.1666
2024 | 5 | 80578.1879 | 0 | 360639.9723 | 0 | 0 | [6 empty] | 441218.1603
2024 | 6 | 87735.705 | 0 | 375221.7338 | 0 | 0 | [6 empty] | 462957.4389
2024 | 7 | 95645.5841 | 0 | 386792.0813 | 0 | 0 | [6 empty] | 482437.6654
2024 | 8 | 94911.3122 | 0 | 386428.4876 | 0 | 0 | [6 empty] | 481339.7998
2024 | 9 | 81282.6413 | 0 | 369588.598 | 0 | 0 | [6 empty] | 450871.2393
2024 | 10 | 75071.0745 | 0 | 345005.0921 | 0 | 0 | [6 empty] | 420076.1666
2024 | 11 | 61983.035 | 0 | 315448.8546 | 0 | 0 | [6 empty] | 377431.8896
2024 | 12 | 63788.9881 | 0 | 323785.758 | 0 | 0 | [6 empty] | 387574.746
2025 | 1 | 63806.5527 | 0 | 350823.1528 | 0 | 0 | [6 empty] | 414629.7055
2025 | 2 | 60434.578 | 0 | 323172.5992 | 0 | 0 | [6 empty] | 383607.1772
2025 | 3 | 68052.7004 | 0 | 325985.3501 | 0 | 0 | [6 empty] | 394038.0505
2025 | 4 | 71339.8341 | 0 | 331313.259 | 0 | 0 | [6 empty] | 402653.0931
2025 | 5 | 81594.1831 | 0 | 364779.6535 | 0 | 0 | [6 empty] | 446373.8366
2025 | 6 | 88841.9479 | 0 | 379341.5344 | 0 | 0 | [6 empty] | 468183.4824
2025 | 7 | 96851.5612 | 0 | 390901.088 | 0 | 0 | [6 empty] | 487752.6492
2025 | 8 | 96108.031 | 0 | 390520.8879 | 0 | 0 | [6 empty] | 486628.9189
2025 | 9 | 82307.5187 | 0 | 373699.318 | 0 | 0 | [6 empty] | 456006.8368
2025 | 10 | 76017.6315 | 0 | 349111.1051 | 0 | 0 | [6 empty] | 425128.7367
2025 | 11 | 62764.5674 | 0 | 319545.844 | 0 | 0 | [6 empty] | 382310.4114
2025 | 12 | 64593.2913 | 0 | 327816.4131 | 0 | 0 | [6 empty] | 392409.7044
2026 | 1 | 64611.0774 | 0 | 354827.7838 | 0 | 0 | [6 empty] | 419438.8612
2026 | 2 | 61196.5861 | 0 | 327235.158 | 0 | 0 | [6 empty] | 388431.7441
2026 | 3 | 68910.764 | 0 | 330150.3401 | 0 | 0 | [6 empty] | 399061.1042
2026 | 4 | 72239.3446 | 0 | 335598.0256 | 0 | 0 | [6 empty] | 407837.3702
2026 | 5 | 82622.9887 | 0 | 369129.1274 | 0 | 0 | [6 empty] | 451752.1161
2026 | 6 | 89962.1393 | 0 | 383751.8037 | 0 | 0 | [6 empty] | 473713.9429
2026 | 7 | 98072.7442 | 0 | 395316.6628 | 0 | 0 | [6 empty] | 493389.407
2026 | 8 | 97319.839 | 0 | 394906.2123 | 0 | 0 | [6 empty] | 492226.0513
2026 | 9 | 83345.3187 | 0 | 378135.1392 | 0 | 0 | [6 empty] | 461480.4579
2026 | 10 | 76976.1235 | 0 | 353679.4749 | 0 | 0 | [6 empty] | 430655.5984
2026 | 11 | 63555.9539 | 0 | 324411.9648 | 0 | 0 | [6 empty] | 387967.9188
2026 | 12 | 65407.7359 | 0 | 332958.8123 | 0 | 0 | [6 empty] | 398366.5482
2027 | 1 | 65425.7463 | 0 | 360155.4097 | 0 | 0 | [6 empty] | 425581.156
2027 | 2 | 61968.2023 | 0 | 332557.8267 | 0 | 0 | [6 empty] | 394526.029
2027 | 3 | 69779.6468 | 0 | 335349.4514 | 0 | 0 | [6 empty] | 405129.0982
2027 | 4 | 73150.1968 | 0 | 340621.1247 | 0 | 0 | [6 empty] | 413771.3215
2027 | 5 | 83664.7663 | 0 | 373994.5545 | 0 | 0 | [6 empty] | 457659.3208
2027 | 6 | 91096.4549 | 0 | 388520.3577 | 0 | 0 | [6 empty] | 479616.8126
2027 | 7 | 99309.3249 | 0 | 399984.4187 | 0 | 0 | [6 empty] | 499293.7436
2027 | 8 | 98546.9265 | 0 | 399451.3547 | 0 | 0 | [6 empty] | 497998.2812
2027 | 9 | 84396.204 | 0 | 382605.7027 | 0 | 0 | [6 empty] | 467001.9067
2027 | 10 | 77946.7008 | 0 | 358068.0481 | 0 | 0 | [6 empty] | 436014.7489
2027 | 11 | 64357.3189 | 0 | 328743.3951 | 0 | 0 | [6 empty] | 393100.714
2027 | 12 | 66232.4497 | 0 | 337202.4713 | 0 | 0 | [6 empty] | 403434.921
2028 | 1 | 66250.6871 | 0 | 364339.3022 | 0 | 0 | [6 empty] | 430589.9894
2028 | 2 | 62749.5477 | 0 | 336965.0377 | 0 | 0 | [6 empty] | 399714.5853
2028 | 3 | 70659.4852 | 0 | 339537.9428 | 0 | 0 | [6 empty] | 410197.428
2028 | 4 | 74072.5338 | 0 | 344821.6224 | 0 | 0 | [6 empty] | 418894.1562
2028 | 5 | 84719.6796 | 0 | 378177.2812 | 0 | 0 | [6 empty] | 462896.9608
2028 | 6 | 92245.0728 | 0 | 392700.5684 | 0 | 0 | [6 empty] | 484945.6412
2028 | 7 | 100561.4974 | 0 | 404148.1779 | 0 | 0 | [6 empty] | 504709.6753
2028 | 8 | 99789.486 | 0 | 403605.8707 | 0 | 0 | [6 empty] | 503395.3567
2028 | 9 | 85460.3398 | 0 | 386803.1375 | 0 | 0 | [6 empty] | 472263.4772
2028 | 10 | 78929.5161 | 0 | 362270.4008 | 0 | 0 | [6 empty] | 441199.9169
2028 | 11 | 65168.7882 | 0 | 332932.3832 | 0 | 0 | [6 empty] | 398101.1714
2028 | 12 | 67067.5621 | 0 | 341325.1696 | 0 | 0 | [6 empty] | 408392.7317
2029 | 1 | 67086.0295 | 0 | 368408.0692 | 0 | 0 | [6 empty] | 435494.0987
2029 | 2 | 63540.7448 | 0 | 340772.2128 | 0 | 0 | [6 empty] | 404312.9576
2029 | 3 | 71550.4173 | 0 | 343567.1613 | 0 | 0 | [6 empty] | 415117.5786
2029 | 4 | 75006.5004 | 0 | 348823.3226 | 0 | 0 | [6 empty] | 423829.8229
2029 | 5 | 85787.894 | 0 | 382109.1036 | 0 | 0 | [6 empty] | 467896.9976
2029 | 6 | 93408.1735 | 0 | 396568.3216 | 0 | 0 | [6 empty] | 489976.4951
2029 | 7 | 101829.4583 | 0 | 407956.5921 | 0 | 0 | [6 empty] | 509786.0504
2029 | 8 | 101047.7128 | 0 | 407399.0147 | 0 | 0 | [6 empty] | 508446.7275
2029 | 9 | 86537.8931 | 0 | 390645.1097 | 0 | 0 | [6 empty] | 477183.0027
2029 | 10 | 79924.7234 | 0 | 366109.8742 | 0 | 0 | [6 empty] | 446034.5976
2029 | 11 | 65990.4891 | 0 | 336725.1679 | 0 | 0 | [6 empty] | 402715.657
2029 | 12 | 67913.2044 | 0 | 345022.5837 | 0 | 0 | [6 empty] | 412935.7881
2030 | 1 | 67931.9046 | 0 | 372044.5914 | 0 | 0 | [6 empty] | 439976.496
2030 | 2 | 64341.9181 | 0 | 344421.7067 | 0 | 0 | [6 empty] | 408763.6247
2030 | 3 | 72452.5829 | 0 | 347286.5025 | 0 | 0 | [6 empty] | 419739.0854
2030 | 4 | 75952.2432 | 0 | 352651.9549 | 0 | 0 | [6 empty] | 428604.1981
2030 | 5 | 86869.5773 | 0 | 386048.3329 | 0 | 0 | [6 empty] | 472917.9102
2030 | 6 | 94585.9395 | 0 | 400615.3349 | 0 | 0 | [6 empty] | 495201.2744
2030 | 7 | 103113.4067 | 0 | 412031.1022 | 0 | 0 | [6 empty] | 515144.5089
2030 | 8 | 102321.8043 | 0 | 411436.6448 | 0 | 0 | [6 empty] | 513758.4491
2030 | 9 | 87629.033 | 0 | 394674.0509 | 0 | 0 | [6 empty] | 482303.0838
2030 | 10 | 80932.4791 | 0 | 370127.3808 | 0 | 0 | [6 empty] | 451059.86
2030 | 11 | 66822.5507 | 0 | 340802.9123 | 0 | 0 | [6 empty] | 407625.4631
2030 | 12 | 68769.5091 | 0 | 349171.945 | 0 | 0 | [6 empty] | 417941.4541
2031 | 1 | 68788.4451 | 0 | 376263.2526 | 0 | 0 | [6 empty] | 445051.6977
2031 | 2 | 65153.1932 | 0 | 348696.2324 | 0 | 0 | [6 empty] | 413849.4255
2031 | 3 | 73366.1239 | 0 | 351578.0312 | 0 | 0 | [6 empty] | 424944.1551
2031 | 4 | 76909.9106 | 0 | 356936.6615 | 0 | 0 | [6 empty] | 433846.5721
2031 | 5 | 87964.8994 | 0 | 390301.5594 | 0 | 0 | [6 empty] | 478266.4587
2031 | 6 | 95778.5557 | 0 | 404858.857 | 0 | 0 | [6 empty] | 500637.4127
2031 | 7 | 104413.5441 | 0 | 416260.273 | 0 | 0 | [6 empty] | 520673.8172
2031 | 8 | 103611.9606 | 0 | 415655.2282 | 0 | 0 | [6 empty] | 519267.1887
2031 | 9 | 88733.9309 | 0 | 398970.955 | 0 | 0 | [6 empty] | 487704.8858
2031 | 10 | 81952.9414 | 0 | 374539.9703 | 0 | 0 | [6 empty] | 456492.9118
2031 | 11 | 67665.1036 | 0 | 345412.5194 | 0 | 0 | [6 empty] | 413077.623
2031 | 12 | 69636.6108 | 0 | 353950.9799 | 0 | 0 | [6 empty] | 423587.5907
2032 | 1 | 69655.7856 | 0 | 381181.4041 | 0 | 0 | [6 empty] | 450837.1897
2032 | 2 | 65974.6974 | 0 | 353919.3241 | 0 | 0 | [6 empty] | 419894.0215
2032 | 3 | 74291.1834 | 0 | 356584.0718 | 0 | 0 | [6 empty] | 430875.2552
2032 | 4 | 77879.6532 | 0 | 361922.7358 | 0 | 0 | [6 empty] | 439802.389
2032 | 5 | 89074.0322 | 0 | 395253.3635 | 0 | 0 | [6 empty] | 484327.3957
2032 | 6 | 96986.2094 | 0 | 409799.3519 | 0 | 0 | [6 empty] | 506785.5613
2032 | 7 | 105730.0748 | 0 | 421170.4985 | 0 | 0 | [6 empty] | 526900.5732
2032 | 8 | 104918.3842 | 0 | 420516.0909 | 0 | 0 | [6 empty] | 525434.4751
2032 | 9 | 89852.7602 | 0 | 403844.4723 | 0 | 0 | [6 empty] | 493697.2326
2032 | 10 | 82986.2706 | 0 | 379412.8581 | 0 | 0 | [6 empty] | 462399.1287
2032 | 11 | 68518.2801 | 0 | 350308.6011 | 0 | 0 | [6 empty] | 418826.8813
2032 | 12 | 70514.6457 | 0 | 358822.6972 | 0 | 0 | [6 empty] | 429337.3429
2033 | 1 | 70534.0623 | 0 | 385978.6286 | 0 | 0 | [6 empty] | 456512.6908
2033 | 2 | 66806.5599 | 0 | 358632.5386 | 0 | 0 | [6 empty] | 425439.0985
2033 | 3 | 75227.9069 | 0 | 361170.7389 | 0 | 0 | [6 empty] | 436398.6458
2033 | 4 | 78861.623 | 0 | 366381.939 | 0 | 0 | [6 empty] | 445243.562
2033 | 5 | 90197.1498 | 0 | 399568.3445 | 0 | 0 | [6 empty] | 489765.4943
2033 | 6 | 98209.0902 | 0 | 414022.6861 | 0 | 0 | [6 empty] | 512231.7763
2033 | 7 | 107063.2053 | 0 | 425321.0534 | 0 | 0 | [6 empty] | 532384.2587
2033 | 8 | 106241.2802 | 0 | 424592.625 | 0 | 0 | [6 empty] | 530833.9052
2033 | 9 | 90985.6967 | 0 | 407910.0739 | 0 | 0 | [6 empty] | 498895.7706
2033 | 10 | 84032.6288 | 0 | 383497.2523 | 0 | 0 | [6 empty] | 467529.8811
2033 | 11 | 69382.2142 | 0 | 354453.4311 | 0 | 0 | [6 empty] | 423835.6453
2033 | 12 | 71403.7515 | 0 | 362955.0718 | 0 | 0 | [6 empty] | 434358.8234
2034 | 1 | 71423.4129 | 0 | 390064.9109 | 0 | 0 | [6 empty] | 461488.3238
2034 | 2 | 67648.9112 | 0 | 362650.1837 | 0 | 0 | [6 empty] | 430299.0949
2034 | 3 | 76176.4414 | 0 | 365103.0629 | 0 | 0 | [6 empty] | 441279.5042
2034 | 4 | 79855.9743 | 0 | 370216.7436 | 0 | 0 | [6 empty] | 450072.7178
2034 | 5 | 91334.4286 | 0 | 403282.6485 | 0 | 0 | [6 empty] | 494617.0771
2034 | 6 | 99447.39 | 0 | 417663.3036 | 0 | 0 | [6 empty] | 517110.6936
2034 | 7 | 108413.145 | 0 | 428918.72 | 0 | 0 | [6 empty] | 537331.865
2034 | 8 | 107580.8565 | 0 | 428169.846 | 0 | 0 | [6 empty] | 535750.7025
2034 | 9 | 92132.9182 | 0 | 411532.3053 | 0 | 0 | [6 empty] | 503665.2235
2034 | 10 | 85092.1803 | 0 | 387182.0604 | 0 | 0 | [6 empty] | 472274.2407
2034 | 11 | 70257.0414 | 0 | 358220.4754 | 0 | 0 | [6 empty] | 428477.5168
2034 | 12 | 72304.0679 | 0 | 366730.1887 | 0 | 0 | [6 empty] | 439034.2567
2035 | 1 | 72323.9772 | 0 | 393829.9488 | 0 | 0 | [6 empty] | 466153.9261
2035 | 2 | 68501.8835 | 0 | 366410.3517 | 0 | 0 | [6 empty] | 434912.2352
2035 | 3 | 77136.9357 | 0 | 368850.5793 | 0 | 0 | [6 empty] | 445987.515
2035 | 4 | 80862.8631 | 0 | 373947.21 | 0 | 0 | [6 empty] | 454810.0732
2035 | 5 | 92486.0471 | 0 | 406957.3345 | 0 | 0 | [6 empty] | 499443.3816
2035 | 6 | 100701.3034 | 0 | 421305.1746 | 0 | 0 | [6 empty] | 522006.478
2035 | 7 | 109780.1059 | 0 | 432523.1483 | 0 | 0 | [6 empty] | 542303.2542
2035 | 8 | 108937.3231 | 0 | 431724.5321 | 0 | 0 | [6 empty] | 540661.8552
2035 | 9 | 93294.6047 | 0 | 415106.7878 | 0 | 0 | [6 empty] | 508401.3925
2035 | 10 | 86165.0915 | 0 | 390846.32 | 0 | 0 | [6 empty] | 477011.4115
2035 | 11 | 71142.8991 | 0 | 362081.3534 | 0 | 0 | [6 empty] | 433224.2525
2035 | 12 | 73215.7363 | 0 | 370740.5904 | 0 | 0 | [6 empty] | 443956.3267
2036 | 1 | 73235.8966 | 0 | 397925.2537 | 0 | 0 | [6 empty] | 471161.1503
2036 | 2 | 69365.6108 | 0 | 370484.0621 | 0 | 0 | [6 empty] | 439849.6729
2036 | 3 | 78109.5408 | 0 | 372840.5687 | 0 | 0 | [6 empty] | 450950.1094
2036 | 4 | 81882.4477 | 0 | 377826.1446 | 0 | 0 | [6 empty] | 459708.5923
2036 | 5 | 93652.1862 | 0 | 410730.0896 | 0 | 0 | [6 empty] | 504382.2758
2036 | 6 | 101971.0271 | 0 | 425040.4392 | 0 | 0 | [6 empty] | 527011.4663
2036 | 7 | 111164.3024 | 0 | 436254.2482 | 0 | 0 | [6 empty] | 547418.5506
2036 | 8 | 110310.8932 | 0 | 435461.2054 | 0 | 0 | [6 empty] | 545772.0986
2036 | 9 | 94470.9387 | 0 | 418880.9074 | 0 | 0 | [6 empty] | 513351.8461
2036 | 10 | 87251.5309 | 0 | 394619.0476 | 0 | 0 | [6 empty] | 481870.5785
2036 | 11 | 72039.9265 | 0 | 365797.6817 | 0 | 0 | [6 empty] | 437837.6082
2036 | 12 | 74138.8996 | 0 | 374306.4353 | 0 | 0 | [6 empty] | 448445.3349
2037 | 1 | 74159.3141 | 0 | 401362.9671 | 0 | 0 | [6 empty] | 475522.2812
2037 | 2 | 70240.2287 | 0 | 373895.9372 | 0 | 0 | [6 empty] | 444136.1659
2037 | 3 | 79094.4092 | 0 | 376269.4877 | 0 | 0 | [6 empty] | 455363.8969
2037 | 4 | 82914.888 | 0 | 381286.9544 | 0 | 0 | [6 empty] | 464201.8424
2037 | 5 | 94833.0289 | 0 | 414154.4417 | 0 | 0 | [6 empty] | 508987.4706
2037 | 6 | 103256.7605 | 0 | 428436.0898 | 0 | 0 | [6 empty] | 531692.8503
2037 | 7 | 112565.9521 | 0 | 439632.17 | 0 | 0 | [6 empty] | 552198.1221
2037 | 8 | 111701.7824 | 0 | 438846.01 | 0 | 0 | [6 empty] | 550547.7924
2037 | 9 | 95662.1049 | 0 | 422358.6231 | 0 | 0 | [6 empty] | 518020.728
2037 | 10 | 88351.6689 | 0 | 398250.4363 | 0 | 0 | [6 empty] | 486602.1052
2037 | 11 | 72948.2643 | 0 | 369665.0799 | 0 | 0 | [6 empty] | 442613.3442
2037 | 12 | 75073.703 | 0 | 378340.1607 | 0 | 0 | [6 empty] | 453413.8637
2038 | 1 | 75094.3749 | 0 | 405488.2194 | 0 | 0 | [6 empty] | 480582.5943
2038 | 2 | 71125.8745 | 0 | 378007.1053 | 0 | 0 | [6 empty] | 449132.9798
2038 | 3 | 80091.6956 | 0 | 380304.0523 | 0 | 0 | [6 empty] | 460395.748
2038 | 4 | 83960.3461 | 0 | 385240.9554 | 0 | 0 | [6 empty] | 469201.3015
2038 | 5 | 96028.7606 | 0 | 418044.1124 | 0 | 0 | [6 empty] | 514072.873
2038 | 6 | 104558.7054 | 0 | 432323.9631 | 0 | 0 | [6 empty] | 536882.6685
2038 | 7 | 113985.2749 | 0 | 443517.0941 | 0 | 0 | [6 empty] | 557502.369
2038 | 8 | 113110.2091 | 0 | 442692.7707 | 0 | 0 | [6 empty] | 555802.9798
2038 | 9 | 96868.2903 | 0 | 426205.7935 | 0 | 0 | [6 empty] | 523074.0838
2038 | 10 | 89465.6784 | 0 | 402128.5328 | 0 | 0 | [6 empty] | 491594.2112
2038 | 11 | 73868.0552 | 0 | 373638.0025 | 0 | 0 | [6 empty] | 447506.0577
2038 | 12 | 76020.2931 | 0 | 382368.0143 | 0 | 0 | [6 empty] | 458388.3074
2039 | 1 | 76041.2257 | 0 | 409576.1129 | 0 | 0 | [6 empty] | 485617.3386
2039 | 2 | 72022.6872 | 0 | 382160.7777 | 0 | 0 | [6 empty] | 454183.4649
2039 | 3 | 81101.5567 | 0 | 384476.1441 | 0 | 0 | [6 empty] | 465577.7008
2039 | 4 | 85018.9863 | 0 | 389358.693 | 0 | 0 | [6 empty] | 474377.6793
2039 | 5 | 97239.5691 | 0 | 421980.4786 | 0 | 0 | [6 empty] | 519220.0477
2039 | 6 | 105877.0664 | 0 | 436070.9671 | 0 | 0 | [6 empty] | 541948.0335
2039 | 7 | 115422.4937 | 0 | 447117.4142 | 0 | 0 | [6 empty] | 562539.9079
2039 | 8 | 114536.3943 | 0 | 446223.0356 | 0 | 0 | [6 empty] | 560759.4299
2039 | 9 | 98089.6843 | 0 | 429789.4242 | 0 | 0 | [6 empty] | 527879.1084
2039 | 10 | 90593.7342 | 0 | 405829.7091 | 0 | 0 | [6 empty] | 496423.4434
2039 | 11 | 74799.4435 | 0 | 377515.3149 | 0 | 0 | [6 empty] | 452314.7584
2039 | 12 | 76978.8186 | 0 | 386343.5956 | 0 | 0 | [6 empty] | 463322.4142
2040 | 1 | 77000.0151 | 0 | 413588.2211 | 0 | 0 | [6 empty] | 490588.2362
2040 | 2 | 72930.8076 | 0 | 386139.3001 | 0 | 0 | [6 empty] | 459070.1077
2040 | 3 | 82124.1509 | 0 | 388398.0298 | 0 | 0 | [6 empty] | 470522.1807
2040 | 4 | 86090.9746 | 0 | 393233.068 | 0 | 0 | [6 empty] | 479324.0425
2040 | 5 | 98465.6445 | 0 | 425836.5473 | 0 | 0 | [6 empty] | 524302.1917
2040 | 6 | 107212.0503 | 0 | 439975.5467 | 0 | 0 | [6 empty] | 547187.597
2040 | 7 | 116877.8341 | 0 | 451061.197 | 0 | 0 | [6 empty] | 567939.0311
2040 | 8 | 115980.5621 | 0 | 450159.8742 | 0 | 0 | [6 empty] | 566140.4362
2040 | 9 | 99326.4785 | 0 | 433759.4142 | 0 | 0 | [6 empty] | 533085.8928
2040 | 10 | 91736.0135 | 0 | 409880.0058 | 0 | 0 | [6 empty] | 501616.0192
2040 | 11 | 75742.5755 | 0 | 381739.4283 | 0 | 0 | [6 empty] | 457482.0038
2040 | 12 | 77949.43 | 0 | 390689.289 | 0 | 0 | [6 empty] | 468638.719
2041 | 1 | 77970.8937 |  | 417639.631 | 0 | 0 | [6 empty] | 495610.5247
2041 | 2 | 73850.3784 |  | 390159.2413 | 0 | 0 | [6 empty] | 464009.6197
2041 | 3 | 83159.6388 |  | 392359.921 | 0 | 0 | [6 empty] | 475519.5598
2041 | 4 | 87176.4794 |  | 397145.9955 | 0 | 0 | [6 empty] | 484322.4749
2041 | 5 | 99707.1792 |  | 429727.8528 | 0 | 0 | [6 empty] | 529435.0319
2041 | 6 | 108563.8668 |  | 443915.0879 | 0 | 0 | [6 empty] | 552478.9547
2041 | 7 | 118351.5246 |  | 455039.7658 | 0 | 0 | [6 empty] | 573391.2904
2041 | 8 | 117442.939 |  | 454131.4458 | 0 | 0 | [6 empty] | 571574.3848
2041 | 9 | 100578.8673 |  | 437766.0753 | 0 | 0 | [6 empty] | 538344.9427
2041 | 10 | 92892.6955 |  | 413970.7255 | 0 | 0 | [6 empty] | 506863.421
2041 | 11 | 76697.5994 |  | 386010.8063 | 0 | 0 | [6 empty] | 462708.4057
2041 | 12 | 78932.2796 |  | 395083.8638 | 0 | 0 | [6 empty] | 474016.1435
2042 | 1 | 78954.014 |  | 421730.7275 | 0 | 0 | [6 empty] | 500684.7415
2042 | 2 | 74781.5438 |  | 394221.0326 | 0 | 0 | [6 empty] | 469002.5764
2042 | 3 | 84208.1829 |  | 396362.2259 | 0 | 0 | [6 empty] | 480570.4089
2042 | 4 | 88275.6711 |  | 401097.8592 | 0 | 0 | [6 empty] | 489373.5304
2042 | 5 | 100964.3681 |  | 433654.7171 | 0 | 0 | [6 empty] | 534619.0852
2042 | 6 | 109932.728 |  | 447889.9038 | 0 | 0 | [6 empty] | 557822.6318
2042 | 7 | 119843.7966 |  | 459053.4274 | 0 | 0 | [6 empty] | 578897.224
2042 | 8 | 118923.7548 |  | 458138.0569 | 0 | 0 | [6 empty] | 577061.8118
2042 | 9 | 101847.0473 |  | 441809.7462 | 0 | 0 | [6 empty] | 543656.7934
2042 | 10 | 94063.962 |  | 418102.2718 | 0 | 0 | [6 empty] | 512166.2337
2042 | 11 | 77664.6649 |  | 390329.9779 | 0 | 0 | [6 empty] | 467994.6428
2042 | 12 | 79927.5218 |  | 399527.87 | 0 | 0 | [6 empty] | 479455.3918
2043 | 1 | 79949.5302 |  | 425861.8993 | 0 | 0 | [6 empty] | 505811.4296
2043 | 2 | 75724.4502 |  | 398325.1094 | 0 | 0 | [6 empty] | 474049.5596
2043 | 3 | 85269.948 |  | 400405.3567 | 0 | 0 | [6 empty] | 485675.3047
2043 | 4 | 89388.7224 |  | 405089.0466 | 0 | 0 | [6 empty] | 494477.769
2043 | 5 | 102237.4087 |  | 437617.4652 | 0 | 0 | [6 empty] | 539854.874
2043 | 6 | 111318.849 |  | 451900.3101 | 0 | 0 | [6 empty] | 563219.1591
2043 | 7 | 121354.8844 |  | 463102.4914 | 0 | 0 | [6 empty] | 584457.3758
2043 | 8 | 120423.242 |  | 462180.0167 | 0 | 0 | [6 empty] | 582603.2587
2043 | 9 | 103131.2174 |  | 445890.7686 | 0 | 0 | [6 empty] | 549021.9861
2043 | 10 | 95249.9967 |  | 422275.0521 | 0 | 0 | [6 empty] | 517525.0488
2043 | 11 | 78643.924 |  | 394697.4778 | 0 | 0 | [6 empty] | 473341.4017
2043 | 12 | 80935.3128 |  | 404021.8636 | 0 | 0 | [6 empty] | 484957.1764
2044 | 1 | 80957.5987 |  | 430033.5392 | 0 | 0 | [6 empty] | 510991.1379
2044 | 2 | 76679.2454 |  | 402471.9122 | 0 | 0 | [6 empty] | 479151.1577
2044 | 3 | 86345.1006 |  | 404489.7299 | 0 | 0 | [6 empty] | 490834.8305
2044 | 4 | 90515.8079 |  | 409119.9489 | 0 | 0 | [6 empty] | 499635.7568
2044 | 5 | 103526.5009 |  | 441616.4251 | 0 | 0 | [6 empty] | 545142.926
2044 | 6 | 112722.4473 |  | 455946.6257 | 0 | 0 | [6 empty] | 568669.073
2044 | 7 | 122885.0251 |  | 467187.27 | 0 | 0 | [6 empty] | 590072.2952
2044 | 8 | 121941.6359 |  | 466257.637 | 0 | 0 | [6 empty] | 588199.2728
2044 | 9 | 104431.5794 |  | 450009.4878 | 0 | 0 | [6 empty] | 554441.0672
2044 | 10 | 96450.9859 |  | 426489.4779 | 0 | 0 | [6 empty] | 522940.4638
2044 | 11 | 79635.5303 |  | 399113.8467 | 0 | 0 | [6 empty] | 478749.377
2044 | 12 | 81955.8109 |  | 408566.4067 | 0 | 0 | [6 empty] | 490522.2176
2045 | 1 | 81978.3778 |  | 434246.0434 | 0 | 0 | [6 empty] | 516224.4212
2045 | 2 | 77646.0795 |  | 406661.8857 | 0 | 0 | [6 empty] | 484307.9653
2045 | 3 | 87433.8097 |  | 408615.766 | 0 | 0 | [6 empty] | 496049.5757
2045 | 4 | 91657.1046 |  | 413190.9614 | 0 | 0 | [6 empty] | 504848.066
2045 | 5 | 104831.847 |  | 445651.9275 | 0 | 0 | [6 empty] | 550483.7745
2045 | 6 | 114143.7433 |  | 460029.172 | 0 | 0 | [6 empty] | 574172.9153
2045 | 7 | 124434.4592 |  | 471308.0782 | 0 | 0 | [6 empty] | 595742.5374
2045 | 8 | 123479.1749 |  | 470371.2324 | 0 | 0 | [6 empty] | 593850.4073
2045 | 9 | 105748.3375 |  | 454166.2517 | 0 | 0 | [6 empty] | 559914.5892
2045 | 10 | 97667.1181 |  | 430745.965 | 0 | 0 | [6 empty] | 528413.0831
2045 | 11 | 80639.6397 |  | 403579.6315 | 0 | 0 | [6 empty] | 484219.2711
2045 | 12 | 82989.1762 |  | 413162.0681 | 0 | 0 | [6 empty] | 496151.2443
2046 | 1 | 83012.0277 |  | 438499.8123 | 0 | 0 | [6 empty] | 521511.8399
2046 | 2 | 78625.1043 |  | 410895.4794 | 0 | 0 | [6 empty] | 489520.5836
2046 | 3 | 88536.246 |  | 412783.8902 | 0 | 0 | [6 empty] | 501320.1363
2046 | 4 | 92812.7917 |  | 417302.4831 | 0 | 0 | [6 empty] | 510115.2748
2046 | 5 | 106153.6519 |  | 449724.3064 | 0 | 0 | [6 empty] | 555877.9584
2046 | 6 | 115582.9602 |  | 464148.2733 | 0 | 0 | [6 empty] | 579731.2335
2046 | 7 | 126003.4298 |  | 475465.2339 | 0 | 0 | [6 empty] | 601468.6637
2046 | 8 | 125036.1004 |  | 474521.1204 | 0 | 0 | [6 empty] | 599557.2208
2046 | 9 | 107081.6983 |  | 458361.412 | 0 | 0 | [6 empty] | 565443.1102
2046 | 10 | 98898.5843 |  | 435044.9329 | 0 | 0 | [6 empty] | 533943.5173
2046 | 11 | 81656.4096 |  | 408095.385 | 0 | 0 | [6 empty] | 489751.7946
2046 | 12 | 84035.571 |  | 417809.4226 | 0 | 0 | [6 empty] | 501844.9936
2047 | 1 | 84058.7106 |  | 442795.2501 | 0 | 0 | [6 empty] | 526853.9607
2047 | 2 | 79616.4734 |  | 415173.1472 | 0 | 0 | [6 empty] | 494789.6206
2047 | 3 | 89652.5828 |  | 416994.5318 | 0 | 0 | [6 empty] | 506647.1146
2047 | 4 | 93983.0506 |  | 421454.9171 | 0 | 0 | [6 empty] | 515437.9677
2047 | 5 | 107492.1232 |  | 453833.8989 | 0 | 0 | [6 empty] | 561326.0221
2047 | 6 | 117040.3239 |  | 468304.2571 | 0 | 0 | [6 empty] | 585344.581
2047 | 7 | 127592.1832 |  | 479659.0576 | 0 | 0 | [6 empty] | 607251.2408
2047 | 8 | 126612.657 |  | 478707.621 | 0 | 0 | [6 empty] | 605320.278
2047 | 9 | 108431.8711 |  | 462595.3231 | 0 | 0 | [6 empty] | 571027.1943
2047 | 10 | 100145.5779 |  | 439386.8058 | 0 | 0 | [6 empty] | 539532.3837
2047 | 11 | 82685.9999 |  | 412661.6665 | 0 | 0 | [6 empty] | 495347.6663
2047 | 12 | 85095.1596 |  | 422509.0518 | 0 | 0 | [6 empty] | 507604.2115
2048 | 1 | 85118.591 |  | 447132.7649 | 0 | 0 | [6 empty] | 532251.3559
2048 | 2 | 80620.3424 |  | 419495.3482 | 0 | 0 | [6 empty] | 500115.6906
2048 | 3 | 90782.9953 |  | 421248.1244 | 0 | 0 | [6 empty] | 512031.1197
2048 | 4 | 95168.0651 |  | 425648.6706 | 0 | 0 | [6 empty] | 520816.7357
2048 | 5 | 108847.4711 |  | 457981.0449 | 0 | 0 | [6 empty] | 566828.516
2048 | 6 | 118516.0632 |  | 472497.4536 | 0 | 0 | [6 empty] | 591013.5168
2048 | 7 | 129200.9689 |  | 483889.8728 | 0 | 0 | [6 empty] | 613090.8417
2048 | 8 | 128209.092 |  | 482931.0574 | 0 | 0 | [6 empty] | 611140.1495
2048 | 9 | 109799.0681 |  | 466868.3432 | 0 | 0 | [6 empty] | 576667.4113
2048 | 10 | 101408.2945 |  | 443772.0119 | 0 | 0 | [6 empty] | 545180.3064
2048 | 11 | 83728.572 |  | 417279.0412 | 0 | 0 | [6 empty] | 501007.6132
2048 | 12 | 86168.1084 |  | 427261.5437 | 0 | 0 | [6 empty] | 513429.6521
2049 | 1 | 86191.8352 |  | 451512.769 | 0 | 0 | [6 empty] | 537704.6042
2049 | 2 | 81636.8691 |  | 423862.5458 | 0 | 0 | [6 empty] | 505499.4149
2049 | 3 | 91927.6609 |  | 425545.1062 | 0 | 0 | [6 empty] | 517472.7671
2049 | 4 | 96368.0213 |  | 429884.1547 | 0 | 0 | [6 empty] | 526252.176
2049 | 5 | 110219.9083 |  | 462166.0877 | 0 | 0 | [6 empty] | 572385.9959
2049 | 6 | 120010.4098 |  | 476728.196 | 0 | 0 | [6 empty] | 596738.6059
2049 | 7 | 130830.0395 |  | 488158.0057 | 0 | 0 | [6 empty] | 618988.0452
2049 | 8 | 129825.6562 |  | 487191.7554 | 0 | 0 | [6 empty] | 617017.4117
2049 | 9 | 111183.5038 |  | 471180.8334 | 0 | 0 | [6 empty] | 582364.3372
2049 | 10 | 102686.9325 |  | 448200.9835 | 0 | 0 | [6 empty] | 550887.9161
2049 | 11 | 84784.2897 |  | 421948.0809 | 0 | 0 | [6 empty] | 506732.3706
2049 | 12 | 87254.5858 |  | 432067.4928 | 0 | 0 | [6 empty] | 519322.0786
2050 | 1 | 87278.6118 |  | 455935.6785 | 0 | 0 | [6 empty] | 543214.2903
2050 | 2 | 82666.2129 |  | 428275.2086 | 0 | 0 | [6 empty] | 510941.4215
2050 | 3 | 93086.7594 |  | 429885.9197 | 0 | 0 | [6 empty] | 522972.6791
2050 | 4 | 97583.1074 |  | 434161.7846 | 0 | 0 | [6 empty] | 531744.8921
2050 | 5 | 111609.6502 |  | 466389.3735 | 0 | 0 | [6 empty] | 577999.0237
2050 | 6 | 121523.5984 |  | 480996.8205 | 0 | 0 | [6 empty] | 602520.4189
2050 | 7 | 132479.6507 |  | 492463.7856 | 0 | 0 | [6 empty] | 624943.4363
2050 | 8 | 131462.6034 |  | 491490.0438 | 0 | 0 | [6 empty] | 622952.6472
2050 | 9 | 112585.3956 |  | 475533.1583 | 0 | 0 | [6 empty] | 588118.5539
2050 | 10 | 103981.6927 |  | 452674.1576 | 0 | 0 | [6 empty] | 556655.8503
2050 | 11 | 85853.3188 |  | 426669.3636 | 0 | 0 | [6 empty] | 512522.6824
2050 | 12 | 88354.7624 |  | 436927.5005 | 0 | 0 | [6 empty] | 525282.2628
2051 | 1 | 88379.0913 |  | 460401.9138 | 0 | 0 | [6 empty] | 548781.0051
2051 | 2 | 83708.5356 |  | 432733.8099 | 0 | 0 | [6 empty] | 516442.3454
2051 | 3 | 94260.4727 |  | 434271.0122 | 0 | 0 | [6 empty] | 528531.4849
2051 | 4 | 98813.5144 |  | 438481.9798 | 0 | 0 | [6 empty] | 537295.4942
2051 | 5 | 113016.9152 |  | 470651.2517 | 0 | 0 | [6 empty] | 583668.167
2051 | 6 | 123055.8665 |  | 485303.6662 | 0 | 0 | [6 empty] | 608359.5326
2051 | 7 | 134150.0616 |  | 496807.5444 | 0 | 0 | [6 empty] | 630957.606
2051 | 8 | 133120.1905 |  | 495826.2542 | 0 | 0 | [6 empty] | 628946.4447
2051 | 9 | 114004.9635 |  | 479925.6859 | 0 | 0 | [6 empty] | 593930.6495
2051 | 10 | 105292.7782 |  | 457191.9752 | 0 | 0 | [6 empty] | 562484.7534
2051 | 11 | 86935.8271 |  | 431443.4739 | 0 | 0 | [6 empty] | 518379.301
2051 | 12 | 89468.8109 |  | 441842.1748 | 0 | 0 | [6 empty] | 531310.9857
2052 | 1 | 89493.4465 |  | 464911.8992 | 0 | 0 | [6 empty] | 554405.3458
2052 | 2 | 84764.0006 |  | 437238.8278 | 0 | 0 | [6 empty] | 522002.8285
2052 | 3 | 95448.9852 |  | 438700.8351 | 0 | 0 | [6 empty] | 534149.8204
2052 | 4 | 100059.4353 |  | 442845.1638 | 0 | 0 | [6 empty] | 542904.5991
2052 | 5 | 114441.9241 |  | 474952.0752 | 0 | 0 | [6 empty] | 589393.9993
2052 | 6 | 124607.4546 |  | 489649.0754 | 0 | 0 | [6 empty] | 614256.53
2052 | 7 | 135841.5343 |  | 501189.6172 | 0 | 0 | [6 empty] | 637031.1515
2052 | 8 | 134798.6778 |  | 500200.7211 | 0 | 0 | [6 empty] | 634999.3989
2052 | 9 | 115442.4305 |  | 484358.7876 | 0 | 0 | [6 empty] | 599801.2181
2052 | 10 | 106620.3949 |  | 461754.8819 | 0 | 0 | [6 empty] | 568375.2768
2052 | 11 | 88031.9845 |  | 436271.003 | 0 | 0 | [6 empty] | 524302.9875
2052 | 12 | 90596.9062 |  | 446812.1307 | 0 | 0 | [6 empty] | 537409.0368
2053 | 1 | 90621.8525 |  | 469466.0634 | 0 | 0 | [6 empty] | 560087.9159
2053 | 2 | 85832.7739 |  | 441790.7457 | 0 | 0 | [6 empty] | 527623.5196
2053 | 3 | 96652.4834 |  | 443175.845 | 0 | 0 | [6 empty] | 539828.3284
2053 | 4 | 101321.0658 |  | 447251.7643 | 0 | 0 | [6 empty] | 548572.8301
2053 | 5 | 115884.9007 |  | 479292.1996 | 0 | 0 | [6 empty] | 595177.1004
2053 | 6 | 126178.6065 |  | 494033.3934 | 0 | 0 | [6 empty] | 620211.9998
2053 | 7 | 137554.3345 |  | 505610.3419 | 0 | 0 | [6 empty] | 643164.6764
2053 | 8 | 136498.3288 |  | 504613.7821 | 0 | 0 | [6 empty] | 641112.1109
2053 | 9 | 116898.0223 |  | 488832.838 | 0 | 0 | [6 empty] | 605730.8604
2053 | 10 | 107964.7513 |  | 466363.3278 | 0 | 0 | [6 empty] | 574328.0791
2053 | 11 | 89141.9631 |  | 441152.5485 | 0 | 0 | [6 empty] | 530294.5116
2053 | 12 | 91739.2254 |  | 451837.9899 | 0 | 0 | [6 empty] | 543577.2153
2054 | 1 | 91764.4863 |  | 474064.8391 | 0 | 0 | [6 empty] | 565829.3253
2054 | 2 | 86915.0231 |  | 446390.0518 | 0 | 0 | [6 empty] | 533305.0749
2054 | 3 | 97871.1563 |  | 447696.5026 | 0 | 0 | [6 empty] | 545567.6589
2054 | 4 | 102598.604 |  | 451702.2134 | 0 | 0 | [6 empty] | 554300.8173
2054 | 5 | 117346.0715 |  | 483671.9843 | 0 | 0 | [6 empty] | 601018.0558
2054 | 6 | 127769.5686 |  | 498456.9686 | 0 | 0 | [6 empty] | 626226.5372
2054 | 7 | 139288.7311 |  | 510070.0594 | 0 | 0 | [6 empty] | 649358.7905
2054 | 8 | 138219.4105 |  | 509065.7777 | 0 | 0 | [6 empty] | 647285.1882
2054 | 9 | 118371.9674 |  | 493348.2156 | 0 | 0 | [6 empty] | 611720.183
2054 | 10 | 109326.0584 |  | 471017.7672 | 0 | 0 | [6 empty] | 580343.8256
2054 | 11 | 90265.9373 |  | 446088.7148 | 0 | 0 | [6 empty] | 536354.6521
2054 | 12 | 92895.948 |  | 456920.3813 | 0 | 0 | [6 empty] | 549816.3292
2055 | 1 | 92921.5273 |  | 478708.6632 | 0 | 0 | [6 empty] | 571630.1905
2055 | 2 | 88010.9182 |  | 451037.2394 | 0 | 0 | [6 empty] | 539048.1576
2055 | 3 | 99105.1952 |  | 452263.2735 | 0 | 0 | [6 empty] | 551368.4688
2055 | 4 | 103892.2503 |  | 456196.9473 | 0 | 0 | [6 empty] | 560089.1977
2055 | 5 | 118825.6659 |  | 488091.7915 | 0 | 0 | [6 empty] | 606917.4574
2055 | 6 | 129380.591 |  | 502920.1525 | 0 | 0 | [6 empty] | 632300.7434
2055 | 7 | 141044.9964 |  | 514569.1137 | 0 | 0 | [6 empty] | 655614.1101
2055 | 8 | 139962.1929 |  | 513557.0514 | 0 | 0 | [6 empty] | 653519.2442
2055 | 9 | 119864.4971 |  | 497905.3019 | 0 | 0 | [6 empty] | 617769.799
2055 | 10 | 110704.53 |  | 475718.6593 | 0 | 0 | [6 empty] | 586423.1893
2055 | 11 | 91404.0834 |  | 451080.1132 | 0 | 0 | [6 empty] | 542484.1966
2055 | 12 | 94067.2554 |  | 462059.9407 | 0 | 0 | [6 empty] | 556127.1961
2056 | 1 | 94093.1573 |  | 483397.9771 | 0 | 0 | [6 empty] | 577491.1344
2056 | 2 | 89120.6312 |  | 455732.807 | 0 | 0 | [6 empty] | 544853.4382
2056 | 3 | 100354.7939 |  | 456876.6283 | 0 | 0 | [6 empty] | 557231.4222
2056 | 4 | 105202.2081 |  | 460736.4069 | 0 | 0 | [6 empty] | 565938.615
2056 | 5 | 120323.9163 |  | 492551.9871 | 0 | 0 | [6 empty] | 612875.9033
2056 | 6 | 131011.9264 |  | 507423.2997 | 0 | 0 | [6 empty] | 638435.2261
2056 | 7 | 142823.4061 |  | 519107.8518 | 0 | 0 | [6 empty] | 661931.2579
2056 | 8 | 141726.9497 |  | 518087.9497 | 0 | 0 | [6 empty] | 659814.8994
2056 | 9 | 121375.8459 |  | 502504.4823 | 0 | 0 | [6 empty] | 623880.3282
2056 | 10 | 112100.3825 |  | 480466.4677 | 0 | 0 | [6 empty] | 592566.8502
2056 | 11 | 92556.5802 |  | 456127.3615 | 0 | 0 | [6 empty] | 548683.9417
2056 | 12 | 95253.3316 |  | 467257.3113 | 0 | 0 | [6 empty] | 562510.6429
2057 | 1 | 95279.5601 |  | 488133.2264 | 0 | 0 | [6 empty] | 583412.7865
2057 | 2 | 90244.3364 |  | 460477.2583 | 0 | 0 | [6 empty] | 550721.5947
2057 | 3 | 101620.1485 |  | 461537.0421 | 0 | 0 | [6 empty] | 563157.1905
2057 | 4 | 106528.6828 |  | 465321.037 | 0 | 0 | [6 empty] | 571849.7198
2057 | 5 | 121841.0578 |  | 497052.94 | 0 | 0 | [6 empty] | 618893.9978
2057 | 6 | 132663.831 |  | 511966.7681 | 0 | 0 | [6 empty] | 644630.5991
2057 | 7 | 144624.2394 |  | 523686.6236 | 0 | 0 | [6 empty] | 668310.863
2057 | 8 | 143513.958 |  | 522658.8222 | 0 | 0 | [6 empty] | 666172.7802
2057 | 9 | 122906.251 |  | 507146.1456 | 0 | 0 | [6 empty] | 630052.3966
2057 | 10 | 113513.835 |  | 485261.6605 | 0 | 0 | [6 empty] | 598775.4955
2057 | 11 | 93723.6086 |  | 461231.0848 | 0 | 0 | [6 empty] | 554954.6934
2057 | 12 | 96454.3629 |  | 472513.1432 | 0 | 0 | [6 empty] | 568967.5061
2058 | 1 | 96480.9221 |  | 492914.8611 | 0 | 0 | [6 empty] | 589395.7831
2058 | 2 | 91382.2102 |  | 465271.1021 | 0 | 0 | [6 empty] | 556653.3123
2058 | 3 | 102901.4577 |  | 466244.9948 | 0 | 0 | [6 empty] | 569146.4525
2058 | 4 | 107871.8829 |  | 469951.2872 | 0 | 0 | [6 empty] | 577823.1701
2058 | 5 | 123377.3286 |  | 501595.0227 | 0 | 0 | [6 empty] | 624972.3514
2058 | 6 | 134336.5641 |  | 516550.9187 | 0 | 0 | [6 empty] | 650887.4829
2058 | 7 | 146447.7791 |  | 528305.7823 | 0 | 0 | [6 empty] | 674753.5614
2058 | 8 | 145323.4984 |  | 527270.0216 | 0 | 0 | [6 empty] | 672593.52
2058 | 9 | 124455.9527 |  | 511830.6842 | 0 | 0 | [6 empty] | 636286.6369
2058 | 10 | 114945.1095 |  | 490104.7107 | 0 | 0 | [6 empty] | 605049.8202
2058 | 11 | 94905.3519 |  | 466391.9149 | 0 | 0 | [6 empty] | 561297.2668
2058 | 12 | 97670.5377 |  | 477828.0941 | 0 | 0 | [6 empty] | 575498.6318
2059 | 1 | 97697.4318 |  | 497743.3354 | 0 | 0 | [6 empty] | 595440.7672
2059 | 2 | 92534.4312 |  | 470114.8528 | 0 | 0 | [6 empty] | 562649.284
2059 | 3 | 104198.9228 |  | 471000.9714 | 0 | 0 | [6 empty] | 575199.8942
2059 | 4 | 109232.019 |  | 474627.6115 | 0 | 0 | [6 empty] | 583859.6305
2059 | 5 | 124932.9701 |  | 506178.6112 | 0 | 0 | [6 empty] | 631111.5812
2059 | 6 | 136030.3885 |  | 521176.1159 | 0 | 0 | [6 empty] | 657206.5043
2059 | 7 | 148294.3114 |  | 532965.6842 | 0 | 0 | [6 empty] | 681259.9956
2059 | 8 | 147155.8549 |  | 531921.9037 | 0 | 0 | [6 empty] | 679077.7586
2059 | 9 | 126025.1942 |  | 516558.4942 | 0 | 0 | [6 empty] | 642583.6885
2059 | 10 | 116394.4306 |  | 494996.0959 | 0 | 0 | [6 empty] | 611390.5266
2059 | 11 | 96101.9955 |  | 471610.4908 | 0 | 0 | [6 empty] | 567712.4863
2059 | 12 | 98902.0471 |  | 483202.8289 | 0 | 0 | [6 empty] | 582104.876
2060 | 1 | 98929.2802 |  | 502619.1084 | 0 | 0 | [6 empty] | 601548.3886
2060 | 2 | 93701.1803 |  | 475009.0298 | 0 | 0 | [6 empty] | 568710.2101
2060 | 3 | 105512.7473 |  | 475805.4619 | 0 | 0 | [6 empty] | 581318.2092
2060 | 4 | 110609.3049 |  | 479350.4682 | 0 | 0 | [6 empty] | 589959.7731
2060 | 5 | 126508.2262 |  | 510804.0845 | 0 | 0 | [6 empty] | 637312.3108
2060 | 6 | 137745.5699 |  | 525842.727 | 0 | 0 | [6 empty] | 663588.2969
2060 | 7 | 150164.1264 |  | 537666.6885 | 0 | 0 | [6 empty] | 687830.8149
2060 | 8 | 149011.3152 |  | 536614.8274 | 0 | 0 | [6 empty] | 685626.1426
2060 | 9 | 127614.2221 |  | 521329.9752 | 0 | 0 | [6 empty] | 648944.1973
2060 | 10 | 117862.026 |  | 499936.2986 | 0 | 0 | [6 empty] | 617798.3246
2060 | 11 | 97313.7274 |  | 476887.4587 | 0 | 0 | [6 empty] | 574201.1861
2060 | 12 | 100149.0843 |  | 488638.0202 | 0 | 0 | [6 empty] | 588787.1045
2061 | 1 | 100176.6608 |  | 507542.6432 | 0 | 0 | [6 empty] | 607719.304
2061 | 2 | 94882.6408 |  | 479954.1581 | 0 | 0 | [6 empty] | 574836.7989
2061 | 3 | 106843.1375 |  | 480658.961 | 0 | 0 | [6 empty] | 587502.0986
2061 | 4 | 112003.9567 |  | 484120.3205 | 0 | 0 | [6 empty] | 596124.2772
2061 | 5 | 128103.3446 |  | 515471.8256 | 0 | 0 | [6 empty] | 643575.1701
2061 | 6 | 139482.3778 |  | 530551.123 | 0 | 0 | [6 empty] | 670033.5007
2061 | 7 | 152057.5174 |  | 542409.1578 | 0 | 0 | [6 empty] | 694466.6753
2061 | 8 | 150890.1707 |  | 541349.1548 | 0 | 0 | [6 empty] | 692239.3255
2061 | 9 | 129223.2857 |  | 526145.5307 | 0 | 0 | [6 empty] | 655368.8164
2061 | 10 | 119348.126 |  | 504925.8059 | 0 | 0 | [6 empty] | 624273.9319
2061 | 11 | 98540.7378 |  | 482223.4719 | 0 | 0 | [6 empty] | 580764.2097
2061 | 12 | 101411.8451 |  | 494134.3479 | 0 | 0 | [6 empty] | 595546.1931
2062 | 1 | 101439.7694 |  | 512514.4078 | 0 | 0 | [6 empty] | 613954.1772
2062 | 2 | 96078.9981 |  | 484950.7681 | 0 | 0 | [6 empty] | 581029.7662
2062 | 3 | 108190.3025 |  | 485561.9687 | 0 | 0 | [6 empty] | 593752.2712
2062 | 4 | 113416.1934 |  | 488937.636 | 0 | 0 | [6 empty] | 602353.8294
2062 | 5 | 129718.5754 |  | 520182.2206 | 0 | 0 | [6 empty] | 649900.796
2062 | 6 | 141241.0847 |  | 535301.6779 | 0 | 0 | [6 empty] | 676542.7626
2062 | 7 | 153974.7819 |  | 547193.458 | 0 | 0 | [6 empty] | 701168.2399
2062 | 8 | 152792.7163 |  | 546125.2511 | 0 | 0 | [6 empty] | 698917.9675
2062 | 9 | 130852.6377 |  | 531005.5678 | 0 | 0 | [6 empty] | 661858.2054
2062 | 10 | 120852.964 |  | 509965.1099 | 0 | 0 | [6 empty] | 630818.0739
2062 | 11 | 99783.2193 |  | 487619.1911 | 0 | 0 | [6 empty] | 587402.4104
2062 | 12 | 102690.5279 |  | 499692.4998 | 0 | 0 | [6 empty] | 602383.0277
2063 | 1 | 102718.8043 |  | 517534.8746 | 0 | 0 | [6 empty] | 620253.6789
2063 | 2 | 97290.44 |  | 489999.3959 | 0 | 0 | [6 empty] | 587289.8359
2063 | 3 | 109554.4535 |  | 490514.99 | 0 | 0 | [6 empty] | 600069.4435
2063 | 4 | 114846.2367 |  | 493802.8869 | 0 | 0 | [6 empty] | 608649.1236
2063 | 5 | 131354.1724 |  | 524935.6593 | 0 | 0 | [6 empty] | 656289.8317
2063 | 6 | 143021.9668 |  | 540094.7693 | 0 | 0 | [6 empty] | 683116.7362
2063 | 7 | 155916.2208 |  | 552019.9579 | 0 | 0 | [6 empty] | 707936.1787
2063 | 8 | 154719.2508 |  | 550943.485 | 0 | 0 | [6 empty] | 705662.7358
2063 | 9 | 132502.5338 |  | 535910.4973 | 0 | 0 | [6 empty] | 668413.0311
2063 | 10 | 122376.7761 |  | 515054.7077 | 0 | 0 | [6 empty] | 637431.4838
2063 | 11 | 101041.3671 |  | 493075.2843 | 0 | 0 | [6 empty] | 594116.6513
2063 | 12 | 103985.3334 |  | 505313.1711 | 0 | 0 | [6 empty] | 609298.5045
[14 empty] | 1078062.336 | 0%
2007 |  | 749620.269 | 766119.4788 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  |  | 0 | 2145121.11 | 0%
2008 |  | 721384.279 | 258225 | 0 | 6959.072 | 4500 | 0 | 0 | 0 | 0 |  |  | 991068.351 | 2163412.843 | 0%
2009 |  | 715316.129 | 225928 | 0 | 6243.207 | 130575 | 0 | 0 | 0 | 0 |  |  | 1078062.336 | 2244008.3846 | 0%
2010 |  | 700571.713 | 227430 | 1210527.039 | 6592.358 | 0 | 0 | 0 | 0 | 0 |  |  | 2145121.11 | 2152488.2726 | 0%
2011 |  | 737954.811 | 226755 | 1177915.252 | 7159.005 | 0 | 0 | 13628.775 | 0 | 0 |  |  | 2163412.843 | 5555677.9685 | 0%
2012 |  | 736959.8724 | 225675 | 1184367.714 | 6108.396 | 0 | 0 | 63284.5599 | 27612.8423 | 0 |  |  | 2244008.3846 | 6409853.9237 | -393000%
2013 |  | 758684.1007 | 86175 | 1202479.9527 | 5251.1829 | 0 | 0 | 61754.2453 | 38143.7911 | 0 |  |  | 2152488.2726 | 6535346.639 | -29600%
2014 |  | 800964.1544 | 0 | 3751337.0767 | 0 | 521550 | 184143 | 63274.2018 | 38695.4701 | 195714.0656 |  |  | 5555677.9685 | 5947552.7772 | -32000%
2015 |  | 816569.5069 | 0 | 3907837.2817 | 0 | 1102340 | 244050 | 64328.0298 | 38582.1427 | 236146.9626 |  |  | 6413783.9237 | 5612410.2451 | 0%
2016 |  | 804974.4374 | 0 | 3969952.328 | 0 | 1102340 | 285480 | 63764.6575 | 38634.8858 | 270200.3303 |  |  | 6535642.639 | 5667272.7011 | 0%
2017 |  | 814871.1652 | 0 | 4029501.612 | 0 | 1102340 | 360 | 0 | 0 | 480 |  |  | 5947872.7772 | 5708061.6513 | 0%
2018 |  | 836068.8366 | 0 | 3941141.4085 | 0 | 835200 | 0 | 0 | 0 | 0 |  |  | 5612410.2451 | 5254013.2963 | 0%
2019 |  | 846610.6704 | 0 | 3985462.0307 | 0 | 835200 | 0 | 0 | 0 | 0 |  |  | 5667272.7011 | 4959571.6508 | 0%
2020 |  | 857285.4243 | 0 | 4012376.227 | 0 | 838400 | 0 | 0 | 0 | 0 |  |  | 5708061.6513 | 5018402.2874 | 0%
2021 |  | 868094.7741 | 0 | 4043518.5222 | 0 | 342400 | 0 | 0 | 0 | 0 |  |  | 5254013.2963 | 5078425.6582 | 0%
2022 |  | 879040.4169 | 0 | 4080531.2339 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4959571.6508 | 5139722.6026 | 0%
2023 |  | 890124.0713 | 0 | 4128278.2161 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5018402.2874 | 5204321.1202 | 0%
2024 |  | 901347.4774 | 0 | 4177078.1808 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5078425.6582 | 5273128.0536 | 0%
2025 |  | 912712.3973 | 0 | 4227010.2053 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5139722.6026 | 5335301.0902 | 0%
2026 |  | 924220.6153 | 0 | 4280100.5049 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5204321.1202 | 5393729.7739 | 0%
2027 |  | 935873.9383 | 0 | 4337254.1153 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5273128.0536 | 5453035.4079 | 0%
2028 |  | 947674.1958 | 0 | 4387626.8944 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5335301.0902 | 5517399.7391 | 0%
2029 |  | 959623.2405 | 0 | 4434106.5334 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5393729.7739 | 5589117.4462 | 0%
2030 |  | 971722.9485 | 0 | 4481312.4594 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5453035.4079 | 5653429.5521 | 0%
2031 |  | 983975.2194 | 0 | 4533424.5197 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5517399.7391 | 5711401.2165 | 0%
2032 |  | 996381.9769 | 0 | 4592735.4693 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5589117.4462 | 5768872.1017 | 0%
2033 |  | 1008945.1688 | 0 | 4644484.3833 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5653429.5521 | 5827759.2841 | 0%
2034 |  | 1021666.7676 | 0 | 4689734.4489 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5711401.2165 | 5883300.4628 | 0%
2035 |  | 1034548.7707 | 0 | 4734323.331 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5768872.1017 | 5944136.174 | 0%
2036 |  | 1047593.2005 | 0 | 4780166.0836 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5827759.2841 | 6004163.327 | 0%
2037 |  | 1060802.1051 | 0 | 4822498.3577 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5883300.4628 | 6065896.458 | 0%
2038 |  | 1074177.5582 | 0 | 4869958.6158 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5944136.174 | 6128274.7538 | 0%
2039 |  | 1087721.6599 | 0 | 4916441.6671 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6004163.327 | 6191305.0717 | 0%
2040 |  | 1101436.5366 | 0 | 4964459.9214 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6065896.458 | 6254994.3434 | 0%
2041 |  | 1115324.3416 | 0 | 5012950.4121 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6128274.7538 | 6319349.5755 | 0%
2042 |  | 1129387.2553 | 0 | 5061917.8163 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6191305.0717 | 6384377.8503 | 0%
2043 |  | 1143627.4857 | 0 | 5111366.8577 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6254994.3434 | 6450086.3268 | 0%
2044 |  | 1158047.2684 | 0 | 5161302.3071 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6319349.5755 | 6516482.2414 | 0%
2045 |  | 1172648.8674 | 0 | 5211728.9829 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6384377.8503 | 6583572.9089 | 0%
2046 |  | 1187434.5752 | 0 | 5262651.7515 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6450086.3268 | 6651365.7233 | 0%
2047 |  | 1202406.7132 | 0 | 5314075.5282 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6516482.2414 | 6719868.1584 | 0%
2048 |  | 1217567.6321 | 0 | 5366005.2768 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6583572.9089 | 6789087.7693 | 0%
2049 |  | 1232919.7121 | 0 | 5418446.0112 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6651365.7233 | 6859032.1926 | 0%
2050 |  | 1248465.3636 | 0 | 5471402.7948 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6719868.1584 | 6929709.1479 | 0%
2051 |  | 1264207.0273 | 0 | 5524880.742 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6789087.7693 | 7001126.4381 | 0%
2052 |  | 1280147.1746 | 0 | 5578885.018 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6859032.1926 | 7073291.9509 | 0%
2053 |  | 1296288.3083 | 0 | 5633420.8396 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6929709.1479 | 7146213.6594 | 0%
2054 |  | 1312632.9624 | 0 | 5688493.4756 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7001126.4381 | 7219899.6233 | 0%
2055 |  | 1329183.7032 | 0 | 5744108.2476 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7073291.9509 | 7294357.9894 | 0%
2056 |  | 1345943.1292 | 0 | 5800270.5302 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7146213.6594 | 7369596.993 | 0%
2057 |  | 1362913.8716 | 0 | 5856985.7517 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7219899.6233 | 7445624.9587 | 0%
2058 |  | 1380098.5949 | 0 | 5914259.3945 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7294357.9894 | 7522450.3014 | 0%
2059 |  | 1397499.9971 | 0 | 5972096.9959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7369596.993 | 7600081.5273 | 0%
2060 |  | 1415120.8103 | 0 | 6030504.1484 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7445624.9587 | 7678527.235 | 0%
2061 |  | 1432963.8009 | 0 | 6089486.5005 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7522450.3014
2062 |  | 1451031.7705 | 0 | 6149049.7568 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7600081.5273
2063 |  | 1469327.5557 | 0 | 6209199.6792 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 7678527.235

## NEW NEL,SALES,Unbilled ST
OPC 012959
FPL RC-16
BILLED SALES, UNBILLED SALES, NET ENERGY FOR LOAD,
DELIVERED SALES AND FORECASTS OF LOSSES.
(Based on 20 Year Normals)
|  |  | BILLED | DELIVERED | TOTAL | LINE | COMPANY | TOTAL | TOTAL LOSS
| MONTH | NEL | SALES | SALES | UNBILLED | LOSS | USE | LOSS | % OF NEL
2004 |  | 108093463 | 100626214.497 | 100684971.297 | 51022294.1171 | 7267948.806 | 140542.897 | 7408491.703 | 6.854%
2005 |  | 111300768 | 103802730.366 | 103494243.366 | 47978976.4786 | 7670034.649 | 136489.985 | 7806524.634 | 7.014%
2006 |  | 113137277 | 105228047.6113 | 105212920.2803 | 46875322.7052 | 7794187.2787 | 130169.441 | 7924356.7197 | 7.004%
2007 |  | 114314587 | 106913929.15 | 106729298.1455 | 44917667.5616 | 7455552.0865 | 129736.768 | 7585288.8545 | 6.635%
2008 |  | 111100357 | 103911982.772 | 103740787.228 | 44544187.2105 | 7236755.976 | 122813.796 | 7359569.772 | 6.624%
2009 |  | 111237416 | 103909489.524 | 103923413.524 | 43849551.6558 | 7191082.596 | 122919.88 | 7314002.476 | 6.575%
2007 | January | 8457601 | 8668887.61 | 7932169.61 | 2907009.3876 | 513979.844 | 11451.546 | 525431.39 | 6.213%
| February | 7476205 | 7574647.094 | 7042442.094 | 2405071.284 | 423726.78 | 10036.126 | 433762.906 | 5.802%
| March | 8426529 | 7491790.904 | 7967937.904 | 2727758.3179 | 449502.952 | 9088.144 | 458591.096 | 5.442%
| April | 8774734 | 7604488.16 | 8132695.1555 | 3321835.1179 | 632243.1545 | 9795.69 | 642038.8445 | 7.317%
| May | 9318740 | 8376287.267 | 8701269.267 | 3658585.5339 | 607150.887 | 10319.846 | 617470.733 | 6.626%
| June | 10592821 | 9218517.693 | 9917019.693 | 4224158.7647 | 665028.778 | 10772.529 | 675801.307 | 6.38%
| July | 10979151 | 10282883.837 | 10143932.837 | 4253020.5608 | 823182.156 | 12036.007 | 835218.163 | 7.607%
| August | 11978003 | 10371781.381 | 11231296.381 | 4988425.9492 | 734882.6 | 11824.019 | 746706.619 | 6.234%
| September | 11283134 | 10848349.828 | 10468144.828 | 4476648.2003 | 803332.243 | 11656.929 | 814989.172 | 7.223%
| October | 10293316 | 9554350.737 | 9430137.737 | 4678346.1483 | 851555.015 | 11623.248 | 863178.263 | 8.386%
| November | 8434259 | 8733071.78 | 8004243.78 | 3814821.297 | 418751.685 | 11263.535 | 430015.22 | 5.098%
| December | 8300094 | 8188872.859 | 7758008.859 | 3461987 | 532215.992 | 9869.149 | 542085.141 | 6.531%
| TOTAL | 114314587 | 106913929.15 | 106729298.1455 | 44917667.5616 | 7455552.0865 | 129736.768 | 7585288.8545 | 6.635%
|  | 1.041% | 1.602% | 1.441% | -4.176% | -4.345% | -0.3324% | -4.279%
2008 | January | 8158564 | 8470750.247 | 7773957.247 | 2700158.4138 | 374281.524 | 10325.229 | 384606.753 | 4.714%
| February | 7896972 | 7524833.655 | 7368404.655 | 2547915.4321 | 519059.385 | 9507.96 | 528567.345 | 6.693%
| March | 8325921 | 7446360.085 | 7754317.085 | 2836821.3464 | 562044.53 | 9559.385 | 571603.915 | 6.865%
| April | 8619990 | 7712149.116 | 8218531.116 | 3320970.4386 | 393383.05 | 8075.834 | 401458.884 | 4.657%
| May | 10292599 | 8420389.152 | 9153877.152 | 4061926.0318 | 1128438.315 | 10283.533 | 1138721.848 | 11.06%
| June | 10508760 | 9854130.911 | 10105443.911 | 4310839.3663 | 392336.231 | 10979.858 | 403316.089 | 3.838%
| July | 10745283 | 9852979 | 9676714.204 | 4161924.78 | 1057466.222 | 11102.574 | 1068568.796 | 9.945%
| August | 11090020 | 9770559 | 10362505.873 | 4665682.3644 | 717326.302 | 10187.825 | 727514.127 | 6.56%
| September | 10640369 | 10336112 | 10299167.275 | 4621615.1893 | 329493.78 | 11707.945 | 341201.725 | 3.207%
| October | 9367637 | 9150907 | 8632523.104 | 4182457 | 725318.481 | 9795.415 | 735113.896 | 7.847%
| November | 7648144 | 7651233.836 | 7378389.836 | 3919204 | 258490.629 | 11263.535 | 269754.164 | 3.527%
| December | 7806098 | 7721578.77 | 7016955.77 | 3214672.848 | 779117.527 | 10024.703 | 789142.23 | 10.11%
| TOTAL | 111100357 | 103911982.772 | 103740787.228 | 44544187.2105 | 7236755.976 | 122813.796 | 7359569.772 | 6.624%
2009 | January | 8007278 | 7949034.662 | 7513268.662 | 2778907.2682 | 484925.84 | 9083.498 | 494009.338 | 6.17%
| February | 7235663 | 7469330.12 | 6835326.12 | 2144903.2807 | 392165.909 | 8170.971 | 400336.88 | 5.533%
| March | 8009351 | 6950861.034 | 7460003.034 | 2654074.728 | 540779.442 | 8568.524 | 549347.966 | 6.859%
| April | 8493145 | 7523513.553 | 8152950.553 | 3283512.1302 | 331674.184 | 8520.263 | 340194.447 | 4.006%
| May | 9656281 | 8319518.283 | 8618451.283 | 3582444.85 | 1027539.916 | 10289.801 | 1037829.717 | 10.75%
| June | 10367469 | 9212089.855 | 9950520.855 | 4320875.6499 | 406473.818 | 10474.327 | 416948.145 | 4.022%
| July | 11007925 | 10109168.403 | 9896531.403 | 4108238.8352 | 1099776.575 | 11617.022 | 1111393.597 | 10.1%
| August | 11448322 | 10005086.994 | 10678186.994 | 4781339.3748 | 758887.896 | 11247.11 | 770135.006 | 6.727%
| September | 10342759 | 10124234.235 | 9993213.235 | 4650318 | 337929.809 | 11615.956 | 349545.765 | 3.38%
| October | 10338743 | 9598261.308 | 9331106.308 | 4383163 | 996375.729 | 11260.963 | 1007636.692 | 9.746%
| November | 8115012 | 8529354.52 | 8079339.52 | 3933148 | 25223.274 | 10449.206 | 35672.48 | 0.4396%
| December | 8215468 | 8119036.557 | 7414515.557 | 3228626.5389 | 789330.204 | 11622.239 | 800952.443 | 9.749%
| TOTAL | 111237416 | 103909489.524 | 103923413.524 | 43849551.6558 | 7191082.596 | 122919.88 | 7314002.476 | 6.575%
2010 | January | 9390504 | 9190609.328 | 8839621.328 | 2877638.5052 | 540352.938 | 10529.734 | 550882.672 | 5.866%
| February | 7653971 | 7673815.05 | 7076735.05 | 2280559.2078 | 567548.7 | 9687.25 | 577235.95 | 7.542%
| March | 7879751.5 | 7350261.345 | 7584294.345 | 2514592.126 | 286364.734 | 9092.421 | 295457.155 | 3.75%
| April | 8037871 | 7041000.479 | 7634483.479 | 3108075 | 393267.761 | 10119.76 | 403387.521 | 5.019%
| May | 10395115 | 8451975.06 | 9240213.06 | 3896313 | 1143850.971 | 11050.969 | 1154901.94 | 11.11%
| June | 11409507 | 10174179.499 | 10904588.499 | 4626722 | 492434.58 | 12483.921 | 504918.501 | 4.425%
| July | 11649520 | 10681472.721 | 10441919.721 | 4387169 | 1194839.247 | 12761.032 | 1207600.279 | 10.37%
| August | 11521499 | 10556122.421 | 10894853.421 | 4725900 | 614490.574 | 12155.005 | 626645.579 | 5.439%
| September | 10666454 | 10383432.869 | 10335868.869 | 4678336 | 318006.07 | 12579.061 | 330585.131 | 3.099%
| October | 9299921 | 9039614.774 | 8406425.774 | 4045147 | 882747.396 | 10747.83 | 893495.226 | 9.608%
| November | 7811927 | 7993522.727 | 7650107.727 | 3701732 | 151674.11 | 10145.163 | 161819.273 | 2.071%
| December | 8887492 | 8069110.604 | 8139636.604 | 3772258 | 737056.795 | 10798.601 | 747855.396 | 8.415%
| TOTAL | 114603532.5 | 106605116.877 | 107148747.877 | 44614441.839 | 7322633.876 | 132150.747 | 7454784.623 | 6.505%
2011 | January | 7922768 | 8390413.447 | 7581323.447 | 2963168 | 330649.283 | 10795.27 | 341444.553 | 4.31%
| February | 7253717 | 7081196.725 | 6800802.725 | 2682774 | 442582.263 | 10332.012 | 452914.275 | 6.244%
| March | 8196116.5 | 7155217.339 | 7656680.339 | 3184237 | 528065.493 | 11370.668 | 539436.161 | 6.582%
| April | 9460285 | 8402569.867 | 9198493.867 | 3980161 | 248841.743 | 12949.39 | 261791.133 | 2.767%
| May | 10098308 | 8930549.498 | 9058096.498 | 4107708 | 1028456.167 | 11755.335 | 1040211.502 | 10.3%
| June | 10539641 | 10028106.151 | 10309364.151 | 4388966 | 217736.319 | 12540.53 | 230276.849 | 2.185%
| July | 11211614 | 10051637.074 | 11047731.074 | 5385060 | 151382.433 | 12500.493 | 163882.926 | 1.462%
| August | 11325605 | 10489122.466 | 10567032.466 | 5462970 | 745565.926 | 13006.608 | 758572.534 | 6.698%
| September | 10530592 | 10748507.38 | 9870682.38 | 4585145 | 646465.238 | 13444.382 | 659909.62 | 6.267%
| October | 9050810 | 9085583.075 | 8483851.075 | 3983413 | 555439.092 | 11519.833 | 566958.925 | 6.264%
| November | 8021393 | 7544303.75 | 7586718 | 4025826.681 | 423436.616 | 11238.384 | 434675 | 5.419%
| December | 7931422 | 7595995.04 | 7560800.04 | 3990632 | 359123.47 | 11498.49 | 370621.96 | 4.673%
| TOTAL | 111542271.5 | 105503201.812 | 105721576.062 | 48740060.681 | 5677744.043 | 142951.395 | 5820695.438 | 5.218%
2012 | January | 7979304 | 7998375.699 | 7519892.134 | 3512321 | 446899.637 | 12512.229 | 459411.866 | 5.758%
| February | 7702146 | 7127076.045 | 7280572 | 3665817 | 410159.015 | 11414.985 | 421574 | 5.473%
| March | 8639929 | 7624983.318 | 8149116.318 | 4189950 | 479728.903 | 11083.779 | 490812.682 | 5.681%
| April | 8509236 | 8237156.535 | 8016770.535 | 3969564 | 481486.829 | 10978.636 | 492465.465 | 5.787%
| May | 9894790 | 8382089.855 | 9321939.855 | 4909414 | 561077.82 | 11772.325 | 572850.145 | 5.789%
| June | 10242699 | 9760441.682 | 9643564.682 | 4792537 | 587153.512 | 11980.806 | 599134.318 | 5.849%
| July | 11225750 | 10162616.489 | 10544138.489 | 5174059 | 669861.629 | 11749.882 | 681611.511 | 6.072%
| August | 11202980 | 10482002.429 | 10514843.429 | 5206900 | 674438.153 | 13698.418 | 688136.571 | 6.142%
| September | 10233593 | 10073713.6 | 9577272.0369 | 4710458.2597 | 644420.0141 | 11900.949 | 656320.9631 | 6.413%
| October | 9654295 | 9501696.953 | 9109917.9934 | 4318679.2992 | 532112.2576 | 12264.749 | 544377.0066 | 5.639%
| November | 7423333 | 7764955.901 | 7016295.901 | 3570019 | 396520.543 | 10516.556 | 407037.099 | 5.483%
| December | 8157450 | 7347612.48 | 7675796.0393 | 3898202.9982 | 471794.1117 | 9859.849 | 481653.9607 | 5.904%
NEL | TOTAL | 110865505 | 104462720.986 | 104370119.4127 | 51917921.5571 | 6355652.4243 | 139733.163 | 6495385.5873 | 5.859%
2013 | January | 8088864 | 7849218.641 | 7611099.4072 | 3660083.7644 | 467777.7848 | 9986.808 | 477764.5928 | 5.906%
| February | 7467802 | 7277962.856 | 7056147.7845 | 3438268.6928 | 402533.7875 | 9120.428 | 411654.2155 | 5.512%
| March | 7936038 | 7135972.143 | 7490007.1542 | 3792303.704 | 435704.2208 | 10326.625 | 446030.8458 | 5.62%
| April | 8967220 | 7842667.833 | 8456993.293 | 4406629.164 | 499764.231 | 10462.476 | 510226.707 | 5.69%
| May | 9493988 | 8805291.229 | 8945753.8501 | 4547091.7851 | 537321.1109 | 10913.039 | 548234.1499 | 5.775%
| June | 10459525 | 9306491.772 | 9826784.0155 | 5067384.0286 | 621958.7485 | 10782.236 | 632740.9845 | 6.049%
| July | 10649066 | 9913331.173 | 10012460.2344 | 5166513.0899 | 624621.0596 | 11984.706 | 636605.7656 | 5.978%
| August | 11392218 | 10456021.327 | 10731202.8139 | 5441694.5768 | 649279.0531 | 11736.133 | 661015.1861 | 5.802%
| September | 10228764 | 10595317.182 | 9633417.9343 | 4479795.3282 | 584266.1147 | 11079.951 | 595346.0657 | 5.82%
| October | 9968681 | 9259377.811 | 9390018.3639 | 4610435.8811 | 567606.1651 | 11056.471 | 578662.6361 | 5.805%
| November | 8505690 | 8408752.384 | 8021497.1101 | 4223180.6073 | 474089.6329 | 10103.257 | 484192.8899 | 5.693%
| December | 8497355 | 8091641.989 | 8036085.7003 | 4167624.3195 | 451347.0237 | 9922.276 | 461269.2997 | 5.428%
NEL | TOTAL | 111655211 | 104942046.34 | 105211467.6614 | 53001004.9417 | 6316268.9326 | 127474.406 | 6443743.3386 | 5.771%
2014 | January | 8633765 | 8345525.509 | 8103587.5097 | 3925686.3192 | 520742.2793 | 9435.211 | 530177.4903 | 6.141%
| February | 7957338 | 7869289.084 | 7548084.5404 | 3604481.7766 | 400231.4266 | 9022.033 | 409253.4596 | 5.143%
| March | 8490634 | 7620792.541 | 8054749.7902 | 4038439.0268 | 426573.8448 | 9310.365 | 435884.2098 | 5.134%
| April | 9229956 | 8042109.746 | 8745991.3474 | 4742320.6272 | 473842.4286 | 10122.224 | 483964.6526 | 5.243%
| May | 10400290 | 9393818.88 | 9851075.4389 | 5199577.1861 | 538767.0591 | 10447.502 | 549214.5611 | 5.281%
| June | 10437993 | 9808038.836 | 9909924.836 | 5301463 | 517841.635 | 10226.529 | 528068.164 | 5.059%
| July | 11387222 | 10465474.969 | 10851483.2589 | 5687471.5031 | 523212.7969 | 12525.9442 | 535738.7411 | 4.705%
| August | 12124907 | 11083309.188 | 11516183.25 | 6120345.5651 | 595386.3523 | 13337.3977 | 608723.75 | 5.02%
| September | 10640900 | 11187606.693 | 10115280.2915 | 5048019.1636 | 513914.7185 | 11704.99 | 525619.7085 | 4.94%
| October | 10073732 | 9676364.706 | 9552272.7272 | 4923927.1859 | 510378.1676 | 11081.1052 | 521459.2728 | 5.176%
| November | 8128958 | 8365937.397 | 7720250.5306 | 4278240.3205 | 399765.6156 | 8941.8538 | 408707.4694 | 5.028%
| December | 8457394 | 7905623.538 | 8061689.9188 | 4434306.7012 | 386400.9478 | 9303.1334 | 395704.0812 | 4.679%
NEL | TOTAL | 115963089 | 109763891.087 | 110030573.4395 | 57304278.3753 | 5807057.2722 | 125458.2883 | 5932515.5605 | 5.116%
2015 | January | 8447758 | 8340178.47 | 8014092.6972 | 4108220.9274 | 424372.769 | 9292.5338 | 433665.3028 | 5.133%
| February | 7676502 | 7566226.972 | 7256241.2414 | 3798235.1978 | 411816.6064 | 8444.1522 | 420260.7586 | 5.475%
| March | 9442613 | 8199346.417 | 8994891.3234 | 4593780.1042 | 437334.8023 | 10386.8743 | 447721.6766 | 4.742%
| April | 10158631 | 9169231.413 | 9700972.3628 | 5125521.054 | 446484.1431 | 11174.4941 | 457658.6372 | 4.505%
| May | 10806023 | 9968768.373 | 10332459.4437 | 5489212.1247 | 461676.931 | 11886.6253 | 473563.5563 | 4.382%
| June | 11385195 | 10592318.256 | 10877291.5518 | 5774185.4205 | 495379.7337 | 12523.7145 | 507903.4482 | 4.461%
| July | 11894253 | 11383778.25 | 11340324.5182 | 5730731.6887 | 540844.8035 | 13083.6783 | 553928.4818 | 4.657%
| August | 11883008.3158 | 11567444.2348 | 11299713.0519 | 5463000.5058 | 570223.9548 | 13071.3091 | 583295.2639 | 4.909%
| September | 10918440.8839 | 10763932.4476 | 10383579.9885 | 5082648.0467 | 522850.6104 | 12010.285 | 534860.8954 | 4.899%
| October | 10212629.8598 | 9919147.7853 | 9712053.2142 | 4875553.4756 | 489342.7528 | 11233.8928 | 500576.6457 | 4.902%
| November | 8459488.791 | 8644886.1489 | 8091050.3807 | 4321717.7074 | 359132.9726 | 9305.4377 | 368438.4103 | 4.355%
| December | 8678969.889 | 8446881.2159 | 8263868.2069 | 4138704.6983 | 405554.8153 | 9546.8669 | 415101.6822 | 4.783%
NEL | TOTAL | 119963512.7395 | 114562139.9835 | 114266537.9806 | 58501510.9513 | 5565014.8949 | 131959.864 | 5696974.7589 | 4.749%
2016 | January | 8808803.1126 | 8917398.3182 | 8363934.4901 | 3585240.8703 | 435178.9391 | 9689.6834 | 444868.6225 | 5.05%
| February | 8194553.2661 | 8167237.9819 | 7783188.0293 | 3201190.9176 | 402351.2283 | 9014.0086 | 411365.2369 | 5.02%
| March | 8995609.4588 | 8168815.7011 | 8552166.7204 | 3584541.937 | 433547.568 | 9895.1704 | 443442.7384 | 4.93%
| April | 9297257.7505 | 8388072.3386 | 8872767.9588 | 4069237.5572 | 414262.8081 | 10226.9835 | 424489.7916 | 4.566%
| May | 10568988.1145 | 9468446.9559 | 10108340.8669 | 4709131.4681 | 449021.3606 | 11625.8869 | 460647.2476 | 4.358%
| June | 11074872.6884 | 10339615.7126 | 10585532.465 | 4955048.2205 | 477157.8634 | 12182.36 | 489340.2234 | 4.418%
| July | 11833884.0518 | 10988780.3122 | 11283171.3378 | 5249439.2462 | 537695.4415 | 13017.2725 | 550712.714 | 4.654%
| August | 11995478.8044 | 11141395.2032 | 11406662.7581 | 5514706.801 | 575621.0197 | 13195.0267 | 588816.0463 | 4.909%
| September | 11061196.7521 | 10884947.0946 | 10519342.6851 | 5149102.3915 | 529686.7506 | 12167.3164 | 541854.0671 | 4.899%
| October | 10360328.1894 | 10055549.141 | 9852512.0437 | 4946065.2942 | 496419.7847 | 11396.361 | 507816.1457 | 4.902%
| November | 8615994.3188 | 8785132.8432 | 8240739.5808 | 4401672.0318 | 365777.1442 | 9477.5938 | 375254.738 | 4.355%
| December | 8817793.1842 | 8592819.0382 | 8396051.7989 | 4204904.7925 | 412041.8128 | 9699.5725 | 421741.3853 | 4.783%
NEL | TOTAL | 119624759.6915 | 113898210.6407 | 113964410.7348 | 53570281.5279 | 5528761.721 | 131587.2357 | 5660348.9567 | 4.732%
2017 | January | 8847227.7248 | 9004443.4065 | 8400418.5544 | 3600879.9405 | 437077.2199 | 9731.9505 | 446809.1704 | 5.05%
| February | 7987296.8639 | 8066989.3148 | 7586335.8646 | 3120226.4903 | 392174.9727 | 8786.0266 | 400960.9993 | 5.02%
| March | 8977158.7784 | 8077662.2968 | 8534625.5748 | 3577189.7683 | 432658.3289 | 9874.8747 | 442533.2036 | 4.93%
| April | 9245820.192 | 8354144.3901 | 8823678.912 | 4046724.2903 | 411970.8777 | 10170.4022 | 422141.28 | 4.566%
| May | 10504682.4024 | 9413082.8616 | 10046837.9066 | 4680479.3352 | 446289.3452 | 11555.1506 | 457844.4959 | 4.358%
| June | 10996325.5152 | 10271030.0623 | 10510455.8772 | 4919905.1501 | 473773.6799 | 12095.9581 | 485869.638 | 4.418%
| July | 11750677.7317 | 10911212.9083 | 11203837.185 | 5212529.4269 | 533914.8012 | 12925.7455 | 546840.5467 | 4.654%
| August | 11913188.2102 | 11064065.7754 | 11328411.5209 | 5476875.1724 | 571672.1822 | 13104.507 | 584776.6893 | 4.909%
| September | 10982746.7766 | 10809027.7952 | 10444735.7329 | 5112583.1101 | 525930.0222 | 12081.0215 | 538011.0436 | 4.899%
| October | 10297901.7267 | 9989465.9202 | 9793145.4421 | 4916262.6321 | 493428.5927 | 11327.6919 | 504756.2846 | 4.902%
| November | 8563161.1415 | 8731789.0633 | 8190207.4612 | 4374681.0299 | 363534.203 | 9419.4773 | 372953.6803 | 4.355%
| December | 8765716.2294 | 8541075.5649 | 8346465.6041 | 4180071.0691 | 409608.3373 | 9642.2879 | 419250.6252 | 4.783%
NEL | TOTAL | 118831903.2927 | 113233989.3594 | 113209155.636 | 53218407.4151 | 5492032.5631 | 130715.0936 | 5622747.6567 | 4.732%
2018 | January | 8870942.0427 | 8992474.4796 | 8422935.2345 | 3610531.824 | 438248.772 | 9758.0362 | 448006.8082 | 5.05%
| February | 8017769.4211 | 8093679.9757 | 7615278.7044 | 3132130.5527 | 393671.1703 | 8819.5464 | 402490.7167 | 5.02%
| March | 9035659.8035 | 8121872.2462 | 8590242.7648 | 3600501.0714 | 435477.8129 | 9939.2258 | 445417.0387 | 4.93%
| April | 9319909.821 | 8415734.9142 | 8894385.7918 | 4079151.949 | 415272.1283 | 10251.9008 | 425524.0292 | 4.566%
| May | 10579453.2385 | 9483707.4978 | 10118349.8706 | 4713794.3218 | 449465.9694 | 11637.3986 | 461103.3679 | 4.358%
| June | 11066887.9938 | 10340219.1339 | 10577900.572 | 4951475.7599 | 476813.845 | 12173.5768 | 488987.4218 | 4.418%
| July | 11819273.5615 | 10977758.4137 | 11269240.775 | 5242958.1212 | 537031.5856 | 13001.2009 | 550032.7865 | 4.654%
| August | 11981913.5038 | 11128251.0551 | 11393763.3306 | 5508470.3967 | 574970.0684 | 13180.1049 | 588150.1732 | 4.909%
| September | 11045420.7316 | 10871051.3906 | 10504339.4834 | 5141758.4895 | 528931.2855 | 12149.9628 | 541081.2483 | 4.899%
| October | 10362644.8188 | 10049302.3489 | 9854715.1224 | 4947171.263 | 496530.7871 | 11398.9093 | 507929.6964 | 4.902%
| November | 8625899.3691 | 8790652.2501 | 8250213.2338 | 4406732.2467 | 366197.646 | 9488.4893 | 375686.1353 | 4.355%
| December | 8837189.9807 | 8607098.6603 | 8414520.8767 | 4214154.4631 | 412948.195 | 9720.909 | 422669.104 | 4.783%
NEL | TOTAL | 119562964.2862 | 113871802.366 | 113905885.76 | 53548830.4591 | 5525559.2655 | 131519.2607 | 5657078.5262 | 4.731%
2019 | January | 8942566.1931 | 9065413.3079 | 8490942.1696 | 3639683.3248 | 441787.2007 | 9836.8228 | 451624.0235 | 5.05%
| February | 8075362.6545 | 8155034.8219 | 7669980.7669 | 3154629.2698 | 396498.9887 | 8882.8989 | 405381.8876 | 5.02%
| March | 9100368.4495 | 8180104.8705 | 8651761.5681 | 3626285.9675 | 438596.4761 | 10010.4053 | 448606.8814 | 4.93%
| April | 9379119.9374 | 8472111.3677 | 8950892.5208 | 4105067.1205 | 417910.3847 | 10317.0319 | 428227.4166 | 4.566%
| May | 10639385.29 | 9540239.195 | 10175669.7955 | 4740497.7211 | 452012.1707 | 11703.3238 | 463715.4945 | 4.358%
| June | 11123540.7455 | 10395724.8891 | 10632050.1373 | 4976822.9692 | 479254.7134 | 12235.8948 | 491490.6082 | 4.418%
| July | 11875449.9247 | 11031748.2161 | 11322802.8623 | 5267877.6155 | 539584.0674 | 13062.9949 | 552647.0624 | 4.654%
| August | 12039816.6405 | 11181611.4925 | 11448824.2051 | 5535090.328 | 577748.6371 | 13243.7983 | 590992.4354 | 4.909%
| September | 11099342.8193 | 10923850.6382 | 10555620.0935 | 5166859.7834 | 531513.4487 | 12209.2771 | 543722.7258 | 4.899%
| October | 10419902.569 | 10101519.7821 | 9909166.3582 | 4974506.3595 | 499274.3179 | 11461.8928 | 510736.2107 | 4.902%
| November | 8681518.2554 | 8842769.7053 | 8303409.7356 | 4435146.3899 | 368558.8497 | 9549.6701 | 378108.5198 | 4.355%
| December | 8900710.5371 | 8665704.4834 | 8475003.3433 | 4244445.2498 | 415916.4122 | 9790.7816 | 425707.1938 | 4.783%
NEL | TOTAL | 120277084.0159 | 114555832.7696 | 114586123.5563 | 53866912.099 | 5558655.6672 | 132304.7924 | 5690960.4596 | 4.732%
2020 | January | 9016209.2198 | 9135654.7504 | 8560866.0223 | 3669656.5216 | 445425.3674 | 9917.8301 | 455343.1975 | 5.05%
| February | 8363012.3992 | 8345847.8176 | 7943190.5414 | 3266999.2454 | 410622.5442 | 9199.3136 | 419821.8578 | 5.02%
| March | 9188430.1405 | 8341104.9517 | 8735482.2172 | 3661376.5109 | 442840.6501 | 10107.2732 | 452947.9233 | 4.93%
| April | 9473915.7985 | 8556179.2347 | 9041360.2374 | 4146557.5136 | 422134.2538 | 10421.3074 | 432555.5611 | 4.566%
| May | 10738660.768 | 9632444.8588 | 10270618.3715 | 4784731.0263 | 456229.8696 | 11812.5268 | 468042.3965 | 4.358%
| June | 11221913.3317 | 10489970.9857 | 10726076.1577 | 5020836.1983 | 483493.0694 | 12344.1047 | 495837.174 | 4.418%
| July | 11974215.7979 | 11126119.1144 | 11416972.4744 | 5311689.5583 | 544071.6862 | 13171.6374 | 557243.3236 | 4.654%
| August | 12139256.2252 | 11274266.3087 | 11543382.6487 | 5580805.8983 | 582520.3946 | 13353.1818 | 595873.5764 | 4.909%
| September | 11192684.9094 | 11014884.0402 | 10644389.6412 | 5210311.4993 | 535983.3148 | 12311.9534 | 548295.2682 | 4.899%
| October | 10513055.2461 | 10189086.7655 | 9997753.1149 | 5018977.8487 | 503737.7703 | 11564.3608 | 515302.1311 | 4.902%
| November | 8768822.8434 | 8926141.8945 | 8386911.9232 | 4479747.8774 | 372265.215 | 9645.7051 | 381910.9202 | 4.355%
| December | 8994975.9863 | 8755110.8725 | 8564760.2222 | 4289397.2271 | 420321.2906 | 9894.4736 | 430215.7642 | 4.783%
NEL | TOTAL | 121585152.666 | 115786811.5947 | 115831763.5721 | 54441086.9252 | 5619645.426 | 133743.6679 | 5753389.0939 | 4.732%
2021 | January | 9119977.6908 | 9236900.1565 | 8659393.902 | 3711890.9726 | 450551.8133 | 10031.9755 | 460583.7888 | 5.05%
| February | 8242166.389 | 8320511.0354 | 7828410.9811 | 3219790.9183 | 404689.0248 | 9066.383 | 413755.4079 | 5.02%
| March | 9298358.2696 | 8354601.9833 | 8839991.3883 | 3705180.3233 | 448138.6873 | 10228.1941 | 458366.8814 | 4.93%
| April | 9585900.4606 | 8657841.1535 | 9148231.9567 | 4195571.1265 | 427124.0133 | 10544.4905 | 437668.5038 | 4.566%
| May | 10856106.1647 | 9741455.9173 | 10382944.9339 | 4837060.1431 | 461219.514 | 11941.7168 | 473161.2308 | 4.358%
| June | 11223998.8162 | 10543360.3664 | 10728069.4957 | 5021769.2724 | 483582.9219 | 12346.3987 | 495929.3206 | 4.418%
| July | 11949712.5098 | 11114558.7184 | 11393609.4942 | 5300820.0481 | 542958.3318 | 13144.6838 | 556103.0156 | 4.654%
| August | 12163876.8596 | 11275489.9961 | 11566794.7424 | 5592124.7945 | 583701.8526 | 13380.2645 | 597082.1171 | 4.909%
| September | 11214034.9946 | 11036568.4593 | 10664693.8513 | 5220250.1865 | 537005.7048 | 12335.4385 | 549341.1433 | 4.899%
| October | 10536200.8334 | 10209986.7456 | 10019764.2109 | 5030027.6518 | 504846.8016 | 11589.8209 | 516436.6225 | 4.902%
| November | 8826227.3496 | 8962769.683 | 8441816.2754 | 4509074.2442 | 374702.2241 | 9708.8501 | 384411.0742 | 4.355%
| December | 9088423.3945 | 8828853.3213 | 8653738.1857 | 4333959.1086 | 424687.9432 | 9997.2657 | 434685.2089 | 4.783%
NEL | TOTAL | 122104983.7323 | 116282897.536 | 116327459.4175 | 54677518.7899 | 5643208.8327 | 134315.4821 | 5777524.3148 | 4.732%
2022 | January | 9141505.8466 | 9293140.8619 | 8679834.8272 | 3720653.0738 | 451615.3631 | 10055.6564 | 461671.0195 | 5.05%
| February | 8239664.5873 | 8327874.2503 | 7826034.7695 | 3218813.593 | 404566.1868 | 9063.631 | 413629.8178 | 5.02%
| March | 9280554.0364 | 8343792.6671 | 8823064.8229 | 3698085.7488 | 447280.604 | 10208.6094 | 457489.2135 | 4.93%
| April | 9553467.0919 | 8633989.5227 | 9117279.4155 | 4181375.6416 | 425678.8626 | 10508.8138 | 436187.6764 | 4.566%
| May | 10842339.0516 | 9720227.4482 | 10369777.8577 | 4830926.0511 | 460634.6209 | 11926.573 | 472561.1939 | 4.358%
| June | 11324421.1798 | 10588281.176 | 10824054.7245 | 5066699.5996 | 487909.592 | 12456.8633 | 500366.4553 | 4.418%
| July | 12051148.8634 | 11211208.3103 | 11490325.3106 | 5345816.5999 | 547567.289 | 13256.2637 | 560823.5528 | 4.654%
| August | 12265436.922 | 11370370.9604 | 11663369.577 | 5638815.2165 | 588575.3643 | 13491.9806 | 602067.3449 | 4.909%
| September | 11307258.7451 | 11128519.2588 | 10753350.8565 | 5263646.8142 | 541469.904 | 12437.9846 | 553907.8886 | 4.899%
| October | 10626691.223 | 10296237.834 | 10105819.1734 | 5073228.1535 | 509182.6893 | 11689.3603 | 520872.0496 | 4.902%
| November | 8908032.0677 | 9042420.2828 | 8520058.1304 | 4550866.0011 | 378175.102 | 9798.8353 | 387973.9373 | 4.355%
| December | 9176286.9192 | 8912407.1087 | 8737399.334 | 4375858.2264 | 428793.6695 | 10093.9156 | 438887.5851 | 4.783%
NEL | TOTAL | 122716806.5339 | 116868469.6813 | 116910368.7992 | 54964784.7193 | 5671449.2475 | 134988.4872 | 5806437.7347 | 4.732%
2023 | January | 9243522.2475 | 9390382.9268 | 8776699.1211 | 3762174.4207 | 456655.252 | 10167.8745 | 466823.1264 | 5.05%
| February | 8330864.3963 | 8420390.1112 | 7912656.363 | 3254440.6724 | 409044.0825 | 9163.9508 | 418208.0333 | 5.02%
| March | 9385274.833 | 8437249.4719 | 8922623.3594 | 3739814.5599 | 452327.6714 | 10323.8023 | 462651.4737 | 4.93%
| April | 9661921.3585 | 8731752.4226 | 9220781.9286 | 4228844.0658 | 430511.3165 | 10628.1135 | 441139.43 | 4.566%
| May | 10965417.2263 | 9830570.845 | 10487491.6946 | 4885764.9154 | 465863.5727 | 12061.9589 | 477925.5317 | 4.358%
| June | 11453703.016 | 10708847.1474 | 10947624.2781 | 5124542.0462 | 493479.6646 | 12599.0733 | 506078.7379 | 4.418%
| July | 12185876.3684 | 11337744.1519 | 11618783.0103 | 5405580.9046 | 553688.8941 | 13404.464 | 567093.3582 | 4.654%
| August | 12400884.3977 | 11496664.5446 | 11792168.4105 | 5701084.7705 | 595075.0143 | 13640.9728 | 608715.9872 | 4.909%
| September | 11430301.331 | 11250526.3138 | 10870365.9639 | 5320924.4205 | 547362.0356 | 12573.3315 | 559935.3671 | 4.899%
| October | 10740069.8577 | 10407209.3219 | 10213640.5033 | 5127355.602 | 514615.2776 | 11814.0768 | 526429.3544 | 4.902%
| November | 9002073.0871 | 9138450.0136 | 8610003.3558 | 4598908.9442 | 382167.4509 | 9902.2804 | 392069.7313 | 4.355%
| December | 9273261.2703 | 9006542.5097 | 8829735.5522 | 4422101.9867 | 433325.1307 | 10200.5874 | 443525.7181 | 4.783%
NEL | TOTAL | 124073169.3899 | 118156329.7804 | 118202573.5406 | 55571537.3089 | 5734115.3629 | 136480.4863 | 5870595.8492 | 4.732%
2024 | January | 9351770.4487 | 9495350.3276 | 8879480.4923 | 3806232.1514 | 462003.0088 | 10286.9475 | 472289.9563 | 5.05%
| February | 8655555.6755 | 8645999.472 | 8221048.1929 | 3381280.8723 | 424986.3713 | 9521.1112 | 434507.4826 | 5.02%
| March | 9495599.2451 | 8625013.8689 | 9027509.2784 | 3783776.2818 | 457644.8075 | 10445.1592 | 468089.9667 | 4.93%
| April | 9776526.4155 | 8834926.1068 | 9330154.4021 | 4279004.5771 | 435617.8343 | 10754.1791 | 446372.0134 | 4.566%
| May | 11097007.7568 | 9947954.8995 | 10613346.878 | 4944396.5556 | 471454.1703 | 12206.7085 | 483660.8788 | 4.358%
| June | 11593799.7051 | 10838704.1842 | 11081530.8333 | 5187223.2047 | 499515.6921 | 12753.1797 | 512268.8718 | 4.418%
| July | 12333305.1655 | 11475594.7019 | 11759350.9227 | 5470979.4255 | 560387.6071 | 13566.6357 | 573954.2428 | 4.654%
| August | 12549707.8935 | 11635162.3971 | 11933686.6821 | 5769503.7105 | 602216.5327 | 13804.6787 | 616021.2114 | 4.909%
| September | 11565880.6261 | 11384769.3604 | 10999303.6456 | 5384037.9957 | 553854.5118 | 12722.4687 | 566576.9805 | 4.899%
| October | 10864018.8715 | 10529022.7012 | 10331514.1005 | 5186529.395 | 520554.3503 | 11950.4208 | 532504.7711 | 4.902%
| November | 9103850.4401 | 9242973.202 | 8707347.9721 | 4650904.1651 | 386488.2325 | 10014.2355 | 396502.468 | 4.355%
| December | 9377315.2879 | 9107995.1941 | 8928812.8274 | 4471721.7983 | 438187.4137 | 10315.0468 | 448502.4605 | 4.783%
NEL | TOTAL | 125764337.5312 | 119763466.4157 | 119813086.2274 | 56315590.1329 | 5812910.5326 | 138340.7713 | 5951251.3038 | 4.732%
2025 | January | 9462381.7257 | 9604975.7266 | 8984505.5977 | 3851251.6695 | 467467.5081 | 10408.6199 | 477876.128 | 5.05%
| February | 8527176.8783 | 8619235.7874 | 8099113.9904 | 3331129.8724 | 418682.9933 | 9379.8946 | 428062.8879 | 5.02%
| March | 9609242.3608 | 8637619.7462 | 9135550.304 | 3829060.4302 | 463121.8902 | 10570.1666 | 473692.0568 | 4.93%
| April | 9894125.7956 | 8940969.2675 | 9442384.4854 | 4330475.6482 | 440857.7718 | 10883.5384 | 451741.3102 | 4.566%
| May | 11229671.5298 | 10067197.7839 | 10740228.5268 | 5003506.3911 | 477090.3643 | 12352.6387 | 489443.003 | 4.358%
| June | 11733493.6411 | 10968834.656 | 11215052.4309 | 5249724.166 | 505534.3672 | 12906.843 | 518441.2102 | 4.418%
| July | 12479943.6355 | 11612862.0914 | 11899165.2875 | 5536027.3621 | 567050.41 | 13727.938 | 580778.348 | 4.654%
| August | 12698676.7314 | 11773381.0546 | 12075343.1614 | 5837989.4689 | 609365.0256 | 13968.5444 | 623333.57 | 4.909%
| September | 11703663.5501 | 11520149.093 | 11130337.0072 | 5448177.3831 | 560452.513 | 12874.0299 | 573326.5429 | 4.899%
| October | 10992446.7626 | 10653983.0005 | 10453647.0407 | 5247841.4232 | 526708.0305 | 12091.6914 | 538799.7219 | 4.902%
| November | 9212216.9585 | 9352570.5899 | 8810994.7741 | 4706265.6075 | 391088.7457 | 10133.4387 | 401222.1844 | 4.355%
| December | 9487461.7409 | 9215709.869 | 9033691.1462 | 4524246.8847 | 443334.3868 | 10436.2079 | 453770.5947 | 4.783%
NEL | TOTAL | 127030501.3102 | 120967488.6661 | 121020013.7524 | 56895696.3067 | 5870754.0064 | 139733.5514 | 6010487.5579 | 4.732%
2026 | January | 9584990.6771 | 9724015.0267 | 9100922.4621 | 3901154.32 | 473524.7253 | 10543.4897 | 484068.215 | 5.05%
| February | 8638616.7091 | 8731450.1915 | 8204959.5599 | 3374663.6885 | 424154.6709 | 9502.4784 | 433657.1492 | 5.02%
| March | 9736321.4679 | 8751330.1661 | 9256364.9876 | 3879698.51 | 469246.5267 | 10709.9536 | 479956.4803 | 4.93%
| April | 10026908.2396 | 9060210.8563 | 9569104.4114 | 4388592.0651 | 446774.2291 | 11029.5991 | 457803.8281 | 4.566%
| May | 11379133.2392 | 10201667.3065 | 10883175.9773 | 5070100.7359 | 483440.2153 | 12517.0466 | 495957.2619 | 4.358%
| June | 11890927.8662 | 11115468.8306 | 11365530.4678 | 5320162.3731 | 512317.3778 | 13080.0207 | 525397.3984 | 4.418%
| July | 12645144.44 | 11767531.088 | 12056678.1526 | 5609309.4377 | 574556.6285 | 13909.6589 | 588466.2874 | 4.654%
| August | 12867087.9685 | 11929383.5958 | 12235487.6806 | 5915413.5225 | 617446.4911 | 14153.7968 | 631600.2878 | 4.909%
| September | 11860546.5874 | 11673740.2764 | 11279534.8261 | 5521208.0723 | 567965.16 | 13046.6012 | 581011.7612 | 4.899%
| October | 11140899.8507 | 10797318.1394 | 10594823.6339 | 5318713.5668 | 533821.2269 | 12254.9898 | 546076.2168 | 4.902%
| November | 9342124.5698 | 9481326.2552 | 8935244.484 | 4772631.7956 | 396603.7488 | 10276.337 | 406880.0858 | 4.355%
| December | 9621788.8051 | 9345922.4709 | 9161593.555 | 4588302.8796 | 449611.2824 | 10583.9677 | 460195.2501 | 4.783%
NEL | TOTAL | 128734490.4204 | 122579364.2034 | 122643420.1984 | 57659950.9671 | 5949462.2825 | 141607.9395 | 6091070.222 | 4.731%
2027 | January | 9760614.8965 | 9883345.5245 | 9267677.1786 | 3972634.5338 | 482201.0415 | 10736.6764 | 492937.7179 | 5.05%
| February | 8800503.9599 | 8893449.9114 | 8358720.0971 | 3437904.7194 | 432103.3085 | 9680.5544 | 441783.8628 | 5.02%
| March | 9912148.0979 | 8911667.5338 | 9423524.1624 | 3949761.348 | 477720.5726 | 10903.3629 | 488623.9355 | 4.93%
| April | 10205380.5025 | 9222483.3506 | 9739428.0722 | 4466706.0697 | 454726.5117 | 11225.9186 | 465952.4302 | 4.566%
| May | 11573422.0797 | 10379034.5341 | 11068996.7772 | 5156668.3129 | 491694.5381 | 12730.7643 | 504425.3024 | 4.358%
| June | 12092262.63 | 11304395.3464 | 11557969.3101 | 5410242.2767 | 520991.831 | 13301.4889 | 534293.3199 | 4.418%
| July | 12854205.2987 | 11964204.6684 | 12256009.9594 | 5702047.5677 | 584055.7135 | 14139.6258 | 598195.3393 | 4.654%
| August | 13078584.1551 | 12126004.7167 | 12436602.2601 | 6012645.111 | 627595.4524 | 14386.4426 | 641981.895 | 4.909%
| September | 12058077.2905 | 11866873.5439 | 11467389.1066 | 5613160.6737 | 577424.2988 | 13263.885 | 590688.1839 | 4.899%
| October | 11327047.1399 | 10977426.4194 | 10771846.83 | 5407581.0843 | 542740.558 | 12459.7519 | 555200.3099 | 4.902%
| November | 9505157.3474 | 9642837.0246 | 9091176.6508 | 4855920.7105 | 403525.0235 | 10455.6731 | 413980.6966 | 4.355%
| December | 9786970.1003 | 9507722.9903 | 9318874.4849 | 4667072.205 | 457329.9484 | 10765.6671 | 468095.6155 | 4.783%
NEL | TOTAL | 130954373.4984 | 124679445.5642 | 124758214.8895 | 58652344.6126 | 6052108.798 | 144049.8108 | 6196158.6089 | 4.732%
2028 | January | 9931782.3488 | 10054971.598 | 9430200.2069 | 4042300.8139 | 490657.1813 | 10924.9606 | 501582.1419 | 5.05%
| February | 9201536.7239 | 9187354.2808 | 8739621.0817 | 3594567.6149 | 451793.9517 | 10121.6904 | 461915.6421 | 5.02%
| March | 10084480.9386 | 9163497.3987 | 9587361.7759 | 4018431.992 | 486026.2337 | 11092.929 | 497119.1628 | 4.93%
| April | 10381375.2295 | 9382083.6046 | 9907387.3154 | 4543735.7028 | 462568.4014 | 11419.5128 | 473987.9141 | 4.566%
| May | 11765755.0866 | 10554318.2448 | 11252946.9882 | 5242364.4463 | 499865.7677 | 12942.3306 | 512808.0983 | 4.358%
| June | 12292397.2751 | 11491840.2761 | 11749261.0606 | 5499785.2308 | 529614.5775 | 13521.637 | 543136.2145 | 4.418%
| July | 13062740.8513 | 12160073.4619 | 12454840.9061 | 5794552.6749 | 593530.9302 | 14369.0149 | 607899.9452 | 4.654%
| August | 13291065.7581 | 12322876.8332 | 12638653.8853 | 6110329.7271 | 637791.7004 | 14620.1723 | 652411.8728 | 4.909%
| September | 12258298.2404 | 12061765.961 | 11657801.8469 | 5706365.613 | 587012.2654 | 13484.1281 | 600496.3935 | 4.899%
| October | 11517352.3045 | 11160756.125 | 10952824.1014 | 5498433.5894 | 551859.1156 | 12669.0875 | 564528.2031 | 4.902%
| November | 9673902.862 | 9808878.2318 | 9252572.7462 | 4942128.1039 | 410688.8226 | 10641.2931 | 421330.1158 | 4.355%
| December | 9958731.413 | 9675569.5078 | 9482420.7201 | 4748979.3162 | 465356.0884 | 10954.6046 | 476310.6929 | 4.783%
NEL | TOTAL | 133419419.0317 | 127023985.5237 | 127105892.6348 | 59741974.8252 | 6166765.0359 | 146761.3609 | 6313526.3969 | 4.732%
2029 | January | 10111352.3222 | 10234293.7468 | 9600701.4061 | 4115386.9755 | 499528.4285 | 11122.4876 | 510650.9161 | 5.05%
| February | 9123462.5411 | 9216785.1426 | 8665466.2103 | 3564068.0432 | 447960.5221 | 10035.8088 | 457996.3309 | 5.02%
| March | 10265664.1793 | 9233052.2326 | 9759613.5047 | 4090629.3153 | 494758.444 | 11292.2306 | 506050.6746 | 4.93%
| April | 10566271.6487 | 9549809.6951 | 10083841.8215 | 4624661.4417 | 470806.9285 | 11622.8988 | 482429.8273 | 4.566%
| May | 11966654.4243 | 10737874.2053 | 11445090.1683 | 5331877.4047 | 508400.9362 | 13163.3199 | 521564.2561 | 4.358%
| June | 12501090.1918 | 11687453.0708 | 11948732.9377 | 5593157.2716 | 538606.0548 | 13751.1992 | 552357.254 | 4.418%
| July | 13279426.7873 | 12363926.9711 | 12661442.9425 | 5890673.2429 | 603376.4754 | 14607.3695 | 617983.8449 | 4.654%
| August | 13511779.5305 | 12527407.8988 | 12848533.5916 | 6211798.9357 | 648382.9814 | 14862.9575 | 663245.9389 | 4.909%
| September | 12466564.6962 | 12264349.0851 | 11855865.9685 | 5803315.8191 | 596985.5065 | 13713.2212 | 610698.7277 | 4.899%
| October | 11714923.0425 | 11351271.9294 | 11140710.8208 | 5592754.7106 | 561325.8063 | 12886.4153 | 574212.2217 | 4.902%
| November | 9849024.0494 | 9981228.8923 | 9420066.8331 | 5031592.6514 | 418123.2899 | 10833.9265 | 428957.2163 | 4.355%
| December | 10135433.2415 | 9849021.4345 | 9650671.1739 | 4833242.3908 | 473613.091 | 11148.9766 | 484762.0676 | 4.783%
NEL | TOTAL | 135491646.6548 | 128996474.3042 | 129080737.3788 | 60683158.2027 | 6261868.4647 | 149040.8113 | 6410909.276 | 4.732%
2030 | January | 10296129.319 | 10418796.6207 | 9776146.6598 | 4190592.4299 | 508656.917 | 11325.7423 | 519982.6592 | 5.05%
| February | 9293983.297 | 9387337.5409 | 8827426.852 | 3630681.741 | 456333.0634 | 10223.3816 | 466556.445 | 5.02%
| March | 10452522.9939 | 9402854.5451 | 9937261.0274 | 4165088.2233 | 503764.1912 | 11497.7753 | 515261.9665 | 4.93%
| April | 10757581.998 | 9723111.1977 | 10266417.4134 | 4708394.4391 | 479331.2444 | 11833.3402 | 491164.5846 | 4.566%
| May | 12174380.1017 | 10927724.6869 | 11643762.1633 | 5424431.9154 | 517226.1203 | 13391.8181 | 530617.9384 | 4.358%
| June | 12717217.1898 | 11889886.9175 | 12155310.4234 | 5689855.4213 | 547917.8275 | 13988.9389 | 561906.7664 | 4.418%
| July | 13503033.6751 | 12574635.3688 | 12874643.8506 | 5989863.9032 | 613536.4874 | 14853.337 | 628389.8245 | 4.654%
| August | 13738781.0756 | 12738097.4936 | 13064392.4258 | 6316158.8354 | 659275.9906 | 15112.6592 | 674388.6498 | 4.909%
| September | 12680462.1881 | 12472556.7831 | 12059285.2791 | 5902887.3314 | 607228.4006 | 13948.5084 | 621176.9091 | 4.899%
| October | 11918268.8273 | 11547143.9879 | 11334089.5205 | 5689832.8639 | 571069.2111 | 13110.0957 | 584179.3068 | 4.902%
| November | 10032237.45 | 10159942.269 | 9595300.6907 | 5125191.2857 | 425901.2981 | 11035.4612 | 436936.7593 | 4.355%
| December | 10322619.5292 | 10031590.7707 | 9828904.6315 | 4922505.1465 | 482360.0162 | 11354.8815 | 493714.8977 | 4.783%
NEL | TOTAL | 137887217.6448 | 131273678.1819 | 131362940.9376 | 61755483.5361 | 6372600.7678 | 151675.9394 | 6524276.7072 | 4.732%
2031 | January | 10456551.4816 | 10595086.9049 | 9928467.0649 | 4255885.3064 | 516582.2101 | 11502.2066 | 528084.4167 | 5.05%
| February | 9442529.2719 | 9535690.1286 | 8968515.8432 | 3688711.021 | 463626.6465 | 10386.7822 | 474013.4287 | 5.02%
| March | 10615454.7724 | 9550859.2675 | 10092161.0084 | 4230012.7619 | 511616.7638 | 11677.0002 | 523293.7641 | 4.93%
| April | 10924210.7706 | 9874126.323 | 10425438.3284 | 4781324.7673 | 486755.8103 | 12016.6318 | 498772.4422 | 4.566%
| May | 12358461.8376 | 11094693.8983 | 11819820.7332 | 5506451.6022 | 525046.7963 | 13594.308 | 538641.1043 | 4.358%
| June | 12908220.1881 | 12069012.8558 | 12337874.0064 | 5775312.7528 | 556147.1395 | 14199.0422 | 570346.1817 | 4.418%
| July | 13704041.5161 | 12762580.392 | 13066297.4024 | 6079029.7633 | 622669.668 | 15074.4457 | 637744.1136 | 4.654%
| August | 13943404.8885 | 12927770.7626 | 13258971.9723 | 6410230.973 | 669095.1708 | 15337.7454 | 684432.9162 | 4.909%
| September | 12872844.6532 | 12660031.1166 | 12242243.5179 | 5992443.3743 | 616441.0062 | 14160.1291 | 630601.1353 | 4.899%
| October | 12102016.1024 | 11723719.1102 | 11508830.3403 | 5777554.6044 | 579873.5444 | 13312.2177 | 593185.7621 | 4.902%
| November | 10193745.6018 | 10319627.927 | 9749774.6342 | 5207701.3116 | 432757.8475 | 11213.1202 | 443970.9676 | 4.355%
| December | 10488399.2088 | 10192896.8166 | 9986755.3259 | 5001559.8209 | 490106.6438 | 11537.2391 | 501643.8829 | 4.783%
NEL | TOTAL | 140009880.293 | 133306095.5031 | 133385150.1775 | 62706218.0591 | 6470719.2471 | 154010.8683 | 6624730.1155 | 4.732%
2032 | January | 10621903.8894 | 10763843.72 | 10085468.7244 | 4323184.8252 | 524751.0708 | 11684.0943 | 536435.165 | 5.05%
| February | 9852206.7672 | 9832061.4515 | 9357627.5951 | 3848750.9688 | 483741.7447 | 10837.4274 | 494579.1721 | 5.02%
| March | 10783703.2829 | 9803810.7044 | 10252115.6305 | 4297055.8949 | 519725.5788 | 11862.0736 | 531587.6524 | 4.93%
| April | 11096396.6025 | 10030131.1585 | 10589762.5811 | 4856687.3175 | 494427.9851 | 12206.0363 | 506634.0214 | 4.566%
| May | 12547689.9388 | 11266724.3727 | 12000801.3652 | 5590764.31 | 533086.1146 | 13802.4589 | 546888.5735 | 4.358%
| June | 13104050.2276 | 12252885.8911 | 12525051.3491 | 5862929.768 | 564584.4232 | 14414.4553 | 578998.8784 | 4.418%
| July | 13909330.4122 | 12954867.8768 | 13262032.7821 | 6170094.6734 | 631997.3666 | 15300.2635 | 647297.63 | 4.654%
| August | 14151891.817 | 13121240.5722 | 13457225.0077 | 6506079.1089 | 679099.7284 | 15567.081 | 694666.8094 | 4.909%
| September | 13068871.7984 | 12851050.9502 | 12428667.8951 | 6083696.0538 | 625828.1443 | 14375.759 | 640203.9033 | 4.899%
| October | 12288761.2973 | 11903410.6246 | 11686422.1355 | 5866707.5646 | 588821.5244 | 13517.6374 | 602339.1618 | 4.902%
| November | 10357467.5758 | 10481731.2275 | 9906365.9806 | 5291342.3178 | 439708.3809 | 11393.2143 | 451101.5952 | 4.355%
| December | 10654767.3616 | 10355613.5474 | 10145166.3477 | 5080895.1181 | 497880.7698 | 11720.2441 | 509601.0139 | 4.783%
NEL | TOTAL | 142437040.9707 | 135617372.097 | 135696707.3942 | 63778187.9211 | 6583652.8314 | 156680.7451 | 6740333.5765 | 4.732%
2033 | January | 10789008.5971 | 10933831.7643 | 10244134.1878 | 4391197.5416 | 533006.4998 | 11867.9095 | 544874.4093 | 5.05%
| February | 9750316.1053 | 9843101.8469 | 9260851.8278 | 3808947.5224 | 478738.9298 | 10725.3477 | 489464.2775 | 5.02%
| March | 10950766.6687 | 9856264.2885 | 10410943.5493 | 4363626.7832 | 527777.2761 | 12045.8433 | 539823.1194 | 4.93%
| April | 11266443.5529 | 10184558.6728 | 10752045.6084 | 4931113.7189 | 502004.8566 | 12393.0879 | 514397.9445 | 4.566%
| May | 12734062.3224 | 11436359.8437 | 12179050.7455 | 5673804.6206 | 541004.1083 | 14007.4686 | 555011.5769 | 4.358%
| June | 13296301.8952 | 12433667.2788 | 12708808.4293 | 5948945.7711 | 572867.5338 | 14625.9321 | 587493.4658 | 4.418%
| July | 14110107.0228 | 13143253.6744 | 13453465.8643 | 6259157.9611 | 641120.0407 | 15521.1177 | 656641.1585 | 4.654%
| August | 14354555.4365 | 13309848.4582 | 13649940.5797 | 6599250.0826 | 688824.8457 | 15790.011 | 704614.8567 | 4.909%
| September | 13257758.1697 | 13035926.757 | 12608301.303 | 6171624.6286 | 634873.3327 | 14583.534 | 649456.8667 | 4.899%
| October | 12467551.091 | 12076010.5135 | 11856448.467 | 5952062.5821 | 597388.3178 | 13714.3062 | 611102.624 | 4.902%
| November | 10513181.6876 | 10636468.4858 | 10055298.2334 | 5370892.3297 | 446318.9543 | 11564.4999 | 457883.4541 | 4.355%
| December | 10813479.4888 | 10510600.3316 | 10296287.5198 | 5156579.5179 | 505297.1416 | 11894.8274 | 517191.969 | 4.783%
NEL | TOTAL | 144303532.0378 | 137399891.9156 | 137475576.3154 | 64627203.0598 | 6669221.8372 | 158733.8852 | 6827955.7224 | 4.732%
2034 | January | 10948687.4341 | 11096140.4455 | 10395748.8073 | 4456187.8797 | 540895.0706 | 12043.5562 | 552938.6268 | 5.05%
| February | 9896604.3113 | 9989889.4613 | 9399796.3897 | 3866094.8081 | 485921.6569 | 10886.2647 | 496807.9216 | 5.02%
| March | 11109725.0195 | 10001192.7797 | 10562065.9745 | 4426968.0029 | 535438.3475 | 12220.6975 | 547659.045 | 4.93%
| April | 11427842.0911 | 10331288.2211 | 10906075.0886 | 5001754.8704 | 509196.3762 | 12570.6263 | 521767.0025 | 4.566%
| May | 12911640.8236 | 11597717.6753 | 12348889.523 | 5752926.7182 | 548548.4957 | 14202.8049 | 562751.3006 | 4.358%
| June | 13480076.7456 | 12606220.8251 | 12884463.2382 | 6031169.1313 | 580785.423 | 14828.0844 | 595613.5074 | 4.418%
| July | 14303149.7246 | 13323903.5478 | 13637524.9501 | 6344790.5337 | 649891.3098 | 15733.4647 | 665624.7745 | 4.654%
| August | 14550660.451 | 13491804.1645 | 13836419.4859 | 6689405.8551 | 698235.2386 | 16005.7265 | 714240.9651 | 4.909%
| September | 13441339.4228 | 13215211.7137 | 12782889.4742 | 6257083.6156 | 643664.4753 | 14785.4734 | 658449.9486 | 4.899%
| October | 12641970.2787 | 12244070.9819 | 12022318.4198 | 6035331.0534 | 605745.6916 | 13906.1673 | 619651.8589 | 4.902%
| November | 10665008.0364 | 10787386.91 | 10200512.0481 | 5448456.1915 | 452764.4795 | 11731.5088 | 464495.9883 | 4.355%
| December | 10968726.6343 | 10661954.0404 | 10444109.4349 | 5230611.586 | 512551.6001 | 12065.5993 | 524617.1994 | 4.783%
NEL | TOTAL | 146345430.9732 | 139346780.7662 | 139420812.8344 | 65540780.2459 | 6763638.1647 | 160979.9741 | 6924618.1387 | 4.732%
2035 | January | 11105891.1025 | 11255454.0392 | 10545013.261 | 4520170.8079 | 548661.3613 | 12216.4802 | 560877.8415 | 5.05%
| February | 10042333.7322 | 10135357.2202 | 9538210.2174 | 3923023.8051 | 493076.9476 | 11046.5671 | 504123.5147 | 5.02%
| March | 11270203.5231 | 10146742.4528 | 10714633.6159 | 4490914.9682 | 543172.6834 | 12397.2239 | 555569.9073 | 4.93%
| April | 11592676.1194 | 10480398.4988 | 11063383.2028 | 5073899.6723 | 516540.9728 | 12751.9437 | 529292.9165 | 4.566%
| May | 13093591.3808 | 11762812.6393 | 12522909.8013 | 5833996.8344 | 556278.6289 | 14402.9505 | 570681.5794 | 4.358%
| June | 13668404.2129 | 12783036.9482 | 13064469.5078 | 6115429.3939 | 588899.4604 | 15035.2446 | 603934.7051 | 4.418%
| July | 14500514.2792 | 13508793.9029 | 13825704.7629 | 6432340.2539 | 658858.9506 | 15950.5657 | 674809.5163 | 4.654%
| August | 14750803.1591 | 13677660.2584 | 14026737.8894 | 6781417.8849 | 707839.3863 | 16225.8835 | 724065.2698 | 4.909%
| September | 13628830.4356 | 13398251.1264 | 12961195.878 | 6344362.6365 | 652642.8442 | 14991.7135 | 667634.5577 | 4.899%
| October | 12820511.3566 | 12415903.53 | 12192108.2264 | 6120567.3329 | 614300.5676 | 14102.5625 | 628403.1301 | 4.902%
| November | 10821584.3797 | 10942389.6188 | 10350268.9795 | 5528446.6936 | 459411.6574 | 11903.7428 | 471315.4003 | 4.355%
| December | 11129277.6603 | 10818255.3538 | 10596981.5541 | 5307172.8939 | 520053.9008 | 12242.2054 | 532296.1062 | 4.783%
NEL | TOTAL | 148424621.3414 | 141325055.5886 | 141401616.8965 | 66471743.1775 | 6859737.3614 | 163267.0835 | 7023004.4449 | 4.732%
2036 | January | 11268307.0207 | 11420124.4694 | 10699226.7316 | 4586275.156 | 556685.1514 | 12395.1377 | 569080.2891 | 5.05%
| February | 10459987.1499 | 10434993.1217 | 9934897.5017 | 4086179.536 | 513583.6623 | 11505.9859 | 525089.6482 | 5.02%
| March | 11433478.394 | 10400063.0912 | 10869859.7763 | 4555976.2211 | 551041.7915 | 12576.8262 | 563618.6177 | 4.93%
| April | 11759207.7102 | 10631500.1284 | 11222311.3732 | 5146787.4659 | 523961.2086 | 12935.1285 | 536896.337 | 4.566%
| May | 13277178.3408 | 11929486.5578 | 12698495.1601 | 5915796.0682 | 564078.2845 | 14604.8962 | 578683.1806 | 4.358%
| June | 13859036.6671 | 12961754.0483 | 13246678.9191 | 6200720.939 | 597112.8076 | 15244.9403 | 612357.748 | 4.418%
| July | 14700930.0732 | 13696271.2732 | 14016793.8198 | 6521243.4855 | 667965.2303 | 16171.0231 | 684136.2534 | 4.654%
| August | 14954329.1547 | 13866531.6715 | 14220273.5066 | 6874985.3206 | 717605.8861 | 16449.7621 | 734055.6481 | 4.909%
| September | 13819218.6533 | 13584252.5456 | 13142257.5614 | 6432990.3364 | 661759.9514 | 15201.1405 | 676961.0919 | 4.899%
| October | 13000422.0465 | 12589733.3784 | 12363200.513 | 6206457.4711 | 622921.0693 | 14300.4643 | 637221.5335 | 4.902%
| November | 10976851.9172 | 11097463.0157 | 10498774.1077 | 5607768.5631 | 466003.2723 | 12074.5371 | 478077.8094 | 4.355%
| December | 11285874.1942 | 10972008.4422 | 10746088.3184 | 5381848.4394 | 527371.4142 | 12414.4616 | 539785.8758 | 4.783%
NEL | TOTAL | 150794821.3218 | 143584181.7434 | 143658857.2889 | 67517029.0024 | 6970089.7294 | 165874.3035 | 7135964.0328 | 4.732%
2037 | January | 11425304.6869 | 11579969.7862 | 10848295.5868 | 4650174.24 | 564441.265 | 12567.8352 | 577009.1002 | 5.05%
| February | 10337190.9302 | 10430230.5098 | 9818265.6323 | 4038209.3624 | 507554.388 | 11370.91 | 518925.298 | 5.02%
| March | 11593354.6849 | 10440381.0351 | 11021854.8913 | 4619683.2186 | 558747.1034 | 12752.6902 | 571499.7936 | 4.93%
| April | 11923575.8608 | 10780129.7375 | 11379174.8806 | 5218728.3617 | 531285.0468 | 13115.9334 | 544400.9802 | 4.566%
| May | 13458266.8554 | 12093937.2379 | 12871690.9678 | 5996482.0917 | 571771.794 | 14804.0935 | 586575.8876 | 4.358%
| June | 14045983.7358 | 13137484.2817 | 13425365.7827 | 6284363.5926 | 605167.371 | 15450.5821 | 620617.9531 | 4.418%
| July | 14896894.0821 | 13879829.9244 | 14203638.264 | 6608171.9323 | 676869.2346 | 16386.5835 | 693255.8181 | 4.654%
| August | 15153981.1543 | 14051525.4649 | 14410125.2887 | 6966771.756 | 727186.4864 | 16669.3793 | 743855.8656 | 4.909%
| September | 14007397.0132 | 13767400.0726 | 13321217.6412 | 6520589.3246 | 670771.2353 | 15408.1367 | 686179.372 | 4.899%
| October | 13180213.5128 | 12762478.0529 | 12534179.4197 | 6292290.6913 | 631535.8582 | 14498.2349 | 646034.0931 | 4.902%
| November | 11134089.2064 | 11253357.1659 | 10649163.1987 | 5688096.7241 | 472678.5096 | 12247.4981 | 484926.0078 | 4.355%
| December | 11445853.4911 | 11128375.6683 | 10898416.0534 | 5458137.1091 | 534846.9988 | 12590.4388 | 547437.4377 | 4.783%
NEL | TOTAL | 152602105.2139 | 145305098.9373 | 145381387.6071 | 68341698.4043 | 7052855.2911 | 167862.3157 | 7220717.6069 | 4.732%
2038 | January | 11585946.4409 | 11743405.1108 | 11000824.4933 | 4715556.4916 | 572377.4065 | 12744.5411 | 585121.9476 | 5.05%
| February | 10484671.4664 | 10578076.731 | 9958342.6696 | 4095822.4302 | 514795.6582 | 11533.1386 | 526328.7968 | 5.02%
| March | 11754271.5755 | 10586856.8684 | 11174839.3092 | 4683804.871 | 566502.5676 | 12929.6987 | 579432.2663 | 4.93%
| April | 12088141.2543 | 10929275.9091 | 11536226.6253 | 5290755.5871 | 538617.6737 | 13296.9554 | 551914.629 | 4.566%
| May | 13640432.3286 | 12259024.4161 | 13045916.7951 | 6077647.9661 | 579511.058 | 15004.4756 | 594515.5335 | 4.358%
| June | 14235622.6315 | 13315062.8956 | 13606625.5356 | 6369210.6061 | 613337.911 | 15659.1849 | 628997.0959 | 4.418%
| July | 15096315.9526 | 14066355.9922 | 14393779.6515 | 6696634.2654 | 685930.3535 | 16605.9475 | 702536.3011 | 4.654%
| August | 15356082.9432 | 14239256.4357 | 14602306.6085 | 7059684.4382 | 736884.6434 | 16891.6912 | 753776.3347 | 4.909%
| September | 14196290.3083 | 13952020.9495 | 13500857.6338 | 6608521.1225 | 679816.7552 | 15615.9193 | 695432.6745 | 4.899%
| October | 13359919.3585 | 12935514.9891 | 12705076.9025 | 6378083.036 | 640146.5447 | 14695.9113 | 654842.4559 | 4.902%
| November | 11292481.9976 | 11409725.3027 | 10800657.4656 | 5769015.1988 | 479402.8018 | 12421.7302 | 491824.532 | 4.355%
| December | 11609532.1664 | 11287091.5439 | 11054266.2313 | 5536189.8863 | 542495.4497 | 12770.4854 | 555265.9351 | 4.783%
NEL | TOTAL | 154699708.4238 | 147301667.1441 | 147379719.9213 | 69280925.8993 | 7149818.8232 | 170169.6793 | 7319988.5025 | 4.732%
2039 | January | 11753154.8007 | 11912166.8653 | 11159588.3741 | 4783611.3951 | 580637.9563 | 12928.4703 | 593566.4266 | 5.05%
| February | 10640813.4475 | 10733438.6643 | 10106646.3487 | 4156819.0795 | 522462.204 | 11704.8948 | 534167.0988 | 5.02%
| March | 11924824.9014 | 10742037.7897 | 11336985.1298 | 4751766.4196 | 574722.4642 | 13117.3074 | 587839.7716 | 4.93%
| April | 12262316.2885 | 11087226.9034 | 11702449.2582 | 5366988.7743 | 546378.4823 | 13488.5479 | 559867.0303 | 4.566%
| May | 13830982.2038 | 12432600.7611 | 13228161.5918 | 6162549.6051 | 587606.5316 | 15214.0804 | 602820.612 | 4.358%
| June | 14432107.1823 | 13499857.6168 | 13794428.4703 | 6457120.4586 | 621803.3942 | 15875.3179 | 637678.7121 | 4.418%
| July | 15301873.115 | 14259073.095 | 14589770.8132 | 6787818.1769 | 695270.2413 | 16832.0604 | 712102.3017 | 4.654%
| August | 15565090.0377 | 14433100.7425 | 14801054.2767 | 7155771.7111 | 746914.162 | 17121.599 | 764035.761 | 4.909%
| September | 14393340.9619 | 14143776.8361 | 13688255.3808 | 6700250.2558 | 689252.906 | 15832.6751 | 705085.581 | 4.899%
| October | 13548086.5236 | 13116356.3743 | 12884020.9695 | 6467914.851 | 649162.659 | 14902.8952 | 664065.5542 | 4.902%
| November | 11457801.7804 | 11573219.4009 | 10958777.0311 | 5853472.4811 | 486421.1674 | 12603.582 | 499024.7493 | 4.355%
| December | 11777871.0594 | 11451561.2548 | 11214553.7359 | 5616464.9623 | 550361.6654 | 12955.6582 | 563317.3235 | 4.783%
NEL | TOTAL | 156888262.3023 | 149384416.3042 | 149464691.3802 | 70260548.1703 | 7250993.8336 | 172577.0885 | 7423570.9221 | 4.732%
2040 | January | 11923409.6648 | 12084803.6188 | 11321244.9024 | 4852906.2458 | 589049.0117 | 13115.7506 | 602164.7624 | 5.05%
| February | 11080020.8882 | 11048317.0337 | 10523805.6476 | 4328394.8597 | 544027.2177 | 12188.023 | 556215.2407 | 5.02%
| March | 12100107.8597 | 11010409.6761 | 11503627.4334 | 4821612.6171 | 583170.3076 | 13310.1186 | 596480.4262 | 4.93%
| April | 12442590.0681 | 11250213.5305 | 11874492.183 | 5445891.2695 | 554411.0361 | 13686.8491 | 568097.8851 | 4.566%
| May | 14028188.8905 | 12612247.0724 | 13416773.0642 | 6250417.2613 | 595984.8185 | 15431.0078 | 611415.8263 | 4.358%
| June | 14634916.3678 | 13690833.8102 | 13988276.5873 | 6547860.0383 | 630541.3725 | 16098.408 | 646639.7805 | 4.418%
| July | 15512640.1915 | 14457276.2993 | 14790729.4357 | 6881313.1747 | 704846.8517 | 17063.9042 | 721910.7559 | 4.654%
| August | 15777599.7819 | 14630976.5719 | 15003132.6618 | 7253469.2645 | 757111.7604 | 17355.3598 | 774467.1201 | 4.909%
| September | 14592349.4296 | 14338093.5273 | 13877515.0347 | 6792890.772 | 698782.8105 | 16051.5844 | 714834.3948 | 4.899%
| October | 13737709.1206 | 13298798.4062 | 13064349.1296 | 6558441.4954 | 658248.511 | 15111.48 | 673359.9911 | 4.902%
| November | 11625546.5226 | 11738488.8286 | 11119215.9411 | 5939168.6078 | 493542.4804 | 12788.1012 | 506330.5816 | 4.355%
| December | 11949887.857 | 11619017.9388 | 11378343.2366 | 5698493.9055 | 558399.7438 | 13144.8766 | 571544.6204 | 4.783%
NEL | TOTAL | 159404966.6423 | 151779476.314 | 151861505.2572 | 71370859.5116 | 7368115.9218 | 175345.4633 | 7543461.3851 | 4.732%
2041 | January | 12071934.1386 | 12247405.7053 | 11462268.4845 | 4913356.6846 | 596386.5265 | 13279.1276 | 609665.654 | 5.05%
| February | 11217941.3535 | 11185885.9136 | 10654802.5279 | 4382273.299 | 550799.09 | 12339.7355 | 563138.8255 | 5.02%
| March | 12250716.5522 | 11147458.4083 | 11646811.8006 | 4881626.6914 | 590428.9634 | 13475.7882 | 603904.7516 | 4.93%
| April | 12597469.829 | 11390247.9356 | 12022300.5171 | 5513679.2729 | 561312.0951 | 13857.2168 | 575169.3119 | 4.566%
| May | 14202610.2 | 12769138.892 | 13583592.2556 | 6328132.6365 | 603395.0732 | 15622.8712 | 619017.9444 | 4.358%
| June | 14816669.6019 | 13860952.841 | 14161999.1044 | 6629178.8999 | 638372.1609 | 16298.3366 | 654670.4975 | 4.418%
| July | 15705050.7844 | 14636699.3813 | 14974185.829 | 6966665.3476 | 713589.3996 | 17275.5559 | 730864.9555 | 4.654%
| August | 15973255.5119 | 14812431.1983 | 15189184.3372 | 7343418.4865 | 766500.5937 | 17570.5811 | 784071.1747 | 4.909%
| September | 14773198.4064 | 14515845.406 | 14049504.7754 | 6877077.8559 | 707443.1127 | 16250.5182 | 723693.6309 | 4.899%
| October | 13907751.6746 | 13463514.2843 | 13226056.9713 | 6639620.5429 | 666396.1765 | 15298.5268 | 681694.7033 | 4.902%
| November | 11769287.6678 | 11883715.2682 | 11256696.6891 | 6012601.9638 | 499644.7622 | 12946.2164 | 512590.9787 | 4.355%
| December | 12097444.4139 | 11762585.7615 | 11518842.3919 | 5768858.5943 | 565294.8331 | 13307.1889 | 578602.0219 | 4.783%
NEL | TOTAL | 161383330.134 | 153675880.9953 | 153746245.684 | 72256490.2753 | 7459562.7868 | 177521.6631 | 7637084.4499 | 4.732%
2042 | January | 12220991.1152 | 12398632.4153 | 11603797.6766 | 4974023.8556 | 603750.3484 | 13443.0902 | 617193.4386 | 5.05%
| February | 11356359.3896 | 11323949.7432 | 10786272.0013 | 4436346.1137 | 557595.393 | 12491.9953 | 570087.3883 | 5.02%
| March | 12401875.7062 | 11285005.4959 | 11790519.4941 | 4941860.1118 | 597714.1489 | 13642.0633 | 611356.2121 | 4.93%
| April | 12752921.2958 | 11530797.0649 | 12170654.4544 | 5581717.5014 | 568238.6279 | 14028.2134 | 582266.8414 | 4.566%
| May | 14377666.2615 | 12926605.2021 | 13751018.5335 | 6406130.8327 | 610832.2952 | 15815.4329 | 626647.7281 | 4.358%
| June | 14999082.9468 | 14031690.2942 | 14336352.5655 | 6710793.104 | 646231.3901 | 16498.9912 | 662730.3813 | 4.418%
| July | 15898149.9437 | 14816768.8845 | 15158298.7449 | 7052322.9644 | 722363.2339 | 17487.9649 | 739851.1988 | 4.654%
| August | 16169616.0333 | 14994537.449 | 15375906.2082 | 7433691.7236 | 775923.2474 | 17786.5776 | 793709.8251 | 4.909%
| September | 14954703.9648 | 14694240.072 | 14222118.9338 | 6961570.5854 | 716134.8566 | 16450.1744 | 732585.031 | 4.899%
| October | 14078409.0429 | 13628826.9718 | 13388349.4919 | 6721093.1055 | 674573.301 | 15486.2499 | 690059.551 | 4.902%
| November | 11913552.6234 | 12029468.6194 | 11394678.434 | 6086302.9201 | 505769.2815 | 13104.9079 | 518874.1894 | 4.355%
| December | 12245532.067 | 11906673.6174 | 11659847.2421 | 5839476.5448 | 572214.7396 | 13470.0853 | 585684.8249 | 4.783%
NEL | TOTAL | 163368860.3901 | 155567195.8297 | 155637813.7802 | 73145329.3628 | 7551340.8635 | 179705.7464 | 7731046.6099 | 4.732%
2043 | January | 12370583.0396 | 12550402.591 | 11745834.8002 | 5034908.7539 | 611140.5981 | 13607.6413 | 624748.2394 | 5.05%
| February | 11495277.3225 | 11462510.8181 | 10918216.2766 | 4490614.2123 | 564416.2408 | 12644.8051 | 577061.0459 | 5.02%
| March | 12553587.9828 | 11423053.3172 | 11934753.0437 | 5002313.9388 | 605025.9924 | 13808.9468 | 618834.9391 | 4.93%
| April | 12908947.3037 | 11671863.4437 | 12319556.7007 | 5650007.1958 | 575190.7609 | 14199.842 | 589390.6029 | 4.566%
| May | 14553360.0856 | 13084648.7819 | 13919054.7771 | 6484413.1911 | 618296.6124 | 16008.6961 | 634305.3085 | 4.358%
| June | 15182159.5231 | 14203049.0976 | 14511339.9533 | 6792704.0468 | 654119.1943 | 16700.3755 | 670819.5698 | 4.418%
| July | 16091940.7724 | 14997487.7874 | 15343071.142 | 7138287.4015 | 731168.4955 | 17701.1348 | 748869.6304 | 4.654%
| August | 16366684.5909 | 15177298.2942 | 15563301.3604 | 7524290.4677 | 785379.8774 | 18003.353 | 803383.2304 | 4.909%
| September | 15136869.211 | 14873280.5252 | 14395360.4639 | 7046370.4064 | 724858.1909 | 16650.5561 | 741508.7471 | 4.899%
| October | 14249684.1015 | 13794739.2769 | 13551229.4265 | 6802860.5561 | 682780.0225 | 15674.6525 | 698454.675 | 4.902%
| November | 12058343.9188 | 12175751.3822 | 11533163.5948 | 6160272.7686 | 511916.1457 | 13264.1783 | 525180.324 | 4.355%
| December | 12394153.2856 | 12051283.9724 | 11801360.1381 | 5910348.9344 | 579159.5789 | 13633.5686 | 592793.1475 | 4.783%
NEL | TOTAL | 165361591.1374 | 157465369.2877 | 157536241.6773 | 74037391.8735 | 7643451.7098 | 181897.7503 | 7825349.4601 | 4.732%
2044 | January | 12520712.3793 | 12702718.7488 | 11888382.1981 | 5096012.3837 | 618557.3976 | 13772.7836 | 632330.1812 | 5.05%
| February | 11634697.4998 | 11601571.4554 | 11050637.5837 | 4545078.5121 | 571261.7488 | 12798.1672 | 584059.9161 | 5.02%
| March | 12705856.0689 | 11561604.2729 | 12079515.0038 | 5062989.243 | 612364.6233 | 13976.4417 | 626341.065 | 4.93%
| April | 13065550.7162 | 11813449.6222 | 12469009.9888 | 5718549.6096 | 582168.6216 | 14372.1058 | 596540.7274 | 4.566%
| May | 14729694.7116 | 13243272.437 | 14087703.8934 | 6562981.066 | 625788.1539 | 16202.6642 | 641990.8181 | 4.358%
| June | 15365902.4809 | 14375032.2069 | 14686964.2787 | 6874913.1378 | 662035.7094 | 16902.4927 | 678938.2022 | 4.418%
| July | 16286426.4019 | 15178859.0958 | 15528506.0061 | 7224560.0481 | 740005.3268 | 17915.069 | 757920.3958 | 4.654%
| August | 16564464.4597 | 15360716.7318 | 15751372.9081 | 7615216.2244 | 794870.6407 | 18220.9109 | 813091.5516 | 4.909%
| September | 15319697.2807 | 15052969.7936 | 14569232.3479 | 7131478.7787 | 733613.2658 | 16851.667 | 750464.9329 | 4.899%
| October | 14421579.7536 | 13961254.034 | 13714699.5359 | 6884924.2806 | 691016.48 | 15863.7377 | 706880.2177 | 4.902%
| November | 12203664.1076 | 12322566.0804 | 11672154.614 | 6234512.8142 | 518085.4631 | 13424.0305 | 531509.4936 | 4.355%
| December | 12543310.562 | 12196419.3156 | 11943383.4531 | 5981476.9517 | 586129.4673 | 13797.6416 | 599927.1089 | 4.783%
NEL | TOTAL | 167361556.4222 | 159370433.7944 | 159441561.8117 | 74932693.05 | 7735896.8984 | 184097.7121 | 7919994.6105 | 4.732%
2045 | January | 12671381.6249 | 12855583.4281 | 12031442.2351 | 5157335.7588 | 626000.87 | 13938.5198 | 639939.3898 | 5.05%
| February | 11774622.2915 | 11741133.9938 | 11183538.1738 | 4599739.9387 | 578132.0332 | 12952.0845 | 591084.1178 | 5.02%
| March | 12858682.6775 | 11700660.7872 | 12224807.9539 | 5123887.1054 | 619730.1726 | 14144.5509 | 633874.7235 | 4.93%
| April | 13222734.4251 | 11955558.1754 | 12619017.0784 | 5787346.0084 | 589172.3389 | 14545.0079 | 603717.3467 | 4.566%
| May | 14906673.2078 | 13402479.0009 | 14256968.817 | 6641835.8245 | 633307.0502 | 16397.3405 | 649704.3907 | 4.358%
| June | 15550315.0006 | 14547642.6063 | 14863228.5816 | 6957421.7998 | 669981.0725 | 17105.3465 | 687086.419 | 4.418%
| July | 16481609.9922 | 15360885.844 | 15714606.3499 | 7311142.3058 | 748873.8712 | 18129.771 | 767003.6422 | 4.654%
| August | 16762958.9455 | 15544795.787 | 15940123.9948 | 7706470.5135 | 804395.6959 | 18439.2548 | 822834.9508 | 4.909%
| September | 15503191.3399 | 15233310.934 | 14743737.5964 | 7216897.176 | 742400.2329 | 17053.5105 | 759453.7434 | 4.899%
| October | 14594098.9298 | 14128374.1048 | 13878762.6071 | 6967285.6783 | 699282.8139 | 16053.5088 | 715336.3227 | 4.902%
| November | 12349515.7685 | 12469915.2621 | 11811653.958 | 6309024.3741 | 524277.3432 | 13584.4673 | 537861.8105 | 4.355%
| December | 12693006.4119 | 12342082.1601 | 12085919.5824 | 6052861.7964 | 593124.5224 | 13962.3071 | 607086.8295 | 4.783%
NEL | TOTAL | 169368790.615 | 161282422.0837 | 161353806.9284 | 75831248.2798 | 7828678.017 | 186305.6697 | 8014983.6866 | 4.732%
2046 | January | 12822593.2902 | 13008999.1923 | 12175017.2982 | 5218879.9022 | 633471.1394 | 14104.8526 | 647575.992 | 5.05%
| February | 11915054.0902 | 11881200.7943 | 11316920.3191 | 4654599.427 | 585027.2116 | 13106.5595 | 598133.7711 | 5.02%
| March | 13012070.5481 | 11840225.3075 | 12370634.4984 | 5185008.6178 | 627122.7721 | 14313.2776 | 641436.0497 | 4.93%
| April | 13380501.3511 | 12098191.7041 | 12769580.7568 | 5856397.6705 | 596202.0428 | 14718.5515 | 610920.5943 | 4.566%
| May | 15084298.6722 | 13562271.3343 | 14426852.5109 | 6720978.847 | 640853.4328 | 16592.7285 | 657446.1613 | 4.358%
| June | 15735400.2928 | 14720883.3084 | 15040135.9308 | 7040231.4694 | 677955.4217 | 17308.9403 | 695264.362 | 4.418%
| July | 16677494.7323 | 15543571.0944 | 15901375.2144 | 7398035.5894 | 757774.2738 | 18345.2442 | 776119.518 | 4.654%
| August | 16962171.3849 | 15729538.5136 | 16129557.7932 | 7798054.869 | 813955.2032 | 18658.3885 | 832613.5918 | 4.909%
| September | 15687354.5845 | 15414307.032 | 14918879.2492 | 7302627.0861 | 751219.2453 | 17256.09 | 768475.3353 | 4.899%
| October | 14767244.5884 | 14296102.3781 | 14043421.4534 | 7049946.1614 | 707579.166 | 16243.969 | 723823.135 | 4.902%
| November | 12495901.5053 | 12617801.4999 | 11951664.117 | 6383808.7785 | 530491.8966 | 13745.4917 | 544237.3882 | 4.355%
| December | 12843243.3749 | 12488275.0433 | 12228970.9443 | 6124504.6794 | 600144.8629 | 14127.5677 | 614272.4306 | 4.783%
NEL | TOTAL | 171383328.415 | 163201367.2024 | 163273010.0854 | 76733073.0977 | 7921796.6683 | 188521.6613 | 8110318.3295 | 4.732%
2047 | January | 12974349.9127 | 13162968.6292 | 12319109.7967 | 5280645.8469 | 640968.3311 | 14271.7849 | 655240.116 | 5.05%
| February | 12055995.3111 | 12021774.2403 | 11450786.3137 | 4709657.9203 | 591947.4026 | 13261.5948 | 605208.9974 | 5.02%
| March | 13166022.4472 | 11980300.3051 | 12516997.2673 | 5246354.8825 | 634542.5553 | 14482.6247 | 649025.18 | 4.93%
| April | 13538854.444 | 12241352.8347 | 12920703.8392 | 5925705.887 | 603257.865 | 14892.7399 | 618150.6049 | 4.566%
| May | 15262574.2327 | 13722652.3263 | 14597357.9665 | 6800411.5272 | 648427.4346 | 16788.8317 | 665216.2662 | 4.358%
| June | 15921161.5994 | 14894757.355 | 15217689.4249 | 7123343.597 | 685958.8968 | 17513.2778 | 703472.1746 | 4.418%
| July | 16874083.841 | 15726917.9385 | 16088815.6681 | 7485241.3266 | 766706.6807 | 18561.4922 | 785268.1729 | 4.654%
| August | 17162105.1461 | 15914947.9935 | 16319677.5061 | 7889970.8392 | 823549.3243 | 18878.3157 | 842427.6399 | 4.909%
| September | 15872190.2416 | 15595961.2029 | 15094660.3749 | 7388670.0112 | 760070.4574 | 17459.4093 | 777529.8667 | 4.899%
| October | 14941019.7163 | 14464441.7707 | 14208678.9153 | 7132907.1558 | 715905.6794 | 16435.1217 | 732340.8011 | 4.902%
| November | 12642823.9471 | 12766227.3911 | 12092187.6059 | 6458867.3706 | 536729.2349 | 13907.1063 | 550636.3412 | 4.355%
| December | 12994024.0148 | 12635000.527 | 12372539.9798 | 6196406.8234 | 607190.6086 | 14293.4264 | 621484.035 | 4.783%
NEL | TOTAL | 173405204.8542 | 165127302.5143 | 165199204.6583 | 77638183.1876 | 8015254.4706 | 190745.7253 | 8206000.1959 | 4.732%
2048 | January | 13126654.0539 | 13317494.3509 | 12463722.1627 | 5342634.6352 | 648492.5718 | 14439.3195 | 662931.8912 | 5.05%
| February | 12197448.3927 | 12162856.7376 | 11585138.4737 | 4764916.3713 | 598892.7258 | 13417.1932 | 612309.9191 | 5.02%
| March | 13320541.1685 | 12120888.2752 | 12663898.9166 | 5307927.0127 | 641989.6567 | 14652.5953 | 656642.252 | 4.93%
| April | 13697796.6834 | 12385044.2197 | 13072389.1691 | 5995271.962 | 610339.938 | 15067.5764 | 625407.5144 | 4.566%
| May | 15441503.0476 | 13883624.8944 | 14768488.2045 | 6880135.2721 | 656029.1897 | 16985.6534 | 673014.8431 | 4.358%
| June | 16107602.1935 | 15069267.8173 | 15395892.1922 | 7206759.647 | 693991.6389 | 17718.3624 | 711710.0013 | 4.418%
| July | 17071380.5667 | 15910929.4971 | 16276930.8085 | 7572760.9583 | 775671.2395 | 18778.5186 | 794449.7582 | 4.654%
| August | 17362763.6289 | 16101027.3379 | 16510486.3668 | 7982219.9872 | 833178.2222 | 19099.04 | 852277.2621 | 4.909%
| September | 16057701.5694 | 15778276.5915 | 15271084.0724 | 7475027.4681 | 768954.0253 | 17663.4717 | 786617.497 | 4.899%
| October | 15115427.3289 | 14633395.2272 | 14374537.8602 | 7216170.1011 | 724262.4986 | 16626.9701 | 740889.4687 | 4.902%
| November | 12790285.7492 | 12915195.5584 | 12233226.9641 | 6534201.5069 | 542989.4708 | 14069.3143 | 557058.7851 | 4.355%
| December | 13145350.9198 | 12782261.1976 | 12516629.1534 | 6268569.4626 | 614261.8804 | 14459.886 | 628721.7664 | 4.783%
NEL | TOTAL | 175434455.3025 | 167060261.7049 | 167132424.3441 | 78546594.3845 | 8109053.0576 | 192977.9008 | 8302030.9584 | 4.732%
2049 | January | 13279508.2995 | 13472578.9942 | 12608856.8513 | 5404847.3197 | 656043.9891 | 14607.4591 | 670651.4482 | 5.05%
| February | 12339415.797 | 12304450.7153 | 11719979.1374 | 4820375.7417 | 605863.3022 | 13573.3574 | 619436.6596 | 5.02%
| March | 13475629.5333 | 12261991.7376 | 12811342.1285 | 5369726.1325 | 649464.2123 | 14823.1925 | 664287.4048 | 4.93%
| April | 13857331.0789 | 12529268.5384 | 13224639.6186 | 6065097.2127 | 617448.3961 | 15243.0642 | 632691.4602 | 4.566%
| May | 15621088.3057 | 14045191.9849 | 14940246.2748 | 6960151.5027 | 663658.8337 | 17183.1971 | 680842.0309 | 4.358%
| June | 16294725.3799 | 15244417.7964 | 15574747.3918 | 7290481.098 | 702053.7902 | 17924.1979 | 719977.9882 | 4.418%
| July | 17269388.1881 | 16095608.9206 | 16465723.7617 | 7660595.9392 | 784668.0993 | 18996.327 | 803664.4263 | 4.654%
| August | 17564150.2658 | 16287779.687 | 16701987.6389 | 8074803.8911 | 842842.0616 | 19320.5653 | 862162.6269 | 4.909%
| September | 16243891.8578 | 15961256.373 | 15448153.4702 | 7561700.9882 | 777870.1065 | 17868.281 | 795738.3876 | 4.899%
| October | 15290470.4705 | 14802965.721 | 14541001.1835 | 7299736.4507 | 732649.7694 | 16819.5175 | 749469.287 | 4.902%
| November | 12938289.5929 | 13064708.6499 | 12374784.7563 | 6609812.5571 | 549272.7181 | 14232.1186 | 563504.8366 | 4.355%
| December | 13297226.7028 | 12930059.6671 | 12661240.953 | 6340993.843 | 621358.8004 | 14626.9494 | 635985.7498 | 4.783%
NEL | TOTAL | 177471115.472 | 169000278.7856 | 169072703.1659 | 79458322.6767 | 8203194.079 | 195218.227 | 8398412.306 | 4.732%
2050 | January | 13432915.2598 | 13628225.2213 | 12754516.341 | 5467284.9627 | 663622.712 | 14776.2068 | 678398.9188 | 5.05%
| February | 12481900.0095 | 12446558.6258 | 11855310.6657 | 4876037.0026 | 612859.2538 | 13730.09 | 626589.3438 | 5.02%
| March | 13631290.3907 | 12403613.2369 | 12959329.6118 | 5431753.3775 | 656966.3595 | 14994.4194 | 671960.7789 | 4.93%
| April | 14017460.6704 | 12674028.4968 | 13377458.0891 | 6135182.9698 | 624583.3746 | 15419.2067 | 640002.5813 | 4.566%
| May | 15801333.2273 | 14207356.5733 | 15112635.2573 | 7040461.6538 | 671316.5034 | 17381.4666 | 688697.97 | 4.358%
| June | 16482534.4957 | 15420210.4237 | 15754258.2131 | 7374509.4432 | 710145.4947 | 18130.7879 | 728276.2826 | 4.418%
| July | 17468110.0147 | 16280959.3894 | 16655197.6833 | 7748747.7371 | 793697.4104 | 19214.921 | 812912.3314 | 4.654%
| August | 17766268.5217 | 16475208.2109 | 16894184.6174 | 8167724.1436 | 852541.0089 | 19542.8954 | 872083.9043 | 4.909%
| September | 16430764.4287 | 16144903.7533 | 15625871.7277 | 7648692.118 | 786818.8602 | 18073.8409 | 804892.7011 | 4.899%
| October | 15466152.2149 | 14973156.2541 | 14708071.8082 | 7383607.6721 | 741067.6392 | 17012.7674 | 758080.4067 | 4.902%
| November | 13086838.1863 | 13214769.3397 | 12516863.5725 | 6685701.9048 | 555579.0918 | 14395.522 | 569974.6138 | 4.355%
| December | 13449654.0019 | 13078398.5728 | 12806377.8906 | 6413681.2226 | 628481.4919 | 14794.6194 | 643276.1113 | 4.783%
NEL | TOTAL | 179515221.4218 | 170947388.0981 | 171020075.4778 | 80373384.2079 | 8297679.2004 | 197466.7436 | 8495145.944 | 4.732%
2051 | January | 13586877.5701 | 13784435.7199 | 12900703.134 | 5529948.6368 | 671228.8708 | 14945.5653 | 686174.4361 | 5.05%
| February | 12624903.5403 | 12589182.9449 | 11991135.4426 | 4931901.1344 | 619880.7038 | 13887.3939 | 633768.0977 | 5.02%
| March | 13787526.6187 | 12545755.3426 | 13107864.1025 | 5494009.8943 | 664496.2369 | 15166.2793 | 679662.5162 | 4.93%
| April | 14178188.5289 | 12819326.8282 | 13530847.5111 | 6205530.5772 | 631745.0104 | 15596.0074 | 647341.0178 | 4.566%
| May | 15982241.0641 | 14370121.665 | 15285658.262 | 7121067.1742 | 679002.3369 | 17580.4652 | 696582.8021 | 4.358%
| June | 16671032.9108 | 15596648.8612 | 15934427.8772 | 7458846.1902 | 718266.8974 | 18338.1362 | 736605.0336 | 4.418%
| July | 17667549.3871 | 16466984.1145 | 16845355.7582 | 7837217.834 | 802759.3245 | 19434.3043 | 822193.6289 | 4.654%
| August | 17969121.8948 | 16663316.1097 | 17087080.6289 | 8260982.3532 | 862275.2319 | 19766.0341 | 882041.266 | 4.909%
| September | 16618322.6368 | 16329221.9692 | 15804242.035 | 7736002.419 | 795800.4469 | 18280.1549 | 814080.6018 | 4.899%
| October | 15642475.666 | 15143969.8581 | 14875752.686 | 7467785.247 | 749516.2567 | 17206.7232 | 766722.9799 | 4.902%
| November | 13235934.2642 | 13365380.3282 | 12659466.0285 | 6761870.9472 | 561908.7081 | 14559.5277 | 576468.2358 | 4.355%
| December | 13602635.4809 | 13227280.5779 | 12952042.5024 | 6486632.8717 | 635630.0794 | 14962.899 | 650592.9784 | 4.783%
NEL | TOTAL | 181566809.5627 | 172901624.3194 | 172974575.9685 | 81291795.2792 | 8392510.1037 | 199723.4905 | 8592233.5942 | 4.732%
2052 | January | 13741397.8909 | 13941213.2034 | 13047419.7565 | 5592839.4248 | 678862.5968 | 15115.5377 | 693978.1344 | 5.05%
| February | 12768428.9235 | 12732326.1726 | 12127455.875 | 4987969.1272 | 626927.7767 | 14045.2718 | 640973.0485 | 5.02%
| March | 13944341.1236 | 12688420.6498 | 13256948.3636 | 5556496.841 | 672053.9847 | 15338.7752 | 687392.7599 | 4.93%
| April | 14339517.7565 | 12965166.2936 | 13684810.8453 | 6276141.3927 | 638933.4417 | 15773.4695 | 654706.9112 | 4.566%
| May | 16163815.1 | 14533490.2953 | 15459318.4296 | 7201969.5271 | 686716.4738 | 17780.1966 | 704496.6704 | 4.358%
| June | 16860224.028 | 15773736.3021 | 16115259.6366 | 7543492.8616 | 726418.145 | 18546.2464 | 744964.3914 | 4.418%
| July | 17867709.6775 | 16653686.3377 | 17036201.2019 | 7926007.7258 | 811853.995 | 19654.4806 | 831508.4756 | 4.654%
| August | 18172713.9171 | 16852106.614 | 17280679.0317 | 8354580.1435 | 872044.9 | 19989.9853 | 892034.8853 | 4.909%
| September | 16806569.8695 | 16514214.2892 | 15983267.6137 | 7823633.4681 | 804815.0289 | 18487.2269 | 823302.2557 | 4.899%
| October | 15819443.9576 | 15315409.5939 | 15044046.7972 | 7552270.6715 | 757995.772 | 17401.3884 | 775397.1603 | 4.902%
| November | 13385580.589 | 13516544.3424 | 12802594.7663 | 6838321.0954 | 568261.6841 | 14724.1386 | 582985.8227 | 4.355%
| December | 13756173.829 | 13376708.372 | 13098237.3493 | 6559850.0727 | 642804.6885 | 15131.7912 | 657936.4797 | 4.783%
NEL | TOTAL | 183625916.6623 | 174863022.4658 | 174936239.6668 | 82213572.3514 | 8487688.4871 | 201988.5083 | 8689676.9955 | 4.732%
2053 | January | 13896478.9085 | 14098560.4116 | 13194668.759 | 5655958.4201 | 686524.0227 | 15286.1268 | 701810.1495 | 5.05%
| February | 12912478.7183 | 12875990.8331 | 12264274.3936 | 5044241.9806 | 634000.5981 | 14203.7266 | 648204.3247 | 5.02%
| March | 14101736.8411 | 12831611.7794 | 13406585.1863 | 5619215.3875 | 679639.7443 | 15511.9105 | 695151.6548 | 4.93%
| April | 14501451.4874 | 13111549.6819 | 13839351.0825 | 6347016.7881 | 646148.8082 | 15951.5966 | 662100.4048 | 4.566%
| May | 16346058.6512 | 14697465.5299 | 15633618.9319 | 7283170.1901 | 694459.0549 | 17980.6645 | 712439.7194 | 4.358%
| June | 17050111.2838 | 15951475.9712 | 16296756.7759 | 7628450.9948 | 734599.3855 | 18755.1224 | 753354.5079 | 4.418%
| July | 18068594.2899 | 16841069.3322 | 17227737.2598 | 8015118.9224 | 820981.5764 | 19875.4537 | 840857.0302 | 4.654%
| August | 18377048.1545 | 17041582.9854 | 17474983.217 | 8448519.154 | 881850.1845 | 20214.753 | 902064.9375 | 4.909%
| September | 16995509.5478 | 16699884.0134 | 16162951.7173 | 7911586.8579 | 813862.77 | 18695.0605 | 832557.8305 | 4.899%
| October | 15997060.2543 | 15487478.5528 | 15212957.1513 | 7637065.4564 | 766506.3367 | 17596.7663 | 784103.103 | 4.902%
| November | 13535779.9507 | 13668264.1361 | 12946252.4544 | 6915053.7748 | 574638.1383 | 14889.3579 | 589527.4963 | 4.355%
| December | 13910271.762 | 13526684.6711 | 13244965.017 | 6633334.1206 | 650005.4462 | 15301.2989 | 665306.7451 | 4.783%
NEL | TOTAL | 185692579.8496 | 176831617.8981 | 176905101.946 | 83138732.0474 | 8583216.0658 | 204261.8378 | 8787477.9036 | 4.732%
2054 | January | 14052123.335 | 14256480.1108 | 13342452.7168 | 5719306.7266 | 694213.2826 | 15457.3357 | 709670.6183 | 5.05%
| February | 13057055.5088 | 13020179.4752 | 12401593.4527 | 5100720.7042 | 641099.295 | 14362.7611 | 655462.056 | 5.02%
| March | 14259716.7365 | 12975331.3783 | 13556777.3895 | 5682166.7153 | 687253.6586 | 15685.6884 | 702939.347 | 4.93%
| April | 14663992.8875 | 13258479.8106 | 13994471.2444 | 6418158.1492 | 653391.2509 | 16130.3922 | 669521.6431 | 4.566%
| May | 16528975.0671 | 14862050.4658 | 15808562.9721 | 7364670.6555 | 702230.2224 | 18181.8726 | 720412.095 | 4.358%
| June | 17240698.1489 | 16129871.1252 | 16478922.6124 | 7713722.1426 | 742810.7685 | 18964.768 | 761775.5364 | 4.418%
| July | 18270206.661 | 17029136.403 | 17419967.2087 | 8104552.9483 | 830142.225 | 20097.2273 | 850239.4523 | 4.654%
| August | 18582128.2076 | 17231748.5169 | 17669996.6085 | 8542801.0399 | 891691.2581 | 20440.341 | 912131.5991 | 4.909%
| September | 17185145.1267 | 16886234.4746 | 16343297.6314 | 7999864.1966 | 822943.8356 | 18903.6596 | 841847.4952 | 4.899%
| October | 16175327.7519 | 15660179.8565 | 15382486.7874 | 7722171.1275 | 775048.1041 | 17792.8605 | 792840.9646 | 4.902%
| November | 13686535.1673 | 13820542.4907 | 13090441.7882 | 6992070.425 | 581038.1905 | 15055.1887 | 596093.3791 | 4.355%
| December | 14064932.0221 | 13677212.2182 | 13392228.1164 | 6707086.3232 | 657232.4805 | 15471.4252 | 672703.9057 | 4.783%
NEL | TOTAL | 187766836.6204 | 178807446.326 | 178881198.5285 | 84067291.1538 | 8679094.5716 | 206543.5203 | 8885638.0919 | 4.732%
2055 | January | 14208333.909 | 14414975.0943 | 13490774.23 | 5782885.4588 | 701930.5117 | 15629.1673 | 717559.679 | 5.05%
| February | 13202161.9046 | 13164894.6727 | 12539415.5312 | 5157406.3173 | 648223.9953 | 14522.3781 | 662746.3734 | 5.02%
| March | 14418283.805 | 13119582.1201 | 13707527.8209 | 5745352.0181 | 694895.8719 | 15860.1122 | 710755.9841 | 4.93%
| April | 14827145.1559 | 13405959.526 | 14150174.3837 | 6489566.8759 | 660660.9124 | 16309.8597 | 676970.7721 | 4.566%
| May | 16712567.7303 | 15027248.2309 | 15984153.7855 | 7446472.4304 | 710030.1203 | 18383.8245 | 728413.9448 | 4.358%
| June | 17431988.1281 | 16308925.0533 | 16661760.4962 | 7799307.8733 | 751052.445 | 19175.1869 | 770227.6319 | 4.418%
| July | 18472550.2601 | 17217890.8872 | 17612894.3565 | 8194311.3426 | 839336.0983 | 20319.8053 | 859655.9036 | 4.654%
| August | 18787957.712 | 17422606.5333 | 17865722.6633 | 8637427.4726 | 901568.2952 | 20666.7535 | 922235.0487 | 4.909%
| September | 17375480.0954 | 17073269.0383 | 16524308.6744 | 8088467.1087 | 832058.3928 | 19113.0281 | 851171.421 | 4.899%
| October | 16354249.6776 | 15833516.6577 | 15552638.7744 | 7807589.2254 | 783621.2286 | 17989.6746 | 801610.9032 | 4.902%
| November | 13837849.0856 | 13973382.2153 | 13235165.4903 | 7069372.5003 | 587461.9613 | 15221.634 | 602683.5953 | 4.355%
| December | 14220157.3782 | 13828293.7838 | 13540029.2843 | 6781108.0007 | 664485.9208 | 15642.1731 | 680128.094 | 4.783%
NEL | TOTAL | 189848724.8417 | 180790543.8132 | 180864565.4907 | 84999266.624 | 8775325.7537 | 208833.5973 | 8984159.351 | 4.732%
2056 | January | 14365113.3957 | 14574048.1828 | 13639635.9243 | 5846695.7422 | 709675.8467 | 15801.6247 | 725477.4714 | 5.05%
| February | 13347800.5414 | 13310139.0247 | 12677743.1322 | 5214299.8497 | 655374.8286 | 14682.5806 | 670057.4092 | 5.02%
| March | 14577441.0724 | 13264366.7052 | 13858839.357 | 5808772.5014 | 702566.5302 | 16035.1852 | 718601.7154 | 4.93%
| April | 14990911.5243 | 13553991.7034 | 14306463.5849 | 6561244.3828 | 667957.9367 | 16490.0027 | 684447.9394 | 4.566%
| May | 16896840.0572 | 15193061.9852 | 16160394.6397 | 7528577.0372 | 717858.8935 | 18586.5241 | 736445.4175 | 4.358%
| June | 17623984.7617 | 16488641.0775 | 16845273.811 | 7885209.7708 | 759324.5675 | 19386.3832 | 778710.9507 | 4.418%
| July | 18675628.5898 | 17407336.1547 | 17806522.0428 | 8284395.6589 | 848563.3555 | 20543.1914 | 869106.547 | 4.654%
| August | 18994540.3389 | 17614160.3916 | 18062164.8726 | 8732400.1399 | 911481.472 | 20893.9944 | 932375.4664 | 4.909%
| September | 17566517.9781 | 17260991.1032 | 16705988.1978 | 8177397.2344 | 841206.6105 | 19323.1698 | 860529.7803 | 4.899%
| October | 16533829.2906 | 16007492.1404 | 15723416.2119 | 7893321.306 | 792225.8665 | 18187.2122 | 810413.0787 | 4.902%
| November | 13989724.5808 | 14126786.1471 | 13380426.3109 | 7146961.4697 | 593909.5729 | 15388.697 | 609298.2699 | 4.355%
| December | 14375950.6269 | 13979932.1661 | 13688371.1832 | 6855400.4869 | 671765.898 | 15813.5457 | 687579.4437 | 4.783%
NEL | TOTAL | 191938282.7578 | 182780946.7821 | 182855239.2682 | 85934675.5799 | 8871911.3785 | 211132.111 | 9083043.4896 | 4.732%
2057 | January | 14522464.5873 | 14733702.2244 | 13789040.4509 | 5910738.7133 | 717449.4254 | 15974.711 | 733424.1365 | 5.05%
| February | 13493974.0807 | 13455915.156 | 12816578.7836 | 5271402.3409 | 662551.9255 | 14843.3715 | 677395.297 | 5.02%
| March | 14737191.5951 | 13409687.8614 | 14010714.9037 | 5872429.3832 | 710265.7807 | 16210.9108 | 726476.6915 | 4.93%
| April | 15155295.2583 | 13702579.2482 | 14463341.9642 | 6633192.0992 | 675282.4693 | 16670.8248 | 691953.2941 | 4.566%
| May | 17081795.4988 | 15359494.9209 | 16337288.8351 | 7610986.0135 | 725716.6887 | 18789.975 | 744506.6637 | 4.358%
| June | 17816691.6252 | 16669022.5532 | 17029465.9744 | 7971429.4347 | 767627.29 | 19598.3608 | 787225.6508 | 4.418%
| July | 18879445.1868 | 17597475.6083 | 18000853.6397 | 8374807.4661 | 857824.1574 | 20767.3897 | 878591.5471 | 4.654%
| August | 19201879.7956 | 17806413.4813 | 18259326.7614 | 8827720.7461 | 921430.9664 | 21122.0678 | 942553.0342 | 4.909%
| September | 17758262.3342 | 17449404.1017 | 16888339.5867 | 8266656.231 | 850388.659 | 19534.0886 | 869922.7476 | 4.899%
| October | 16714069.8825 | 16182109.5204 | 15894822.2301 | 7979368.9407 | 800862.1755 | 18385.4769 | 819247.6524 | 4.902%
| November | 14142164.5579 | 14280757.1518 | 13526227.0283 | 7224838.8172 | 600381.1486 | 15556.381 | 615937.5296 | 4.355%
| December | 14532314.5921 | 14132130.1913 | 13837256.5023 | 6929965.1283 | 679072.5438 | 15985.5461 | 695058.0898 | 4.783%
NEL | TOTAL | 194035548.9945 | 184778692.0189 | 184853256.6603 | 86873535.3143 | 8968853.2303 | 213439.1039 | 9182292.3342 | 4.732%
2058 | January | 14680390.3038 | 14893940.0956 | 13938990.4872 | 5975015.5198 | 725251.3873 | 16148.4293 | 741399.8166 | 5.05%
| February | 13640685.2107 | 13602225.7174 | 12955925.0389 | 5328714.8413 | 669755.4181 | 15004.7537 | 684760.1718 | 5.02%
| March | 14897538.4611 | 13555548.3439 | 14163157.3966 | 5936323.894 | 717993.7723 | 16387.2923 | 734381.0646 | 4.93%
| April | 15320299.6573 | 13851725.0953 | 14620812.6705 | 6705411.4693 | 682634.6572 | 16852.3296 | 699486.9868 | 4.566%
| May | 17267437.5407 | 15526550.2626 | 16514839.7055 | 7693700.9122 | 733603.654 | 18994.1813 | 752597.8352 | 4.358%
| June | 18010112.33 | 16850072.8695 | 17214340.4382 | 8057968.4809 | 775960.7682 | 19811.1236 | 795771.8918 | 4.418%
| July | 19084003.6216 | 17788312.6844 | 18195892.5516 | 8465548.348 | 867118.666 | 20992.404 | 888111.07 | 4.654%
| August | 19409979.8256 | 17999369.2254 | 18457211.8898 | 8923391.0124 | 931416.9581 | 21350.9778 | 952767.9359 | 4.909%
| September | 17950716.7592 | 17638511.5006 | 17071366.2603 | 8356245.772 | 859604.7105 | 19745.7884 | 879350.4989 | 4.899%
| October | 16894974.7778 | 16357372.0458 | 16066859.9905 | 8065733.7168 | 809530.315 | 18584.4723 | 828114.7872 | 4.902%
| November | 14295171.9514 | 14435298.124 | 13672570.4492 | 7303006.042 | 606876.813 | 15724.6891 | 622601.5021 | 4.355%
| December | 14689252.126 | 14284890.7141 | 13986687.9571 | 7004803.285 | 686405.9916 | 16158.1773 | 702564.1689 | 4.783%
NEL | TOTAL | 196140562.5652 | 186783816.6786 | 186858654.8354 | 87815863.2936 | 9066153.1111 | 215754.6188 | 9281907.7299 | 4.732%
2059 | January | 14838893.3926 | 15054764.7013 | 14089488.737 | 6039527.3207 | 733081.8729 | 16322.7827 | 749404.6556 | 5.05%
| February | 13787936.6467 | 13749073.386 | 13095784.4768 | 5386238.4114 | 676985.4396 | 15166.7303 | 692152.1699 | 5.02%
| March | 15058484.7899 | 13701950.936 | 14316169.8014 | 6000457.2768 | 725750.6552 | 16564.3333 | 742314.9884 | 4.93%
| April | 15485928.0555 | 14001432.2104 | 14778878.8857 | 6777903.9522 | 690014.6489 | 17034.5209 | 707049.1698 | 4.566%
| May | 17453769.7039 | 15694231.2683 | 16693050.6183 | 7776723.3022 | 741519.9389 | 19199.1467 | 760719.0856 | 4.358%
| June | 18204250.5242 | 17031795.45 | 17399900.6894 | 8144828.5415 | 784325.1593 | 20024.6756 | 804349.8349 | 4.418%
| July | 19289307.4998 | 17979850.8536 | 18391642.2161 | 8556619.9041 | 876447.0454 | 21218.2382 | 897665.2836 | 4.654%
| August | 19618844.21 | 18193031.0802 | 18655823.8529 | 9019412.6768 | 941439.6284 | 21580.7286 | 963020.3571 | 4.909%
| September | 18143884.8847 | 17828316.8012 | 17255071.6724 | 8446167.548 | 868854.9389 | 19958.2734 | 888813.2123 | 4.899%
| October | 17076547.3341 | 16533282.9973 | 16239532.6864 | 8152417.2371 | 818230.4457 | 18784.2021 | 837014.6477 | 4.902%
| November | 14448749.7257 | 14590411.9877 | 13819459.4091 | 7381464.6585 | 613396.6919 | 15893.6247 | 629290.3166 | 4.355%
| December | 14846766.1091 | 14438216.6182 | 14136668.2904 | 7079916.3307 | 693766.3759 | 16331.4427 | 710097.8187 | 4.783%
NEL | TOTAL | 198253362.876 | 188796358.2902 | 188871471.3359 | 88761677.16 | 9163812.8409 | 218078.6992 | 9381891.5401 | 4.732%
2060 | January | 14997976.7295 | 15216178.9752 | 14240537.9308 | 6104275.2863 | 740941.0243 | 16497.7744 | 757438.7987 | 5.05%
| February | 13935731.131 | 13896460.8658 | 13236159.7021 | 5443974.1226 | 684242.1246 | 15329.3042 | 699571.4289 | 5.02%
| March | 15220033.733 | 13848898.4496 | 14469755.1145 | 6064830.7875 | 733536.5814 | 16742.0371 | 750278.6185 | 4.93%
| April | 15652183.8218 | 14151703.59 | 14937543.825 | 6850671.0225 | 697422.5946 | 17217.4022 | 714639.9968 | 4.566%
| May | 17640795.5451 | 15862541.2297 | 16871924.9754 | 7860054.7682 | 749465.6946 | 19404.8751 | 768870.5697 | 4.358%
| June | 18399109.8928 | 17214193.7528 | 17586150.25 | 8232011.2654 | 792720.6219 | 20239.0209 | 812959.6428 | 4.418%
| July | 19495360.4618 | 18172093.6206 | 18588106.1045 | 8648023.7493 | 885809.4608 | 21444.8965 | 907254.3573 | 4.654%
| August | 19828476.7668 | 18387402.5361 | 18855166.2817 | 9115787.4948 | 951499.1607 | 21811.3244 | 973310.4852 | 4.909%
| September | 18337770.3792 | 18018823.5398 | 17439459.3118 | 8536423.2668 | 878139.52 | 20171.5474 | 898311.0674 | 4.899%
| October | 17258790.943 | 16709845.6888 | 16412843.5428 | 8239421.1208 | 826962.7301 | 18984.67 | 845947.4002 | 4.902%
| November | 14602900.8761 | 14746101.6966 | 13966896.7726 | 7460216.1969 | 619940.9125 | 16063.191 | 636004.1035 | 4.355%
| December | 15004859.4507 | 14592110.8166 | 14287200.2725 | 7155305.6527 | 701153.8328 | 16505.3454 | 717659.1782 | 4.783%
NEL | TOTAL | 200373989.7308 | 190816354.7617 | 190891744.0837 | 89710994.7339 | 9261834.2584 | 220411.3887 | 9482245.6471 | 4.732%
2061 | January | 15157643.219 | 15378185.8802 | 14392140.8264 | 6169260.5989 | 748828.9851 | 16673.4075 | 765502.3926 | 5.05%
| February | 14084071.4336 | 14044390.8877 | 13377053.3458 | 5501923.057 | 691525.6093 | 15492.4786 | 707018.0879 | 5.02%
| March | 15382188.4749 | 13996393.7253 | 14623916.3632 | 6129445.6949 | 741351.7043 | 16920.4073 | 758272.1117 | 4.93%
| April | 15819070.3608 | 14302542.2621 | 15096810.7374 | 6923714.1703 | 704858.646 | 17400.9774 | 722259.6234 | 4.566%
| May | 17828518.6573 | 16031483.4722 | 17051466.2131 | 7943696.9112 | 757441.0737 | 19611.3705 | 777052.4443 | 4.358%
| June | 18594694.1583 | 17397271.2714 | 17773092.6781 | 8319518.318 | 801147.3166 | 20454.1636 | 821601.4801 | 4.418%
| July | 19702166.184 | 18365044.5256 | 18785287.7219 | 8739761.5144 | 895206.0793 | 21672.3828 | 916878.4621 | 4.654%
| August | 20038881.3526 | 18582487.1182 | 19055242.8432 | 9212517.2394 | 961595.7399 | 22042.7695 | 983638.5094 | 4.909%
| September | 18532376.9485 | 18210035.2888 | 17624532.7028 | 8627014.6534 | 887458.6311 | 20385.6146 | 907844.2457 | 4.899%
| October | 17441709.0303 | 16887063.4678 | 16586795.8178 | 8326747.0034 | 835727.3326 | 19185.8799 | 854913.2125 | 4.902%
| November | 14757628.4286 | 14902370.2345 | 14114885.4341 | 7539262.2031 | 626509.6033 | 16233.3913 | 642742.9945 | 4.355%
| December | 15163535.0895 | 14746576.252 | 14438286.7013 | 7230972.6524 | 708568.4996 | 16679.8886 | 725248.3882 | 4.783%
NEL | TOTAL | 202502483.3376 | 192843844.3855 | 192919511.3852 | 90663834.0165 | 9360219.2207 | 222752.7317 | 9582971.9524 | 4.732%
2062 | January | 15317895.7946 | 15540788.4091 | 14544300.2091 | 6234484.4524 | 756745.9001 | 16849.6854 | 773595.5855 | 5.05%
| February | 14232960.3529 | 14192866.2102 | 13518468.0655 | 5560086.3077 | 698836.0309 | 15656.2564 | 714492.2873 | 5.02%
| March | 15544952.2328 | 14144439.6328 | 14778656.6062 | 6194303.2811 | 749196.1791 | 17099.4475 | 766295.6266 | 4.93%
| April | 15986591.113 | 14453951.2861 | 15256682.9064 | 6997034.9015 | 712322.9563 | 17585.2502 | 729908.2066 | 4.566%
| May | 18016942.6704 | 16201061.356 | 17231677.803 | 8027651.3484 | 765446.2305 | 19818.6369 | 785264.8674 | 4.358%
| June | 18791007.0811 | 17581031.5348 | 17960731.5681 | 8407351.3817 | 809605.4052 | 20670.1078 | 830275.513 | 4.418%
| July | 19909728.3789 | 18558707.1437 | 18983190.608 | 8831834.846 | 904637.0696 | 21900.7012 | 926537.7708 | 4.654%
| August | 20250061.8623 | 18778288.3862 | 19256057.2412 | 9309603.701 | 971729.5531 | 22275.068 | 994004.6211 | 4.909%
| September | 18727708.3365 | 18401955.6562 | 17810295.4058 | 8717943.4507 | 896812.4515 | 20600.4792 | 917412.9307 | 4.899%
| October | 17625305.0565 | 17064939.7159 | 16761392.8022 | 8414396.537 | 844524.4187 | 19387.8356 | 863912.2543 | 4.902%
| November | 14912935.4408 | 15059220.6157 | 14263428.3179 | 7618604.2392 | 633102.894 | 16404.229 | 649507.123 | 4.355%
| December | 15322795.9937 | 14901615.8972 | 14589930.4032 | 7306918.7452 | 716010.5149 | 16855.0756 | 732865.5905 | 4.783%
NEL | TOTAL | 204638884.3133 | 194878865.8438 | 194954811.9366 | 91620213.192 | 9458969.6039 | 225102.7727 | 9684072.3767 | 4.732%
2063 | January | 15478737.4189 | 15703989.5846 | 14697018.892 | 6299948.0526 | 764691.9158 | 17026.6112 | 781718.527 | 5.05%
| February | 14382400.7152 | 14341889.6198 | 13660406.5461 | 5618464.9789 | 706173.5283 | 15820.6408 | 721994.1691 | 5.02%
| March | 15708328.2577 | 14293039.0716 | 14933978.9342 | 6259404.8416 | 757070.1624 | 17279.1611 | 774349.3234 | 4.93%
| April | 16154749.5553 | 14605933.7539 | 15417163.6502 | 7070634.7378 | 719815.6806 | 17770.2245 | 737585.9051 | 4.566%
| May | 18206071.2514 | 16371278.2763 | 17412563.2524 | 8111919.7138 | 773481.3207 | 20026.6784 | 793507.9991 | 4.358%
| June | 18988052.4602 | 17765478.1085 | 18149070.551 | 8495512.1564 | 818095.0515 | 20886.8577 | 838981.9092 | 4.418%
| July | 20118050.7954 | 18753085.0863 | 19181818.3374 | 8924245.4075 | 914102.6021 | 22129.8559 | 936232.458 | 4.654%
| August | 20462022.2301 | 18974809.9358 | 19457613.2168 | 9407048.6885 | 981900.7888 | 22508.2245 | 1004409.0133 | 4.909%
| September | 18923768.3253 | 18594588.287 | 17996751.0177 | 8809211.4192 | 906201.1624 | 20816.1452 | 927017.3075 | 4.899%
| October | 17809582.5171 | 17243477.8492 | 16936637.8202 | 8502371.3903 | 853354.1561 | 19590.5408 | 872944.6969 | 4.902%
| November | 15068825.0019 | 15216655.8857 | 14412528.3786 | 7698243.8833 | 639720.9158 | 16575.7075 | 656296.6233 | 4.355%
| December | 15482645.1616 | 15057232.7555 | 14742134.2331 | 7383145.3608 | 723480.0188 | 17030.9097 | 740510.9285 | 4.783%
NEL | TOTAL | 206783233.6901 | 196921458.2141 | 196997684.8298 | 92580150.6307 | 9558087.3033 | 227461.5571 | 9785548.8604 | 4.732%
Note on B45: Anita: Actual thru Dec. For NEL Nov & December are prelim.

## 2016 FCST Trans & Conv Loss
OPC 012960
FPL RC-16
2017 FORECASTED TRANSMISSION, CONVERSION, AND DISTRIBUTION SUBSTATION LOSSES
Florida Power & Light Company
Loss Study - Development of Loss Expansion Factors (Energy)
For the Year Ended December 2017
|  | (1) | (2) | (3) | (4) | (5) |  | INPUT COLUMN
|  | - | - | ENERGY | - | -
Cumulative
Line |  | Flow | Loss | Loss | Expansion | Loss
No |  | MWH | % | Multiplier | Factor | %
- | - | - | - | - | - | -
1 | Net Energy to Transmission | 126985912.6915
2
3 | Generation Step-up Transformer Losses | -234835.5486 | 0.1849% | 1.0019 |  |  | Enter as positive | 234835.5486
4
5 | Flow to Transmission | 126751077.143
6
7 | Transmission Line & Substation Losses | -2040649.6276 | 1.61% |  |  |  | Enter as positive | 2040649.6276
8
9 | Remove JEA/Southern LP, NF & STF Wheeling Losses (1) | 151224
10
11 | Adjusted Transmission Line & Substation Losses | -1889425.6276 | 1.491% | 1.0151
12
13 | Flow on Transmission | 124861651.5154
14
15 | Delivered Sales at Transmission | -8272524.8688 |  |  | 1.017 | 1.673%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (1) | -151224
20
21 | Flow to Distribution | 109076749.6466
22
23 | Distribution Substation Losses | -460540.3532 | 0.4222% | 1.0042 |  |  | Enter as positive | 460540.3532
24
25 | Flow to Primary Lines | 108616209.2934
26
(1) JEA/Southern loss payback and the non firm and short term wheeling losses are excluded from the transmission loss percentage calculation because the flows that create
these losses are not in the flow to transmission. However, because these are real losses they are included in the flow to distribution.
---- Delivered Sales ----
| Retail Transmission |  | 1736882.2298 | Delivered Sales in UI - 2017 Rev Forecast |  |  |  | 1736882.2298
| Wholesale Transmission |  | 6535642.639 | Forecast - 2016 PROJ Delivered Sales |  |  |  | 6535642.639
|  | Delivered Sales at Transmission | 8272524.8688 |  |  |  |  | 8272524.8688
Calculation Net Energy To Transmission Less Southern JEA LP:
Net Energy For Load |  | 119624759.6915 | Forecast |  |  |  |  | 119624759.6915
+ Seminole Load Received |  | 2282100 | Current |  |  |  |  | 2282100
+ St Lucie Entitlement Received |  | 586976 | Current |  |  |  |  | 586976
+ Power wheeled for others |  | 4643301 | Current |  |  |  |  | 4643301
- Southern JEA / Transfers Loss Payback |  | -19451 | Current |  |  |  | Enter as positive | 19451
- Non-Firm Wheeling Losses |  | -77259 | Current |  |  |  | Enter as positive | 77259
- Short Term Firm Wheeling Losses |  | -54514 | Current |  |  |  | Enter as positive | 54514
Seminole + Firm Wheeling - Southern JEA LP |  | 7361153 | Calculation No. 2
Net Energy To Transmission Less Southern JEA LP |  | 126985912.6915 | Calculation No. 1
TYPE | SERVICE | FACTOR | YEAR
ENERGY | T | 1.0192 | #REF!
ENERGY | P | 1.0298 | #REF!
ENERGY | S | 1.0601 | #REF!
DEMAND | T | 1.0234 | #REF!
DEMAND | P | 1.037 | #REF!
DEMAND | S | 1.0761 | #REF!
USING BILLED SALES
*** | NEL | 119624759.6915 | Forecast
| PRIOR MONTH UNBILLED | 4389359.256 | Forecast
| SUBTOTAL | 124014118.9475
| BILLED SALES | -113871155.0269 | Forecast
| COMPANY USE | #REF! | Forecast
| CURRENT MONTH UNBILLED | -4496236.0805 | Forecast
| ENERGY LOST OR UNACCOUNTED FOR | #REF! | Calculation No. 3
| % LOST OR UNACCOUNTED FOR | 5.657%
OVERALL UNBILLED FACTOR
TOTAL DELIVERED MWH |  | 113978031.8514 | Forecast
TOTAL BILLED MWH |  | 113871155.0269 | Forecast
TOTAL UNBILLED FACTOR |  | 1.0009

## 2017 FCST Trans & Conv Losses
OPC 012961
FPL RC-16
2017 FORECASTED TRANSMISSION, CONVERSION, AND DISTRIBUTION SUBSTATION LOSSES
Florida Power & Light Company
Loss Study - Development of Loss Expansion Factors (Energy)
For the Year Ended December 2017
|  | (1) | (2) | (3) | (4) | (5) |  | INPUT COLUMN
|  | - | - | ENERGY | - | -
Cumulative
Line |  | Flow | Loss | Loss | Expansion | Loss
No |  | MWH | % | Multiplier | Factor | %
- | - | - | - | - | - | -
1 | Net Energy to Transmission | 126193056.2927
2
3 | Generation Step-up Transformer Losses | -233369.3161 | 0.1849% | 1.0019 |  |  | Enter as positive | 233369.3161
4
5 | Flow to Transmission | 125959686.9766
6
7 | Transmission Line & Substation Losses | -2027908.5126 | 1.61% |  |  |  | Enter as positive | 2027908.5126
8
9 | Remove JEA/Southern LP, NF & STF Wheeling Losses (1) | 151224
10
11 | Adjusted Transmission Line & Substation Losses | -1876684.5126 | 1.49% | 1.0151
12
13 | Flow on Transmission | 124083002.464
14
15 | Delivered Sales at Transmission | -7719112.596 |  |  | 1.017 | 1.672%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (1) | -151224
20
21 | Flow to Distribution | 108851512.8681
22
23 | Distribution Substation Losses | -459589.3657 | 0.4222% | 1.0042 |  |  | Enter as positive | 459589.3657
24
25 | Flow to Primary Lines | 108391923.5024
26
(1) JEA/Southern loss payback and the non firm and short term wheeling losses are excluded from the transmission loss percentage calculation because the flows that create
these losses are not in the flow to transmission. However, because these are real losses they are included in the flow to distribution.
---- Delivered Sales ----
| Retail Transmission |  | 1771239.8188 | Delivered Sales in UI - 2017 Rev Forecast |  |  |  | 1771239.8188
| Wholesale Transmission |  | 5947872.7772 | Forecast - 2017 PROJ Delivered Sales |  |  |  | 5947872.7772
|  | Delivered Sales at Transmission | 7719112.596 |  |  |  |  | 7719112.596
Calculation Net Energy To Transmission Less Southern JEA LP:
Net Energy For Load |  | 118831903.2927 | Forecast |  |  |  |  | 118831903.2927
+ Seminole Load Received |  | 2282100 | Current |  |  |  |  | 2282100
+ St Lucie Entitlement Received |  | 586976 | Current |  |  |  |  | 586976
+ Power wheeled for others |  | 4643301 | Current |  |  |  |  | 4643301
- Southern JEA / Transfers Loss Payback |  | -19451 | Current |  |  |  | Enter as positive | 19451
- Non-Firm Wheeling Losses |  | -77259 | Current |  |  |  | Enter as positive | 77259
- Short Term Firm Wheeling Losses |  | -54514 | Current |  |  |  | Enter as positive | 54514
Seminole + Firm Wheeling - Southern JEA LP |  | 7361153 | Calculation No. 2
Net Energy To Transmission Less Southern JEA LP |  | 126193056.2927 | Calculation No. 1
TYPE | SERVICE | FACTOR | YEAR
ENERGY | T | 1.0192 | #REF!
ENERGY | P | 1.0298 | #REF!
ENERGY | S | 1.0601 | #REF!
DEMAND | T | 1.0234 | #REF!
DEMAND | P | 1.037 | #REF!
DEMAND | S | 1.0761 | #REF!
USING BILLED SALES
*** | NEL | 118831903.2927 | Forecast
| PRIOR MONTH UNBILLED | 4389359.256 | Forecast
| SUBTOTAL | 123221262.5487
| BILLED SALES | -113871155.0269 | Forecast
| COMPANY USE | #REF! | Forecast
| CURRENT MONTH UNBILLED | -4496236.0805 | Forecast
| ENERGY LOST OR UNACCOUNTED FOR | #REF! | Calculation No. 3
| % LOST OR UNACCOUNTED FOR | 5.657%
OVERALL UNBILLED FACTOR
TOTAL DELIVERED MWH |  | 113978031.8514 | Forecast
TOTAL BILLED MWH |  | 113871155.0269 | Forecast
TOTAL UNBILLED FACTOR |  | 1.0009

## 2018 FCST Trans & Conv Losses
OPC 012962
FPL RC-16
2018 FORECASTED TRANSMISSION, CONVERSION, AND DISTRIBUTION SUBSTATION LOSSES
Florida Power & Light Company
Loss Study - Development of Loss Expansion Factors (Energy)
For the Year Ended December 2018
|  | (1) | (2) | (3) | (4) | (5) |  | INPUT COLUMN
|  | - | - | ENERGY | - | -
Cumulative
Line |  | Flow | Loss | Loss | Expansion | Loss
No |  | MWH | % | Multiplier | Factor | %
- | - | - | - | - | - | -
1 | Net Energy to Transmission | 126924117.2862
2
3 | Generation Step-up Transformer Losses | -234721.2701 | 0.1849% | 1.0019 |  |  | Enter as positive | 234721.2701
4
5 | Flow to Transmission | 126689396.0161
6
7 | Transmission Line & Substation Losses | -2039656.5822 | 1.61% |  |  |  | Enter as positive | 2039656.5822
8
9 | Remove JEA/Southern LP, NF & STF Wheeling Losses (1) | 151224
10
11 | Adjusted Transmission Line & Substation Losses | -1888432.5822 | 1.491% | 1.0151
12
13 | Flow on Transmission | 124800963.4339
14
15 | Delivered Sales at Transmission | -7410765.5096 |  |  | 1.017 | 1.673%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (1) | -151224
20
21 | Flow to Distribution | 109877820.9243
22
23 | Distribution Substation Losses | -463922.6107 | 0.4222% | 1.0042 |  |  | Enter as positive | 463922.6107
24
25 | Flow to Primary Lines | 109413898.3137
26
(1) JEA/Southern loss payback and the non firm and short term wheeling losses are excluded from the transmission loss percentage calculation because the flows that create
these losses are not in the flow to transmission. However, because these are real losses they are included in the flow to distribution.
---- Delivered Sales ----
| Retail Transmission |  | 1798355.2645 | Delivered Sales in UI - 2018 Rev Forecast |  |  |  | 1798355.2645
| Wholesale Transmission |  | 5612410.2451 | Forecast - 2018 PROJ Delivered Sales |  |  |  | 5612410.2451
|  | Delivered Sales at Transmission | 7410765.5096 |  |  |  |  | 7410765.5096
Calculation Net Energy To Transmission Less Southern JEA LP:
Net Energy For Load |  | 119562964.2862 | Forecast |  |  |  |  | 119562964.2862
+ Seminole Load Received |  | 2282100 | Current |  |  |  |  | 2282100
+ St Lucie Entitlement Received |  | 586976 | Current |  |  |  |  | 586976
+ Power wheeled for others |  | 4643301 | Current |  |  |  |  | 4643301
- Southern JEA / Transfers Loss Payback |  | -19451 | Current |  |  |  | Enter as positive | 19451
- Non-Firm Wheeling Losses |  | -77259 | Current |  |  |  | Enter as positive | 77259
- Short Term Firm Wheeling Losses |  | -54514 | Current |  |  |  | Enter as positive | 54514
Seminole + Firm Wheeling - Southern JEA LP |  | 7361153 | Calculation No. 2
Net Energy To Transmission Less Southern JEA LP |  | 126924117.2862 | Calculation No. 1
TYPE | SERVICE | FACTOR | YEAR
ENERGY | T | 1.0192 | #REF!
ENERGY | P | 1.0298 | #REF!
ENERGY | S | 1.0601 | #REF!
DEMAND | T | 1.0234 | #REF!
DEMAND | P | 1.037 | #REF!
DEMAND | S | 1.0761 | #REF!
USING BILLED SALES
*** | NEL | 119562964.2862 | Forecast
| PRIOR MONTH UNBILLED | 4389359.256 | Forecast
| SUBTOTAL | 123952323.5422
| BILLED SALES | -113871155.0269 | Forecast
| COMPANY USE | #REF! | Forecast
| CURRENT MONTH UNBILLED | -4496236.0805 | Forecast
| ENERGY LOST OR UNACCOUNTED FOR | #REF! | Calculation No. 3
| % LOST OR UNACCOUNTED FOR | 5.657%
OVERALL UNBILLED FACTOR
TOTAL DELIVERED MWH |  | 113978031.8514 | Forecast
TOTAL BILLED MWH |  | 113871155.0269 | Forecast
TOTAL UNBILLED FACTOR |  | 1.0009