## Exec Summary
OPC 012982
FPL RC-16
LINE LOSS STUDY - 2014 ACTUALS
Florida Power & Light Company | [9 empty] | Report 3 Lines: | 19816 | Delivered Sales at Transmission - Expansion Factor
Summary of Loss Expansion Factors and Loss Percentages | [10 empty] | 19817 | Delivered Sales at Primary - Expansion Factor
Variance - Year Ended December 2014 vs. Year Ended December 2013 | [10 empty] | 19818 | Delivered Sales at Secondary - Expansion Factor
| Energy Expansion Factor |  |  | Demand - 12 CP Expansion Factor |  |  | Demand - GNCP Expansion Factor
Voltage Level | 2014 | 2013 | Variance | 2014 | 2013 | Variance | 2014 | 2013 | Variance
Transmission | 1.0182 | 1.0192 | -0.00098768 | 1.0231 | 1.0234 | -0.00031524 | 1.0266 | 1.0275 | -0.00090399
Primary | 1.0286 | 1.0298 | -0.0011976 | 1.0368 | 1.037 | -0.00022294 | 1.0429 | 1.0437 | -0.00083227
Secondary | 1.0536 | 1.0601 | -0.0064843 | 1.07 | 1.0761 | -0.0061592 | 1.0824 | 1.0905 | -0.0080241
| Energy Loss % |  |  | Demand Loss % |  |  | Demand - GNCP Loss %
Voltage Level | 2014 | 2013 | Variance | 2014 | 2013 | Variance | 2014 | 2013 | Variance
Transmission | 1.792% | 1.887% | -0.09517% | 2.256% | 2.286% | -0.03011% | 2.592% | 2.677% | -0.0857%
Primary | 2.782% | 2.895% | -0.1131% | 3.547% | 3.568% | -0.02074% | 4.111% | 4.187% | -0.07646%
Secondary | 5.085% | 5.666% | -0.5806% | 6.54% | 7.075% | -0.5349% | 7.615% | 8.295% | -0.6798%

## Loss Expansion Factors - Energy
OPC 012983
FPL RC-16
LINE NO. | FLOW OF ENERGY | FLOW MWH | LOSS % | LOSS MULTIPLIER | EXPANSION FACTOR | CUMULATIVE LOSS %
1 | Net Energy to Transmission | 123388587 | 0% | 0 | 0 | 0%
2
3 | Generation Step-up Transformer Losses | -228183 | 0.1849% | 1.0019 | 0 | 0%
4
5 | Flow to Transmission | 123160404 | 0% | 0 | 0 | 0%
6
7 | Transmission Line & Substation Losses | -2134065 | 0% | 0 | 0 | 0%
8
9 | Remove JEA/Southern Loss Payback & NF Wheeling Losses (a) | 151224 | 0% | 0 | 0 | 0%
10
11 | Adjusted Transmission Line & Substation Losses | -1982841 | 1.61% | 1.0164 | 0 | 0%
12
13 | Flow on Transmission | 121177563 | 0% | 0 | 0 | 0%
14
15 | Delivered Sales at Transmission | -7185763.9384 | 0% | 0 | 1.0182 | 1.792%
16
17 | Seminole & Firm Power Wheeled for Others | -7361153 | 0% | 0 | 0 | 0%
18
19 | Include JEA/Southern LP, NF & STF Wheeling Losses (a) | -151224 | 0% | 0 | 0 | 0%
20
21 | Flow to Distribution | 106479422.0616 | 0% | 0 | 0 | 0%
22
23 | Distribution Substation Losses | -449574 | 0.4222% | 1.0042 | 0 | 0%
24
25 | Flow to Primary Lines | 106029848.0616 | 0% | 0 | 0 | 0%
26
27 | Primary Line Losses | -623574 | 0.5881% | 1.0059 | 0 | 0%
28
29 | Flow on Primary | 105406274.0616 | 0% | 0 | 0 | 0%
30
31 | Delivered Sales at Primary | -2494087.7276 | 0% | 0 | 1.0286 | 2.782%
32
33 | Flow to Secondary | 102912186.334 | 0% | 0 | 0 | 0%
34
35 | Transformer Losses | -2029976 | 1.973% | 1.0201 | 0 | 0%
36
37 | Flow on Secondary | 100882210.334 | 0% | 0 | 0 | 0%
38
39 | Secondary Line & Service Losses | -408253 | 0.4047% | 1.0041 | 0 | 0%
40
41 | Balance For Use | 100473957.334 | 0% | 0 | 0 | 0%
42
43 | Company Use | -123235 | 0% | 0 | 0 | 0%
44
45 | Delivered Sales at Secondary | -100350722.419 | 0% | 0 | 1.0536 | 5.085%
46
47 | NET | -0.085001 | 0% | 0 | 0 | 0%
(a) | JEA/Southern loss payback and the non firm and short term wheeling losses are excluded from the transmission loss percentage calculation
because the flows that create these losses are not in the flow to transmission. However, because these are real losses they are included
in the flow to distribution.

## Losses, Sales & Co Use
OPC 012984
FPL RC-16
LINE NO. | ENERGY LOSSES, SALES, COMPANY USE AND WHEELING | LOSSES (MWH) | SALES (MWH) | NET ENERGY (MWH)
1 | NET ENERGY TO TRANSMISSION (a) | 0 | 0 | 123388587
2
3 | LOSSES & UNACCOUNTED FOR:
4 | Generation Step-Up Transformer Losses (a) | 228183 | 0 | -228183
5 |  |  | 0 | 0
6 | Southern JEA / Transfers Loss Payback, NF and STF Wheeling Losses (a) | 151224 | 0 | 0
7 | Adjusted Transmission Line Losses (a) | 1982841 | 0
8 | Transmission Line Losses (a) | 2134065 |  | -2134065
9
10 | Distribution Substation Transformer Losses (a) | 449574 | 0 | -449574
11
12 | Other Distribution & Unaccounted For: |  | 0 | 0
13 | Primary Line Losses (b) | 623574 | 0 | 0
14
15 | Transformer Losses (b) | 2029976 | 0 | 0
16
17 | Secondary & Service Losses (c) | 408253 | 0 | 0
18
19 | Subtotal - Distribution & Unaccounted For | 3061803 | 0 | -3061803
20
21 | TOTAL LOSSES & UNACCOUNTED FOR (d) | 5873625 | 0 | 0
22
23 | SYSTEM ENERGY NET OF LOSSES & UNACCOUNTED FOR | 0 | 0 | 117514962
24
25 | DELIVERED SALES (e): |  | 0 | 0
26 | Retail:
27 | Transmission | 0 | 1586287.5994 | 0
28 | Primary | 0 | 2494087.7276 | 0
29 | Secondary | 0 | 100350722.419 | 0
30 | Total Retail (f) | 0 | 104431097.746 | 0
31
32 | Wholesale:
33 | Transmission | 0 | 5599476.339 | 0
34 | Primary | 0 | 1e-06 | 0
35 | Total Resale (f) | 0 | 5599476.339 | 0
36
37 | TOTAL DELIVERED SALES (f) | 0 | 110030574.085 | -110030574.085
38
39 | COMPANY USE (g) | 0 | 0 | -123235
40
41 | LESS: TOTAL FIRM POWER WHEELED FOR OTHERS (a) | 0 | 0 | -7361153
42
43 | TOTAL | 0 | 0 | -0.085001
(a) | Power Supply
(b) | Primary line and transformer losses are estimated using the methodology provided by Distribution Engineering.
(c) | Secondary and service losses include electricity theft and unknown usage.
(e) | Ratio of billed sales (R&R Report/Wholesale Log - by class) to delivered sales (F&O Report - total company)
(f) | Also see Financial and Operating Report, page 8-A.
(g) | FERC Form 1, Page 401a

## Data Summary
OPC 012985
FPL RC-16
LINE NO.
|  |  | EXPANSION FACTORS |  | ENERGY
1 |  |  | ENERGY | DEMAND | LOSS %
2 | Transmission | 0 | 1.0182 | 1.0231 | 1.792%
3
4 | Primary | 0 | 1.0286 | 1.0368 | 2.782%
5
6 | Secondary | 0 | 1.0536 | 1.07 | 5.085%
7
8
9 | COMPANY USE - DEMAND: |  | 0 | 0 | 0%
10 | (GSD-1) 12CP - MW | 3826.2243 | 0 | 0 | 0%
11 | (GSD-1) MWH | 25147188.6404 |  | 0 | 0%
12 | Load Factor (line 11 / line10 / 8760) | 0.75027 |  | 0 | 0%
13 | COMPANY USE 12CP DEMAND (rounded) - MW | 18.7506 |  | 0 | 0%
14
15
16 | CALCUATION OF NET ENERGY TO TRANSMISSION LESS SOUTHERN JEA/LP (MWH): |  |  | 0 | 0%
17 | NET ENERGY FOR LOAD |  | 116027434 | 0 | 0%
18
19 | Seminole Load Received | 2282100 | 0 | 0 | 0%
20 | St. Lucie Entitlement Received | 586976 | 0 | 0 | 0%
21 | Power wheeled for others | 4643301 | 0 | 0 | 0%
22 | Southern JEA / Transfers Loss Payback | -19451 | 0 | 0 | 0%
23 | Non-Firm Wheeling Losses | -77259 | 0 | 0 | 0%
24 | Short Term Firm Wheeling Losses | -54514 | 0 | 0 | 0%
25 | TOTAL FIRM POWER WHEELED FOR OTHERS |  | 7361153 | 0 | 0%
26
27 | NET ENERGY TO TRANSMISSION LESS SOUTHERN JEA/LP |  | 123388587 | 0 | 0%
28
29
30 | USING UNBILLED SALES (MWH): |  | 0 | 0 | 0%
31 | NEL | 116027434 | 0 | 0 | 0%
32 | PRIOR MONTH UNBILLED | 4167624 | 0 | 0 | 0%
33 | SUBTOTAL | 120195058 | 0 | 0 | 0%
34 | BILLED SALES | -109763891 | 0 | 0 | 0%
35 | COMPANY USE | -123235 | 0 | 0 | 0%
36 | CURRENT MONTH UNBILLED | -4434307 | 0 | 0 | 0%
37 | ENERGY LOST OR UNACCOUNTED FOR | 5873625 | 0 | 0 | 0%
38 | % LOST OR UNACCOUNTED FOR |  | 5.062% | 0 | 0%
39
40
41 | OVERALL UNBILLED FACTOR: |  | 0 | 0 | 0%
42 | TOTAL DELIVERED MWH | 110030574.085 | 0 | 0 | 0%
43 | TOTAL BILLED MWH | 109763891.085 | 0 | 0 | 0%
44 | TOTAL UNBILLED FACTOR | 1.0024 | 0 | 0 | 0%

## Loss Expansion Factors - Demand
OPC 012986
FPL RC-16
LINE NO. | FLOW OF DEMAND | LOAD FACTORS | ENERGY LOSS % DIVIDED BY (.3 + (.7* LF)) (a) | FLOW MW | LOSS FACTOR | EXPANSION FACTOR
1 | Net Demand to Transmission | 0 | 0 | 20051.9333 |  | 0
2
3 | Generation Step-up Transformer Losses | 0 | 0.23351 | -46.8236 | 1.0023 | 0
4
5 | Flow to Transmission | 0.70279 | 0 | 20005.1097 |  | 0
6
7 | Transmission Line & Substation Losses | 0 | 2.0275 | -405.611 | 1.0207 | 0
8
9 | Flow on Transmission | 0.70579 | 0 | 19599.4987 |  | 0
10
11 | Delivered Demand at Transmission (b) | 0 | 0 | -1153.8782 |  | 1.0231
12
13 | Flow to Distribution | 0 | 0 | 18445.6205 |  | 0
14
15 | Distribution Substation Losses | 0 | 0.55417 | -102.2196 | 1.0056 | 0
16
17 | Flow to Primary Lines | 0.65985 | 0 | 18343.4009 |  | 0
18
19 | Primary Line Losses | 0 | 0.77105 | -141.436 | 1.0078 | 0
20
21 | Flow on Primary | 0.66106 | 0 | 18201.9649 |  | 0
22
23 | Delivered Demand at Primary (c) | 0 | 0 | -321.1285 |  | 1.0368
24
25 | Flow to Secondary | 0 | 0 | 17880.8364 |  | 0
26
27 | Transformer Losses | 0 | 2.5859 | -462.3788 | 1.0265 | 0
28
29 | Flow on Secondary | 0.66115 | 0 | 17418.4576 |  | 0
30
31 | Secondary Line & Service Losses | 0 | 0.53011 | -92.3376 | 1.0053 | 0
32
33 | Balance For Use | 0.66198 | 0 | 17326.12 |  | 0
34
35 | Company Use | 0 | 0 | -18.7506 |  | 0
36
37 | Delivered Demand at Secondary (d) | 0 | 0 | 17307.3694 |  | 1.07
(a) | Westinghouse Formula
(b) | Total Company average 12-month coincident peak MWs at meter for transmission level.
(c) | Total Company average 12-month coincident peak MWs at meter for primary level.
(d) | Total Company average 12-month coincident peak MWs at meter for secondary level.

## Dist GNCP - for ECRC
OPC 012987
FPL RC-16
LINE NO. | FLOW OF DEMAND - DISTRIBUTION | LOAD FACTORS | ENERGY LOSS % DIVIDED BY (.3 + (.7* LF)) (a) | FLOW MW | LOSS FACTOR | EXPANSION FACTOR
1 | Net Demand to Transmission |  |  | 25408.997
2
3 | Generation Step-up Transformer Losses |  | 0.26865 | -68.2612 | 1.0027
4
5 | Flow to Transmission | 0.55481 |  | 25340.7358
6
7 | Transmission Line & Substation Losses |  | 2.3291 | -590.2195 | 1.0238
8
9 | Flow on Transmission | 0.5589 |  | 24750.5163
10
11 | Delivered Demand at Transmission (b) |  |  | 0 |  | 1.0266
12
13 | Flow to Distribution |  |  | 24750.5163
14
15 | Distribution Substation Losses |  | 0.65502 | -162.122 | 1.0066
16
17 | Flow to Primary Lines | 0.49226 |  | 24588.3943
18
19 | Primary Line Losses |  | 0.91081 | -223.953 | 1.0092
20
21 | Flow on Primary | 0.49386 |  | 24364.4413
22
23 | Delivered Demand at Primary (c) |  |  | -400.7882 |  | 1.0429
24
25 | Flow to Secondary |  |  | 23963.6532
26
27 | Transformer Losses |  | 3.0488 | -730.6129 | 1.0314
28
29 | Flow on Secondary | 0.49568 |  | 23233.0403
30
31 | Secondary Line & Service Losses |  | 0.62475 | -145.1495 | 1.0063
32
33 | Balance For Use | 0.49678 |  | 23087.8908
34
35 | Company Use |  |  | -23.386
36
37 | Delivered Demand at Secondary (d) |  |  | 23064.5048 |  | 1.0824
38
39
40 | COMPANY USE - GNCP DEMAND:
41 | (GSD-1) GNCP - KW |  | 4772.11
42 | (GSD-1) KWH |  | 25147188.6404
43 | Load Factor (line 11 / line10 / 8760) |  | 0.60155
44 | COMPANY USE GCP DEMAND (rounded) - MW |  | 23.386
(a) | Westinghouse Formula
(b) | Total Company's transmission group coincident peak (GCP) MWs at meter
(c) | Total Company's primary group coincident peak (GCP) MWs at meter
(d) | Total Company's secondary group coincident peak (GCP) MWs at meter

## Energy Losses by Rate Class
OPC 012988
FPL RC-16
RATE CLASS | DELIVERED MWH SALES | EXPANSION FACTOR | DELIVERED ENERGY AT GENERATION | DELIVERED EFFICIENCY | LOSSES | FUEL COST RECOVERY MULTIPLIER
CILC-1D
Primary | 1053651.9152 | 1.0286 | 1083800.0354 | 0.97218 | 30148.1202 | 0
Secondary | 1701607.1759 | 1.0536 | 1792770.1194 | 0.94915 | 91162.9435 | 0
CILC-1D TOTAL | 2755259.0911 | 1.044 | 2876570.1548 | 0.95783 | 121311.0637 | 0.99365
CILC-1G
Primary | 1974.0884 | 1.0286 | 2030.5729 | 0.97218 | 56.4845 | 0
Secondary | 145022.2972 | 1.0536 | 152791.8105 | 0.94915 | 7769.5132 | 0
CILC-1G TOTAL | 146996.3856 | 1.0532 | 154822.3834 | 0.94945 | 7825.9978 | 1.0024
CILC-1T
Transmission | 1367204.4582 | 1.0182 | 1392150.6759 | 0.98208 | 24946.2177 | 0
CILC-1T TOTAL | 1367204.4582 | 1.0182 | 1392150.6759 | 0.98208 | 24946.2177 | 0.96911
GS(T)-1
Secondary | 5894062.7478 | 1.0536 | 6209834.8699 | 0.94915 | 315772.1221 | 0
GS(T)-1 TOTAL | 5894062.7478 | 1.0536 | 6209834.8699 | 0.94915 | 315772.1221 | 1.0027
GSCU-1
Secondary | 83917.4028 | 1.0536 | 88413.245 | 0.94915 | 4495.8423 | 0
GSCU-1 TOTAL | 83917.4028 | 1.0536 | 88413.245 | 0.94915 | 4495.8423 | 1.0027
GSD(T)-1
Primary | 72888.416 | 1.0286 | 74973.9708 | 0.97218 | 2085.5547 | 0
Secondary | 25074300.2244 | 1.0536 | 26417646.1187 | 0.94915 | 1343345.8943 | 0
GSD(T)-1 TOTAL | 25147188.6404 | 1.0535 | 26492620.0894 | 0.94921 | 1345431.449 | 1.0027
GSLD(T)-1
Primary | 398610.5104 | 1.0286 | 410015.9445 | 0.97218 | 11405.4342 | 0
Secondary | 9976650.8556 | 1.0536 | 10511146.0497 | 0.94915 | 534495.1941 | 0
GSLD(T)-1 TOTAL | 10375261.3659 | 1.0526 | 10921161.9942 | 0.95001 | 545900.6283 | 1.0018
GSLD(T)-2
Primary | 848430.9204 | 1.0286 | 872707.0566 | 0.97218 | 24276.1362 | 0
Secondary | 1634200.6626 | 1.0536 | 1721752.3282 | 0.94915 | 87551.6657 | 0
GSLD(T)-2 TOTAL | 2482631.583 | 1.045 | 2594459.3848 | 0.9569 | 111827.8019 | 0.99462
GSLD(T)-3
Transmission | 161379.3875 | 1.0182 | 164323.94 | 0.98208 | 2944.5525 | 0
GSLD(T)-3 TOTAL | 161379.3875 | 1.0182 | 164323.94 | 0.98208 | 2944.5525 | 0.96911
MET
Primary | 91442.1984 | 1.0286 | 94058.6321 | 0.97218 | 2616.4337 | 0
MET TOTAL | 91442.1984 | 1.0286 | 94058.6321 | 0.97218 | 2616.4337 | 0.97898
OL-1
Secondary | 100694.1274 | 1.0536 | 106088.7762 | 0.94915 | 5394.6488 | 0
OL-1 TOTAL | 100694.1274 | 1.0536 | 106088.7762 | 0.94915 | 5394.6488 | 1.0027
OS-2
Primary | 11289.2713 | 1.0286 | 11612.291 | 0.97218 | 323.0197 | 0
OS-2 TOTAL | 11289.2713 | 1.0286 | 11612.291 | 0.97218 | 323.0197 | 0.97898
RS(T)-1
Secondary | 55191995.7767 | 1.0536 | 58148885.5109 | 0.94915 | 2956889.7342 | 0
RS(T)-1 TOTAL | 55191995.7767 | 1.0536 | 58148885.5109 | 0.94915 | 2956889.7342 | 1.0027
SL-1
Secondary | 517355.4424 | 1.0536 | 545072.5593 | 0.94915 | 27717.1169 | 0
SL-1 TOTAL | 517355.4424 | 1.0536 | 545072.5593 | 0.94915 | 27717.1169 | 1.0027
SL-2
Secondary | 30915.7063 | 1.0536 | 32572.0032 | 0.94915 | 1656.297 | 0
SL-2 TOTAL | 30915.7063 | 1.0536 | 32572.0032 | 0.94915 | 1656.297 | 1.0027
SST-DST
Primary | 15800.4076 | 1.0286 | 16252.5043 | 0.97218 | 452.0967 | 0
SST-DST TOTAL | 15800.4076 | 1.0286 | 16252.5043 | 0.97218 | 452.0967 | 0.97898
SST-TST
Transmission | 57703.7537 | 1.0182 | 58756.625 | 0.98208 | 1052.8713 | 0
SST-TST TOTAL | 57703.7537 | 1.0182 | 58756.625 | 0.98208 | 1052.8713 | 0.96911
TOTAL FPSC | 104431097.746 | 1.0524 | 109907655.6395 | 0.95017 | 5476557.8935 | 1.0017
PR - SEMINOLE
Transmission | 513885.8149 | 1.0182 | 523262.2526 | 0.98208 | 9376.4377 | 0
PR - SEMINOLE TOTAL | 513885.8149 | 1.0182 | 523262.2526 | 0.98208 | 9376.4377 | 0.96911
FULL REQUIREMENTS
Transmission | 4624710.7876 | 1.0182 | 4709093.9547 | 0.98208 | 84383.1671 | 0
FR TOTAL | 4624710.7876 | 1.0182 | 4709093.9547 | 0.98208 | 84383.1671 | 0.96911
PARTIAL REQUIREMENTS
Transmission | 460879.7365 | 1.0182 | 469289.0173 | 0.98208 | 8409.2808 | 0
PR TOTAL | 460879.7365 | 1.0182 | 469289.0173 | 0.98208 | 8409.2808 | 0.96911
TOTAL FERC | 5599476.339 | 1.0182 | 5701645.2246 | 0.98208 | 102168.8856 | 0.96911
TOTAL COMPANY | 110030574.085 | 1.0507 | 115609300.8642 | 0.95175 | 5578726.7792 | 1
COMPANY USE (Secondary) | 123235 | 1.0536 | 129837.2673 | 0.94915 | 6602.2673
TOTAL FPL | 110153809.085 | 1.0507 | 115739138.1314 | 0.95174 | 5585329.0464 | 1
Transmission | 7185763.9384 | 1.0182 | 7316876.4656 |  | 131112.5272
Primary | 2494087.7276 | 1.0286 | 2565451.0076 |  | 71363.28
Secondary | 100350722.419 | 1.0536 | 105726973.391 |  | 5376250.972
TOTAL COMPANY | 110030574.085 |  | 115609300.8642 |  | 5578726.7792
Wheeling | 7512377 | 1.0182 | 7649448.9581 |  | 137071.9581
5715798.7373
JEA/SFP/NF Losses |  |  |  |  | 151224
5867022.7373
Company Use |  |  |  |  | 6602.2673
TOTAL LOSSES |  |  |  |  | 5873625.0046

## 12CP Dem Losses by Rate Class
OPC 012989
FPL RC-16
RATE CLASS | 12CP DEMAND AT METER | EXPANSION FACTOR | 12CP DEMAND AT GENERATION | DELIVERED EFFICIENCY | LOSSES | FUEL COST RECOVERY MULTIPLIER
CILC-1D
Primary | 134614.1402 | 1.0368 | 139565.1438 | 0.96453 | 4951.0036 | 0
Secondary | 208688.1931 | 1.07 | 223290.7206 | 0.9346 | 14602.5275 | 0
CILC-1D TOTAL | 343302.3333 | 1.057 | 362855.8644 | 0.94611 | 19553.5311 | 0.99103
CILC-1G
Primary | 267.9568 | 1.0368 | 277.8121 | 0.96453 | 9.8552 | 0
Secondary | 18501.6265 | 1.07 | 19796.2398 | 0.9346 | 1294.6133 | 0
CILC-1G TOTAL | 18769.5833 | 1.0695 | 20074.0519 | 0.93502 | 1304.4685 | 1.0028
CILC-1T
Transmission | 163745.0833 | 1.0231 | 167524.9728 | 0.97744 | 3779.8894 | 0
CILC-1T TOTAL | 163745.0833 | 1.0231 | 167524.9728 | 0.97744 | 3779.8894 | 0.95927
GS(T)-1
Secondary | 1143540.6667 | 1.07 | 1223557.5748 | 0.9346 | 80016.9081 | 0
GS(T)-1 TOTAL | 1143540.6667 | 1.07 | 1223557.5748 | 0.9346 | 80016.9081 | 1.0032
GSCU-1
Secondary | 9951 | 1.07 | 10647.3008 | 0.9346 | 696.3008 | 0
GSCU-1 TOTAL | 9951 | 1.07 | 10647.3008 | 0.9346 | 696.3008 | 1.0032
GSD(T)-1
Primary | 11024.2014 | 1.0368 | 11429.663 | 0.96453 | 405.4616 | 0
Secondary | 3815200.0486 | 1.07 | 4082160.8317 | 0.9346 | 266960.7831 | 0
GSD(T)-1 TOTAL | 3826224.25 | 1.0699 | 4093590.4946 | 0.93469 | 267366.2446 | 1.0031
GSLD(T)-1
Primary | 59239.844 | 1.0368 | 61418.6394 | 0.96453 | 2178.7955 | 0
Secondary | 1446044.656 | 1.07 | 1547228.6592 | 0.9346 | 101184.0031 | 0
GSLD(T)-1 TOTAL | 1505284.5 | 1.0687 | 1608647.2986 | 0.93575 | 103362.7986 | 1.002
GSLD(T)-2
Primary | 100344.5973 | 1.0368 | 104035.1937 | 0.96453 | 3690.5964 | 0
Secondary | 208207.5693 | 1.07 | 222776.4661 | 0.9346 | 14568.8968 | 0
GSLD(T)-2 TOTAL | 308552.1667 | 1.0592 | 326811.6599 | 0.94413 | 18259.4932 | 0.99311
GSLD(T)-3
Transmission | 21023.5 | 1.0231 | 21508.8062 | 0.97744 | 485.3062 | 0
GSLD(T)-3 TOTAL | 21023.5 | 1.0231 | 21508.8062 | 0.97744 | 485.3062 | 0.95927
MET
Primary | 13481.5833 | 1.0368 | 13977.4255 | 0.96453 | 495.8422 | 0
MET TOTAL | 13481.5833 | 1.0368 | 13977.4255 | 0.96453 | 495.8422 | 0.97211
OL-1
Secondary | 197.9167 | 1.07 | 211.7655 | 0.9346 | 13.8488 | 0
OL-1 TOTAL | 197.9167 | 1.07 | 211.7655 | 0.9346 | 13.8488 | 1.0032
OS-2
Primary | 207.0862 | 1.0368 | 214.7027 | 0.96453 | 7.6165 | 0
Secondary | 616.8304 | 1.07 | 659.9919 | 0.9346 | 43.1614 | 0
OS-2 TOTAL | 823.9167 | 1.0616 | 874.6946 | 0.94195 | 50.7779 | 0.99541
RS(T)-1
Secondary | 10451925.25 | 1.07 | 11183277.2404 | 0.9346 | 731351.9904 | 0
RS(T)-1 TOTAL | 10451925.25 | 1.07 | 11183277.2404 | 0.9346 | 731351.9904 | 1.0032
SL-1
Secondary | 961.5833 | 1.07 | 1028.8682 | 0.9346 | 67.2848 | 0
SL-1 TOTAL | 961.5833 | 1.07 | 1028.8682 | 0.9346 | 67.2848 | 1.0032
SL-2
Secondary | 3534.0833 | 1.07 | 3781.3736 | 0.9346 | 247.2902 | 0
SL-2 TOTAL | 3534.0833 | 1.07 | 3781.3736 | 0.9346 | 247.2902 | 1.0032
SST-DST
Primary | 1949.0833 | 1.0368 | 2020.7691 | 0.96453 | 71.6858 | 0
SST-DST TOTAL | 1949.0833 | 1.0368 | 2020.7691 | 0.96453 | 71.6858 | 0.97211
SST-TST
Transmission | 8121.9167 | 1.0231 | 8309.4029 | 0.97744 | 187.4862 | 0
SST-TST TOTAL | 8121.9167 | 1.0231 | 8309.4029 | 0.97744 | 187.4862 | 0.95927
TOTAL FPSC | 17821388.4167 | 1.0689 | 19048699.5636 | 0.93557 | 1227311.147 | 1.0022
BLOUNTSTOWN
Transmission | 6117.0833 | 1.0231 | 6258.29 | 0.97744 | 141.2067 | 0
BLOUNTSTOWN TOTAL | 6117.0833 | 1.0231 | 6258.29 | 0.97744 | 141.2067 | 0.95927
FKEC
Transmission | 124660.4167 | 1.0231 | 127538.0761 | 0.97744 | 2877.6595 | 0
FKEC TOTAL | 124660.4167 | 1.0231 | 127538.0761 | 0.97744 | 2877.6595 | 0.95927
SEMINOLE
Transmission | 83333.3333 | 1.0231 | 85256.9989 | 0.97744 | 1923.6656 | 0
SEMINOLE TOTAL | 83333.3333 | 1.0231 | 85256.9989 | 0.97744 | 1923.6656 | 0.95927
LCEC
Transmission | 690895 | 1.0231 | 706843.6114 | 0.97744 | 15948.6114 | 0
LCEC TOTAL | 690895 | 1.0231 | 706843.6114 | 0.97744 | 15948.6114 | 0.95927
WAUCHULA
Transmission | 11315.1667 | 1.0231 | 11576.3658 | 0.97744 | 261.1992 | 0
WAUCHULA TOTAL | 11315.1667 | 1.0231 | 11576.3658 | 0.97744 | 261.1992 | 0.95927
WINTER PARK
Transmission | 23000 | 1.0231 | 23530.9317 | 0.97744 | 530.9317 | 0
WINTER PARK TOTAL | 23000 | 1.0231 | 23530.9317 | 0.97744 | 530.9317 | 0.95927
NEW SMRYNA BEACH
Transmission | 21666.6667 | 1.0231 | 22166.8197 | 0.97744 | 500.1531 | 0
NSB TOTAL | 21666.6667 | 1.0231 | 22166.8197 | 0.97744 | 500.1531 | 0.95927
TOTAL FERC | 960987.6667 | 1.0231 | 983171.0937 | 0.97744 | 22183.4271 | 0.95927
TOTAL COMPANY | 18782376.0833 | 1.0665 | 20031870.6574 | 0.93762 | 1249494.574 | 1
COMPANY USE (Secondary) | 18750.5948 | 1.07 | 20062.6292 | 0.9346 | 1312.0343
TOTAL FPL | 18801126.6782 | 1.0665 | 20051933.2865 | 0.93762 | 1250806.6084 | 1

## GNCP Dem Losses by Rate Class
OPC 012990
FPL RC-16
RATE CLASS | DISTRIBUTION GNCP DEMAND | EXPANSION FACTOR | DISTRIBUTION GNCP DEMAND AT GENERATION | DELIVERED EFFICIENCY | LOSSES | COST RECOVERY MULTIPLIER
CILC-1D
Primary | 151916.4947 | 1.0429 | 158429.4795 | 0.95889 | 6512.9848 | 0
Secondary | 235511.5053 | 1.0824 | 254924.7244 | 0.92385 | 19413.2192 | 0
CILC-1D TOTAL | 387428 | 1.0669 | 413354.204 | 0.93728 | 25926.204 | 0.98629
CILC-1G
Primary | 378.4171 | 1.0429 | 394.6407 | 0.95889 | 16.2236 | 0
Secondary | 26128.5829 | 1.0824 | 28282.3626 | 0.92385 | 2153.7797 | 0
CILC-1G TOTAL | 26507 | 1.0819 | 28677.0033 | 0.92433 | 2170.0033 | 1.0001
GS(T)-1
Secondary | 1605649 | 1.0824 | 1738002.6864 | 0.92385 | 132353.6864 | 0
GS(T)-1 TOTAL | 1605649 | 1.0824 | 1738002.6864 | 0.92385 | 132353.6864 | 1.0006
GSCU-1
Secondary | 11473 | 1.0824 | 12418.7197 | 0.92385 | 945.7197 | 0
GSCU-1 TOTAL | 11473 | 1.0824 | 12418.7197 | 0.92385 | 945.7197 | 1.0006
GSD(T)-1
Primary | 13749.5082 | 1.0429 | 14338.979 | 0.95889 | 589.4708 | 0
Secondary | 4758360.4918 | 1.0824 | 5150592.2638 | 0.92385 | 392231.772 | 0
GSD(T)-1 TOTAL | 4772110 | 1.0823 | 5164931.2428 | 0.92394 | 392821.2428 | 1.0005
GSLD(T)-1
Primary | 74495.3923 | 1.0429 | 77689.169 | 0.95889 | 3193.7767 | 0
Secondary | 1818432.6077 | 1.0824 | 1968326.0521 | 0.92385 | 149893.4444 | 0
GSLD(T)-1 TOTAL | 1892928 | 1.0809 | 2046015.2211 | 0.92518 | 153087.2211 | 0.99919
GSLD(T)-2
Primary | 125176.3638 | 1.0429 | 130542.942 | 0.95889 | 5366.5782 | 0
Secondary | 259731.6362 | 1.0824 | 281141.3213 | 0.92385 | 21409.6851 | 0
GSLD(T)-2 TOTAL | 384908 | 1.0696 | 411684.2634 | 0.93496 | 26776.2634 | 0.98873
MET
Primary | 16573 | 1.0429 | 17283.5199 | 0.95889 | 710.5199 | 0
MET TOTAL | 16573 | 1.0429 | 17283.5199 | 0.95889 | 710.5199 | 0.96406
OL-1
Secondary | 27201 | 1.0824 | 29443.1791 | 0.92385 | 2242.1791 | 0
OL-1 TOTAL | 27201 | 1.0824 | 29443.1791 | 0.92385 | 2242.1791 | 1.0006
OS-2
Primary | 12949 | 1.0429 | 13504.1513 | 0.95889 | 555.1513 | 0
OS-2 TOTAL | 12949 | 1.0429 | 13504.1513 | 0.95889 | 555.1513 | 0.96406
RS(T)-1
Secondary | 14177423 | 1.0824 | 15346068.3255 | 0.92385 | 1168645.3255 | 0
RS(T)-1 TOTAL | 14177423 | 1.0824 | 15346068.3255 | 0.92385 | 1168645.3255 | 1.0006
SL-1
Secondary | 140741 | 1.0824 | 152342.2841 | 0.92385 | 11601.2841 | 0
SL-1 TOTAL | 140741 | 1.0824 | 152342.2841 | 0.92385 | 11601.2841 | 1.0006
SL-2
Secondary | 3853 | 1.0824 | 4170.6029 | 0.92385 | 317.6029 | 0
SL-2 TOTAL | 3853 | 1.0824 | 4170.6029 | 0.92385 | 317.6029 | 1.0006
SST-DST
Primary | 5550 | 1.0429 | 5787.9404 | 0.95889 | 237.9404 | 0
SST-DST TOTAL | 5550 | 1.0429 | 5787.9404 | 0.95889 | 237.9404 | 0.96406
TOTAL FPSC | 23465293 | 1.0818 | 25383683.3438 | 0.92442 | 1918390.3438 | 1
TOTAL COMPANY | 23465293 | 1.0818 | 25383683.3438 | 0.92442 | 1918390.3438 | 1
COMPANY USE (Secondary) | 23385.9532 | 1.0824 | 25313.6579 | 0.92385 | 1927.7047
TOTAL FPL | 23488678.9532 | 1.0818 | 25408997.0016 | 0.92442 | 1920318.0484 | 1

## Energy Losses by Rate GROUP
OPC 012991
FPL RC-16
RATE GROUP | DELIVERED MWH SALES | EXPANSION FACTOR | DELIVER ENERGY AT GENERATION | DELIVERED EFFICIENCY | LOSSES | COST RECOVERY MULTIPLIER
CILC-1D / CILC-1G | 2902255.4768 | 1.0445 | 3031392.5382 | 0.9574 | 129137.0615 | 0.99409
GSD-1 / CILC-1G | 25294185.026 | 1.0535 | 26647442.4728 | 0.94922 | 1353257.4468 | 1.0027
GSLD-2 / OS-2 / MET | 2585363.0527 | 1.0444 | 2700130.3079 | 0.9575 | 114767.2553 | 0.99399
GSLD-3 / CILC-1T | 1528583.8457 | 1.0182 | 1556474.616 | 0.98208 | 27890.7702 | 0.96911
OL-1 / SL-1 | 618049.5698 | 1.0536 | 651161.3355 | 0.94915 | 33111.7656 | 1.0027
SL-2 / GSCU-1 | 114833.1091 | 1.0536 | 120985.2483 | 0.94915 | 6152.1392 | 1.0027

## 12CP Dem Losses by Rate Group
OPC 012992
FPL RC-16
RATE CLASS | 12CP DEMAND AT METER | EXPANSION FACTOR | 12CP DEMAND AT GENERATION | DELIVERED EFFICIENCY | LOSSES | FUEL COST RECOVERY MULTIPLIER
CILC-1D / CILC-1G | 362071.9167 | 1.0576 | 382929.9163 | 0.94553 | 20857.9996 | 0.99164
GSD-1 / CILC-1G | 3844993.8333 | 1.0699 | 4113664.5465 | 0.93469 | 268670.7132 | 1.0031
GSLD-2 / OS-2 / MET | 322857.6667 | 1.0582 | 341663.78 | 0.94496 | 18806.1133 | 0.99224
GSLD-3 / CILC-1T | 184768.5833 | 1.0231 | 189033.779 | 0.97744 | 4265.1956 | 0.95927
OL-1 / SL-1 | 1159.5 | 1.07 | 1240.6336 | 0.9346 | 81.1336 | 1.0032
SL-2 / GSCU-1 | 13485.0833 | 1.07 | 14428.6743 | 0.9346 | 943.591 | 1.0032