## Staff INT 29 371 Response
Florida Power & Light Company
Docket No. 160021-EI
Staff's Twenty-Ninth Set of Interrogatories
Interrogatory No. 371
Attachment No. 1
Tab 1 of 1
2017
Site | Unit | Manufacturer | Outage Description | Original Equipment Recommended Interval | PGD FPL Fleet Team Recommended Interval | Total Expected* SH by next Overhaul | Total Expected* Years by next Overhaul
Manatee | 3 | General Electric | Generator major | 48,000 - 64,000 hours (4 - 8 years) | (10 - 12 years) | 98600 | 12
Manatee | 3 | Toshiba | Steam Turbine major | 48,000 Hours (4 - 6 years) | (8 - 12 years) | 98600 | 12
Martin | 8 | General Electric | Generator major | 48,000 - 64,000 hours (4 - 8 years) | (10 - 12 years) | 95700 | 12
Martin | 8 | Toshiba | Steam Turbine major | 48,000 Hours (4 - 6 years) | (8 - 12 years) | 95700 | 12
Ft. Myers | 2 | General Electric | Generator minor | (2 - 3 years) | (3 - 4 years) | 29400 | 4
Ft. Myers | 2 | General Electric | Steam Turbine valves | (3 - 4 years) | (6 - 8 years) | 48900 | 6
West County | 3 | Mitsubishi | Combustion Turbine major | 48,000 Hours (4 - 6 years) | 48,000 Hours (4 - 6 years) | 49200 | 6
Cape Canaveral | 3 | Siemens | Hot Gas Path | 33,000 hours (4 years) | 33,000 hours (4 years) | 35300 | 4
Cape Canaveral | 3 | Siemens | Generator minor | (2 - 3 years) | (3 - 4 years) | 35300 | 4
2018
Site | Unit | Manufacturer | Outage Description | Original Equipment Recommended Interval | PGD FPL Fleet Team Recommended Interval | Total Expected* SH by next Overhaul | Total Expected* Years by next Overhaul
Sanford | 5 | GE | Generator Minor | (2 - 3 years) | (3 - 4 years) | 21100 | 3
Sanford | 5 | Siemens | Steam turbine valves | 24,000 hrs (3-4 years) | 6-8 years | 44200 | 6
West County | 1 | Mitsubishi | Hot Gas Path | 24,000 hrs (3-4 years) | 24,000 hrs (3-4 years) | 28000 | 4
West County | 1 | Mitsubishi | Generator Minor | (2 - 3 years) | (3 - 4 years) | 27300 | 3
Riviera | 5 | Siemens | Hot Gas Path | 33,000 hours (4 years) | 33,000 hours (4 years) | 36600 | 4
- Combined cycle units in the tables above have major overhauls (considered as an outage duration of 21 days or greater)
- Excludes upgrades, balance of plant and HRSG inspections
*Total expected service hours (SH) and years by next similar type overhaul are rounded and assume similar avg unit monthly service hour projections as actuals. Values can vary +/-2,400 hours (or 0.25 years)