## Sheet1
Utilities, Inc. of Florida
Docket No. 160101-WS
Test Year Ending: 12/31/15
Proforma Plant Additions O&M differences
Item # | Capital Project | Exhibit | O&M savings? | Explanation
1 | Cypress Lakes Hydro Tank #1 | PCF-1 Cypress Lakes Hydro Tank #1 | No | Replacing an existing asset with no material operational impact.
2 | Cypress Lakes Sediment Removal | PCF-2 Cypress Lakes WWTP Sediment Removal | No | Periodic activity required to maintain performance of the treatment process.
3 | ER EQ tank-headworks-gates-trees | PCF-3 Eagle Ridge EQ Tank & Plant Improvements | No | Replace assets at the end of their service life.
4 | LB WWTP Sediment Removal | PCF-4 Labrador Sediment Removal | No | Periodic activity required to maintain performance of the treatment process.
5 | Lake Groves Sludge Dewatering Equipment | PCF-5 Lake Groves Sludge Dewatering Equipment | Yes | Reduction in sludge hauling expense of $3,500/month assuming the pilot test shows the efficacy of the equipment as designed. Initial indications are that the solar unit may only be effective at half the design loading rate resulting in a projected savings of about $1,750/month. If the project is not successful and not added to rate base, the O&M impact would be about a 10% increased due to the increase in sludge production from customer growth increasing flow to the plant.
6 | LUSI Oswalt Rd WM relocates | PCF-6 Oswalt Rd WM Relocates | No | Replacing an existing asset due to a Lake Co. road project with no material operational impact.
7 | LUSI SCADA System | PCF-7 LUSI SCADA System | No | Real team monitoring of assets will improve utilization of water production sites while remaining compliant with regulatory limits, but it is not expect to reduce TY O&M.
8 | LUSI TTHM/HAA5 Study | PCF-8 LUSI TTHM & HAA5 Analysis | No | Engineering evaluation mandated by DEP, no physical assets constructed.
9 | Eng-Lake Groves WTP upgrade TTHM/HAA5 | PCF-9 Eng Lake Groves WTP upgrades | No | Engineering design of water plant upgrades to follow.
10 | Eng-LUSI US 27 Ph 3 Utility Relocates | PCF-10 LUSI Eng US 27 Ph 3 Relocates | No | Engineering support for relocation of assets due to FDOT highway project.
10a | LUSI US 27 Ph 3 Utility Relocates | PCF-10a LUSI US 27 Ph 3 Relocates | No | Relocated existing assets in conflict with FDOT highway project.
11 | LW Church Ave FM relocates | PCF-11 Longwood Church Ave FM Relocates | No | Relocated sewer assets in conflict with a city of Longwood road project.
12 | LW I&I Longwood Groves | PCF-12 Longwood Groves I&I Investigation | No | Videoinspection of sewer mains and manholes only.
13 | LW I&I Study Longwood Groves | PCF-13 Longwood Groves I&I Remediation | Yes | It is impossible to quantify the reduction in I&I before the improvements are identified and implemented followed by a wet weather period.
14 | MC Electrical Improvements | PCF-14 Mid-County Electrical Improvements | Yes | Replacing the current generator will reduce repair frequency and costs that are
15 | MC Field Office Replacements | PCF-15 Mid-County Field Office Replacement | No | Replaced asset at end of its service life, no change in general purpose and use.
16 | MC Flow Monitoring & Analysis | PCF-16 Mid-County Flow Monitoring & Analysis | No | Short-term investigation of sources of excess I&I, no impact to O&M.
17 | MC I&I remedies | PCF-17 Mid-County I&I Remediation | Yes | It is impossible to quantify the reduction in I&I before the improvements are identified and implemented followed by a wet weather period. The most likely O&M savings would be from reduced chemical costs. A yearly average reduction of 10% in plant flow may reduce the use of chlorine, sodium bisulfiate, and ferric sulfate by 10%/yr or about $10,5800 (0.10 * (44,827+45,792+15,193)).
18 | MC Methanol pumps & instrumentation | PCF-18 Mid-County Methanol Pumps & Instrumentation | Yes | The purchase of methanol is expected to decrease by as much as 10% through optimization of chemical feed rates, which amount to $4,220/yr (10% of $42,222 in methanol expense in TY)
19 | MC US 19 utility relocations | PCF-19 Mid-County US 19 FM Relocation & GSM Rehab | No | Relocated existing assets in conflict with FDOT highway project.
20 | PB WTP Electrical Improvements | PCF-20 Pennbrooke WTP Electrical Improvements | No | Replace assets at end of their service life and to conform with current electric code.
21 | SH Placida Road Utility Relocates | PCF-21 SH Placida Rd Utility Relocation | No | Relocated existing assets in conflict with Charlotte Co. highway project.
22 | SUC Autumn Drive WM replacement | PCF-22 SUC Autumn Drive WM Replacement | No | Replaced poor quality WM with new materials of the same size.
23 | SUC Lift Station RTU's | PCF-23 SUC Sanlando LS RTU's | No | Newly installed assets are designed to provide real time data monitoring of lift station conditions only.
24 | SUC Markham Woods Utility Relocates | PCF-24 Markham Woods WM Relocates | No | Relocated assets in conflict with Seminole Co. road project.
25 | SUC Myrtle Lake Hills WM | PCF-25 SUC Myrtle Lake Hills WM | No | O&M will increase due to the addition of new customers.
26 | SUC I&I Deficiency Corrections Ph 2 | PCF-26 SUC I&I Study and Remediation, Ph. 2 | Yes | It is impossible to quantify the reduction in I&I before the improvements are identified and implemented followed by a wet weather period.
27 | SUC Shadow Hills diversion | PCF-27 SUC Shadow Hills Diversion | No | It is expected that the cost to divert flow from Shadow Hills plant to the Wekiva plant, treatment and disposal will approximately equal the cost to operate the Shadow Hills plant on an annual basis.
28 | SUC Wekiva blower replacement | PCF-28 SUC Wekiva Blower Replacement | Yes | Purchased power will be reduced by having to run two blowers continuously instead of three. The imputed savings is estimated to be 10% or about $2,000/month.
29 | SUC Des Pinar W-2A & LS A-1 & Genset | PCF-29 SUC Well 2A & LS A1 Electrical & Genset | No | O&M will increase due to the addition of a new emergency generator. The estimated annual cost for diesel fuel use/yr and preventative maintenance expense is $2,000.
30 | SUC Wekiva WWTP Rehab | PCF-30 SUC Wekiva WWTP Rehab | No | The project entails a comprehensive rehabilitation of each of the three treatment trains to restore them to nearly new condition. The plant design will not be modified; there is no imputed O&M savings associated with this project.
31 | TV 401 8th Avenue GSM Replacement | PCF-31 TV 401 8th Street GSM Replacement | Yes | The gravity sewer main was replaced due to its collapsed condition; any reduction in excess I&I at that location will only be known after a period of wet weather occurs and then computing the reduction in purchased sewer expense. To date, no significant reduction in flow at the master lift station has been measured.
32 | UIF Crescent Heights WM replacement | PCF-32 UIF Crescent Heights WM Replacement | No | Replacing assets at the end of their service life with similar sized pipe.
33 | UIF Buena Vista/OW WM replacement | PCF-33 UIF Buena Vista/Orangewood WM Replace | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
34 | UIF Summertree Well Abandonment | PCF-34 UIF Summertree Well Abandonment | No | O&M will increase after termination of wells due to the added cost of purchasing bulk water from Pasco Co.
35 | UIF Lake Tarpon WM replacement | PCF-35 UIF Lake Tarpon WM Replacment | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
36 | UIF Little Wekiva & Jansen Elec Improvements | PCF-36 UIF L. Wekiva & Jansen Electrical Improvements | No | Replacing assets at the end of their service life.
37 | Eng-UIF WM Replacements | PCF-37 UIF Eng WM Replacements | No | Engineering services required in support of 7 water main replacement projects in Seminole/Orange.
38 | UIF Bear Lake WM replacement | PCF-38 UIF Bear Lake WM Replacement | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
39 | UIF Crystal Lake WM replacement | PCF-39 UIF Crystal Lake WM Replacement | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
40 | UIF Little Wekiva WM replacement | PCF-40 UIF Little Wekiva WM Replacement | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
41 | UIF Northwestern FM relocation | PCF-41 UIF Northwestern FM Relocation | No | O&M may increase due to the slightly longer distance with new pipe route and with a reduced pipe diameter.
42 | UIF Oakland Shores WM replacement | PCF-42 UIF Oakland Shores WM Replacement | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
43 | UIF Phillips WM replacement & CL I/C | PCF-43 UIF Phillips WM Replacement | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
44 | UIF Ravenna Park WM replacement | PCF-44 UIF Ravenna Park WM Replacement | No | Previous pipe failures were capitalized due to the replacement of sections of pipe, fittings and valves. Therefore, O&M expense reduction may be minimal.
45 | UIF Ravenna Park/Crystal Lake I/C | PCF-45 UIF Ravenna Park/Crystal Lake Interconnecion | No | O&M may increase slightly (purchased power) due to small increase in system head conditions.
46 | UIF C4500 Kodiak upfitting | PCF-46 C4500 Kodiak Truck Upfitting | No | Truck improvements are designed to extend the service life and improve safety features using the orginal chassis, cab and engine.
47 | UIF GIS Mapping Services | PCF-47 UIF GIS Mapping Services | No | Engineering services only that are required in order to digitize all maps, plans and drawings to GIS specs.