## F 1
Gallons of Water Pumped, Sold and Unaccounted For | [10 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [10 empty] | Page 1 of 1
Docket No.: 160101-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2015
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
[12 empty] | Unaccounted |  | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water |  | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2)(3) |  | (1)+(2)-(3)-(4) |  | For Water
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ |  | _
2015-01-01 |  | 1.5703 |  | 1.6111 |  | 0.001 |  | 1.4294 |  | 0.00418 |  | 0.17856 |  | 11.08%
2015-02-01 |  | 1.4233 |  | 1.4603 |  | 0 |  | 1.2484 |  | 0.0038 |  | 0.20809 |  | 14.25%
2015-03-01 |  | 1.9083 |  | 1.9579 |  | 0 |  | 1.4549 |  | 0.00418 |  | 0.49886 |  | 25.48%
2015-04-01 |  | 1.9451 |  | 1.9957 |  | 0.001 |  | 1.8348 |  | 0.070528 |  | 0.091355 |  | 4.575%
2015-05-01 |  | 2.6173 |  | 2.7175 |  | 0 |  | 2.097 |  | 0.00418 |  | 0.61628 |  | 22.68%
2015-06-01 |  | 2.0676 |  | 2.1509 |  | 0.031 |  | 2.3701 |  | 0.004 |  | -0.19222 |  | -8.81%
2015-07-01 |  | 1.7247 |  | 1.7942 |  | 0 |  | 1.729 |  | 0.00418 |  | 0.060975 |  | 3.398%
2015-08-01 |  | 1.6657 |  | 1.7328 |  | 0.003 |  | 1.5484 |  | 0.0045 |  | 0.18288 |  | 10.54%
2015-09-01 |  | 2.0818 |  | 2.1657 |  | 0.001 |  | 1.3783 |  | 0.19596 |  | 0.59243 |  | 27.34%
2015-10-01 |  | 2.2822 |  | 2.3742 |  | 0.071 |  | 2.0901 |  | 0.12076 |  | 0.23433 |  | 9.583%
2015-11-01 |  | 2.1513 |  | 2.238 |  | 0 |  | 2.0587 |  | 0.0045 |  | 0.17479 |  | 7.81%
2015-12-01 |  | 2.0868 |  | 2.1709 |  | 0 |  | 1.8095 |  | 0.01314 |  | 0.34826 |  | 16.04%
|  | - |  |  |  | - |  | - |  | - |  | - |  | -
Total |  | 23.5244 |  | 24.3692 |  | 0.108 |  | 21.0487 |  | 0.43391 |  | 2.9946 |  | 12.23%
|  | = |  |  |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)
* Emergency interconnect with City of Altamonte Springs
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing
Reconciliation of gallons sold:
Reconciliation of gallons sold: The amounts on Sch. F-1 and F-9 are the same.
Sch. E-2 shows the total for Seminole County, consisting of nine systems - Bear Lake, Crystal Lake, Jansen,
Little Wekiva, Oakland Shores, Park Ridge, Phillips, Revenna Park and Weathersfield. The amount on Sch E-2
170.920 mg. The aggregate amount of sales of the individual systems is 170.790. The difference is only 0.0761%.
This is most likely due to the fact that the amounts on F-1 and F-9 are the sums of actual readings whereas the amount
on E-2 is taken from the billing analysis which is rounded to the nearest 1,000 gallons.

## F 2
Gallons of Wastewater Treated | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [8 empty] | Page 1 of 1
Docket No.: 160101-WS | [8 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2015
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | (Name) |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2015-01-01 | [9 empty] | 0 |  | 0
2015-02-01 | [9 empty] | 0 |  | 0
2015-03-01 |  |  | Not Applicable - water only system | [6 empty] | 0 |  | 0
2015-04-01 | [9 empty] | 0 |  | 0
2015-05-01 | [9 empty] | 0 |  | 0
2015-06-01 | [9 empty] | 0 |  | 0
2015-07-01 | [9 empty] | 0 |  | 0
2015-08-01 | [9 empty] | 0 |  | 0
2015-09-01 | [9 empty] | 0 |  | 0
2015-10-01 | [9 empty] | 0 |  | 0
2015-11-01 | [9 empty] | 0 |  | 0
2015-12-01 | [9 empty] | 0 |  | 0
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 0 | [7 empty] | 0 |  | 0
|  | = |  | = |  | = |  | = |  | = |  | =

## F 3
Water Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [8 empty] | Schedule F-3
Docket No.: 160101-WS | [8 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [5 empty] | Max Day Design per Sanitary Survey |  |  | 332898
on the DEP operating or construction permit, provide an explanation.
[7 empty] | AADF per Cup |  |  | 96877
2 | Maximum Day
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2015-09-04 | 205500
| Explain, on a separate sheet of paper if fire flow, line breaks, | [7 empty] | Main break
| or other unusual occurrences affected the flow this day. | [7 empty] | 2015-05-28 | 126200
Next highest day, no incidents
3 | Five Day Max. Year
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2015-05-21 | 103500
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2015-05-14 | 116000
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2015-05-27 | 116600
| these days. | [6 empty] | (4) | 2015-05-17 | 120100
[8 empty] | (5) | 2015-05-28 | 126200
[9 empty] | AVERAGE | 116480
[9 empty] | Max Month | 87660.199
4 | Average Daily Flow | [7 empty] | Annual | 66764.9595
5 | Required Fire Flow | [7 empty] | * 600 gpm for 2 hours
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.
* Land Development Code of Seminloe County
Single family & duplexes - 600 gpm minimum
All others - 1,250 gpm minimum

## F 4
Wastewater Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [8 empty] | Schedule F-4
Docket No.: 160101-WS | [8 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
|  | Not Applicable - water only system | [6 empty] | _ |  | _
1. | Plant Capacity
The hydraulic rated capacity. If different from that shown
on the DEP operating or construction permit, provide an explanation.
2. | Average Daily Flow Max Month (a)
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.

## F 5
Used and Useful Calculations |  |  |  |  | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) |  |  |  |  | Schedule F-5
Docket No.: 160101-WS |  |  |  |  | Page 1 of 1
Test Year Ended: December 31, 2015 |  |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 300 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 0 | gpm
(System has only one well)
| Ground storage capacity, gal. |  |  |  | 16800 | gallons
| Usable ground storage (90%), gal. |  |  |  | 15120 | gallons
| Elevated Storage |  |  |  | 0 | gallons
| Usable ground storage (100%), gal. |  |  |  | 0 | gallons
| Hydropneumatic storage capacity, gal. |  |  |  | 7000 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 15120 | gallons
| Maximum day demand, with no incidents |  |  |  | 126200 | gpd
| Peak hour demand = 2x max day/1440 |  |  |  | 175.2778 | gpm
| Fire flow requirement |  | 600 gpm for 2 hours |  | 72000 | gpd
| Unaccounted for water |  | 12.23% | of water pumped | 8204.3019 | gpd
| Acceptable unaccounted for |  | 10% |  | 6706.085 | gpd
| Excess unaccounted for |  |  |  | 1498.2169 | gpd
Used & Useful Analysis, in accordance with Rule 25-30.4325:
No usable storage
Water Treatment Plant
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand |  |  | 126200 | gpd
| B = | Property needed to serve five years after TY |  |  | 0 | gpd
| C = | Fire flow demand |  |  | 0 | gpd
| D = | Excess Unaccounted for water |  |  | 1498.2169 | gpd
| E = | Firm Reliable Capacity |  |  | 0 | gpd
Storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand |  |  | 126200 | gallons
| B = | Property needed to serve five years after TY |  |  | 0 | gallons
| C = | Fire flow demand |  |  | 0 | gallons
| D = | Excess Unaccounted for water |  |  | 1498.2169 | gallons
| E = | Firm Reliable Capacity |  |  | 15120 | gallons
The above used and useful factor is applicable to the distribution reservoir accounts.
68

## F 6
Used and Useful Calculations |  | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) |  | Schedule F-6
Docket No.: 160101-WS |  | Page 1 of 1
Test Year Ended: December 31, 2015 |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
Not Applicable - water only system.

## F 7
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [5 empty] | Schedule F-7
Docket No.: 160101-WS | [5 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Water Distribution System
Used & useful was last set for this system in Docket Nos. 120209-WS.
The water distribution system was found to be built out and 100% U&U. Circumstances have not changed.
The system remains 100% used & useful.

## F 8
Margin Reserve Calculations |  | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) |  | Schedule F-8
Docket No.: 160101-WS |  | Page 1 of 1
Test Year Ended: December 31, 2015 |  | Preparer: Seidman, F.
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5,F-6,F-7
Not applicable. Used & useful was last set for this system in Docket Nos. 120209-WS.
All water is purchased. The system was found to be built out and 100% U&U. Circumstances have not changed.
The system remains 100% used & useful.

## F 9
Equivalent Residential Connections - Water | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [8 empty] | Schedule F-9
Docket No.: 160101-WS | [8 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2011 | 232 | 217 |  | 224.5 |  | 21974960 | 97884.0089 | 22102840 |  | 225.8064
2 | 2012 | 217 | 215 |  | 216 |  | 21089790 | 97637.9167 | 21175660 |  | 216.8795 |  | -3.953%
3 | 2013 | 215 | 213 |  | 214 |  | 20007484 | 93492.9159 | 20056144 |  | 214.5205 |  | -1.088%
4 | 2014 | 213 | 221 |  | 217 |  | 18967368 | 87407.2258 | 19125028 |  | 218.8037 |  | 1.997%
5 | 2015 | 221 | 217 |  | 219 |  | 20182530 | 92157.6712 | 21048730 |  | 228.3991 |  | 4.385%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 0.3352%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 218.749 |  | 1 | 225.8064
[6 empty] | X Coefficient: |  | 0.71096 |  | 2 | 216.8795
[6 empty] | R^2: |  | 0.035705 |  | 3 | 214.5205
[10 empty] | 4 | 218.8037
[10 empty] | 5 | 228.3991
[10 empty] | 10 | 225.8586
[7 empty] | Five year growth |  |  |  | -2.5405 | Ercs
[7 empty] | Annual average growth |  |  |  | -0.50811 | Ercs

## F 10
Equivalent Residential Connections - Wastewater | [7 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Seminole - Oakland Shores (252-295) | [7 empty] | Schedule F-10
Docket No.: 160101-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) |  | (3) | (4) | (5) | (6) | (7) | (8) | (9)
|  | SFR Customers |  |  |  | SFR | Gallons/ | Total | Total | Annual
Line | [5 empty] | Gallons | SFR | Gallons | ERCs | % Incr.
No. | Year | Beginning |  | Ending | Average | Sold | (5)/(4) | Sold | (7)/(6) | in ERCs
1 | 2011
2 | 2012 |  | Not Applicable - water only system.
3 | 2013
4 | 2014
5 | 2015
Average Growth Through 5-Year Period (Col. 8)