## Infiltration
System | 4" Pipe |  |  | 6" Pipe |  |  | 8" Pipe |  |  | 10" Pipe |  |  | 12" Pipe |  |  | 15" Pipe |  |  | 18" Pipe |  |  | Total Allowable I&I(1)
| ft | in-miles | Allowable I&I(1) | ft | in-miles | Allowable I&I(1) | ft | in-miles | Allowable I&I(1) | ft | in-miles | Allowable I&I(1) | ft | in-miles | Allowable I&I(1) | ft | in-miles | Allowable I&I(1) | ft | in-miles | Allowable I&I(1) | gpd | gpy
Cypress Lakes | 0 | 0 | 0 | 483 | 0.54886 | 274.4318 | 43535 | 65.9621 | 32981.0606 | 118 | 0.22348 | 111.7424 | 2963 | 6.7341 | 3367.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 36734.2803 | 13408012.3106
Eagle Ridge | 0 | 0 | 0 | 0 | 0 | 0 | 56845 | 86.1288 | 43064.3939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43064.3939 | 15718503.7879
Cross Creek | 0 | 0 | 0 | 0 | 0 | 0 | 14380 | 21.7879 | 10893.9394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10893.9394 | 3976287.8788
Labrador | 0 | 0 | 0 | 0 | 0 | 0 | 27825 | 42.1591 | 21079.5455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21079.5455 | 7694034.0909
Lake Placid | 0 | 0 | 0 | 0 | 0 | 0 | 4155 | 6.2955 | 3147.7273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3147.7273 | 1148920.4545
Longwood | 0 | 0 | 0 | 0 | 0 | 0 | 15528 | 23.5273 | 11763.6364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11763.6364 | 4293727.2727
LUSI | 0 | 0 | 0 | 131 | 0.14886 | 74.4318 | 90664 | 137.3697 | 68684.8485 | 350 | 0.66288 | 331.4394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69090.7197 | 25218112.6894
Mid-County | 0 | 0 | 0 | 0 | 0 | 0 | 84087 | 127.4045 | 63702.2727 | 5010 | 9.4886 | 4744.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68446.5909 | 24983005.6818
Pennbrooke | 0 | 0 | 0 | 0 | 0 | 0 | 46816 | 70.9333 | 35466.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35466.6667 | 12945333.3333
Sandalhaven | 0 | 0 | 0 | 2325 | 2.642 | 1321.0227 | 43245 | 65.5227 | 32761.3636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34082.3864 | 12440071.0227
Sanlando | 1583 | 1.1992 | 599.6212 | 7339 | 8.3398 | 4169.8864 | 421401 | 638.4864 | 319243.1818 | 45681 | 86.517 | 43258.5227 | 2009 | 4.5659 | 2282.9545 | 180 | 0.51136 | 255.6818 | 0 | 0 | 0 | 369809.8485 | 134980594.697
Tierra Verde | 0 | 0 | 0 | 0 | 0 | 0 | 27885 | 42.25 | 21125 | 440 | 0.83333 | 416.6667 | 4021 | 9.1386 | 4569.3182 | 3461 | 9.8324 | 4916.1932 | 3125 | 10.6534 | 5326.7045 | 36353.8826 | 13269167.1402
UIF Marion | 0 | 0 | 0 | 0 | 0 | 0 | 2798 | 4.2394 | 2119.697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2119.697 | 773689.3939
UIF Pasco
Wis Bar | 0 | 0 | 0 | 0 | 0 | 0 | 4662 | 7.0636 | 3531.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3531.8182 | 1289113.6364
Summertree | 372 | 0.28182 | 140.9091 | 3825 | 4.3466 | 2173.2955 | 30585 | 46.3409 | 23170.4545 | 2677 | 5.0701 | 2535.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28019.697 | 10227189.3939
UIF Seminole
Weathersfield | 0 | 0 | 0 | 0 | 0 | 0 | 45856 | 69.4788 | 34739.3939 | 1751 | 3.3163 | 1658.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36397.5379 | 13285101.3258
Lincoln Heights | 0 | 0 | 0 | 6018 | 6.8386 | 3419.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3419.3182 | 1248051.1364
Notes:
(1) At 500 gpd/in-mi

## Inflow
System | WWTP Flow | WWTP Flow | Billed Water Flow |  | Calculated Billed Water Returned to WWTP |  |  | Allowable Inflow(1)
| gpd | gal/yr | Residential | Non-Residential | Residential (80%) | Non-Residential (90%) | Total
Cypress Lakes | 99674 | 36381010 | 40703771 | 1336290 | 32563016.8 | 1202661 | 33765677.8 | 3376567.78
Eagle Ridge | 213178 | 77809970 | 57599000 | 41028000 | 46079200 | 36925200 | 83004400 | 8300440 | MFRs use 60% for residential because area is heavily landscaped
Cross Creek | 58249 | 21260885 | 66136000 |  | 52908800 | 0 | 52908800 | 5290880 | MFRs do not do a calculation for Cross Creek
Labrador | 56165 | 20500225 | 13584000 | 2985130 | 10867200 | 2686617 | 13553817 | 1355381.7
Lake Placid | 18749 | 6843385 | 2088930 | 4475280 | 1671144 | 4027752 | 5698896 | 569889.6
Longwood | 376284.9315 | 137344000 | check for revised MFR sheet | 2283761 | #VALUE! | 2055384.9 | #VALUE! | #VALUE!
LUSI | 451110 | 164655150 | 369274419 | 0 | 295419535.2 | 0 | 295419535.2 | 29541953.52 | MFRs use 45% for residential because area is heavily landscaped; check for water used by WW customers
Mid-County | 773340 | 282269100 | 130810000 | 185188000 | 104648000 | 166669200 | 271317200 | 27131720 | no F-1 in MFRs
Pennbrooke | 98397 | 35914905 | 103670904 | 2040450 | 82936723.2 | 1836405 | 84773128.2 | 8477312.82
Sandalhaven | 138286 | 50474390 | 21141000 | 15358000 | 16912800 | 13822200 | 30735000 | 3073500 | MFRs use 90 and 96% references docket 060285
Sanlando | 2004742 | 731730830 | 1359282799 | 256291071 | 1087426239.2 | 230661963.9 | 1318088203.1 | 131808820.31 | MFRs use 39% for residential because area is heavily landscaped; check for water used by WW customers
Tierra Verde |  | 129033140 | 126870000 | 16838000 | 101496000 | 15154200 | 116650200 | 11665020 | used billed water flow from the 2008 rate case as a proxy for current flows
UIF Marion | 17000 | 6205000 | 2021700 | 4122943 | 1617360 | 3710648.7 | 5328008.7 | 532800.87
UIF Pasco
Wis Bar | 15140.6301 | 5526330 | 3622137 | 99210 | 2897709.6 | 89289 | 2986998.6 | 298699.86
Summertree | 91361.6438 | 33347000 | 26377016 | 807910 | 21101612.8 | 727119 | 21828731.8 | 2182873.18
UIF Seminole
Weathersfield | 133107.4219 | 48584209 | 67872053 | 1533960 | 54297642.4 | 1380564 | 55678206.4 | 5567820.64
Lincoln Heights | 63842.3589 | 23302461 | 12888970 | 2014360 | 10311176 | 1812924 | 12124100 | 1212410 | MFRs use 84 and 96% based on docket 07-0505
Notes
(1) Based on 10% of billed water returned to WWTP

## I&I Summary ATW-3
System | Total WW flow | Water Returned to WWTP | Allowable Inflow | Allowable Infiltration | Excess I&I
Cypress Lakes | 36381010 | 33765677.8 | 3376567.78 | 13408012.3106 | -14169247.8906 | OK
Eagle Ridge | 77809970 | 83004400 | 8300440 | 15718503.7879 | -29213373.7879 | OK
Cross Creek | 21260885 | see below | see below | see below | see below | OK; verify Lee County numbers?
Labrador | 20500225 | 13553817 | 1355381.7 | 7694034.0909 | -2103007.7909 | OK
Lake Placid | 6843385 | 5698896 | 569889.6 | 1148920.4545 | -574321.0545 | OK
Longwood | 137344000 | see below | see below | see below | see below | OK based on 120 gpcd criteria
LUSI | 164655150 | 295419535.2 | 29541953.52 | 25218112.6894 | -185524451.4094 | OK
Mid-County | 282269100 | 271317200 | 27131720 | 24983005.6818 | -41162825.6818 | OK
Pennbrooke | 35914905 | 84773128.2 | 8477312.82 | 12945333.3333 | -70280869.3533 | OK
Sandalhaven | 50474390 | 30735000 | 3073500 | 12440071.0227 | 4225818.9773 | over
Sanlando | 731730830 | 1318088203.1 | 131808820.31 | 134980594.697 | -853146788.107 | OK
Tierra Verde | 129033140 | 116650200 | 11665020 | 13269167.1402 | -12551247.1402 | OK
UIF Marion | 6205000 | 5328008.7 | 532800.87 | 773689.3939 | -429498.9639 | OK
UIF Pasco
Wis Bar | 5526330 | 2986998.6 | 298699.86 | 1289113.6364 | 951517.9036 | over
Summertree | 33347000 | 21828731.8 | 2182873.18 | 10227189.3939 | -891794.3739 | OK
UIF Seminole
Weathersfield | 48584209 | 55678206.4 | 5567820.64 | 13285101.3258 | -25946919.3658 | OK
Lincoln Heights | 23302461 | 12124100 | 1212410 | 1248051.1364 | 8717899.8636 | over
LONGWOOD
Longwood Subschedule | Based on No of Bills Sched E2 | Equivalency Factor | ERUs
Res | 1553.25 | 1 | 1553.25
GS 5/8 | 50.8333 | 1 | 50.8333
GS 1 | 10.0833 | 2.5 | 25.2083
GS 1.5 | 7.0833 | 5 | 35.4167
GS 2 | 7 | 10 | 70
GS 3 | 4 | 20 | 80
|  | Total | 1814.7083
|  | WW flow (gpd) | 376284.9315
|  | gpd/ERU | 207.3528
|  | cap/ERU | 2.5
|  | gpd/cap | 82.9411
CROSS CREEK
Longwood Subschedule |  | Equivalency Factor | ERUs Form 2015 AR
Res |  | 1 | 908
GS 5/8 |  | 1 | 0
GS 1 |  | 2.5 | 0
GS 1.5 |  | 5 | 0
GS 2 |  | 10 | 0
GS 3 |  | 20 | 0
|  | Total | 908
|  | WW flow (gpd) | 58249
|  | gpd/ERU | 64.1509
|  | cap/ERU | 2.5
|  | gpd/cap | 25.6604

## EUW ATW-2
System | Water Pumped | Water Purcahsed | Water Sold | Other Uses | UAW | % UAW | % Other Uses
Cypress Lakes | 68.16 | 0 | 44.584 | 16.824 | 6.752 | 9.906% | 24.68%
Labrador | 22.463 | 0 | 17.213 | 1.97 | 3.28 | 14.6% | 8.77%
Lake Placid | 5.359 | 0 | 4.659 | 0 | 0.7 | 13.06% | 0%
LUSI - Main | 1393933 | 0 | 1313905 | 9704 | 70324 | 5.045% | 0.6962%
LUSI - Four Lakes | 6.85 | 0 | 5.994 | 0.242 | 0.614 | 8.964% | 3.533%
LUSI Lake Saunders | 4.341 | 0 | 2.284 | 2.074 | -0.017 | -0.3916% | 47.78% | *
Pasco - Summertree | 58.599 |  | 27.358 | 27.854 | 3.387 | 5.78% | 47.53% | *
Pasco - Orangewood, etc. | 75.988 | 0 | 61.93 | 0.638 | 13.42 | 17.66% | 0.8396%
Pennbrooke | 141.733 | 0 | 130.049 | 1.659 | 10.025 | 7.073% | 1.171%
Sanlando | 2352.807 | 0 | 2222.137 | 9.982 | 120.688 | 5.13% | 0.4243%
UIF Marion | 55.316 | 0 | 48.285 | 0.75 | 6.281 | 11.35% | 1.356%
UIF Orange - Davis Shores | 0 | 3.678 | 3.718 | 0.012 | -0.052 | -1.414% | 0.3263%
UIF Orange - Crescent Hts | 0 | 17.855 | 17.436 | 0.002 | 0.417 | 2.335% | 0.0112%
UIF Pinellas - Lake Tarpon | 16.562 | 0.01 | 12.848 | 0.376 | 3.348 | 20.2% | 2.269%
UIF Seminole - Bear Lake | 14.353 | 3.028 | 15.134 | 0.549 | 1.698 | 9.769% | 3.159%
UIF Seminole - Ravenna Park, etc. | 23.86 | 0 | 20.631 | 0.616 | 2.613 | 10.95% | 2.582%
UIF Seminole - Crystal Lake | 0 | 10.698 | 10.666 | 0.122 | -0.09 | -0.8413% | 1.14%
UIF Seminole - Jansen | 20.602 | 0 | 19.005 | 0.579 | 1.018 | 4.941% | 2.81%
UIF Seminole - Little Wekiva | 4.951 | 0 | 3.42 | 0.798 | 0.733 | 14.81% | 16.12%
UIF Seminole - Oakland Shores | 24.369 | 0.108 | 21.049 | 0.434 | 2.994 | 12.23% | 1.773%
UIF Seminole - Park Ridge | 6.092 | 0 | 5.816 | 0.218 | 0.058 | 0.9521% | 3.578%
Uif Seminole - Phillips | 5.835 | 0.341 | 5.334 | 0.128 | 0.714 | 11.56% | 2.073%
UIF Seminole - Weathersfield | 73.444 | 6.348 | 69.735 | 1.031 | 9.026 | 11.31% | 1.292%

## UAW I&I Summary
System | Excess UAW (%) | Excess I&I (gallons) | Excess I&I (%)
Sandalhaven |  | 4225818.9773 | 8.372%
Wis Bar |  | 951517.9036 | 17.22%
Lincoln Heights |  | 8717899.8636 | 37.41%
Labrador | 4.602%
Lake Placid | 3.062%
Pasco - Orangewood, etc. | 7.661%
UIF Marion | 1.355%
UIF Pinellas - Lake Tarpon | 10.2%
UIF Seminole - Ravenna Park, etc. | 0.9514%
UIF Seminole - Little Wekiva | 4.805%
UIF Seminole - Oakland Shores | 2.232%
Uif Seminole - Phillips | 1.561%
UIF Seminole - Weathersfield | 1.312%
LUSI Lake Saunders | ??
Pasco - Summertree | ??