## Summary
System | Wastewater Treatment | Wastewater Collection
Crownwood | 53.2% | NA
Eagle Ridge | 100% | NA
Labrador | 40.59% | NA
Lake Placid | 29.79% | NA
LUSI | 53.55% | NA
Mid County | 93.67% | 100%
Sandalhaven - EWD Cap | 42.24% | NA
Sandalhaven - Lift Station | 11.27% | NA
Sandalhaven - Force Main | 13.55% | NA
Sandalhaven - Pumps | 27.25% | NA

## Initial List
System | Water | Distribution | Wastewater | MFR U&U | Notes | Collection
Crownwood | No | No | Yes | 100% | calc 53.73% but system is substantially built out | No
Eagle Ridge | No | No | Yes | 100% | calc 73.52% but system is substantially built out | Yes | mmm
Labrador | No | No | Yes | 100% | calc 40.27% but system is substantially built out and unchanged | No
Lake Placid | No | No | Yes | 100% | calc 20.83% but system is substantially built out | No
Mid-County | No | No | Yes | 100% | calc 91.75% but system is substantially built out | Yes | 50 open lots out of?????
Sandalhaven | No | No | Yes | 100% | various | Yes | need to look at lot count
LUSI | No | No | Yes | 59% | except for resue which is 100% | No

## I&I template
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Length of | 6" | Length of |  |  | Allowable |  | Avg Test | Avg Test Yr | Water | Water Sold | Allowable |  | Returned |  | Actual | Actual
| 6" Collection | Line | 8" Collection | 6" Line | Total | Infiltration | Total Water | Year | Wastewater | Sold | To Wastewater | Inflow (10% | Allowable | Water Sold | Estimated | WW | WW | Excess | Percent
| Line | inch feet | Line | inch feet | Inch miles | (500gpd/in-mi) | Sold | Water ERCs | ERCs | Adjustment | ERC | water sold) | I&I | (80% sold) | WW and I&I | Treated | Treated | I&I | Excess
| (ft) | (in-ft) | (ft) | (in-ft) | (in-mi) | (1,000gal ) | (1,000 gal) |  |  |  | (1,000 gal) | (1,000 gal) | (1,000 gal) | (1,000 gal) | (1,000 gal) | (gpd) | (1,000 gal) | (1,000 gal) | I&I
Arredondo Farms |  | 0 | 26310 | 210480 | 39.8636 | 7275.1136 | 32360.2 | 637.3333 | 382.9167 | 0.60081 | 19442.3534 | 1944.2353 | 9219.349 | 15553.8827 | 24773.2317 | 46000 | 16790 | -7983.2317 | 0%
Beecher's Point | N/A Interconnected
Chuluota |  | 0 | 32791 | 262328 | 49.6833 | 9067.2083 | 153222.3 | 1496.9167 | 606.9167 | 0.40544 | 62123.1426 | 6212.3143 | 15279.5226 | 49698.5141 | 64978.0367 | 114000 | 41610 | -23368.0367 | 0%
Fl. Central Commerce Park |  | 0 | 7364 | 58912 | 11.1576 | 2036.2576 | N/A
Holiday Haven |  | 0 | 9808 | 78464 | 14.8606 | 2712.0606 | 4881.3 | 127.5 | 113.5 | 0.8902 | 4345.3141 | 434.5314 | 3146.592 | 3476.2513 | 6622.8433 | 17000 | 6205 | -417.8433 | 0%
Interlachen Estates/Park Manor |  | 0 | 1363 | 10904 | 2.0652 | 376.8902 | 11304.7 | 294.5 | 31 | 0.10526 | 1189.9684 | 118.9968 | 495.887 | 951.9747 | 1447.8617 | 4000 | 1460 | 12.1383 | 0.8314%
Jasmine Lakes |  | 0 | 63269 | 506152 | 95.8621 | 17494.8371 | 92262.5 | 1617.75 | 1603.5833 | 0.99124 | 91454.5556 | 9145.4556 | 26640.2927 | 73163.6445 | 99803.9371 | 205000 | 74825 | -24978.9371 | 0%
Jungle Den |  | 0 | 4704 | 37632 | 7.1273 | 1300.7273 | 1669.3 | 115 | 137 | 1.1913 | 1988.6443 | 198.8644 | 1499.5917 | 1590.9155 | 3090.5072 | 15000 | 5475 | 2384.4928 | 43.55%
Kings Cove |  | 0 | 11905 | 95240 | 18.0379 | 3291.9129 | 31887 | 209 | 201 | 0.96172 | 30666.445 | 3066.6445 | 6358.5574 | 24533.156 | 30891.7134 | 30100 | 10986.5 | -19905.2134 | 0%
Lake Gibson Estates | N/A Interconnected
Lake Suzy |  | 0 | 18747 | 149976 | 28.4045 | 5183.8295 | 37404.9 | 807.3333 | 498.6667 | 0.61767 | 23103.9349 | 2310.3935 | 7494.223 | 18483.1479 | 25977.371 | 56000 | 20440 | -5537.371 | 0%
Leisure Lakes |  | 0 | 13567 | 108536 | 20.5561 | 3751.4811 | 6532.9 | 291.6667 | 283.5833 | 0.97229 | 6351.8453 | 635.1845 | 4386.6656 | 5081.4763 | 9468.1419 | 19000 | 6935 | -2533.1419 | 0%
Morningview |  | 0 | 2856 | 22848 | 4.3273 | 789.7273 | 2274.3 | 46.4167 | 44.5 | 0.95871 | 2180.3882 | 218.0388 | 1007.7661 | 1744.3105 | 2752.0766 | 5000 | 1825 | -927.0766 | 0%
Palm Port | 2558 | 15348 | 5191 | 41528 | 10.772 | 1965.8845 | 4597 | 110.5833 | 107.9167 | 0.97589 | 4486.1454 | 448.6145 | 2414.499 | 3588.9164 | 6003.4154 | 15000 | 5475 | -528.4154 | 0%
Palm Terrace |  | 0 | 41118 | 328944 | 62.3 | 11369.75 | 60710.6 | 1203.9167 | 1033 | 0.85803 | 52091.6867 | 5209.1687 | 16578.9187 | 41673.3494 | 58252.268 | 123000 | 44895 | -13357.268 | 0%
Rosalie Oaks |  | 0 | 4162 | 33296 | 6.3061 | 1150.8561 | 2335.3 | 97 | 98 | 1.0103 | 2359.3753 | 235.9375 | 1386.7936 | 1887.5002 | 3274.2938 | 10000 | 3650 | 375.7062 | 10.29%
Silver Lake Oaks |  | 0 | 1722 | 13776 | 2.6091 | 476.1591 | 1709.7 | 46 | 45 | 0.97826 | 1672.5326 | 167.2533 | 643.4124 | 1338.0261 | 1981.4384 | 5000 | 1825 | -156.4384 | 0%
South Seas |  | 0 | 9180 | 73440 | 13.9091 | 2538.4091 | N/A
Summit Chase |  | 0 | 6039 | 48312 | 9.15 | 1669.875 | 7194.7 | 221 | 218 | 0.98643 | 7097.0344 | 709.7034 | 2379.5784 | 5677.6275 | 8057.206 | 29000 | 10585 | 2527.794 | 23.88%
Sunny Hills |  | 0 | 25791 | 206328 | 39.0773 | 7131.6023 | 42721.3 | 648 | 182 | 0.28086 | 11998.8836 | 1199.8884 | 8331.4906 | 9599.1069 | 17930.5976 | 23000 | 8395 | -9535.5976 | 0%
Valencia Terrace |  | 0 | 14941 | 119528 | 22.6379 | 4131.4129 | 23375.1 | 386.3333 | 372.3333 | 0.96376 | 22528.0299 | 2252.803 | 6384.2159 | 18022.424 | 24406.6398 | 36000 | 13140 | -11266.6398 | 0%
Venetian Village |  | 0 | 7408 | 59264 | 11.2242 | 2048.4242 | 9935.1 | 168.75 | 95.5 | 0.56593 | 5622.5307 | 562.2531 | 2610.6773 | 4498.0245 | 7108.7018 | 10000 | 3650 | -3458.7018 | 0%
Village Water |  | 0 | 17445 | 139560 | 26.4318 | 4823.8068 | 22275.5 | 333.3333 | 174.5 | 0.5235 | 11661.2243 | 1166.1224 | 5989.9292 | 9328.9794 | 15318.9086 | 34000 | 12410 | -2908.9086 | 0%
The Woods | 4850 | 29100 |  | 0 | 5.5114 | 1005.8239 | 3728.6 | 78 | 74 | 0.94872 | 3537.3897 | 353.739 | 1359.5628 | 2829.9118 | 4189.4746 | 9000 | 3285 | -904.4746 | 0%
Zephyr Shores | N/A Interconnected
Column Notes
| 1,2 | From MFRs map verified
| 7,8,9 | From MFRs
| 10 | Ratio of water to Wastewater ERCs
| 14 | column 14 plus column 6
| 17 | from DMR analysis

## Template
SANDALHAVEN
Line | Description
1 | Test Year Flows(1)
2 | from Schedule F-2
3 | gallons per day (gpd)
4
5 | Growth Adjustment
6 | Test Year ERCs(2)
7 | Annual Growth Using Linear Regression (ERCs/yr)(3)
8 | Growth for Five year Period (ERCs)
9 | Test Year gpd/ERC (Line 3 /Line 6)
10 | Growth Allowance (gpd) (Line 8*Line 9)
11
12 | Test year Flow Plus Growth Allowance (Line 3+line 10)
13
14 | Inflow/Infiltration Adjustment
15 | Excess I&I (gpy)
16 | Excess I&I (gpd)
17
18 | Test year Flow with Growth Allowance Less I&I (Line 12-Line 14)
19
20 | Capacity (gpd)
21
22 | Used and Useful Percentage
23 | Non-Used and Useful Percentage
Notes
(1) Since the decomissioning of the WWTP all Sandalhaven flow pass through the force main and is treated by EWD
(2) From MFR Schedue F-10
(3) Linear regression results in negtive growth

## Crownwood
Crownwood
Line | Description
1 | Test Year Flows(1)
2 | Max Three Month (gpd) | 20666.6667
3
4 | Growth Adjustment
5 | Test Year ERCs(2) | 573
6 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 3
7 | Growth for Five year Period (ERCs) | 17
8 | Test Year gpd/ERC (Line 2 /Line 5) | 36.0675
9 | Growth Allowance (gpd) (Line 8*Line 7) | 613.1472
10
11 | Test year Flow Plus Growth Allowance (Line 2+line 9) | 21279.8138
12
13 | Inflow/Infiltration Adjustment
14 | Excess I&I (gpy) | 0
15 | Excess I&I (gpd) | 0
16
17 | Test year Flow with Growth Allowance Less I&I (Line 11-Line 15) | 21279.8138
18
19 | Capacity (gpd) | 40000
20
21 | Used and Useful Percentage | 53.2%
22 | Non-Used and Useful Percentage | 46.8%
Notes
(1) From test year DMRs
(2) From MFR Schedue F-10
(3) From MFR Schedue F-10

## Crownwood Flow
|  | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.025
| Feb | 0.025
| Mar | 0.031 | 0.027
| Apr | 0.018 | 0.024667
| May | 0.016 | 0.021667
| Jun | 0.019 | 0.017667
| Jul | 0.018 | 0.017667
| Aug | 0.018 | 0.018333
| Sept | 0.017 | 0.017667
| Oct | 0.017 | 0.017333
| Nov | 0.017 | 0.017
| Dec | 0.017 | 0.017
2015 | Jan | 0.019 | 0.017667
| Feb | 0.025 | 0.020333
| Mar | 0.018 | 0.020667
| Apr | 0.016 | 0.019667
| May | 0.016 | 0.016667
| Jun | 0.014 | 0.015333
| Jul | 0.015 | 0.015
| Aug | 0.015 | 0.014667
| Sept | 0.016 | 0.015333
| Oct | 0.014 | 0.015
| Nov | 0.016 | 0.015333
| Dec | 0.017 | 0.015667
2015 | Ann Avg | 0.01675
| Max Mo | 0.025
| Max 3 Mo | 0.020667

## LUSI 2
LUSI
Line | Description
1 | Test Year Flows(1)
2 | Annual Average (MGD) | 0.45207
3
4 | Growth Adjustment
5 | Test Year ERCs(2) | 3441
6 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 126.2
7 | Growth for Five year Period (ERCs) | 631
8 | Test Year gpd/ERC (Line 2 /Line 5) | 131.3775
9 | Growth Allowance (MGD) (Line 8*Line 7) | 0.082899
10
11 | Test year Flow Plus Growth Allowance (Line 2+line 9) | 0.53497
12
13 | Inflow/Infiltration Adjustment
14 | Excess I&I (gpy) | 0
15 | Excess I&I (gpd) | 0
16
17 | Test year Flow with Growth Allowance Less I&I (Line 11-Line 15) | 0.53497
18
19 | Capacity (MGD) | 0.999
20
21 | Used and Useful Percentage | 53.55%
22 | Non-Used and Useful Percentage | 46.45%
Notes
(1) From test year DMRs
(2) From MFR Schedue F-10
(3) From MFR Schedue F-10

## LUSI Flow
|  | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.384
| Feb | 0.422
| Mar | 0.444 | 0.41667
| Apr | 0.422 | 0.42933
| May | 0.402 | 0.42267
| Jun | 0.404 | 0.40933
| Jul | 0.424 | 0.41
| Aug | 0.416 | 0.41467
| Sept | 0.395 | 0.41167
| Oct | 0.396 | 0.40233
| Nov | 0.411 | 0.40067
| Dec | 0.446 | 0.41767
2015 | Jan | 0.48484 | 0.44728
| Feb | 0.495 | 0.47528
| Mar | 0.531 | 0.50361
| Apr | 0.45 | 0.492
| May | 0.409 | 0.46333
| Jun | 0.411 | 0.42333
| Jul | 0.484 | 0.43467
| Aug | 0.45 | 0.44833
| Sept | 0.408 | 0.44733
| Oct | 0.442 | 0.43333
| Nov | 0.474 | 0.44133
| Dec | 0.386 | 0.434
2015 | Ann Avg | 0.45207
| Max Mo | 0.531
| Max 3 Mo | 0.50361

## Mid County 2
MID COUNTY
Line | Description
1 | Test Year Flows(1)
2 | Annual Average (MGD) | 0.78942
3
4 | Growth Adjustment
5 | Test Year ERCs(2) | 2001
6 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 27.2
7 | Growth for Five year Period (ERCs) | 136
8 | Test Year gpd/ERC (Line 2 /Line 5) | 394.5111
9 | Growth Allowance (MGD) (Line 8*Line 7) | 0.053654
10
11 | Test year Flow Plus Growth Allowance (Line 2+line 9) | 0.84307
12
13 | Inflow/Infiltration Adjustment
14 | Excess I&I (gpy) | 0
15 | Excess I&I (gpd) | 0
16
17 | Test year Flow with Growth Allowance Less I&I (Line 11-Line 15) | 0.84307
18
19 | Capacity (gpd) | 0.9
20
21 | Used and Useful Percentage | 93.67%
22 | Non-Used and Useful Percentage | 6.326%
Notes
(1) From test year DMRs
(2) From MFR Schedue F-10
(3) From MFR Schedue F-10

## Mid County Flow
|  | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.626
| Feb | 0.682
| Mar | 0.729 | 0.679
| Apr | 0.72 | 0.71033
| May | 0.71 | 0.71967
| Jun | 0.75 | 0.72667
| Jul | 0.758 | 0.73933
| Aug | 0.733 | 0.747
| Sept | 0.847 | 0.77933
| Oct | 0.772 | 0.784
| Nov | 0.7 | 0.773
| Dec | 0.723 | 0.73167
2015 | Jan | 0.679 | 0.70067
| Feb | 0.722 | 0.708
| Mar | 0.757 | 0.71933
| Apr | 0.683 | 0.72067
| May | 0.875 | 0.77167
| Jun | 0.736 | 0.76467
| Jul | 0.916 | 0.84233
| Aug | 1.098 | 0.91667 | rain event
| Sept | 0.931 | 0.98167
| Oct | 0.712 | 0.91367
| Nov | 0.697 | 0.78
| Dec | 0.667 | 0.692
2015 | Ann Avg | 0.78942
| Max Mo | 1.098
| Max 3 Mo | 0.98167

## Sandalhaven
SANDALHAVEN
Line | Description | Capacity Fees paid to EWD | Master Lift Station | Pumping Plant | Force Main
1 | Test Year Flows(1)
2 | from Schedule F-2 | 50.474 | 29.847 | 29.847 | 50.474
3 | gallons per day (gpd) | 138284.9315 | 81772.6027 | 81772.6027 | 138284.9315
4
5 | Growth Adjustment
6 | Test Year ERCs(2) | 1365 | xx | xx | 1365
7 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 0 | 0 | 0 | 0
8 | Growth for Five year Period (ERCs) | 0 | 0 | 0 | 0
9 | Test Year gpd/ERC (Line 3 /Line 6) | 101.3076 | xx | xx | 101.3076
10 | Growth Allowance (gpd) (Line 8*Line 9) | 0 | xx | xx | 0
11
12 | Test year Flow Plus Growth Allowance (Line 3+line 10) | 138284.9315 | 81772.6027 | 81772.6027 | 138284.9315
13
14 | Inflow/Infiltration Adjustment
15 | Excess I&I (gpy)(4) | 4225818.9773 | 2498871.0824 | 2498871.0824 | 4225818.9773
16 | Excess I&I (gpd) | 11577.5862 | 6846.2221 | 6846.2221 | 11577.5862
17
18 | Test year Flow with Growth Allowance Less I&I (Line 12-Line 16) | 126707.3453 | 74926.3806 | 74926.3806 | 126707.3453
19
20 | Capacity (gpd) | 300000 | 665000 | 275000 | 935000
21
22 | Used and Useful Percentage | 42.24% | 11.27% | 27.25% | 13.55%
23 | Non-Used and Useful Percentage | 57.76% | 88.73% | 72.75% | 86.45%
Notes
(1) Since the decomissioning of the WWTP all Sandalhaven flow pass through the force main and is treated by EWD
(2) From MFR Schedue F-10
(3) Linear regression results in negtive growth
| (4) Excess I&I for Master Lift Station and Pumping Plant calculated as follows. |  | Total | Lift Station | Pumps
|  | Test Year Flow | 50474000 | 29847000 | 29847000
|  | Ratio to Total | 100% | 59.13% | 59.13%
|  | Total Excess I&I | 4225818.9773 | 4225818.9773 | 4225818.9773
|  | Allocated I&I | 4225818.9773 | 2498871.0824 | 2498871.0824

## Sandalhaven Flow
|  | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.626
Feb
| Mar |  | 0.626
| Apr |  | #DIV/0!
| May |  | #DIV/0!
| Jun |  | #DIV/0!
| Jul |  | #DIV/0!
| Aug |  | #DIV/0!
| Sept |  | #DIV/0!
| Oct |  | #DIV/0!
| Nov |  | #DIV/0!
| Dec |  | #DIV/0!
2015 | Jan | 0.17857 | 0.17857
| Feb | 0.18471 | 0.18164
| Mar | 0.18839 | 0.18389
| Apr | 0.14923 | 0.17411
| May | 0.10745 | 0.14836
| Jun | 0.13877 | 0.13182
| Jul | 0.11977 | 0.122
| Aug | 0.10497 | 0.12117
| Sept | 0.10707 | 0.1106
| Oct | 0.11284 | 0.10829
| Nov | 0.13083 | 0.11691
| Dec | 0.14619 | 0.12996
2015 | Ann Avg | 0.13907
| Max Mo | 0.18839
| Max 3 Mo | 0.18389

## Lake Placid 2
LAKE PLACID
Line | Description
1 | Test Year Flows(1)
2 | Annual Average (MGD) | 0.018417
3
4 | Growth Adjustment
5 | Test Year ERCs(2) | 349
6 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 31.8
7 | Growth for Five year Period (ERCs) | 159
8 | Test Year gpd/ERC (Line 2 /Line 5) | 52.7698
9 | Growth Allowance (MGD) (Line 8*Line 7) | 0.0083904
10
11 | Test year Flow Plus Growth Allowance (Line 2+line 9) | 0.026807
12
13 | Inflow/Infiltration Adjustment
14 | Excess I&I (gpy) | 0
15 | Excess I&I (gpd) | 0
16
17 | Test year Flow with Growth Allowance Less I&I (Line 11-Line 15) | 0.026807
18
19 | Capacity (gpd) | 0.09
20
21 | Used and Useful Percentage | 29.79%
22 | Non-Used and Useful Percentage | 70.21%
Notes
(1) From test year DMRs
(2) From MFR Schedue F-10
(3) From MFR Schedue F-10

## Lake Placid flow
|  | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.019
| Feb | 0.022
| Mar | 0.02 | 0.020333
| Apr | 0.014 | 0.018667
| May | 0.012 | 0.015333
| Jun | 0.012 | 0.012667
| Jul | 0.023 | 0.015667
| Aug | 0.02 | 0.018333
| Sept | 0.024 | 0.022333
| Oct | 0.019 | 0.021
| Nov | 0.017 | 0.02
| Dec | 0.016 | 0.017333
2015 | Jan | 0.021 | 0.018
| Feb | 0.023 | 0.02
| Mar | 0.025 | 0.023
| Apr | 0.018 | 0.022
| May | 0.016 | 0.019667
| Jun | 0.019 | 0.017667
| Jul | 0.014 | 0.016333
| Aug | 0.016 | 0.016333
| Sept | 0.019 | 0.016333
| Oct | 0.014 | 0.016333
| Nov | 0.015 | 0.016
| Dec | 0.021 | 0.016667
2015 | Ann Avg | 0.018417
| Max Mo | 0.025
| Max 3 Mo | 0.023

## Labrador 2
LABRADOR
Line | Description
1 | Test Year Flows(1)
2 | Max Three Month (MGD) | 0.087667
3
4 | Growth Adjustment
5 | Test Year ERCs(2) | 1081
6 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 0
7 | Growth for Five year Period (ERCs) | 0
8 | Test Year gpd/ERC (Line 2 /Line 5) | 81.0977
9 | Growth Allowance (MGD) (Line 8*Line 7) | 0
10
11 | Test year Flow Plus Growth Allowance (Line 2+line 9) | 0.087667
12
13 | Inflow/Infiltration Adjustment
14 | Excess I&I (gpy) | 0
15 | Excess I&I (gpd) | 0
16
17 | Test year Flow with Growth Allowance Less I&I (Line 11-Line 15) | 0.087667
18
19 | Capacity (gpd) | 0.216
20
21 | Used and Useful Percentage | 40.59%
22 | Non-Used and Useful Percentage | 59.41%
Notes
(1) From test year DMRs
(2) From MFR Schedue F-10
(3) Linear regression results in negtive growth

## Labrador Flow
|  | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.069
| Feb | 0.074
| Mar | 0.081 | 0.074667
| Apr | 0.052 | 0.069
| May | 0.032 | 0.055
| Jun | 0.027 | 0.037
| Jul | 0.037 | 0.032
| Aug | 0.035 | 0.033
| Sept | 0.035 | 0.035667
| Oct | 0.041 | 0.037
| Nov | 0.054 | 0.043333
| Dec | 0.067 | 0.054
2015 | Jan | 0.084 | 0.068333
| Feb | 0.092 | 0.081
| Mar | 0.087 | 0.087667
| Apr | 0.057 | 0.078667
| May | 0.03 | 0.058
| Jun | 0.026 | 0.037667
| Jul | 0.029 | 0.028333
| Aug | 0.066 | 0.040333
| Sept | 0.047 | 0.047333
| Oct | 0.042 | 0.051667
| Nov | 0.058 | 0.049
| Dec | 0.058 | 0.052667
2015 | Ann Avg | 0.056333
| Max Mo | 0.092
| Max 3 Mo | 0.087667

## Eagle Ridge 2
EAGLE RIDGE
Line | Description | Plant
1 | Test Year Flows(1)
2 | Max Three Month (MGD) | 0.23867
3
4 | Growth Adjustment
5 | Test Year ERCs(2) | 1312
6 | Annual Growth Using Linear Regression (ERCs/yr)(3) | 33
7 | Growth for Five year Period (ERCs) | 165
8 | Test Year gpd/ERC (Line 2 /Line 5) | 181.9106
9 | Growth Allowance (MGD) (Line 8*Line 7) | 0.030015
10
11 | Test year Flow Plus Growth Allowance (Line 2+line 9) | 0.26868
12
13 | Inflow/Infiltration Adjustment
14 | Excess I&I (gpy) | 0
15 | Excess I&I (gpd) | 0
16
17 | Test year Flow with Growth Allowance Less I&I (Line 11-Line 15) | 0.26868
18
19 | Capacity (gpd) | 0.318
20
21 | Used and Useful Percentage | 84.49%
22 | Non-Used and Useful Percentage | 15.51%
Notes
(1) From test year DMRs
(2) From MFR Schedue F-10
(3) Linear regression results in negtive growth

## Eagle Ridge Flow
|  | Cross Creek |  | Eagle Ridge
|  | Mo Avg. | 3 Mo Avg | Mo Avg. | 3 Mo Avg
2014 | Jan | 0.085 |  | 0.223
| Feb | 0.098 |  | 0.233
| Mar | 0.097 | 0.093333 | 0.231 | 0.229
| Apr | 0.068 | 0.087667 | 0.214 | 0.226
| May | 0.038 | 0.067667 | 0.197 | 0.214
| Jun | 0.032 | 0.046 | 0.198 | 0.203
| Jul | 0.034 | 0.034667 | 0.195 | 0.19667
| Aug | 0.035 | 0.033667 | 0.194 | 0.19567
| Sept | 0.037 | 0.035333 | 0.196 | 0.195
| Oct | 0.053 | 0.041667 | 0.204 | 0.198
| Nov | 0.062 | 0.050667 | 0.214 | 0.20467
| Dec | 0.057 | 0.057333 | 0.212 | 0.21
2015 | Jan | 0.086 | 0.068333 | 0.225 | 0.217
| Feb | 0.104 | 0.082333 | 0.236 | 0.22433
| Mar | 0.096 | 0.095333 | 0.24 | 0.23367
| Apr | 0.068 | 0.089333 | 0.24 | 0.23867
| May | 0.037 | 0.067 | 0.199 | 0.22633
| Jun | 0.035 | 0.046667 | 0.195 | 0.21133
| Jul | 0.035 | 0.035667 | 0.2 | 0.198
| Aug | 0.035 | 0.035 | 0.204 | 0.19967
| Sept | 0.04 | 0.036667 | 0.204 | 0.20267
| Oct | 0.045 | 0.04 | 0.194 | 0.20067
| Nov | 0.057 | 0.047333 | 0.218 | 0.20533
| Dec | 0.056 | 0.052667 | 0.214 | 0.20867
2015 | Ann Avg | 0.057833 |  | 0.21408
| Max Mo | 0.104 |  | 0.24
| Max 3 Mo | 0.095333 |  | 0.23867