## Firm Capacity %
DRAFT | DBCEC 003945
Hourly Firm Capacity Pecentages of Nameplate Rating for Solar
FPLC - DeSoto, Florida
Lat: N 27.3 ; Lon: W 81.8 (WGS84)
Axis Tilt | F20 | degrees
Azimuth | 195 | degrees
AC Size | 75 | MW
DC to AC Ratio | 1.5
Net Capacity Factor - SunEdison 345W - F20 - SMA 750CP-US | Column Labels
Hour Ending | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
1 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
2 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
3 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
4 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
5 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
6 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
7 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
8 | 0.0015% | 1.923% | 0% | 1.95% | 6.273% | 6.608% | 5.336% | 2.062% | 0.03766% | 0% | 8.35% | 0.4317% | 2.738%
9 | 23.85% | 26.18% | 10.29% | 18.69% | 22.78% | 20.89% | 19% | 16.97% | 15.17% | 14.03% | 36.97% | 26.84% | 20.91%
10 | 51.11% | 52.17% | 37.74% | 47.9% | 48.92% | 43.51% | 43.09% | 41.87% | 40.55% | 41.61% | 60.28% | 50.43% | 46.54%
11 | 71.35% | 72.59% | 63.66% | 71.9% | 70.39% | 63.47% | 64.1% | 63.61% | 62.19% | 65.05% | 76.92% | 68.45% | 67.76%
12 | 80.44% | 79.58% | 80.83% | 87.15% | 85.34% | 76.51% | 76.27% | 77.55% | 76.41% | 80.17% | 82.07% | 76.12% | 79.86%
13 | 79.62% | 79.25% | 83.32% | 89.63% | 88.4% | 80.85% | 82.31% | 84.1% | 79.79% | 82.79% | 82.16% | 76.53% | 82.41%
14 | 79.54% | 76.58% | 84.07% | 88.55% | 88.5% | 79.6% | 82.07% | 80% | 78.91% | 81.19% | 79.1% | 74.88% | 81.11%
15 | 74.49% | 73.42% | 83.41% | 87.72% | 85.07% | 75.01% | 79.79% | 77.46% | 76.68% | 79.76% | 68.92% | 66.17% | 77.36%
16 | 62.25% | 65.98% | 80% | 84.89% | 80.25% | 68.78% | 69.43% | 68.96% | 67.63% | 72.24% | 54.71% | 54% | 69.12%
17 | 41.06% | 46.95% | 72.04% | 75.42% | 67.7% | 54.04% | 54.33% | 54.48% | 52.21% | 56.63% | 29.36% | 28.34% | 52.76%
18 | 7.937% | 19.06% | 52.91% | 53.57% | 48.22% | 38.33% | 37.57% | 34.86% | 34.47% | 32.94% | 0.2271% | 0.3392% | 30.11%
19 | 0% | 0% | 26.11% | 26.75% | 25.72% | 19.86% | 19.58% | 17.79% | 13.31% | 5.939% | 0% | 0% | 13%
20 | 0% | 0% | 0.2116% | 2.623% | 4.944% | 5.543% | 5.864% | 3.008% | 0.06354% | 0% | 0% | 0% | 1.868%
21 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
22 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
23 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
24 | [12 empty] | 0% | bar: Column Labels Jan to Column Labels Dec
Average | 23.82% | 24.74% | 28.11% | 30.7% | 30.1% | 26.37% | 26.61% | 25.95% | 24.89% | 25.51% | 24.13% | 21.77% | 26.06%

## 2022 Projected Solar Impacts
DRAFT Attorney-Client Work Product | Attorney-Client Work Product
DBCEC 003946
Projected Hourly Peak Load After Accounting For Impacts of Solar (PV) Nameplate MW Amounts Indicated Below
Year | Month | Hour Ending | Assumed Firm Capacity % for Solar at Hour Ending | 2022 Load Forecast by Hour for Summer Peak Day * | 1500 MW PV | 2000 MW PV | 2500 MW PV | 2610 MW PV
2022 | 8 | 16 | 68.96% | 24811.7936 | 23777.3596 | 23432.5482 | 23087.7369 | 23011.8784
2022 | 8 | 17 | 54.48% | 24966.6213 | 24149.36 | 23876.9395 | 23604.5191 | 23544.5866
2022 | 8 | 18 | 34.86% | 24456.6842 | 23933.7126 | 23759.3888 | 23585.0649 | 23546.7137
2022 | 8 | 19 | 17.79% | 23426.8668 | 23160.0476 | 23071.1078 | 22982.1681 | 22962.6013
2022 | 8 | 20 | 3.008% | 21898.4758 | 21853.3606 | 21838.3222 | 21823.2838 | 21819.9753
* For hour ending on peak day (w/o any solar impact)
Conclusion: Once installed PV nameplate MW level reaches 2,610 MW, FPL's remaining peak load shifts from hour-ending 17 (4 to 5 p.m.)
to hour-ending 18 (5 to 6 p.m.). During hour 18, the projected firm capacity of PV decreases from 54% of nameplate rating to
35% of nameplate rating.

## Load graph
DBCEC 003947 |  | 2017 TYSP Load Forecast for August 2022
|  | 1500 | 2000 | 2500 | 2610
Hour | Capacity Factor | Firm for 1500 | Firm for 2200 | Firm for 2500 | Firm for 2610
0.66667 | 68.96% | 1034.4341 | 1379.2454 | 1724.0568 | 1799.9153
0.70833 | 54.48% | 817.2613 | 1089.6818 | 1362.1022 | 1422.0347
0.75 | 34.86% | 522.9716 | 697.2954 | 871.6193 | 909.9705
0.79167 | 17.79% | 266.8192 | 355.759 | 444.6987 | 464.2655
0.83333 | 3.008% | 45.1152 | 60.1536 | 75.192 | 78.5005
Hour | Load Forecast | Remaining Load w/ 1500 MW PV | Remaining Load w/ 2000 MW PV | Remaining Load w/ 2500 MW PV | Remaining Load w/ 2610 MW PV
0.66667 | 24811.7936 | 23777.3596 | 23432.5482 | 23087.7369 | 23011.8784
0.70833 | 24966.6213 | 24149.36 | 23876.9395 | 23604.5191 | 23544.5866
0.75 | 24456.6842 | 23933.7126 | 23759.3888 | 23585.0649 | 23546.7137
0.79167 | 23426.8668 | 23160.0476 | 23071.1078 | 22982.1681 | 22962.6013
0.83333 | 21898.4758 | 21853.3606 | 21838.3222 | 21823.2838 | 21819.9753

## Calculations
DBCEC 003948
Projected Solar Impact on Hourly Load
|  | PV Nameplate MW = | PV Nameplate MW = | PV Nameplate MW = | PV Nameplate MW =
Hour Ending | Solar Firm Capacity % | 1500 | 2000 | 2500 | 2610
16 | 68.96% | 1034.4341 | 1379.2454 | 1724.0568 | 1799.9153
17 | 54.48% | 817.2613 | 1089.6818 | 1362.1022 | 1422.0347
18 | 34.86% | 522.9716 | 697.2954 | 871.6193 | 909.9705
19 | 17.79% | 266.8192 | 355.759 | 444.6987 | 464.2655
20 | 3.008% | 45.1152 | 60.1536 | 75.192 | 78.5005
Hour Ending | Forecasted Hourly Load Before PV Impact | Projected Hourly Load After PV Impact
16 | 24811.7936 | 23777.3596 | 23432.5482 | 23087.7369 | 23011.8784
17 | 24966.6213 | 24149.36 | 23876.9395 | 23604.5191 | 23544.5866
18 | 24456.6842 | 23933.7126 | 23759.3888 | 23585.0649 | 23546.7137
19 | 23426.8668 | 23160.0476 | 23071.1078 | 22982.1681 | 22962.6013
20 | 21898.4758 | 21853.3606 | 21838.3222 | 21823.2838 | 21819.9753