## Econimic Results
Filename: 2016 SE Florida Study Additional Plans to Address Questions(6)
DRAFT Attorney-Client Work Product
SE Florida Study: Economic Results for Iteration # 4
(CPVRR, millions, 2017$, 2017-2061)
| Early Fort Lauderdale Retirement Question |  |  | Retirement of Two 800 MW Units Question
| -1 | -2 |  |  | -1 | -2
| Resource Plan 2 | Modified Plan 2 to Address |  |  | Resource Plan 1 | Modified Plan 1 to Address
| (from Iteration # 1) | Early PFL Retirement Question |  |  | (from Iteration # 1) | Retirement of Two 800 MW Units
Year | Unit Additions | Unit Additions |  | Year | Unit Additions | Unit Additions
2018 | --- | CSQ line in-service 12/31/2018 |  | 2018 | --- | CSQ line in-service 12/31/2018
2019 | OCEC | OCEC; Lauderdale 4 & 5 retired 1/1/2019 |  | 2019 | OCEC | OCEC
2020 | 300 MW Solar | 250 MW PPA; 300 MW Solar |  | 2020 | 300 MW Solar | 300 MW Solar
2021 | --- | 100 MW PPA |  | 2021 | --- | Martin 1 & 2 retired; new Martin CC # 1 added
2022 | OCEC Incremental MW | OCEC Incremental MW; Ft. Lauderdale 2x1 CC (1,163 MW) |  | 2022 | OCEC Incremental MW | OCEC Incremental MW
2023 | 1,414 MW Solar | 1,414 MW Solar |  | 2023 | 1,414 MW Solar | 1,414 MW Solar
2024 | --- | --- |  | 2024 | --- | ---
2025 | Okeechobee CC | 100 MW PPA |  | 2025 | Martin CC | Martin CC
2026 | --- | Okeechobee CC |  | 2026 | --- | ---
2027 | --- | --- |  | 2027 | --- | ---
2028 | Martin CC | Martin CC |  | 2028 | Okeechobee CC | Okeechobee CC
2029 | --- | --- |  | 2029 | --- | ---
2030 | --- | --- |  | 2030 | --- | ---
(1) Generation & Fuel Costs | 94902 | 94963.8651 |  | (1) Generation & Fuel Costs | 94901 | 95274.8619
(2) Pipeline Costs | 20 | 21.8985 |  | (2) Pipeline Costs | 23 | 18.9563
(3) Transmission Integration Costs | 319 | 401.2523 |  | (3) Transmission Integration Costs | 317 | 502.322
(4) Resource Plan Total Costs | 95241 | 95387.0159 |  | (4) Resource Plan Total Costs | 95241 | 95796.1402
(5) Difference from Lowest Cost Plan |  | 146.0159 | -95241 | #VALUE! | 0 | 555.1402
Note: Solar MW total is unchanged from that used in Iterations # 1 and # 2. The annual totals have been changed because the focus of these additional
has now changed to earlier than 2025. The new annual solar values are now based on the planned SOBRA roll out.
EMT: | - No new pipeline so just checking to see if any pipeline / firm |  |  | EMT: | - Any change in firm gas costs w/ 3 CCs added instead of 2?
| gas costs should be accounted for |  |  | E&C: | - Need cost info for two CCs at Martin coming in-service three
E&C: | - Need costs for earlier repowering and for a one-year later CC |  |  |  | years apart.
| at Okeechobee (unless this is simply a one-year escalation) |  |  | TSP: | - Need interconnection and integration cost review.
TSP: | - Need integration cost review |  |  | PGD: | - To supply cost projection to keep existing units operating.
PGD: | - To supply cost projection to keep existing units operating.

## Iteration Plan Compare
Filename: 2016 SE Florida Study Additional Plans to Address Questions(6)
DRAFT Attorney-Client Work Product
SE Florida Study Iteration #1 and Iteration #4 Comparison: Economic Results for Iteration #4*
(CPVRR, millions, 2017$, 2017-2061)
Iteration / Plan | Generation |  | Transmission | Transmission | Pipeline |  | Capital | Firm Gas |  | Total |  | Startup |  | Total Fuel/VOM | Total
| Capital | Land | Interconnection | TX Integration | Capital | Generation | Replacement | Transport | Short Term | Fixed | System | + VOM | Emission | Startup/Emissions | Annual
| FPL | Capital | Costs | Costs | Costs | Fixed O&M** | Charges** | Costs | Purchase | Costs | Net Fuel | Costs | Costs | Costs | Costs
| (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions)
Iteration#4 Plan 1 (Ft Lauderdale Retirement) | 6500.3589 | 0 | 389.6977 | 401.2523 | 21.8985 | 332.2359 | 634.4802 | 0 | 22.7267 | 8302.6501 | 63190.0913 | 1013.7013 | 22880.5732 | 87084.3658 | 95387.0159
Iteration#1 Plan 2 | 5844.9531 | 0 | 378.4874 | 317.2315 | 23.0058 | 385.643 | 837.6914 | 0 | 11.7393 | 7798.7515 | 63444.3379 | 998.6547 | 22999.5644 | 87442.557 | 95241.3085
Differential | -655.4057 | 0 | -11.2103 | -84.0208 | 1.1073 | 53.407 | 203.2112 | 0 | -10.9873 | -503.8986 | 254.2467 | -15.0467 | 118.9912 | 358.1912 | -145.7073
Iteration / Plan | Generation |  | Transmission | Transmission | Pipeline |  | Capital | Firm Gas |  | Total |  | Startup |  | Total Fuel/VOM | Total
| Capital | Land | Interconnection | TX Integration | Capital | Generation | Replacement | Transport | Short Term | Fixed | System | + VOM | Emission | Startup/Emissions | Annual
| FPL | Capital | Costs | Costs | Costs | Fixed O&M** | Charges** | Costs | Purchase | Costs | Net Fuel | Costs | Costs | Costs | Costs
| (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions)
Iteration#4 Plan 2 (Martin Retirement) | 7065.9783 | 0 | 453.4001 | 502.322 | 18.9563 | 332.1083 | 931.1848 | 0 | 11.7393 | 9315.6892 | 62707.8472 | 1026.1303 | 22746.4736 | 86480.4511 | 95796.1402
Iteration#1 Plan 1 | 5845.9619 | 0 | 378.2931 | 319.1334 | 19.9171 | 385.7837 | 837.6914 | 0 | 11.7393 | 7798.5201 | 63444.3379 | 998.6547 | 22999.5644 | 87442.557 | 95241.0771
Differential | -1220.0164 | 0 | -75.1069 | -183.1886 | 0.96081 | 53.6754 | -93.4934 | 0 | 0 | -1517.1691 | 736.4908 | -27.4756 | 253.0908 | 962.1059 | -555.0631
* Note: The book balance for the existing Lauderdale and Martin units are not yet accounted for. Early recovery of those costs would negatively affect the two early retirement plans.
** Note: The values for Iteration #4 represent the incremental costs of installing a new CC minus the operational savings of retiring the old CC.
Differential
IT 4 FL Retire -
IT 4 MR Retire | -565.6195 | 0 | -63.7024 | -101.0698 | 2.9421 | 0.12764 | -296.7046 | 0 | 10.9873 | -1013.0391 | 482.2441 | -12.429 | 134.0996 | 603.9147 | -409.1244
| ok | ok | ? Rick | ok - diff between | ok | ok | 2x1 vs 3x1 | ok | ok
neg is FL is cheaper |  |  |  | Sheridan line |  |  | is ~$60M
| diff bet 2x1 & |  |  | & 2nd AutoTx |  |  | diff of avoided
| 3x1 CC is $406 | [5 empty] | capex between
| Eq Filler $111 | [5 empty] | FL4&5 & MR1&2
is $202M
| 565 | [5 empty] | Eq Filler diff
| 1 | [5 empty] | 17
In-serv yr diff
&18
297
0

## Appendix
| Generation |  | TX | Capital |  | Total Fuel/VOM/Startup/ | -1 | (2) Pipeline | Total Generation & Fuel | (3) Transmission | (4) Resource | (5) Difference
| and Land | Generation | Interconnection | Replacement | Short Term | Emission | Generation | Capital | + Pipeline | Integration | Plan | from Lowest
| Capital | Fixed O&M | Capital FPL | Charges | Purchase | Costs | & Fuel Costs | Costs * | Costs | Costs * | Total Costs | Cost Plan
| (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions) | (Millions)
Iteration#4 Plan - Lauderdale Retirement | 6500.3589 | 332.2359 | 389.6977 | 634.4802 | 22.7267 | 87084.3658 | 94963.8651 | 21.8985 | 94985.7636 | 401.2523 | 95387.0159 | 0
Iteration#4 Plan - Martin Retirement | 7065.9783 | 332.1083 | 453.4001 | 931.1848 | 11.7393 | 86480.4511 | 95274.8619 | 18.9563 | 95293.8182 | 502.322 | 95796.1402 | 409.1244