## Gen Options
DRAFT Attorney-Client Work Product | [6 empty] | Filename: 2016 SE Florida Study Generation Options for Iteration # 2 8 11 2016
8 11 2016
SE Florida Study: Iteration # 2 - Generation Options Under Consideration
-1 | -2 | -3 | -4 | -5 | -6 | -7 | -8
Option Number | Site (County) | Technology | Net MW | Mutually Exclusive to: | Requires New Gas Pipeline from Martin/Hendry ? | EMT & ENV view this resource option as having at least a reasonable probability of success in permitting & constructing a new pipeline by mid-2022 | E&C and ENV view this resource option as having at least a reasonable probability of success in permitting & constructing new generation by mid-2023
1 | Turkey Point (Miami-Dade) | CC | 1751 | --- | Yes | Yes | Yes
2 | Turkey Point (Miami-Dade) | 2 CTs | 469 | --- | No - Will be oil-fired (except when gas is available from TP Unit 5 | Not Applicable | Yes
3 | Andytown (Broward) * | CC | 1751 | Option 4 | Yes | Yes | Yes
4 | Andytown (Broward) * | 2 CTs | 469 | Option 3 | Yes or No (depending upon the resource plan) | Yes | Yes
5 | MDLPAS (Miami-Dade) | CC | 1751 | --- | Yes | Yes | Yes
6 | Fort Lauderdale | Repower existing CCs | 867 (for 1,751 MW CC) or 316 (for 1,200 MW CC) | -- | Yes for 1,751 MW CC. The 1,200 MW CC repowering may require additional compression on FGT. | Yes | Yes
Note: | - Assumption from J. Hampp is that a maximum of approximately 2,250 MW of fossil capacity (CC and/or CT) could be permitted in
Miami-Dade County. Capacity at Andytown in Broward does not affect this upper limit for Miami-Dade.

## Resource Plans
DRAFT Attorney-Client Work Product | [8 empty] | Filename: 2016 SE Florida Study Generation Options for Iteration # 2 8 11 2016
8 11 2016
SE Florida Study: Iteration # 2 - Resource Plans To Be Considered
(A representative list)
Scenario 1: Assumes a new CC is built at Hendry in 2025 with a new pipeline to Hendry by mid-2024. In most cases, a pipeline extension is then needed to serve generation several
years later as shown below.
|  | Generation COD (By Date Shown) | Generation COD (By Date Shown) | Miami-Dade MW | Broward & Miami-Dade MW | Total System MW | Meets 2250 MW Dade Limit? | Meets 3462 MW System Need? | Comment / Question
Anchored by Hendry CC | 1 | Hendry CC (2025) | Andytown CC (2028) | 0 | 1751 | 3502 | Yes | Yes | ---
| 2 | Hendry CC (2025) | Turkey Point CC (2028) | 1751 | 1751 | 3502 | Yes | Yes | ---
" | 3 | Hendry CC (2025) | MDLPAS CC (2028) | 1751 | 1751 | 3502 | Yes | Yes | ---
" | * | Hendry CC | 2 CTs at Hendry and 2 CTs at Andytown (plus 2 FGT-fueled CTs at Pennsuco and 2 oil-fired CTs at Turkey Point) | 938 | 1407 | 3627 | Yes | Yes | Assume FPL would not extend pipeline to Broward for 2 CTs. Dismiss plan. *
" | * | Hendry CC | 2 CTs at Hendry and 2 CTs at MDLPAS (plus 2 FGT-fueled CTs at Pennsuco and 2 oil-fired CTs at Turkey Point) | 1407 | 1407 | 3627 | Yes | Yes | Assume FPL would not extend pipeline to Miami-Dade for 2 CTs. Dismiss plan. *
" | ** | Hendry CC (pipeline stops at Hendry) | 2 CTs at Hendry (plus 2 FGT-fueled CTs at Pennsuco and 2 oil-fired CTs at Turkey Point) | 938 | 938 | 3158 | Yes | No | Would require ~ 350 MW of PV, battery, CTs, and/or PPA **
" | 4 | Hendry CC (2025) | 2 CTs at Andytown, and 2 CTs at Turkey Point, running on oil until the new pipeline is built (CT COD in 2024), plus repower Fort Lauderdale CCs (2028) with the 4 new CTs then switching to gas | 469 | 1805 | 3556 | Yes | Yes | Repower with a 1,751 MW CC (New pipeline from Hendry to Ft. Lauderdale needed by mid-2027)
" | 5 | Hendry CC (2025) (pipeline stops at Hendry) | 2 oil-fired CTs at Andytown and 2 oil-fired CTs at Turkey Point ( 2024), plus smaller repower at Fort Lauderdale CCs (2028), plus 2 CTs at Hendry (2028) | 469 | 1254 | 3474 | Yes | Yes | Would utilize a smaller 2x1 CC repower of approximately 1,200 MW which may require FGT compression.
Scenario 2: Assumes no new CC is built at Hendry in 2025 so a new pipeline would have to start at Martin to serve new gas-fired generation in Broward or Miami-Dade for COD by mid-2024.
|  | Generation COD (By Date Shown) | Generation COD (By Date Shown) | Miami-Dade MW | Broward & Miami-Dade MW | Total System MW | Meets 2250 MW Dade Limit? | Meets 3462 MW System Need? | Comment / Question
Turkey Point CC - centric | ** | Turkey Point CC | 2 CTs at Andytown and 2 gas-fired CTs at Turkey Point | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
| ** | Turkey Point CC | 2 CTs at Andytown (plus 2 FGT-fueled CTs at Pennsuco) | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
" | ** | Turkey Point CC | 2 CTs at Andytown and 2 CTs at MDLPAS | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
Turkey Point CC - centric | 6 | Turkey Point CC (2025) | Andytown CC (2028) | 1751 | 3502 | 3502 | Yes | Yes | ---
| 7 | Turkey Point CC (2025) | Hendry CC (2028) | 1751 | 1751 | 3502 | Yes | Yes | ---
" | ** | 2 CTs at Andytown and 2 gas-fired CTs at Turkey Point | Turkey Point CC | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
" | ** | 2 CTs at Andytown (plus 2 FGT-fueled CTs at Pennsuco) | Turkey Point CC | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
" | ** | 2 CTs at Andytown and 2 CTs at MDLPAS | Turkey Point CC | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
Andytown CC - centric | 8 | Andytown CC (2025) | Turkey Point CC (2028) | 1751 | 3502 | 3502 | Yes | Yes | ---
| 9 | Andytown CC (2025) | MDLPAS CC (2028) | 1751 | 3502 | 3502 | Yes | Yes | ---
" | 10 | Andytown CC (2025) | Hendry CC (2028) | 0 | 1751 | 3502 | Yes | Yes | ---
" | 11 | MDLPAS CC (2025) | Andytown CC (2028) | 1751 | 3502 | 3502 | Yes | Yes | ---
" | ** | Andytown CC | 2 CTs at MDLPAS (plus 2 FGT-fueld CTs at Pennsuco and 2 Oil-fired CTs at Turkey Point) | 1407 | 3158 | 3158 | Yes | No | Would require ~ 350 MW of PV, battery, CTs, and/or PPA **
" | ** | 2 CTs at MDLPAS (plus 2 FGT-fueld CTs at Pennsuco and 2 Oil-fired CTs at Turkey Point) | Andytown CC | 1407 | 3158 | 3158 | Yes | No | Would require ~ 350 MW of PV, battery, CTs, and/or PPA **
MDLPAS CC - centric | 12 | MDLPAS CC (2025) | Hendry CC (2028) | 1751 | 1751 | 3502 | Yes | Yes | ---
| ** | MDLPAS CC | 2 CTs at Andytown (and 2 oil-fired CTs at Turkey Point) | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
" | ** | MDLPAS CC | 2 CTs at Andytown (plus 2 FGT-fueled CTs at Pennsuco) | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
" | ** | 2 CTs at Andytown (and 2 oil-fired CTs at Turkey Point) | MDLPAS CC | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
" | ** | 2 CTs at Andytown (plus 2 FGT-fueled CTs at Pennsuco) | MDLPAS CC | 2220 | 2689 | 2689 | Yes | No | Would require ~ 850 MW of PV, battery, CTs, and/or PPA **
Lauderdale Repower - centric | 13 | 2 CTs at Andytown, and 2 CTs at Turkey Point, running on oil until the new pipeline is built (CT COD in 2023), plus repower Fort Lauderdale CCs (2026) with the 4 new CTs then switching to gas | Hendry CC (2028) | 469 | 1805 | 3556 | Yes | Yes | New pipeline comes from Martin to Broward only by mid-2025. Repowering is with a 1,751 MW CC.
" | 14 | 2 oil-fired CTs at Andytown and 2 oil-fired CTs at Turkey Point ( 2024), plus smaller repower at Fort Lauderdale CCs (2028) | Hendry CC and Hendry 2 CTs (2025) | 469 | 1254 | 3474 | Yes | Yes | Would utilize a smaller 2x1 CC repower of approximately 1,200 MW which may require FGT compression.
** Save for Iteration # 3 when we see how much PV and/or batteries are achievable in Miami-Dade and Broward within the 2023 thru 2030 time frame.