## Sheet1
15 | Total Test Year Adjustment to Utility Plant in Service
16 | (5) Pro Forma Plant Additions: |  | Objective | Description of Work | Regulatory Mandates | Vendor | Total Project Expense to date | Cost Breakdown | Start Date | Completion date | Est Completion date
17 | 354.3 Lift Station | 146393 | Replace L2A Lift Station. Lift Station has been in service since the late 1960's and is in poor condition. It was then damaged further during Hurricane Irma causing it to be knocked over and have water intrustion. Because of its age and damages it must be completely replaced. | Remove existing lift station, excavate and install new lift station including piping discharge, electrical, panel, internal piping, valve vault including check valves and isolation valves. | Failure to replace will result in failure with exfiltration of wastewater into nearshore waters causing potential for a DEP violation. Lift Station is located adjacent to a brackish lagoon. |  | 248.75 | 146393
[6 empty] | B&L Beneway Underground Contractor |  | 140000 | 2017-10-23 |  | 2018-07-31
[6 empty] | Weiler Engineering | 248.75 | 6393 | 2017-12-08
18 | 380.4 WWTP Rehabilitation | 1104764 | Rehabilitation of two existing treatment plants/trains each rated at .250MGD each and a .056MGD stand alone digester. The corrosive nature of wastewater and the saltwater environment of the Florida Keys requires periodic rehabilitation of plant. | Repair/replace steel and other appurtenances on two DAVCO/Evoqua steel wastewater plants (West and East) originally constructed in 1983 and 1995 respectively. Also repair and replace steel on .056MGD stand alone digester. Once repairs/replacements are complete the tanks/basins are to be sand blasted and coated by a qualified industrial painting contractor. | Failure to repair or replace steel or appurtances can lead to problems with the wastewater treatment process. Should the DEP find basins that are corroded or air headers that are leaking as a result of oxidation/corrosion the finding would be a DEP violation - FAILURE TO MAINTAIN. This carries a maximum penalty of $10,000 per day per violation. |  | 95776.91 | 1118671.75
[6 empty] | Evoqua | 93433.16 | 975000 | 2017-10-15 |  | 2018-06-30
[6 empty] | Weiler Engineering | 2343.75 | 129763.75 | 2017-11-02
|  |  |  | Misc. parts for drive chain assembly (all items except for gear drive and motor), Hoist manual base plate mount, 2 winches. |  | Evoqua |  | 13908 | 2018-01-19
19 | 380.4 Chlorine Contact Chamber | 1071814 | Replacement of 4 filters and 4 chlorine contact chambers. These elements are contained within two steel trains that require replacement. The corrosive nature of wastewater and the saltwater environment of the Florida Keys requires periodic rehabilitation of plant. During Hurricane Irma, a leak occurred in the chambers which has been contained. Failure to replace the chambers will lead to additional leaks. | Remove and dispose of 2 existing steel treatment trains, each consisting of 2 filters and 2 chlorine contact chambers. Supply and install 2 new combination filtration and chlorine contact chamber structures. Remove backwash pumps, electrical, etc. and reinstall in new tank. Remove and reinstall handrails and grating system. Supply and install new filter media. Install all piping and valves to create a working system for backwash and bypass. | Failure to repair or replace steel or appurtances can lead to problems with the wastewater treatment process. Should the DEP find basins that are corroded a FAILURE TO MAINTAIN may be issued. If the steel rusts through in the chlorine contact chamber baffle wall the DEP required minimum 15 minutes of detention time may be violated. The structural integrity of the tank is questionable and has already resulted in a minor leak. If the unit is not replaced it is only a matter of time before a minor or major leak occurs and this can lead to actionable environmental fines and other enforcement actions by DEP due to the fact that known problems were not resolved. |  | 5727.5 | 1071814 |  |  | 2018-05-30
[6 empty] | Wharton-Smith Inc. |  | 935000
[6 empty] | Housing Rental Expense |  | 29325
[6 empty] | Weiler Engineering | 19552.67 | 107489 | 2017-08-03
20 | 380.4 Sludge Drying Beds | 15450 | Rehabilitate Drying Bed #1 to specification. Existing media is old and requires replacement as the drying bed is beginning to reject water. | Remove compacted silica sand layer with vacuum truck. Install pea rock to specified level, and install silica sand per specification. | DEP requires permitees to maintain their unit processes. |  | 15449.74 |  |  |  | 2017-08-04
[6 empty] | B.R.I.A.N. Inc. (vac truck) | 4250 |  | 2017-05-31 |  | 2017-08-04
[6 empty] | Silica sand supplier | 5500 |  | 2017-06-21 |  | 2017-08-04
[6 empty] | gravel (pea rock) | 1400 |  | 2017-05-09 |  | 2017-08-04
[6 empty] | material trucking | 4299.74 |  | 2017-06-07 |  | 2017-08-04
[6 empty] | KWRU (labor to install gravel layer and silica layer) |  | 0 |  |  | 2017-08-04
21 | 380.4 Generator | 321006 | Replace Kohler Standby Diesel Generator that supplies standby power to the entire treatment plant. Generator was damaged during Hurricane Irma. | Remove existing 30 year old Kohler generator, modify existing foundation or construct new foundation as necessary, supply new 800KW diesel generator, set up transfer switches, run all wiring, disconnects, and other electrical components. Supply fuel tank, venting, containment, etc. Supply access grating or like, and handrail. | Weiler Engineering to engineer foundation, and system to ensure the generator can withstand 180MPH wind acting as a sheer force per code. Nearshore Electric to perform all necessary electrical work. KWRU to procure generator. KW Welding to supply crane. Unknown General Contractor to construct foundation or foundation elements. |  | 96763.74 | 280144.98
[5 empty] | Global Power Supply Offer Number: GPSQ6863-04 | GPS MTU Genset 800KW | 94937.49 | 255874.98 | 2018-01-17 |  | 2018-06-30
[6 empty] | Weiler Engineering | 1826.25 | 24270 | 2017-10-02
22 | 371.3 Tow behind generator | 83470 | Replace 480VAC, 3 phase Gillette Generator Trailer mounted unit that was destroyed in Hurricane Irma. | Procure 480 VAC, 3 phase, 60KW diesel generator in a trailer package to provide emergency power to all lift stations throughout the service area. | Should the Power generated by the Power Company fail temporary power is necessary to power the lift stations which pump the wastewater to the plant. The trailer unit generator supplies power to the lift stations and the pumps can be run while it is connected. Without a backup source of power it is only a matter of time before sewerage backs up, eventually into residences and businesses. For this reason the DEP requires utilities to have temporary power solutions. | Pantropic Power/Kelly Tractor/Other/GPS |  | 82870.68 |  |  | 2018-02-28
23 | 390.7 Telephone System | 15000 | Provide fiber optic service to the utility to replace very unreliable COMCAST service. The service is capable of providing voice and data (internet & telephone). | Provide fiber to the WWTP location. The SCADA (supervisory control and data acquisition) system requires an internet connection. This allows 24 hour monitoring and control of the wastewater plant and the equipment. This system pushes out all of the alarms to on call personnel. This internet connection is therefore mission critical. | The monitoring and all of the alarms that the SCADA system controls were integrated into the DEP permit application. |  | 0 | 12000 |  |  | 2018-06-30
[5 empty] | phone equipment compatible with fiber optic service | AT&T |  | 4663.2
[5 empty] | Labor and materials to install fiber circuit(2 times temp and permanent office) | AT&T |  | 6488.8
[5 empty] | Service Contract | AT&T |  | 848
24 | 391.7 Service Truck with Crane | 74174 | Acquire new service truck with crane to allow the Utility to pull all of its pumps and equipment safely without having to rely on outside contractors or rental companies to supply this equipment. | KWRU to procure a crane truck with the base weight and crane load capacity to pull and service all of the utility's pumps and other equipment (i.e. Monroe County Detention Center pumps, vacuum sewerage pumps, etc.). | None, however a Utility employee sustained an injury when using a tripod to pull a pump from the lift station with a manual winch. This injury could have been avoided if the Utility had a crane truck at the time the injury occurred. Moreover, the utility has expended significant funds renting cranes and other equipment to lift heavier utility equipment. |  | 40617.41 | 53700.56 |  |  | 2018-03-01
[6 empty] | KKS Auto Sales Used 2011 Ford Utility Truck | 40163.02 | 40163.02 | 2017-12-07 | 2017-12-07
[6 empty] | Ford -Inspection | 250 | 250 | 2017-12-08 | 2017-12-08
[6 empty] | Knapehide | 204.39 | 204.39 | 2017-12-27 | 2017-12-27
[6 empty] | Jack |  | 800 |  |  | 2018-03-01
[6 empty] | Tax, Title, and State Registration |  | 2683.15 |  |  | 2018-03-01
[6 empty] | pipe vise |  | 420 |  |  | 2018-03-01
[6 empty] | DC/AC Power Inverter |  | 980 |  |  | 2018-03-01
[6 empty] | Welder |  | 6500 |  |  | 2018-03-01
[6 empty] | Compressor |  | 1700 |  |  | 2018-03-01
25 | 354.7 Office Structures & Improvements | 288000 | Replace existing office that was substantially damaged in Hurricane Irma . | Install an office of approximately 1400-1500 sq. feet to replace existing. Demo and dispose of existing. Form, reinforce, and pour concrete slab underneath the office unit. | OSHA requires a safe work environment, and mold/water/wind damage precludes use of prior office. A Florida Licensed Mold Assessor stated that the laboratory analysis indicated elevated indoor levels of indoor fungal spores and an indoor source for fungal spores. One employee has resigned citing unsafe work environment which resulted in a workers comp filing. Other employees also had symptoms in the time period just prior to the moisture assessment by the Assessor. |  | 0 | 288000
[6 empty] | PP Keys 2016 LLC |  | 250000 | 2017-10-19 |  | 3/31/2018**
[6 empty] | Demo Contractor |  | 13000 |  |  | 2018-03-31
[6 empty] | concrete slab underneath office |  | 25000 |  |  | 2018-03-31
26 | 395.7 New sandsifter | 44300 | Replace Cherrington sandsifter rendered inoperable after Hurricane Irma. | Purchase Sand Sifter or tractor style unit to replace inoperable Cherrington unit. Sandsifter is used to clean the 4 drying beds that process KWRU's bio-solids. The sandsifter lifts the biosolids onto a screen and allows the silica sand to drop out of the screen while retaining the biosolids material in a hopper. The hopper then lifts hydraulically and dumps the material into a roll off dumpster. | None, however if employees are going to be removing this material with shovels there is increased possibility for workers compensation or short/long term disability claims due to back injury. | Cherrington/ other manufacturer, Kubota, Mahindra, John Deere |  | 44300 |  |  | 2018-04-30
** Contractor related in an onsite meeting on 1/18/2018 that the delivery date of the modular unit may be delayed due to high demand created by recent hurricanes in Houston and Florida therefore original contract date may not be met.