## Schedule 7.1
Florida Power & Light Company
Docket No. 20210015-EI
Staff's Twelfth Data Request
Request No. 1
Attachment 1: Page 1 of 2
NO STE RESOURCE PLAN | [16 empty] | SOLARTOGETHER EXTENSION RESOURCE PLAN
Schedule 7.1 | [16 empty] | Schedule 7.1
Forecast of Capacity, Demand, and Scheduled | [16 empty] | Forecast of Capacity, Demand, and Scheduled
Maintenance At Time Of Summer Peak | [16 empty] | Maintenance At Time Of Summer Peak
-1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17
-17: Capacity | [16 empty] | Capacity
-6: Total; -9: Firm; -10: Total; -13: Total; -15: Generation Only; -17: Above/ | [5 empty] | Total |  |  | Firm | Total |  |  | Total |  | Generation Only |  | Above/
-2: Firm; -3: Firm; -4: Firm; -6: Firm; -7: Total; -9: Summer; -10: Reserve; -13: Reserve; -15: Reserve; -17: (Below) |  | Firm | Firm | Firm |  | Firm | Total |  | Summer | Reserve |  |  | Reserve |  | Reserve |  | (Below)
| Installed | Capacity | Capacity | Firm | Capacity | Peak |  | Peak | Margin Before |  | Scheduled | Margin After |  | Margin After |  | 20% |  | Installed | Capacity | Capacity | Firm | Capacity | Peak |  | Peak | Margin Before |  | Scheduled | Margin After |  | Margin After |  | 20%
August of | Capacity | Import | Export | QF | Available | Demand | DSM | Demand | Maintenance |  | Maintenance | Maintenance |  | Maintenance |  | RM | August of | Capacity | Import | Export | QF | Available | Demand | DSM | Demand | Maintenance |  | Maintenance | Maintenance |  | Maintenance |  | RM
Year | MW | MW | MW | MW | MW | MW | MW | MW | MW | % of Peak | MW | MW | % of Peak | MW | % of Peak | (MW) | Year | MW | MW | MW | MW | MW | MW | MW | MW | MW | % of Peak | MW | MW | % of Peak | MW | % of Peak | (MW)
-1: FPL | FPL
2021 | 27622.6244 | 110 | 0 | 433.5 | 28166.1244 | 24621 | 1821.4833 | 22799.5167 | 5366.6077 | 23.5 | 0 | 5366.6077 | 23.5 | 3545.1244 | 14.4 | 806.7044 | 2021 | 27622.6244 | 110 | 0 | 433.5 | 28166.1244 | 24621 | 1821.4833 | 22799.5167 | 5366.6077 | 23.5 | 0 | 5366.6077 | 23.5 | 3545.1244 | 14.4 | 806.7044
-1: Gulf | Gulf
2021 | 2440.4058 | 1015.46 | 0 | 0 | 3455.8658 | 2462 | 6.3052 | 2455.6948 | 1000.171 | 40.7 | 0 | 1000.171 | 40.7 | 993.8658 | 40.4 | 509.032 | 2021 | 2440.4058 | 1015.46 | 0 | 0 | 3455.8658 | 2462 | 6.3052 | 2455.6948 | 1000.171 | 40.7 | 0 | 1000.171 | 40.7 | 993.8658 | 40.4 | 509.032
-1: Integrated FPL and Gulf | Integrated FPL and Gulf
2022 | 30740.744 | 1125.3116 | 0 | 3.5 | 31869.5557 | 27277.3998 | 1885.7439 | 25391.6559 | 6477.8998 | 25.5 | 0 | 6477.8998 | 25.5 | 4592.1559 | 16.8 | 1399.5686 | 2022 | 30740.744 | 1125.3116 | 0 | 3.5 | 31869.5557 | 27277.3998 | 1885.7439 | 25391.6559 | 6477.8998 | 25.5 | 0 | 6477.8998 | 25.5 | 4592.1559 | 16.8 | 1399.5686
2023 | 31163.3507 | 240.1637 | 0 | 3.5 | 31407.0144 | 27771.3609 | 1942.9721 | 25828.3888 | 5578.6256 | 21.6 | 0 | 5578.6256 | 21.6 | 3635.6535 | 13.1 | 412.9478 | 2023 | 31382.8277 | 240.1637 | 0 | 3.5 | 31626.4914 | 27771.3609 | 1942.9721 | 25828.3888 | 5798.1026 | 22.4 | 0 | 5798.1026 | 22.4 | 3855.1305 | 13.9 | 632.4248
2024 | 31299.7804 | 240.0162 | 0 | 3.5 | 31543.2966 | 28278.2259 | 2006.3259 | 26271.9 | 5271.3966 | 20 | 0 | 5271.3966 | 20 | 3265.0706 | 11.5 | 17.0166 | 2024 | 31874.6345 | 240.0162 | 0 | 3.5 | 32118.1506 | 28278.2259 | 2006.3259 | 26271.9 | 5846.2506 | 22.3 | 0 | 5846.2506 | 22.3 | 3839.9247 | 13.6 | 591.8706
2025 | 31749.946 | 239.8691 | 0 | 3.5 | 31993.3152 | 28675.405 | 2050.2337 | 26625.1713 | 5368.1439 | 20.1 | 0 | 5368.1439 | 20.1 | 3317.9102 | 11.6 | 43.1096 | 2025 | 32586.433 | 239.8691 | 0 | 3.5 | 32829.8022 | 28675.405 | 2050.2337 | 26625.1713 | 6204.6309 | 23.3 | 0 | 6204.6309 | 23.3 | 4154.3972 | 14.5 | 879.5966
2026 | 32434.8888 | 239.7225 | 0 | 3.5 | 32678.1114 | 29051.0117 | 2084.382 | 26966.6297 | 5711.4817 | 21.1 | 0 | 5711.4817 | 21.1 | 3627.0997 | 12.5 | 318.1557 | 2026 | 32564.8664 | 239.7225 | 0 | 3.5 | 32808.0889 | 29051.0117 | 2084.382 | 26966.6297 | 5841.4592 | 21.7 | 0 | 5841.4592 | 21.7 | 3757.0772 | 12.9 | 448.1333
2027 | 32545.8769 | 239.5764 | 0 | 0 | 32785.4533 | 29339.5088 | 2118.4384 | 27221.0704 | 5564.3828 | 20.4 | 0 | 5564.3828 | 20.4 | 3445.9445 | 11.7 | 120.1687 | 2027 | 32473.3525 | 239.5764 | 0 | 0 | 32712.9289 | 29339.5088 | 2118.4384 | 27221.0704 | 5491.8584 | 20.2 | 0 | 5491.8584 | 20.2 | 3373.4201 | 11.5 | 47.6444
2028 | 32902.91 | 239.4306 | 0 | 0 | 33142.3407 | 29720.8182 | 2152.4032 | 27568.415 | 5573.9257 | 20.2 | 0 | 5573.9257 | 20.2 | 3421.5225 | 11.5 | 60.2427 | 2028 | 33131.8912 | 239.4306 | 0 | 0 | 33371.3219 | 29720.8182 | 2152.4032 | 27568.415 | 5802.9068 | 21 | 0 | 5802.9068 | 21 | 3650.5037 | 12.3 | 289.2238
2029 | 34882.988 | 239.2853 | 0 | 0 | 35122.2734 | 30233.4032 | 2186.4631 | 28046.9401 | 7075.3332 | 25.2 | 0 | 7075.3332 | 25.2 | 4888.8701 | 16.2 | 1465.9452 | 2029 | 33418.4823 | 239.2853 | 0 | 0 | 33657.7676 | 30233.4032 | 2186.4631 | 28046.9401 | 5610.8275 | 20 | 0 | 5610.8275 | 20 | 3424.3644 | 11.3 | 1.4395
2030 | 34972.1107 | 239.1405 | 0 | 0 | 35211.2512 | 30832.4082 | 2220.6256 | 28611.7825 | 6599.4686 | 23 | 0 | 6599.4686 | 23 | 4378.843 | 14.2 | 877.1121 | 2030 | 35796.1254 | 239.1405 | 0 | 0 | 36035.2659 | 30832.4082 | 2220.6256 | 28611.7825 | 7423.4834 | 25.9 | 0 | 7423.4834 | 25.9 | 5202.8578 | 16.9 | 1701.1269
-1: Col. (2) represents capacity additions and changes projected to be in-service by June 1st. These MW are generally considered to be available to meet Summer | Col. (2) represents capacity additions and changes projected to be in-service by June 1st. These MW are generally considered to be available to meet Summer
-1: peak loads which are forecasted to occur during August of the year indicated. | peak loads which are forecasted to occur during August of the year indicated.
-1: Col. (6) = Col.(2) + Col.(3) - Col(4) + Col(5). | Col. (6) = Col.(2) + Col.(3) - Col(4) + Col(5).
-1: Col.(7) reflects the 2021 load forecast without incremental DSM or cumulative load management. | Col.(7) reflects the 2021 load forecast without incremental DSM or cumulative load management.
-1: Col.(8) represents cumulative load management capability, plus incremental conservation and load management, from 9/2020-on intended for use with the | Col.(8) represents cumulative load management capability, plus incremental conservation and load management, from 9/2020-on intended for use with the
-1: 2021 load forecast. | 2021 load forecast.
-1: Col.(10) = Col.(6) - Col.(9) | Col.(10) = Col.(6) - Col.(9)
-1: Col.(11) = Col.(10) / Col.(9) | Col.(11) = Col.(10) / Col.(9)
-1: Col.(12) indicates the capacity of units projected to be out-of-service for planned maintenance during the Summer peak period. | Col.(12) indicates the capacity of units projected to be out-of-service for planned maintenance during the Summer peak period.
-1: Col.(13) = Col.(10) - Col.(12) | Col.(13) = Col.(10) - Col.(12)
-1: Col.(14) = Col.(13) / Col.(9) | Col.(14) = Col.(13) / Col.(9)
-1: Col.(15) = Col.(6) - Col.(7) - Col.(12) | Col.(15) = Col.(6) - Col.(7) - Col.(12)
-1: Col.(16) = Col.(15) / Col.(7) | Col.(16) = Col.(15) / Col.(7)
-1: Col.(17) = Col.(6) - (Col.(9)*1.20) | Col.(17) = Col.(6) - (Col.(9)*1.20)

## Schedule 7.2
Florida Power & Light Company
Docket No. 20210015-EI
Staff's Twelfth Data Request
Request No. 1
Attachment 1: Page 2 of 2
NO STE RESOURCE PLAN | [16 empty] | SOLARTOGETHER EXTENSION RESOURCE PLAN
Schedule 7.2 | [16 empty] | Schedule 7.2
Forecast of Capacity, Demand, and Scheduled | [16 empty] | Forecast of Capacity, Demand, and Scheduled
Maintenance At Time Of Winter Peak | [16 empty] | Maintenance At Time Of Winter Peak
-1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17 | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15 | -16 | -17
-17: Capacity | [16 empty] | Capacity
-6: Total; -9: Firm; -10: Total; -13: Total; -15: Generation Only; -17: Above/ | [5 empty] | Total |  |  | Firm | Total |  |  | Total |  | Generation Only |  | Above/
-2: Firm; -3: Firm; -4: Firm; -6: Firm; -7: Total; -9: Winter; -10: Reserve; -13: Reserve; -15: Reserve; -17: (Below) |  | Firm | Firm | Firm |  | Firm | Total |  | Winter | Reserve |  |  | Reserve |  | Reserve |  | (Below)
| Installed | Capacity | Capacity | Firm | Capacity | Peak |  | Peak | Margin Before |  | Scheduled | Margin After |  | Margin After |  | 20% |  | Installed | Capacity | Capacity | Firm | Capacity | Peak |  | Peak | Margin Before |  | Scheduled | Margin After |  | Margin After |  | 20%
January of | Capacity | Import | Export | QF | Available | Demand | DSM | Demand | Maintenance |  | Maintenance | Maintenance |  | Maintenance |  | RM | January of | Capacity | Import | Export | QF | Available | Demand | DSM | Demand | Maintenance |  | Maintenance | Maintenance |  | Maintenance |  | RM
Year | MW | MW | MW | MW | MW | MW | MW | MW | MW | % of Peak | MW | MW | % of Peak | MW | % of Peak | (MW) | Year | MW | MW | MW | MW | MW | MW | MW | MW | MW | % of Peak | MW | MW | % of Peak | MW | % of Peak | (MW)
-1: FPL | FPL
2021 | 26993.4 | 110 | 0 | 403.5 | 27506.9 | 20068 | 1369.7191 | 18698.2809 | 8808.6191 | 47.1 | 0 | 8808.6191 | 47.1 | 7438.9 | 37.1 | 5068.963 | 2021 | 26993.4 | 110 | 0 | 403.5 | 27506.9 | 20068 | 1369.7191 | 18698.2809 | 8808.6191 | 47.1 | 0 | 8808.6191 | 47.1 | 7438.9 | 37.1 | 5068.963
-1: Gulf | Gulf
2021 | 2388 | 994 | 0 | 0 | 3382 | 2174 | 0.59631 | 2173.4037 | 1208.5963 | 55.6 | 0 | 1208.5963 | 55.6 | 1208 | 55.6 | 773.9156 | 2021 | 2388 | 994 | 0 | 0 | 3382 | 2174 | 0.59631 | 2173.4037 | 1208.5963 | 55.6 | 0 | 1208.5963 | 55.6 | 1208 | 55.6 | 773.9156
-1: Integrated FPL and Gulf | Integrated FPL and Gulf
2022 | 28521.4 | 1104 | 0 | 3.5 | 29628.9 | 22461 | 1406.2751 | 21054.7249 | 8574.1751 | 40.7 | 0 | 8574.1751 | 40.7 | 7167.9 | 31.9 | 4363.2301 | 2022 | 28521.4 | 1104 | 0 | 3.5 | 29628.9 | 22461 | 1406.2751 | 21054.7249 | 8574.1751 | 40.7 | 0 | 8574.1751 | 40.7 | 7167.9 | 31.9 | 4363.2301
2023 | 29749.4 | 1104 | 0 | 3.5 | 30856.9 | 22869 | 1443.4258 | 21425.5742 | 9431.3258 | 44 | 0 | 9431.3258 | 44 | 7987.9 | 34.9 | 5146.2109 | 2023 | 29749.4 | 1104 | 0 | 3.5 | 30856.9 | 22869 | 1443.4258 | 21425.5742 | 9431.3258 | 44 | 0 | 9431.3258 | 44 | 7987.9 | 34.9 | 5146.2109
2024 | 29380.4 | 219 | 0 | 3.5 | 29602.9 | 23287 | 1481.7515 | 21805.2485 | 7797.6515 | 35.8 | 0 | 7797.6515 | 35.8 | 6315.9 | 27.1 | 3436.6019 | 2024 | 29380.4 | 219 | 0 | 3.5 | 29602.9 | 23287 | 1481.7515 | 21805.2485 | 7797.6515 | 35.8 | 0 | 7797.6515 | 35.8 | 6315.9 | 27.1 | 3436.6019
2025 | 29395.4 | 219 | 0 | 3.5 | 29617.9 | 23624 | 1526.8118 | 22097.1882 | 7520.7118 | 34 | 0 | 7520.7118 | 34 | 5993.9 | 25.4 | 3101.2742 | 2025 | 29395.4 | 219 | 0 | 3.5 | 29617.9 | 23624 | 1526.8118 | 22097.1882 | 7520.7118 | 34 | 0 | 7520.7118 | 34 | 5993.9 | 25.4 | 3101.2742
2026 | 29390.4 | 219 | 0 | 3.5 | 29612.9 | 23957 | 1556.1813 | 22400.8187 | 7212.0813 | 32.2 | 0 | 7212.0813 | 32.2 | 5655.9 | 23.6 | 2731.9176 | 2026 | 29390.4 | 219 | 0 | 3.5 | 29612.9 | 23957 | 1556.1813 | 22400.8187 | 7212.0813 | 32.2 | 0 | 7212.0813 | 32.2 | 5655.9 | 23.6 | 2731.9176
2027 | 30224.4 | 219 | 0 | 0 | 30443.4 | 24199 | 1585.4542 | 22613.5458 | 7829.8542 | 34.6 | 0 | 7829.8542 | 34.6 | 6244.4 | 25.8 | 3307.1451 | 2027 | 29312.4 | 219 | 0 | 0 | 29531.4 | 24199 | 1585.4542 | 22613.5458 | 6917.8542 | 30.6 | 0 | 6917.8542 | 30.6 | 5332.4 | 22 | 2395.1451
2028 | 30584.4 | 219 | 0 | 0 | 30803.4 | 24552 | 1614.6308 | 22937.3692 | 7866.0308 | 34.3 | 0 | 7866.0308 | 34.3 | 6251.4 | 25.5 | 3278.557 | 2028 | 29272.4 | 219 | 0 | 0 | 29491.4 | 24552 | 1614.6308 | 22937.3692 | 6554.0308 | 28.6 | 0 | 6554.0308 | 28.6 | 4939.4 | 20.1 | 1966.557
2029 | 30584.4 | 219 | 0 | 0 | 30803.4 | 24916 | 1643.7059 | 23272.2941 | 7531.1059 | 32.4 | 0 | 7531.1059 | 32.4 | 5887.4 | 23.6 | 2876.6471 | 2029 | 30284.4 | 219 | 0 | 0 | 30503.4 | 24916 | 1643.7059 | 23272.2941 | 7231.1059 | 31.1 | 0 | 7231.1059 | 31.1 | 5587.4 | 22.4 | 2576.6471
2030 | 32674.4 | 219 | 0 | 0 | 32893.4 | 25289 | 1673.006 | 23615.994 | 9277.406 | 39.3 | 0 | 9277.406 | 39.3 | 7604.4 | 30.1 | 4554.2072 | 2030 | 30681.4 | 219 | 0 | 0 | 30900.4 | 25289 | 1673.006 | 23615.994 | 7284.406 | 30.8 | 0 | 7284.406 | 30.8 | 5611.4 | 22.2 | 2561.2072
-1: Col. (2) represents capacity additions and changes projected to be in-service by January 1st. These MW are generally considered to be available to meet Winter | Col. (2) represents capacity additions and changes projected to be in-service by January 1st. These MW are generally considered to be available to meet Winter
-1: peak loads which are forecasted to occur during January of the year indicated. | peak loads which are forecasted to occur during January of the year indicated.
-1: Col. (6) = Col.(2) + Col.(3) - Col(4) + Col(5). | Col. (6) = Col.(2) + Col.(3) - Col(4) + Col(5).
-1: Col.(7) reflects the 2021 load forecast without incremental DSM or cumulative load management. | Col.(7) reflects the 2021 load forecast without incremental DSM or cumulative load management.
-1: Col.(8) represents cumulative load management capability, plus incremental conservation and load management, from 9/2020-on intended for use with the | Col.(8) represents cumulative load management capability, plus incremental conservation and load management, from 9/2020-on intended for use with the
-1: 2021 load forecast. | 2021 load forecast.
-1: Col.(10) = Col.(6) - Col.(9) | Col.(10) = Col.(6) - Col.(9)
-1: Col.(11) = Col.(10) / Col.(9) | Col.(11) = Col.(10) / Col.(9)
-1: Col.(12) indicates the capacity of units projected to be out-of-service for planned maintenance during the Winter peak period. | Col.(12) indicates the capacity of units projected to be out-of-service for planned maintenance during the Winter peak period.
-1: Col.(13) = Col.(10) - Col.(12) | Col.(13) = Col.(10) - Col.(12)
-1: Col.(14) = Col.(13) / Col.(9) | Col.(14) = Col.(13) / Col.(9)
-1: Col.(15) = Col.(6) - Col.(7) - Col.(12) | Col.(15) = Col.(6) - Col.(7) - Col.(12)
-1: Col.(16) = Col.(15) / Col.(7) | Col.(16) = Col.(15) / Col.(7)
-1: Col.(17) = Col.(6) - (Col.(9)*1.20) | Col.(17) = Col.(6) - (Col.(9)*1.20)