BEFORE THE PUBLIC SERVICE COMMISSION

| In re: Requirement for investor-owned electric utilities to file ongoing storm preparedness plans and implementation cost estimates. | DOCKET NO. 060198-EI ORDER NO. PSC-06-0781-PAA-EI ISSUED: September 19, 2006 |
| --- | --- |

The following Commissioners participated in the disposition of this matter:

LISA POLAK EDGAR, Chairman

J. TERRY DEASON

ISILIO ARRIAGA

MATTHEW M. CARTER II

KATRINA J. TEW

NOTICE OF PROPOSED AGENCY ACTION

ORDER ON INVESTOR-OWNED ELECTRIC UTILITY

STORM PREPAREDNESS PLANS

BY THE COMMISSION:

NOTICE is hereby given by the Florida Public Service Commission that the action discussed herein is preliminary in nature and will become final unless a person whose interests are substantially affected files a petition for a formal proceeding, pursuant to Rule 25-22.029, Florida Administrative Code.

BACKGROUND

On January 23, 2006, our staff conducted a workshop to discuss damage to electric utility facilities resulting from recent hurricanes and to explore ways of minimizing future storm damages and customer outages.  State and local government officials, independent technical experts, and Florida’s electric utilities participated in the workshop.  On January 30, 2006, some participants filed post-workshop comments.

At our February 27, 2006, internal affairs conference, our staff briefed us on recommended actions to address the effects of extreme weather events on electric infrastructure.  We also heard comments from interested persons and Florida’s electric utilities regarding the staff’s recommended actions.  We modified various aspects of our staff’s proposal.  In brief, we decided the following:

- All Florida electric utilities, including municipal utilities and rural electric cooperative utilities, would provide a 2006 Hurricane Preparedness Briefing at our June 5, 2006 internal affairs conference;

- Staff would file a proposed agency action recommendation for the April 4, 2006, agenda conference requiring each investor-owned electric utility to file plans and estimated implementation costs for ongoing storm preparedness initiatives;

- A docket would be opened to initiate rulemaking to adopt distribution construction standards that are more stringent than the minimum safety requirements of the National Electrical Safety Code; and

- A docket would be opened to initiate rulemaking to identify areas and circumstances where distribution facilities should be required to be constructed underground.

On April 25, 2006, in this docket, we issued Order No. PSC-06-0351-PAA-EI, requiring the investor-owned electric utilities to file plans and estimated implementation costs for ten ongoing storm preparedness initiatives on or before June 1, 2006.  The ten ongoing initiatives are:

- A Three-year Vegetation Management Cycle for Distribution Circuits;

- An Audit of Joint-Use Attachment Agreements;

- A Six-year Transmission Structure Inspection Program;

- Hardening of Existing Transmission Structures;

- A Transmission and Distribution Geographic Information System;

- Post-Storm Data Collection and Forensic Analysis;

- Collection of Detailed Outage Data Differentiating Between the

Reliability Performance of Overhead and Underground Systems;

- Increased Utility Coordination with Local Governments;

- Collaborative Research on Effects of Hurricane Winds and Storm Surge;

and

10) A Natural Disaster Preparedness and Recovery Program.

The initiatives listed above are not intended to encompass all reasonable ongoing storm preparedness initiatives.  Rather, we viewed these initiatives as the starting point of an ongoing process.   The docket was kept open for us to address the adequacy of the utility’s plans.

On June 1, 2006, each investor-owned electric utility filed plans addressing each of the ten ongoing storm initiatives.  On July 14, 2006, our staff met informally with the utilities to seek clarifications and additional information.

This Order addresses the adequacy of the investor-owned electric utility plans for implementing the ten initiatives for ongoing storm preparedness identified in Order No. PSC-06-0351-PAA-EI. Moreover, our staff informally asked each municipal electric utility and rural electric cooperative utility to voluntarily file plans regarding the ten initiatives identified in the Order. A summary of the filed plans of the municipal electric utilities and rural electric cooperative utilities is also provided for informational purposes.

We have jurisdiction pursuant to Sections 366.04(2)(c), (2)(f), and (5), and 366.05(7), Florida Statutes.

Initiative 1 –Three-Year Vegetation Management Cycle for Distribution Circuits

In Order No. PSC-06-0351-PAA-EI, we found that “[t]he vegetation management practices of the investor-owned electric utilities do not provide adequate assurance that tree clearances for overhead distribution facilities are being maintained in a manner that is likely to reduce vegetation related storm damage.  We believe that utilities should develop more stringent distribution vegetation management programs.”

Consequently, we required each investor-owned electric utility to provide plans, a timeline for implementation, and cost estimates to implement a three-year trim cycle for all distribution circuits unless shown to be cost prohibitive, and that the plans should enumerate minimum performance requirements. We provided for utility specific flexibility. The Order states that any “alternatives proposed by the utility shall be compared to a three-year trim cycle and must be shown to be equivalent or better in terms of cost and reliability for purposes of preparing for future storms.”

Our review of each investor-owned electric utility’s plans for vegetation management for distribution circuits is provided below and in summary form on Attachment A to this Order.

Individual Plans

As shown by the summary on Attachment A, Tampa Electric Company (TECO) and Florida Public Utilities Company (FPUC) plan to comply with the three-year tree trim cycle for all distribution circuits.  Florida Power & Light Company (FPL), Progress Energy Florida (PEF), and Gulf Power Company (Gulf) proposed alternatives to a standard three-year tree trim cycle for all distribution circuits.  Among the concerns cited by the companies, the potential cost impact associated with the supply and demand of the tree-trimming contractor resources is the most common.  FPL, PEF, and Gulf provided reasons for their individually recommended alternatives; however, only FPL provided a quantitative analysis of the costs of more frequent trimming compared to estimated benefits of reduced storm restoration costs due to avoided storm outages.

FPL:  FPL proposes a three-year average tree trim cycle for feeders and a six-year average cycle for distribution laterals.  FPL currently achieves a three-year average trim cycle on its feeders.  The proposed six-year average for lateral circuits is an increase of 63 percent in historically achieved tree trimming for lateral circuits.  FPL estimates that in 2013, it will complete its transition to an average six-year cycle for lateral circuits.  Table 1 is a summary of the options FPL reviewed.

Table 1

Summary of Vegetation Management Options Considered by FPL

| Vegetation Management Initiative | Average Annual Costs ($millions) | Average Annual Incremental Costs ($millions) | Annual Avoided Storm Outages (measured by Customer Interruption or “CI” | Average Cost per Avoided CI |
| --- | --- | --- | --- | --- |
| Recommended 3-year cycle for all distribution circuits | $102.5 | $43.5 | 155,000 | $280 |
| FPL’s proposed 3-year feeder cycle and 6-year Lateral cycle | $71.9 | $12.9 | 100,000 | $129 |
| FPL’s current program | $59.0 | N/A | N/A | N/A |

Compared with its current tree trimming practice, FPL estimates that moving to a three-year tree trim cycle for all distribution circuits would result in an average incremental annual cost of $43.5 million, while providing a potential incremental benefit of 155,000 fewer storm-related Customer Interruptions (CI).  Therefore, the cost per avoided storm CI to implement a three-year trim cycle for all distribution circuits would be approximately $280 per interruption.  FPL estimates its proposed alternative would result in an average incremental annual cost of $12.9 million, while providing a potential incremental benefit of 100,000 fewer storm-related CI.  Therefore, the cost per avoided storm CI would be approximately $129 for the alternative.  FPL asserts that the additional spending to comply with a three-year tree trim cycle for distribution laterals would result in a diminishing return measured by storm cost savings.  FPL also presented a ten-year total cost analysis which demonstrates its proposed alternative to be more cost effective.  FPL proposes that its plan be reevaluated annually to assess lessons learned and ensure continued effectiveness.

We find FPL’s plan to be reasonably consistent with the compliance options provided by the Order.  FPL has provided more extensive data and analysis than the other two companies that proposed alternative plans.  However, FPL’s analysis is based on various assumptions such as the potential incremental benefit in reduced customer interruptions during storm events.  At this time, there is no substantive forensic data supporting such assumptions.  Therefore, we are uncertain at this time whether FPL’s proposed plan is equivalent to or better than a three-year trim cycle for all circuits in terms of cost and reliability for purposes of preparing for future storms.  We find that FPL’s proposed plan is reasonable for initial implementation because it is an improvement over its current program and it contains a method for us to conduct the necessary ongoing review to ensure that it is equivalent to or better than a three-year trim cycle in terms of cost and reliability for purposes of preparing for future storms.

FPL’s analytical approach appears to be sound.  As more data become available, FPL’s plan and plan implementation shall be reevaluated annually to assess the need for any adjustment.  This annual assessment shall be conducted consistent with the requirements of this Order. In particular, to ensure that the level of vegetation management is achieving this Commission’s goal of reducing future storm impact, FPL shall collect forensic data to evaluate the correlation between the storm-related CI and the frequency of the trim cycles.

PEF: As shown by the summary on Attachment A, PEF’s plan is an alternative to a three-year tree trim cycle for all distribution circuits.  PEF calls for a fully integrated vegetation management program using a number of prioritization ranking factors for targeted trimming to balance the cycle trimming approach.  PEF believes its program is better than a three-year tree trim cycle for all distribution circuits.  PEF estimates that a three-year cycle for all circuits would immediately increase costs by approximately $7 million in the first year and could increase its overall budget by more than 3% per year.

PEF’s plan includes a goal of a three-year average trim cycle.  However, PEF has not shown whether it has achieved that goal or whether it will increase the trim frequency to move toward that goal.  PEF provided reasons why it believes its alternative is better.  However, its plan provides no quantitative comparisons of the costs and benefits similar to FPL’s analysis.  Nor does PEF’s plan contain a method for us to conduct the necessary ongoing review to ensure that it is equivalent to or better than a three-year trim cycle in terms of cost and reliability for purposes of preparing for future storms.  Therefore, PEF’s current plan shall be revised to address these concerns.  PEF will bring its plan into full compliance with Order No. PSC-06-0351-PAA-EI by September 28, 2006, and our staff will consult with PEF about any remaining data requirements.

As more data becomes available, PEF’s plan shall be reevaluated annually to assess the need for any adjustment.  This annual assessment shall be conducted consistent with the requirements of this Order. In particular, to ensure the level of vegetation management is achieving this Commission’s goal of reducing future storm impact, PEF shall collect forensic data to evaluate the correlation between the storm-related CI and the frequency of the trim cycles.

TECO:  As shown in summary form on Attachment A, TECO’s plan calls for targeted tree trimming.  TECO will ensure that every circuit is trimmed every three years.  TECO alleges contractor resource constraints due to increased demand. TECO is planning a phased-in approach to transition from the current vegetation management program to the three-year program.  A two to three year transition period is planned to stabilize costs and conduct training.  We find that TECO’s plan will comply with the three-year trim cycle requirement when fully implemented.  As more data becomes available, TECO’s plan shall be reevaluated annually to assess the need for any adjustment.  This annual assessment shall be conducted consistent with the requirements of this Order.

GULF:  As shown in summary form on Attachment A, Gulf’s plan is an alternative to a three-year tree trim cycle for all distribution circuits. Gulf plans to continue its current reliability-based program. Gulf’s reliability-based program targets vegetation based on the following priorities: Trouble Ticket Pruning, Targeted Hot Spot Pruning, and Full Maintenance Pruning. Gulf described its Full Maintenance Pruning as follows: If the field patrol determines that reliability is deteriorating due to the overall condition of vegetation on the entire circuit, then the entire circuit will be scheduled for pruning. In full maintenance pruning, the main feeder as well as all taps and laterals will be pruned to establish a minimum of three years of clearance on the entire circuit. In addition, small trees on the right-of-way that will present future problems will be removed.

Gulf does not believe a cyclical approach is better with respect to the impact on storm hardening.  Gulf asserts that the vast majority of tree caused outages during storms have historically been caused by trees falling into the road right-of-way.  Gulf believes neither cyclical nor reliability based programs would have a significant impact on these trees.  Gulf estimates that a three-year cycle for all circuits would require an annual budget of $7.4 million, representing an annual incremental cost of $4.2 million.

In its response to staff’s data request, Gulf states that it is evaluating a process that will ensure each distribution circuit is evaluated on a cyclical basis. An appropriate cycle will be established for each circuit to insure it is evaluated with respect to potential for storm damage. Circuits with a high customer count and heavy forest cover will be evaluated on a shorter cycle than will circuits with no forest cover. The entire circuit, main feeder lines and laterals, will be evaluated and vegetation concerns will be corrected.  Critical circuits in heavily forested areas may be evaluated for trimming annually while circuits on the beach may not require evaluation on a regular basis.  It is conceivable that the frequency of circuit specific trim cycles could range from one to ten years.  Gulf estimates the annual incremental cost of this program would be approximately $1,000,000.

We note that Gulf is the only company that does not incorporate a cyclical approach in its plan.  While we find that Gulf’s assumption regarding outages caused by trees falling into the road right-of-way may be valid for major storms with extreme winds, we also believe that cyclical trimming should result in fewer storm-related customer interruptions for named storms with wind speeds less than 100 miles per hour, as indicated by FPL’s data.  Gulf did not offer any data to support its argument.

Order No. PSC-06-0351-PAA-EI requires that “alternatives proposed by the utility shall be compared to a three-year trim cycle and must be shown to be equivalent or better in terms of cost and reliability for purposes of preparing for future storms.”  Gulf’s responses to staff’s data request stated reasons why it believes its alternative is better.  However, Gulf provided no quantitative comparisons of the costs and benefits similar to FPL’s analysis.  Nor does Gulf’s vegetation management plan contain a method for us to conduct the necessary ongoing review to ensure that it is equivalent to or better than a three-year trim cycle in terms of cost and reliability for purposes of preparing for future storms.  Therefore, Gulf’s current plan shall be revised.  Gulf will bring its plan into full compliance with Order No. PSC-06-0351-PAA-EI by September 28, 2006, and our staff will consult with Gulf about any remaining data requirements.

FPUC:  As shown in summary form on Attachment A, FPUC’s plan calls for a three-year trim cycle for all feeders.  For laterals, FPUC’s plan includes a three-year trim cycle for the NE division and an alternative of a five-year trim cycle for its NW division.  Subsequent to its filing, FPUC provided additional clarification that the company will implement the three-year tree trim cycle for all distribution circuits.  Based on FPUC’s clarifications, we find that FPUC’s plan complies with the three-year trim cycle requirement.  As more data becomes available, FPUC’s plan shall be reevaluated annually to assess the need for any adjustment.  This annual assessment shall be conducted consistent with the requirements of this Order.

Conclusion

Based on the foregoing, we find that the plans filed by TECO and FPUC comply with the three-year trim cycle required by Order No. PSC-06-0351-PAA-EI.  We find that the proposed alternative plan filed by FPL is reasonably consistent with the compliance options provided by the Order.  FPL’s analytical approach appears to be sound and we believe the method can be used to determine whether the proposed plan is equivalent to or better than a three-year trim cycle in terms of cost and reliability for purposes of preparing for future storms.  In addition, we find that the phase-in approach proposed by TECO and FPL is reasonable for initial implementation.

The alternative plans filed by PEF and Gulf are based on their current vegetation management programs.  They do not contain a method or data for us to conduct the necessary ongoing review to ensure that they are equivalent to or better than a three-year trim cycle in terms of cost and reliability for purposes of preparing for future storms.  Therefore, their current plans shall be revised.  These two companies will bring their plans to full compliance with Order No. PSC-06-0351-PAA-EI by September 28, 2006.

All plans shall be reevaluated annually to assess the need for any adjustment.  This annual assessment shall be conducted consistent with the requirements of this Order.

Initiative 2 –Audit of Joint-Use Attachment Agreements

In Order No. PSC-06-0351-PAA-EI, we found that “Florida’s utilities have not provided adequate assurance that their practices and procedures governing joint-use facilities avoid storm damages and customer outages.”

Consequently, we required each investor-owned electric utility to provide plans, a timeline for implementation, costs, and rate impacts to audit joint-use agreements that include pole strength assessments.  The plans were to enumerate minimum performance requirements.  We provided for utility specific flexibility.

Review of Plans for Audit of Joint-Use Attachment Agreements

Our review of each investor-owned electric utility’s plans for an audit of joint-use attachment agreements is provided below and on Attachment A.

FPL: Currently, FPL partners with CATV and telecommunication companies to complete system-wide pole attachment surveys on a five-year cycle.  The system-wide attachment surveys focus on compliance issues associated with existing pole attachment agreements for all FPL-owned and third party-owned poles.  The current attachment surveys do not explicitly include pole strength assessments.  Prospectively, FPL proposes to include pole strength assessments addressing the impacts of existing pole attachments in conjunction with its eight-year wooden pole inspection program.  Data on the poles will be collected and stored in an information database.  FPL will continue to verify all attachments have been made pursuant to a current joint-use agreement on a five-year cycle system-wide pole attachment survey.  FPL’s plan will be implemented in January 2007 at an estimated incremental annual cost of $1.2 to 2.5 million.

PEF: PEF currently performs a pole agreement compliance audit on a five-year cycle.  The current pole attachment compliance audit does not explicitly address pole strength assessments.  PEF has developed a plan that includes pole strength assessment for all PEF-owned and third party-owned poles in conjunction with its eight-year wood pole inspection cycle.  Data on the poles will be collected and stored in electronic format.  PEF will continue to verify all attachments have been made pursuant to a current joint-use agreement on a five-year cycle.  PEF initiated this plan in 2006 with completion cycles of eight years and an estimated incremental annual cost of $80,000.

TECO:  Currently, TECO performs periodic inspections and/or audits of all joint-use attachments to its facilities. TECO has proposed a plan to audit all joint-use agreements including pole strength assessment for all TECO-owned and third party-owned poles.  This audit will be performed in conjunction with its eight-year wood pole inspection cycle. Stress calculation will also be performed on poles during the eight-year inspection cycle. Data on the poles will be collected and stored in a GIS database.  TECO will verify all attachments have been made pursuant to a current joint-use agreement including strength assessments during the eight-year pole inspection cycle.  TECO’s plan will be implemented in January 2007 with a completion cycle of eight-years at an estimated annual cost of $5 million.  TECO’s cost estimate associated with Initiative 2 does not appear comparable to estimates of the other utilities because TECO’s cost estimate of $5 million is commingled with its cost to perform pole inspections.

GULF:  Since 1991, Gulf has conducted field audits of joint-use poles every five years.  Gulf has proposed a plan to audit all joint-use agreements of Gulf-owned poles and third party-owned poles on a five-year cycle. Pole strength assessments and stress calculations will be performed on a 5% random sample of Gulf-owned poles that are 20 years old or more and have three or more attachments.  Data on poles will be collected and stored in a database. Gulf will verify all attachments have been made pursuant to a current joint-use agreement on a five-year cycle.  Gulf will use results of its 2006 survey to revise its cost estimates and scope of work for 2007.  Preliminary cost estimates for 2007 show a $5.375 million increase relative to 2005.  Gulf’s cost estimate associated with just Initiative 2 appears to include activities and costs to perform pole inspections on an eight-year cycle.

FPUC:  FPUC’s plan was silent on how the utility currently audits joint-use attachment agreements. FPUC has proposed a plan to audit all joint-use agreements including pole strength assessment for all FPUC-owned and third-party-owned poles. This audit will be performed in conjunction with its eight-year wood pole inspection cycle. Stress calculation will also be performed on poles during the eight-year inspection cycle. Data on the poles will be collected and stored in a database. FPUC’s plan will be implemented in January 2007 with a completion cycle of eight-years at an estimated annual cost of $20,300.

Conclusion

We find that each of the utilities’ plans for auditing joint-use attachment agreements include strength assessments and are consistent with the intent of Order No. PSC-06-0351-PAA-EI.  All plans shall be reevaluated annually to assess the need for any adjustment.  This annual assessment shall be conducted consistent with the requirements of this Order.

Initiative 3 – Six-year Transmission Structure Inspection Program

In Order No. PSC-06-0351-PAA-EI, we were “not convinced that current utility transmission facility inspections are adequate to prepare for future storms.”

Consequently, we required each investor-owned electric utility to provide plans, a timeline for implementation, costs, and rate impacts to implement a plan for fully inspecting all transmission towers and other transmission line supporting equipment on a six-year cycle.  We provided for utility-specific flexibility.  Order No. PSC-06-0351-PAA-EI states that any “alternatives shall be compared to a six-year inspection cycle methodology and must be shown to be equivalent or better in terms of cost and reliability for purposes of preparing for future storms.”

In Order No. PSC-06-0351-PAA-EI, we noted that Order No. PSC-06-0144-PAA-EI does not address whether an eight year inspection cycle for all transmission facilities is adequate to prepare for future storms.  Also, Order No. PSC-06-0144-PAA-EI does not address the full inspection of all transmission poles, towers, and other line supporting structures.  Therefore, we required each investor-owned electric utility to develop a plan to fully inspect on a six-year cycle all transmission structures, substations, and all hardware associated with these facilities that are not already addressed by Order No. PSC-06-0144-PAA-EI.

Individual Plans

Our review of each investor-owned electric utility’s plan for a six-year transmission inspection program is provided below and on Attachment A.

FPL:  FPL’s prior transmission structure inspection program focused on performing detailed inspections on ten percent of its transmission structures every four years and fully inspecting substations every three months.   FPL is now increasing its sample and inspection methodology to achieve what it believes to be “the equivalent of a non-sample six-year inspection cycle.”  The estimated increase in annual inspection costs is $2.3 million.  FPL is currently implementing upgrades to its transmission structure inspection program this year.

PEF:  PEF’s existing transmission structure inspection program is indexed to a five-year cycle for structures.  PEF completes a full inspection of its substations once per year.  PEF is not proposing any changes to its current program.  PEF will not incur any incremental costs associated with transmission structure inspections.

TECO:  TECO’s plan establishes a six-year transmission structure inspection program consistent with the requirements of Order No. PSC-06-0351-PAA-EI . The estimated increase in annual inspection costs and additional maintenance is $2.97 million.  TECO currently completes a full inspection of its substations once per year and no enhancements of substation inspection activities are planned.

GULF:  Gulf fully inspects its substations annually and schedules inspections of its transmission structures based on achieving a six-year inspection cycle for all of its facilities. Gulf will not incur any incremental costs associated with transmission structure inspections.

FPUC:  FPUC is developing a program for inspecting its transmission structures on a six-year cycle.  The program includes coordination with customers who own transmission structures.  The estimated increase in annual inspection costs is $18,000.  FPUC currently fully inspects its substations at least once per year and no enhancements of substation inspection activities are planned.

Conclusion

We find that each of the utility’s transmission structure inspection plans is consistent with the intent of Order No. PSC-06-0351-PAA-EI.  Over time, as each utility collects and reviews its storm performance data, each utility will become better able to address the adequacy of its efforts to prepare for future storms.  Each utility’s transmission structure inspection program shall continue to be monitored consistent with the requirements of this Order.

Initiative 4 – Hardening of Existing Transmission Structures

In Order No. PSC-06-0351-PAA-EI, we concluded that the electric utilities “have not shown the extent of utility efforts in this area nor the criteria used to select which transmission structures are upgraded or replaced.”

Consequently, we required each investor-owned electric utility to provide a plan, a timeline for implementation, costs, and rate impacts to implement a plan to upgrade and replace existing transmission structures.  We provided for utility specific flexibility.  The Order states that “the plan shall include the scope of activity, any limiting factors, and the criteria used for selecting transmission upgrades and replacements.”

Individual Plans

Our review of each investor-owned electric utility’s plans for hardening existing transmission structures is provided below and on Attachment A.

FPL:  FPL currently upgrades its existing transmission structures during roadway relocation projects and as other maintenance activities provide cost-efficient opportunities.  Two specific activities included in its program are upgrading un-guyed single wood pole transmission structures and replacement of ceramic post line insulators with a type of polymer insulators to ensure the structures meet extreme wind load criteria.  FPL estimates these two activities will be completed within 10 to 15 years.  FPL projects an increased level of transmission upgrade activities relative to 2005 resulting in additional annual expenses between $3.3 and $6 million beginning in 2007.

PEF:  PEF currently upgrades its existing transmission structures during roadway relocation projects and as other maintenance activities provide cost-efficient opportunities.  A primary component in its plan includes changing out existing wooden transmission poles with either concrete or steel.  Over the next ten years, PEF estimates the program will reduce the percentage of wooden transmission poles from 75 percent to 50 percent.  PEF does not plan to expand its existing program at this time.  Consequently, PEF is not expected to incur any costs associated with any incremental changes to its plan relative to 2005.

TECO:  TECO currently upgrades its existing transmission structures during roadway relocation projects and as other maintenance activities provide cost-efficient opportunities.  TECO’s plan includes the systematic replacement of wooden transmission structures with non-wooden structures based primarily on pole inspection results.  TECO does not plan to expand its existing program at this time.  Consequently, TECO is not expected to incur any costs associated with any incremental changes to its plan relative to 2005.

GULF:  Gulf currently upgrades its existing transmission structures during roadway relocation projects, and as other maintenance activities provide cost-efficient opportunities.  Gulf’s plan includes a five-year program to install storm guys on H-frame transmission structures not currently guyed.  In addition, Gulf began a ten-year program to replace all wooden cross-arms with steel.  For new construction beginning in 2007, Gulf will implement a “loss of conductor” contingency design standard.  A “loss of conductor” contingency is a design standard directed at avoiding cascading transmission tower failures.  In 2007, Gulf will begin incurring approximately $600,000 in incremental annual capital construction costs relative to 2005.

FPUC:  FPUC plans to replace 180 wooden transmission poles on its system with concrete poles as necessary and economically practicable.  The total project costs are estimated to be $4.5 million for replacement of all 180 wooden transmission poles. To date, FPUC has not established a timeline for completing the pole change outs because the poles are currently sound, and transmission line upgrades that may require stronger poles have not been scheduled at this time.

Conclusion

Based on the available information, we find that each utility’s transmission plans for hardening existing transmission structures is consistent with the intent of Order No. PSC-06-0351-PAA-EI.  Utilities are in the process of implementing forensic data collection.  Over time, as each utility collects and reviews its storm performance data, each utility will become better able to address the adequacy of its efforts to prepare for future storms. Each utility’s plans for hardening existing transmission structures shall continue to be monitored consistent with the requirements of this Order.

The following three initiatives are addressed together because effective implementation of any one initiative is dependent on effective implementation of the other two initiatives.

Initiative 5 – A Transmission and Distribution Geographic Information System

Initiative 6 – Post-Storm Data Collection and Forensic Analysis

Initiative 7 – Collection of Detailed Outage Data Differentiating Between Overhead and Underground Systems

In Order No. PSC-06-0351-PAA-EI, we concluded that the electric utilities should develop a transmission and distribution geographic information system (GIS) adequate to provide assurance “that sufficiently detailed data is collected to conduct forensic reviews, assess performance of overhead and underground systems, determining whether appropriate maintenance has been performed and evaluation of storm hardening options.”

The Order also states that

[i]n addition to the general need to increase post-storm data collection, utilities shall collect specific storm performance data that differentiates between overhead and underground systems.  Data regarding overhead and underground system performance is needed to adequately inform customers and communities who are considering their options.  The same data is needed by the utility to address storm hardening options that reduce storm damage, storm restoration costs, and customer outages.

Consequently, we required each investor-owned electric utility to provide a plan, timeline for implementation, costs, and rate impacts to implement plans to develop a GIS program, collect post-storm data on competing technologies, perform forensic analysis, and assess the reliability of overhead and underground systems on an ongoing basis.  We intended for the utilities to have the flexibility to propose plans that are efficient and cost-effective.

Individual Plans

Our review of each investor-owned electric utility’s plans for storm hardening initiatives 5, 6 and 7 is provided below and in summary form on Attachment A.

FPL:  FPL has initiated GIS programs for its distribution and transmission systems and is in the process of fully representing its facilities in the electronic model.  To comply with Initiative 5, FPL plans to implement a new maintenance management system to complement its GIS and other information systems.  This will allow better information on equipment maintenance and performance.  FPL already has a GIS and an asset management system for its transmission system.

For forensic data collection and analysis, FPL proposes that post-storm performance data be collected from a randomly selected sample of locations.  The specific method of sampling is yet to be determined.  Our staff will work with FPL to acquire a better understanding of how sampling will be done.  FPL contends that immediately following a destructive storm, personnel qualified for gathering storm damage data are in limited supply and complete enumeration of all damaged facilities to determine a statistically valid sample of the affected area would take too long.  FPL proposes that while storm damage data are being gathered from a sample of locations, it is important for restoration crews to begin their work in the other areas.  This will allow the collection of sample observations for forensic analysis without restricting early restoration work.  Inclusion of overhead and underground performance will be included in FPL’s plan for managing its assets and performing forensic analyses.  FPL’s proposed plans will have an incremental cost of $6.3 million for adding additional pole attribute information to its GIS and an annual maintenance cost of $0.5 million.  FPL’s proposed alternatives for Initiatives 6 and 7 require no additional costs.

PEF: Although PEF’s present GIS is not capable of providing the information necessary to comply with Order No. PSC-06-0351-PAA-EI, PEF plans is to make the necessary changes to its GIS so that it will be in compliance with the Order.  For distribution, PEF’s GIS will need to be enhanced to include specific information about distribution asset performance.  For transmission, PEF’s GIS does not contain maintenance information.

PEF has established procedures for gathering post-storm performance data for the 2006 hurricane season.  The goal of PEF’s data gathering procedures is to be able to provide the PEF Forensic Assessor (distribution) and a consultant (transmission) with the data gathered so that each will be able to make recommendations for improvements in its system.  PEF’s plans include assessing differences in damage sustained between underground and overhead facilities and determining whether customer outages are caused by failures in underground or overhead components.  PEF plans’ estimated cost to comply with Initiatives 5, 6, and 7 will be $8.8 million initially for developing its computer system and inspecting its facilities, with an annual maintenance cost of $0.3 million and a per storm cost of $0.9 million.

TECO:  TECO began to implement a new distribution and transmission GIS in the Fall of 2005 and implementation will be completed by the Summer of 2007.  This system along with TECO’s outage management system, will provide a variety of functions with information about system performance.  Following major storms, TECO will use information from these systems, along with information collected from a representative sample of storm damaged areas, to determine the causes of equipment failure and to determine preventive measures to harden these systems.  TECO currently categorizes equipment-failure outages into underground and overhead equipment.  The present information systems will be amended as necessary to provide reliability-performance comparisons between underground and overhead systems.  The cost for TECO to make changes necessary to comply with Initiatives 5, 6, and 7 is $1.1 million with an additional forensic analysis cost of $ 0.1 million per storm.

GULF:  GULF presently has a GIS, excluding complete transmission information, for its distribution and transmission structures. At the present rate of processing, the GIS will include all transmission-system information within six years.  For post-storm performance data gathering, Gulf intends to employ contractors to survey a percentage of the lines in the damaged areas.  Crews will cover inland and coastal areas and overhead and underground outages.  The cost for Gulf to continue developing its GIS and use the system according to the initiatives is $75,000 initially and $125,000 per storm.

FPUC:  FPUC, NW Florida Division, presently has a GIS capable of collecting all of the necessary information.  Additional procedures will be developed to enable the division to track all specific hurricane outages, identify the causes of the outages, and count the numbers of customer outages.  The utility now has the ability to report performance information differentiating between overhead and underground facilities.  FPUC, NE Florida Division, presently has only limited GIS capabilities.  FPUC has plans to upgrade NE Florida’s GIS to have the same capabilities as NW Florida’s and then also develop the additional procedures pertaining to the performance of its electric infrastructure.  FPUC states that it will make changes necessary for both divisions to be in compliance with Order No. PSC-06-0351-PAA-EI.  The initial cost for FPUC to upgrade its system is $207,000, and after the upgrades are implemented in 2007, there will be a per storm cost of $10,000.

Conclusion

We find the utilities’ filed plans adequate for carrying out Initiatives 5, 6, and 7.  Utility implementation of the plans shall be monitored consistent with the requirements of this Order.

Initiative 8 – Increased Coordination with Local Governments

By Order No. PSC-06-0351-PAA-EI, we noted that the electric utilities needed to develop “better communication between the utilities and the cities and counties they serve.”   The goal of this better communication is to promote on-going dialogue, in addition to the general need to increase pre- and post-storm coordination. The increased coordination and communication will also facilitate the collection and analysis of more detailed information on the operational characteristics of underground and overhead systems. This additional data is also necessary to more fully inform customers and communities who are considering undergrounding as an option, as well as to assess the most cost effective storm hardening.

One example of better coordination was suggested at our January 23, 2006 infrastructure hardening workshop.  Mayor Anne Castro of the City of Dania Beach suggested that a more integrated partnership between local governments and utilities could assist utilities in better serving customers.  Mayor Castro explained:

We want to be the eyes and ears for FPL.  We have offered [to] train our public service people, our public safety people, especially after a hurricane or even on an ongoing basis during the year, as to what to look for in their infrastructure.  If they could teach us what to look for as far as poles being bad or wires being bad or fuses hanging or loose ends hanging, our folks as they routinely do this through code enforcement, through the fire department, through the police department, are happy to go out there and take a look.  Even our citizens on patrol…turn in half of the code violations anyway … they can report all that, they can create a list….

To facilitate increased governmental interaction, we required each IOU to provide a plan, detailing activities, a timeline for implementation, and associated cost and rate impacts for expanding any existing program or initiating new utility/local government liaison programs. The goal of increased discussion is to reach some accommodation or agreement on mutual concerns and to prioritize needs, within the given time and financial constraints.  This could include not only optimal system planning or upgrades such as undergrounding or expansion of facilities but also tree trimming and storm restoration priorities.

Individual Plans

A discussion of each utility’s plans for increased coordination with local governments is provided below and in table format on Attachment A.   We caution, however, that plans are only as good as their implementation and follow-through procedures.  Even an ambitious plan can be inadequate if not timely implemented with adequate resources to achieve the desired results.  Therefore, approval of these plans is a first step and we will continue to monitor the implementation and any subsequent modifications of the plans.

FPL:  FPL’s plan consists of three subsections, each addressing a different mode of operation:  (1) Storm Mode; (2) Storm Recovery Mode; and (3) Normal Operations.  The plan subsections addressing Storm Mode and Storm Recovery Mode include the traditional pre-storm planning and post-storm restoration activities and indicate that FPL is increasing the level of pre/post storm related information shared with local governments.  Noted in the plan is an annual campaign to identify special needs customers under the Medically Essential Program to alert local officials to customers who may need extra care in relocation and service restoration.   FPL will continue to coordinate with each local emergency operation center (EOC) before and after storms and has pledged to have FPL representatives in County EOCs during storm activity.  FPL has also pledged to coordinate local restoration efforts with local officials to better meet critical local needs.  FPL also plans to expand the timeliness and extent of the information available to the local community during both pre-and post-storm activities.

Under its plan for Normal Operations, FPL will expand its existing “Right Tree, Right Place” program, and enhance its community outreach teams to improve local communication.  FPL also pledges to develop a program to allow local governments to alert the utility when facilities appear in need of repair.  Similar to the approach described by Mayor Castro, the program will train public works departments and other governmental departments to report conditions observed during their normal work activities and receive feedback from FPL on its response to their concerns.  FPL plans to continue its current External Affairs Support efforts to work with local officials throughout the year to identify problem areas and potential solutions.  It has also recently implemented an e-mail distribution network that can target messages to specific audiences to share breaking news and important updates.

The costs associated with FPL’s planned enhancements are for program startup as well as training local governmental participants.  Initial startup costs are estimated to be $125,000 and the ongoing annual expense associated with training is estimated to be $12,000. FPL provided supplemental data addressing training of local governmental volunteers to find and report potential reliability concerns.  FPL states its plan will not be fully operational until the first part of 2007.

PEF:  While PEF did not propose any additional programs, it did note planned improvements in its storm preparedness coordination and its information update activities associated with storm restoration.  Improvements include more efficient process and reporting mechanisms to facilitate easier use by city and county governments.  PEF also plans to enhance its educational efforts to prepare customers for storm related activities and coordinate with local governments on prioritizing local restoration activities.

As part of its response to the July 14 meeting, PEF provided a detailed list of activities envisioned for a cross functional team to improve staff training and communications.  This team will include representatives in the areas of public policy, community relations and commercial/industrial and governmental accounting.  As part of the implementation of this cross functional team, PEF notes that more than 70 employees will be utilized to support these communication efforts.  An in-house improvement to facilitate better communication includes a task specific electronic site to insure that information is timely updated.  Continuing interaction with community representatives will provide feedback on the effectiveness of existing programs and form the basis for changes.  Communication with local governments will be through mailings, coordination meetings, update calls, e-mails and workshops.  In addition, PEF states it is in the process of revising its existing underground conversion tariff to offer more flexibility to local governments in managing project costs.  PEF also plans to continue its vegetation management education as well as its street lighting reporting and repair program.

Because the plans initially anticipate primarily a continuing of current efforts or redirection of existing staff and resources, PEF did not provide incremental cost impacts.  However, it did note that as the programs are refined, additional costs may be incurred.

TECO:  TECO asserts it has very good relationships with local governments within its service territory.  TECO plans to continue its ongoing discussions with local officials regarding issues such as storm preparedness and storm restoration activities.  TECO notes that it currently hosts a storm preparation workshop with local government officials and safety personnel each year prior to storm season.  Based on its experience in 2004, TECO plans to place additional personnel in local EOC’s during storms to facilitate timely communication.  TECO also assists in training local EOC participants which allows establishment of personal relationships with local participants and encourages cooperation.

As part of its on-going activities, TECO plans to increase its efforts in vegetation management coordination and develop educational material related to overhead-to-underground conversion projects.  Part of this effort is working with local governments to develop viable tree ordinances that meet both the local and utility needs.  In addition, TECO also plans to develop a program to train local government representatives in the identification and reporting of damaged or unsafe system conditions to expedite repairs.

Since many of the activities are already in place, there are minimal incremental costs.  Preliminary estimates to develop the educational and training materials for this new program are $75,000 annually. TECO will implement its plan in the first part of 2007.

GULF:  Gulf believes it enjoys very positive relationships with local governments within its service territory. Storm related activities include notifying all local governments when a storm becomes imminent and providing a single point of contact for governments to call for additional information. It also staffs local EOC’s on a 24 hour basis, if necessary. These Gulf representatives also provide updated restoration information after storms.  Gulf also sets up temporary customer service in or near government facilities to expedite the handling of customer issues.

On an ongoing basis, Gulf conducts Community Leader Forums where government and civic leaders are invited to discuss critical issues, including storm related matters and overhead-to-underground conversion projects, and other matters of common interest.  Gulf also indicated that it will create a website for county building and electrical inspectors as a central information source on the electric system, planned improvements and storm preparation and restoration.  Gulf assigns designated employees to maintain active relationships with local governments, including Line Clearing Specialists which serve a single point of contact for vegetation management issues for local governments.  To facilitate underground conversions, Gulf indicated that it works to identify and involve all affected parties early on to facilitate cost effective planning and construction.  It also stresses the need for a single point of coordination and contact with the authority to make timely decisions.

Since many of these activities are being conducted today, Gulf states that there are no incremental costs associated with its plan.  To the extent programs or initiatives are expanded or modified, additional costs may be incurred.

FPUC:  FPUC is in the unique position of serving two small compact service territories which enables it to maintain an ongoing close relationship with local governments as a regular business practice.  Since FPUC employees often live and work in the communities they serve, they bring a different perspective to the process of local government communications.  The utility has received no complaints about the level or timeliness or coordination of information from its local governments.

FPUC notes that, due to limited resources, it is not able to have employees at all government locations throughout storm related activities; however, staff can be relocated from undamaged areas to assist in areas hit hardest by weather activity.  The cost of additional personnel is estimated at $9,700 per activity.  In lieu of a physical presence at local EOC’s, FPUC suggests that it may be more cost effective to institute daily communication procedure to ensure that necessary information is received in a timely manner at EOC’s during storms.

Conclusion

Based on the available information, we find that each investor-owned electric utility’s plan is consistent with the requirements of Order No. PSC-06-0351-PAA-EI. There are, however, no objective metrics to judge whether any of the plans will accomplish the desired level of coordination. How the plans are implemented and ultimately perceived by the local governments will determine their effectiveness.  Utility implementation of the plans shall be monitored consistent with the requirements of this Order.

Initiative 9 – Collaborative Research on Effects of Hurricane Winds and Storm Surge

In Order No. PSC-06-0351-PAA-EI, we noted that “the utilities appeared to be unaware of work being done by universities to study the effects of hurricane winds and storm surge within Florida.  Each utility appeared engaged in independent efforts to gather its own data with little, if any, coordination of resources and information.”  We concluded that “Florida would be better served by consolidating utility resources through a centrally coordinated research and development effort with universities as well as research organizations.  The same data is needed by the utility to address storm hardening options that reduce storm damage, storm restoration costs, and customer outages.”

Consequently, we required each investor-owned electric utility to establish a plan that increases collaborative research, establishes continuing collaboration, identifies objectives, promotes cost sharing, and funds necessary work.  The investor-owned electric utilities were required to solicit participation from the municipal electric utilities and rural electric cooperative electric utilities in addition to available educational and research organizations.

Individual Plans

Each investor-owned electric utility filed plans supporting a non-profit, member supported organization to coordinate all research efforts directed at better understanding storm effects on utility infrastructure and development of technologies that reduce storm restoration costs and outages to customers.  On June 9, 2006, a workshop was held at the Public Utility Research Center, located in the Warrington College of Business at the University of Florida (PURC) to discuss collaborative research efforts.  The June 9 PURC workshop on research in electric infrastructure hardening provided a forum where utilities expressed their specific interests and various research organizations described their abilities and resources.  On July 19, 2006, the Florida electric utilities, including municipal electric utilities and cooperative electric utilities, provided a copy of a Memorandum of Understanding (MOU) that establishes the administrative requirements for creating a statewide collaborative research effort.

Pursuant to the MOU, a statewide collaborative research effort will be coordinated through PURC.  Each research project will be approved by a steering committee comprised of experienced electric utility engineering staff.  However, the MOU is silent regarding the frequency of steering committee meetings and whether any research project would be pursued by a time certain.  On June 9 and July 14, 2006, several potential research activities were identified for review by the steering committee, including efforts to gather better wind data associated with failed poles.  As of August 8, 2006, the steering committee had not established a schedule for selecting research activities and setting funding levels.  At this time, estimated costs associated with funding the organization and resultant joint research have not been projected.

Conclusion

We note that the investor-owned electric utility plans for collaborative research do not establish a sufficiently detailed schedule for selecting collaborative research activities and establishing project funding levels.  Nevertheless, each investor-owned electric utility has made progress in establishing a plan that may increase collaborative research, establish continuing collaboration, identify objectives, promote cost sharing, and fund necessary work.  All investor-owned electric utilities, all municipal electric utilities, and most rural electric cooperative utilities have participated in establishing a cost allocation methodology and an administrative structure.  We therefore find that the investor-owned electric utility plans for collaborative research adequate for carrying out Initiative 9.  Our staff will monitor the utilities continued efforts on collaborative research and will keep us informed on the progress of these activities.

Initiative 10 – Natural Disaster Preparedness and Recovery Program

In Order No. PSC-06-0351-PAA-EI, we noted that “[a] key element in minimizing storm-caused outages is having a natural disaster preparedness and recovery plan.  A formal disaster plan provides an effective means to document lessons learned, improve disaster recovery training, pre-storm staging activities, and post-storm recovery.”

Consequently, we required each investor-owned electric utility “to develop, if it has not already, a formal disaster preparedness and recovery plan that outlines its disaster recovery procedures.  Each utility shall maintain a current copy of its utility disaster plan with the Commission on a going-forward basis.”

Individual Plans

Our review of each investor-owned electric utility’s plans for natural disaster preparedness and recovery is provided below and in summary form on Attachment A.  We have reviewed these plans for content such as safety procedures, pre/post storm procedures, forensic data collection, and for frequency of updates to their respective plans.

We note that each of the natural disaster preparedness and recovery plans will be available to the EOC staff and to the PSC staff during training and actual emergencies.

FPL: FPL has a formal disaster preparedness and recovery plan. The plan is reviewed and updated by FPL on an annual basis.  The plan contains pre/post emergency procedures and safety procedures for natural disasters. The plan has a procedure for collecting forensic data after a disaster.

PEF: PEF has a formal disaster preparedness and recovery plan. The plan is reviewed and updated by PEF on an annual basis. The plan contains pre/post emergency procedures and safety procedures for natural disasters. The plan has a procedure for collecting forensic data after a disaster.

TECO: TECO has a formal disaster preparedness and recovery plan. The plan is reviewed and updated by TECO on an annual basis. The plan contains pre/post emergency procedures and safety procedures for a wide scope of natural and man made disasters.

GULF: Gulf has a formal disaster preparedness and recovery plan that has been filed with the Commission. The plan is reviewed and updated by Gulf on an annual basis. The plan contains pre/post emergency procedures and safety procedures for natural disasters.

FPUC: FPUC has a formal disaster preparedness and recovery plan. The plan is reviewed and updated by FPUC on an annual basis. The plan contains pre/post emergency procedures and safety procedures for natural disasters. FPUC will develop a procedure for gathering forensic data per their response to Initiative 6 “Post-Storm Data Collection and Forensic Analysis” discussed above.

Conclusion

The plans for all investor-owned electric utilities satisfy the intent of initiative 10 of Order No. PSC-06-0351-PAA-EI.  The plans are “living documents” and subject to constant revision as new lessons are learned.  They will be reviewed and updated annually with lessons learned from storms and forensics data that is collected and analyzed.  The plans will be relied on by EOC and PSC staff during training and actual emergencies.

Monitoring Requirements

In Order No. PSC-06-0351-PAA-EI, we noted that the ten listed ongoing storm preparedness initiatives “are not intended to encompass all reasonable ongoing storm preparedness initiatives.  We view these initiatives as the starting point of an ongoing process.  Utilities and interested persons are encouraged to identify additional initiatives and to suggest alternative plans so long as the same objectives are achieved in a cost effective manner.”

The plans that have been developed and discussed in this Order are based on the prevailing utility management views and the data that is available at this time.  As experience reveals new information, utility management can be expected to change and improve their implementation strategy and even identify new storm hardening initiatives.  Thus, the investor-owed electric utilities shall provide periodic updates and status reports on their ongoing storm hardening initiatives in order for us to effectively monitor utility programs.

Our staff inquired whether the investor-owned electric utilities would be willing to provide status reports and updates on their respective storm hardening initiatives by March 1.  The March 1 date was suggested because it is the filing date for the Annual Distribution Service Reliability Report pursuant to Rule 25-6.0455, Florida Administrative Code.  All investor-owned electric utilities have indicated that they can provide annual updates of their storm hardening initiatives on or before March 1.  However, additional dialogue is necessary to address details regarding the content and format of such updates.  Assuming there is no protest to this Order, our staff will schedule a staff workshop in October addressing the format and summary information to be reported on or before March 1, 2007.

We find that the most effective method to monitor each utility’s ongoing storm hardening initiatives is in conjunction with our annual review of distribution reliability performance because the storm hardening initiatives are primarily reliability performance activities.  Our staff intends to include an additional section in its 2007 review of electric utility reliability performance addressing the ten listed ongoing storm preparedness initiatives and any additional storm hardening initiatives proposed by either the utilities or this Commission.

The storm hardening initiatives shall be monitored and reported in the following manner:

- Initiatives 1 through 7 – This Commission shall monitor these initiatives through our annual review of distribution service reliability performance because the storm hardening initiatives involve reliability performance activities.

- Initiative 8 – This Commission shall monitor this initiative for increased coordination with local governments through our review of electric utilities’ dialogue  with local governments and selected review of utility activities in this area.

- Initiative 9 – This Commission shall monitor this initiative for collaborative research on effects of hurricane winds and storm surge by reviewing the electric utilities’ participation in studies and projects undertaken by the collaborative research efforts.

- Initiative 10 – This Commission shall monitor this initiative regarding the electric utilities’ natural disaster preparedness and recovery plans by reviewing and maintaining current copies of the plans.

Each utility shall file updates of its storm hardening plans by March 1, 2007.  Our staff’s 2007 review of investor-owned electric utility reliability performance shall include an additional section addressing utility ongoing storm hardening initiatives.

Municipal Electric Utility and Rural Electric Cooperative Utility Storm Hardening Plans

In order to gauge the level of storm preparation throughout the State of Florida, our staff solicited storm hardening plans consistent with the requirements of Order PSC-06-0351-PAA-EI from the electric municipal utilities and the electric cooperative utilities.  There are 34 electric municipal utilities and 18 electric cooperative utilities operating in Florida. Our staff is continuing its efforts to collect information on plans and plan implementation from all such utilities.

Our initial assessment of the electric municipal utilities’ and the electric cooperative utilities’ plans are summarized below by initiative in a generalized format.

Initiative 1 – Three-Year Vegetation Trim Cycle

The electric municipal utilities’ and the electric cooperative utilities’ vegetation management programs are consistent with the intent of Order PSC-06-0351-PAA-EI.  Electric cooperative utilities using trim cycles greater than three years in rural areas assert that their vegetation trim clearance practices are more aggressive for these areas and provide better overall performance in terms of cost and customer outages than what would be achieved on a three-year cycle.

Initiative 2 – Joint-Use Pole Attachment Audits

At this time, most electric municipal (24) and cooperative (12) utilities perform field audits of the attachments.  Most of these utilities have not provided information regarding their practices for concluding pole strength assessments associated with joint-use poles.  However, these utilities design poles to the NESC safety standards and indicate they have experienced few pole failures due to overloading.  On August 8, 2006, our staff met with the Florida Electric Cooperatives Association, Inc. (FECA) and the Florida Municipal Electric Association, Inc. (FMEA) and the Associations indicated they will provide the information shortly.

Initiative 3 – Six-Year Inspection Cycle for Transmission Structures

Many electric municipal utilities (16) do not have transmission structures.  Most electric cooperative utilities (10) with transmission facilities reported inspection cycles of less than six years.

Initiative 4 – Storm Hardening Activities Associated with Wooden Transmission Structures

Of the electric municipal utilities and electric cooperative utilities which have wooden transmission facilities, some utilities plan to replace wood transmission poles with non-wood poles (9) while others do not (10).

Initiative 5 – Geographic Information System (GIS)

Most larger municipal (16) and most cooperative (9) electric utilities have an electronic GIS system.  Some municipal (6) and cooperative (4) electric utilities are in the process of implementing a GIS system. Many of the smaller utilities only have a paper system and do not plan to implement a GIS system.

Initiative 6 – Post-Storm Data Collection and Forensic Analysis

Most electric municipal utilities (28) and electric cooperative utilities (18) indicate that their current post-storm data collection programs meet the needs of the utility.  The post-storm reviews generally focus on identifying lessons learned.

Initiative 7 – Outage Data Differentiating Between Overhead and Underground Systems

Almost all the municipal and cooperative electric utilities reported that detailed outage data is routinely collected.  The electric municipal utilities and cooperative electric utilities are capable of providing overhead and underground performance data.

Initiative 8 – Increase Coordination with Local Governments

This initiative is primarily directed at increasing dialog and coordination regarding vegetation management issues and underground issues.  Municipal electric utilities tend to address these local issues through their governance process that includes public meetings.  The cooperative electric utilities assert their historical level of dialogue and interaction with local governments regarding vegetation management issues and undergrounding projects has been effective.

Initiative 9 – Collaborative Research

By Order No. PSC-06-0351-PAA-EI, the IOUs were directed to solicit participation from municipal and cooperative electric utilities.  As previously discussed, through FMEA and FECA,  electric municipal and cooperative utilities are participating in such a statewide collaborative research effort.

Initiative 10 – Disaster Preparedness and Recovery Plan

As of August 8, 2006, most municipal electric utilities did not indicate they have a natural disaster preparedness and recovery plan.  Most cooperative electric utilities indicated they have such a plan.  On August 8, 2006, our staff met with FECA and FMEA to clarify this initiative, and staff requested that the member utilities file their natural disaster preparedness and recovery plan with this Commission.  FECA and FMEA agreed to solicit such plans from their members and file the plans by August 22, 2006.

Based on the foregoing, it is

ORDERED by the Florida Public Service Commission that by September 28, 2006, Progress Energy Florida and Gulf Power Company shall file revised vegetation management plans which include appropriate means of evaluating the effectiveness of their programs, in compliance with Order No. PSC-06-0351-PAA-EI.  It is further

ORDERED that all investor-owned electric utilities shall file updates of their storm hardening plans by March 1, 2007.  Our staff’s 2007 review of investor-owned electric utility reliability performance shall include an additional section addressing utility ongoing storm hardening initiatives.  It is further

ORDERED that storm hardening initiatives 1 through 7 shall be monitored through this Commission’s annual review of distribution service reliability performance.  It is further

ORDERED that Initiative 8 shall be monitored for increased coordination with local governments through this Commission’s review of electric utilities’ dialogue with local governments and selected review of utility activities in this area.  It is further

ORDERED that Initiative 9 shall be monitored for collaborative research on effects of hurricane winds and storm surge by reviewing the electric utilities’ participation in studies and projects undertaken by the collaborative research efforts.  It is further

ORDERED that Initiative 10 shall be monitored regarding the investor-owned electric utilities’ natural disaster preparedness and recovery plans by reviewing and maintaining current copies of the plans.  It is further

ORDERED that Attachment A, attached to this Order, is incorporated herein by reference.  It is further

ORDERED that the provisions of this Order, issued as proposed agency action, shall become final and effective upon the issuance of a Consummating Order unless an appropriate petition, in the form provided by Rule 28-106.201, Florida Administrative Code, is received by the Director, Division of the Commission Clerk and Administrative Services, 2540 Shumard Oak Boulevard, Tallahassee, Florida 32399-0850, by the close of business on the date set forth in the "Notice of Further Proceedings" attached hereto.  It is further

ORDERED that this docket shall remain open for Progress Energy Florida and Gulf Power Company to file revised vegetation management plans.

By ORDER of the Florida Public Service Commission this  19th day of September, 2006.

|  | BLANCA S. BAYÓ, Director Division of the Commission Clerk and Administrative Services |
| --- | --- |

| By: | /s/ Kay Flynn |
| --- | --- |
|  | Kay Flynn, Chief Bureau of Records |

This is a facsimile copy. Go to the Commission's Web site, http://www.floridapsc.com or fax a request to 1-850-413-7118, for a copy of the order with signature.

( S E A L )

RG

NOTICE OF FURTHER PROCEEDINGS OR JUDICIAL REVIEW

The Florida Public Service Commission is required by Section 120.569(1), Florida Statutes, to notify parties of any administrative hearing that is available under Section 120.57, Florida Statutes, as well as the procedures and time limits that apply.  This notice should not be construed to mean all requests for an administrative hearing will be granted or result in the relief sought.

Mediation may be available on a case-by-case basis.  If mediation is conducted, it does not affect a substantially interested person's right to a hearing.

The action proposed herein is preliminary in nature. Any person whose substantial interests are affected by the action proposed by this order may file a petition for a formal proceeding, in the form provided by Rule 28-106.201, Florida Administrative Code.  This petition must be received by the Director, Division of the Commission Clerk and Administrative Services, 2540 Shumard Oak Boulevard, Tallahassee, Florida 32399-0850, by the close of business on October 10, 2006.

In the absence of such a petition, this order shall become final and effective upon the issuance of a Consummating Order.

Any objection or protest filed in this/these docket(s) before the issuance date of this order is considered abandoned unless it satisfies the foregoing conditions and is renewed within the specified protest period.

Initiative 1 – A Three-year Vegetation Management Cycle for Distribution Circuits

Order Requirement:

1.	3 Year Tree Trim Cycle for Primary Feeders (minimum).

2.	3 year cycle for laterals as well, if not cost prohibitive.

3.	Utilities may propose alternatives to the requirements described below.  Any alternatives must include a complete description of the alternative as well as the reason why the alternative is equivalent or better in terms of cost and avoiding future storm damages.

4.	Timeline for implementation.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million)* | Utility Alternative Incremental Cost Impact ($ million)* |
| --- | --- | --- | --- |
| FPL | 1. Average 3 year trim cycle for feeders. 2. Average 6 year trim cycle for laterals, instead of 3 year cycle. 3. FPL’s analysis of its alternative focused on the lateral trimming program. FPL believes that its analysis, demonstrates that its proposed alternative is more cost effective. (The 3 year cycle would cost average $30.3 million per year more than the 6 year cycle, while providing a potential incremental benefit of 55,000 fewer storm-related Customer Interruptions.) 4. Year One for implementation is 2007. | Year One – $88.9 Annual - $43.4 | Year One –$15.5 Annual - $12.9 |
| PEF | 1. Targeted feeder trim based on prioritization (3 year weighted average trim cycle). 2. Not specified for laterals. 3. PEF provided reasons why it believes its alternative is better; however, there are no quantitative comparisons of the costs and benefits. 4. Year One for implementation is 2007. | Year One - $7 Annual – 3% minimum increase in tree trim budget | Year One – Annual – N/R |
| TECO | 1. Feeder trim based on prioritization (All trimmed every 3 years). 2. Every circuit including open secondaries, cabled secondaries, and appropriate services is trimmed every 3 years. 3. TECO’s program is a three-year trim-cycle program. 4. Year One for implementation is 2007. Assuming 2 to 3 year transition allowed to stabilize costs, conduct training, etc. | Year One – N/R Annual $3.4 | Not applicable. |
| GULF | 1. Reliability based trimming instead of cycle based. 2. Not based on fixed year cycle. 3. GULF provided reasons why it believes its alternative is better; however, there are no quantitative comparisons of the costs and benefits. 4. Year One for implementation is 2007. | Year One – Annual - $4.2 | Year One – NR Annual – N/R |
| FPUC | 1. All feeders on a three-year trim cycle. 2. Laterals may be on a three-year trim cycle or an alternative 5-year trim cycle in the NW service area. 3. The 5-year trim cycle is less expensive. 4. Year One for implementation is 2007. | Year One – N/R Annual - $.342 | Year One – N/R Annual - $.228 |

*	The incremental cost impact is based on comparisons with the existing trimming program forward.  “N/R” No Response.  Not Applicable.: Not Applicable.  “Year One” First Year of Implementation.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 2 – Audit of Joint-Use Attachment Agreements

Order Requirement:

1.	(a) Each investor-owned electric utility shall develop a plan for auditing joint-use agreements that includes pole strength assessments.

(b) These audits shall include both poles owned by the electric utility and poles owned by other utilities to which the electric utility has attached its electrical equipment.

2.	The location of each pole, the type and ownership of the facilities attached and the age of the pole and the attachments to it should be identified.

3.	Each investor-owned utility shall verify that such attachments have been made pursuant to a current joint-use agreement.

4.	Stress calculations shall be made to ensure that each joint-use pole is not overloaded or approaching overloading for instances not already addressed by Order No. PSC-06-0144-PAA-EI.

5.	Provide compliance cost estimate and cost estimate for alternative action if any.

6.	Provide a timeline for implementation.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) * | Utility Alternative Incremental Cost Impact ($ million) * |
| --- | --- | --- | --- |
| FPL | 1. (a) Plan includes performing pole strength assessment during eight-year wood pole inspection cycle. (b) Plan includes auditing all FPL owned and third-party poles during eight-year wood pole inspection cycle. 2. All required data will be collected during inspections and stored in the attachment information database. 3. Will verify attachments have been made pursuant to current joint-use agreement through a 5 year system wide pole attachment survey. 4. Stress calculations will be performed during eight-year wood pole inspection cycle. 5. See columns to the right. 6. Plan will be initiated January 2007 with completion cycles of eight-years. | Annual - $1.2 – 1.5 | Not Applicable |
| PEF | 1. (a) Plan includes performing pole strength assessment during eight-year wood pole inspection cycle. (b) Plan includes auditing all PEF owned and third-party poles during eight-year wood pole inspection cycle. 2. All required data will be collected on select poles and stored in electronic format. 3. Will verify attachments have been made pursuant to a current joint-use agreement during eight-year wood pole inspection cycle. 4. Stress calculations will be performed on select poles during eight-year wood pole inspection cycle. 5. See columns to the right. 6. Plan initiated 2006 with completion cycles of eight-years. | Annual - $.080 | Not Applicable |
| TECO | 1. (a) Plan includes performing pole strength assessment during eight-year wood pole inspection cycle. (b) Plan includes auditing all TECO owned poles and third-party poles per Joint-Use contract agreements on a eight-year cycle. 2. All required data will be collected during the eight-year wood pole inspection cycle and stored in GIS database. 3. Will verify attachments have been made pursuant to a current joint-use agreement during eight-year wood pole inspection cycle. 4. Stress calculations will be performed during eight-year wood pole inspection cycle. 5. See columns to the right. 6. Plan will be initiated January 2007 with completion cycles of eight-years. | Annual - $5 | Not Applicable |
| Gulf | 1. (a) Plan proposes to do pole strength assessment on 5% random sample of Gulf owned poles that are 20 years old or more and with 3 or more attachments. (b) Plan includes auditing all Gulf owned poles and third-party poles per Joint-Use contract agreements on a 10 year cycle. 2. All required data will be collected and stored during 10 year inspection cycle. 3. Will verify attachments have been made pursuant to current joint-use agreement through a 10 year cycle. 4. Stress assessment will be performed on 5% random sample of Gulf owned poles that are 20 years old or more and with 3 or more attachments. 5. See columns to the right. 6. Plan will be initiated January 2007 with completion cycles of 10 years. | Annual - $5.375 | Not Applicable |
| FPUC | 1. (a) Plan includes performing pole strength assessment during eight-year wood pole inspection cycle. (b) Plan includes auditing all FPUC owned and third-party poles during eight-year wood pole inspection cycle. 2. All required data will be collected during inspections and stored in a database. 3. Will verify attachments have been made pursuant to a current joint-use agreement during eight-year wood pole inspection cycle. 4. Stress calculations will be performed during eight-year wood pole inspection cycle. 5. See columns to the right 6. Plan will be initiated January 2007 with completion cycles of eight-years. | Annual - $.020 | Not Applicable |

*	Incremental cost impact is calculated using 2005 as a base year.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 3 – Six-year Transmission Inspection Program

Order Requirement:

1.	Develop a plan to fully inspect all transmission towers and other transmission supporting equipment (such as insulators, guying, grounding, splices, cross-braces, bolts etc.).

2.	Develop a plan to fully inspect all substations (including relay, capacitor, and switching stations).

3.	Provide a timeline for implementation.

4.	Provide compliance cost estimate and cost estimate for alternative actions if any.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) * | Utility Alternative Incremental Cost Impact ($ million) * |
| --- | --- | --- | --- |
| FPL | 1. Wood pole inspection activities (PSC-06-0144-PAA-EI Docket No. 060078-EI). Circuits with structures containing wood cross-arm structures inspected at least every 4 years. Steel and/or concrete structures (no wood) inspection activities 10% sample every 4-year program will be augmented to achieve equivalent of a non-sample six-year inspection cycle. Inspection of insulators, wires, etc., are included in the augmented efforts. 2. Substations fully inspected quarterly. 3. Plan already implemented. 4. Estimated incremental costs relative to 2005 is $12.9 million, annually. | Annual - $2.3 | Not Applicable |
| PEF | 1. Wood pole inspection activities (PSC-06-0144-PAA-EI Docket No. 060078-EI). Structures on a 5-year inspection cycle. All other portions of the system: inspected on a three-year cycle. 2. Monthly visual substation inspection. 3. Plan already implemented. 4. Estimated incremental costs relative to 2005 is $0. | Annual - $ 0 | Not Applicable |
| TECO | 1. Wood pole inspection activities (PSC-06-0144-PAA-EI Docket No. 060078-EI). Structures on a 6 year cycle, All other portions of the system: inspected annually. 2. Substations fully inspected at least annually. 3. Plan already implemented. 4. Estimated incremental costs relative to 2005 is $0. | Annual - $2.97 | Not Applicable |
| Gulf | 1. Wood pole inspection activities (PSC-06-0144-PAA-EI Docket No. 060078-EI). All other portions of the system: Gulf does not hold itself to a rigid number of annual inspections. Period of 12 years will show that on average a six-year cycle is achieved. 2. Substations at least annually. Structures inside new substations built to withstand wind speed in excess of 150MPH. 3. Plan already implemented. 4. Estimated incremental costs relative to 2005 is $0. | Annual - $ 0 | Not Applicable |
| FPUC | 1. Will develop procedures for climbing inspections of owned 69 and 138 KV structures. Coordination/process for customer-owned 69 KV line will be developed. 2. No plan provided for substations. 3. Plan already implemented. 4. Estimated incremental costs relative to 2005 is $18,000, annually. | Annual - $.018 | Not Applicable |

*	Incremental cost impact is calculated using 2005 as a base year.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 4 – Hardening of Existing Transmission Structures

Order Requirement:

1.	Develop a plan to upgrade and replace existing transmission structures.  Provide scope of activity, limiting factors, and criteria for selecting structure to upgrade and replace.

2.	Provide a timeline for implementation.

3.	Provide compliance cost estimate and cost estimate for alternative actions if any.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) * | Company Alternative Incremental Cost Impact ($ million) * |
| --- | --- | --- | --- |
| FPL | 1. Incremental upgrades during relocations and other maintenance. Upgrade un-guyed single wood pole structures. Ceramic post line insulator replacements. 2. Plan completed in 10-15 years. 3. Estimated incremental costs relative to 2005 is between $3.3 and 6 million, annually. | One Time - $0 Annual - $3.3-6 | Not Applicable |
| PEF | 1. Incremental upgrades during relocations and other maintenance. 2. Plan completed in 10 or more years. 3. Estimated incremental costs relative to 2005 are $0. | One Time - $0 Annual - $2.8 | Not Applicable |
| TECO | 1. Incremental phase out of wood transmission structures during all new construction, relocations, and other maintenance. 2. Plan is on-going with no completion date. 3. Estimated incremental costs relative to 2005 are a one time cost of $2.5 million. | One Time - $2.5 Annual - $0 | Not Applicable |
| GULF | 1. Storm guy H-Frames. Replace wood cross-arms with steel cross-arms and other activities. 2. Plan completed in 10-15 years. 3. Estimated incremental costs relative to 2005 are $0.6 million. | One Time - $0.2 Annual - $0.6 | Not Applicable |
| FPUC | 1. Replacement of 180 wood poles on 69 KV line with concrete as necessary and when economically practical. 2. Plan is on-going with no completion date. 3. Estimated total cost is $4.5 million. | One Time - $4.5 Annual - $0 | Not Applicable |

*	Incremental cost impact is calculated using 2005 as a base year.  “One Time” refers to total project costs.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 5 - A Transmission and Distribution Geographic Information System

Order Requirement:

Develop a program that collects data -

1.  To conduct forensic reviews;

2.  To assess the performance of underground systems relative to overhead systems;

3.  To  determine whether appropriate maintenance has been performed; and

4.  To evaluate storm hardening options.

5.  Provide a timeline for implementation.

The utilities have the flexibility to propose a methodology that is efficient and cost effective

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) * | Utility Alternative Incremental Cost Impact ($ million) * |
| --- | --- | --- | --- |
| FPL | Transmission: FPL currently has its transmission lines and structures identified by geographic area and sub-area, and GPS location. 1. FPL’s proposed alternative does not include forensic reviews. 2. FPL’s proposed alternative does not include underground versus overhead. 3. FPL’s proposed alternative does not include determination of appropriate maintenance. 4. FPL’s proposed alternative does not include evaluation of storm hardening options. 5. None. Distribution: Combine existing analytical systems to have all facilities in a GIS platform, being able to identify performance of circuits and certain devices, providing a good forensic analysis of FPL’s facilities after a hurricane, identifying maintenance and providing a separate view of hardened facilities. 1. Combine existing analytical systems to have all facilities in a GIS platform, being able to identify performance of circuits and certain devices, providing a good forensic analysis of FPL’s facilities after a hurricane, identifying maintenance and providing a separate view of hardened facilities. 2. FPL’s proposed alternative does not include underground versus overhead. 3. FPL’s proposed alternative does not include determination of appropriate maintenance. 4. FPL’s proposed alternative does not include evaluation of storm hardening options. 5. Three years. | One Time - $14.55 Annual - $3.13 | One Time – $6.3 Annual - $.5 |
| PEF | Transmission: PEF plans to “populate” the system (present GIS system) with maintenance data that will be captured in PEF’s Transmission Line Inspection Plan. 1. PEF’s plan does not include forensic reviews. 2. PEF’s plan does not include underground versus overhead performance assessment. 3. PEF’s plan does not include determination of appropriate maintenance. 4. PEF’s plan does not include evaluation of storm hardening options. 5. Six years. Distribution: PEF plans to create an environment that contains all the elements referenced by the order, change its current GIS system from location driven to asset driven, and thereby be able to collect data from many sources which would provide it with the ability to look for trends in performance of individual assets. 1. PEF’s plan does not include forensic reviews 2. PEF’s plan does not include underground versus overhead. 3. PEF’s plan does not include determination of appropriate maintenance. 4. PEF’s plan does not include evaluation of storm hardening options 5. 6 years | One Time - $8.8 Annual - $.30 | Not Applicable |
| TECO | TECO is in the process of implementing a new GIS system. The field assets that will be incorporated in the GIS will include all distribution, transmission, substation and lighting facilities for TECO’s entire system. GIS, in conjunction with current OMS, will provide information on location and system performance. 1. TECO’s plan includes forensic reviews on a statistical sampled basis. 2. TECO’s plan includes forensic reviews with regard to types of materials and construction, and location 3. TECO’s plan does not include determination of appropriate maintenance. 4. TECO’s plan includes assessment of future preventive measures where possible. 5. Not Applicable. | One time - $.4 Annual – Not Applicable. | Not Applicable |
| Gulf | Gulf describes its GIS system, but does not mention location or performance data. 1. Gulf’s plan does include forensic reviews 2. Gulf’s plan does include underground versus overhead. 3. Gulf’s plan does include determination of appropriate maintenance. 4. Gulf’s plan does include evaluation of storm hardening options 5. 6 Years | One Time - $0 Annual - $.075 | Not Applicable |
| FPUC | 1-4. NW Fl Division currently has in place GIS system capable of collecting all of the necessary information. Additional procedures will be developed to ensure that NW Fl can use the data as ordered. 1-4. NE Florida Division does not have this capability but will upgrade its present system 5. Not Applicable. | One Time - $.19 Annual - $.0 | Not Applicable |

*	The incremental cost impact is based on comparisons with the existing trimming program going forward.  “Year One” refers to First Year of Implementation.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 6 – Post-Storm Data Collection and Forensic Analysis

Order Requirement:

1.	Develop a program that collects post-storm information for performing forensic analyses.

2.	Provide a timeline for implementation.

The utilities have the flexibility to propose a methodology that is efficient and cost effective.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) * | Utility Alternative Incremental Cost Impact ($ million) * |
| --- | --- | --- | --- |
| FPL | 1. Distribution: Divide a sample of damaged poles among forensics teams, observations will be made on all damaged samples. Capture information such as location, attachments, and area wind speed. Transmission: For the 2004 and 2005 storm season FPL used the storm management system called Orion Storm. The system captures 100% of the damaged impacted lines. Forty-one percent of the lines imported included detailed data collected with the Orion Storm Program. Fifty-nine percent of the lines impacted did not involve damaged facilities. FPL proposes to collect data for these transmission facilities to meet the Commission initiative. 2. Distribution: Available for 2006 storm season. Transmission: Currently activated program. | One Time - $0 Annual - $.050-.10 | Not Applicable |
| PEF | 1. Distribution: PEF has implemented the Forensic Assessment process for the upcoming 2006 storm season. Transmission: PEF will hire a contractor. The contractor will collect detailed post storm data necessary to perform storm damage and forensic analysis. 2. Available for 2006 storm season. | One Time - $0 Annual $.9/ per storm | Not Applicable |
| TECO | 1. Distribution & Transmission: TECO plans to implement a formal process to randomly sample system damage following a major weather event in a statistically significant manner. This information will be used to perform forensic analysis in an attempt to categorize the root cause of equipment failure. 2. 1 Year. | One time - $.2 Annual - $.1 per storm | Not Applicable |
| Gulf | 1. Distribution & Transmission: Concurrent with storm restoration, crews of contractors will survey a sample of the lines affected by the storm. Inland and coastal areas will be surveyed. 2. No Response. | One time - $0 Annual - $.125/per storm | Not Applicable |
| FPUC | 1. Distribution & Transmission: FPUC will develop a procedure to better track specific hurricane outages, identify outage causes, and count the numbers of customers affected. 2. No Response. | One Time - $.017 Annual - $.010/per storm | Not Applicable |

*	The incremental cost impact is based on comparisons with the existing trimming program going forward.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 7 – Collection of Detailed Outage Data Differentiating between the Reliability Performance of Overhead and Underground Systems

Order Requirement:

1.	Collect specific storm performance data that differentiates between overhead and underground systems, to determine the percentage of storm caused outages that occur on overhead and underground systems, and to assess the performance and failure mode of competing technologies such as direct bury cable versus cable-in-conduit, and concrete poles versus wooden poles, and location factors such as front-lot versus back-lot, and pad-mounted versus vault.

2.	Provide a timeline for implementation.

The utilities have the flexibility to propose a methodology that is efficient and cost effective.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) | Company Alternative Incremental Cost Impact ($ million) |
| --- | --- | --- | --- |
| FPL | 1. FPL proposes analyzing storm specific samples of locations (feeders, laterals, etc.) based on identifying GIS information established in compliance with initiatives #5 and #6. FPL does not plan to hold up storm restoration in order to ensure complete enumerations or adequate sample sizes for making valid inferences. FPL stresses that this would be particularly true of smaller storms, from which recovery is typically more rapid. Feeders tend to be hybrids with regard to underground and overhead. Forensics teams will be augmented to assess the damages to the various locations. Laterals tend to be either one or the other, so assessments with regard to overhead or underground will be available by knowing a lateral’s location. 2. No Response. | One Time - $0 Annual - $.05-.1/per storm | Not Applicable |
| PEF | 1. The implementation of the new GIS system would enhance PEF’s ability to collect data relevant to assess performance, and PEF would use this data to analyze and compare the performance of its overhead and underground systems. 2. No Response. | Response One Time – No Response Annual – No Response | Not Applicable |
| TECO | 1 TECO currently collects outage data. TECO will implement to fully comply with the Commission initiative for the collection of detailed outage data differentiating between the reliability performance of overhead and underground systems. 2. 1 Year. | One Time - $.5 Annual - $0 | Not Applicable |
| GULF | 1 Gulf will record numbers of overhead and underground customers and calculate SAIDI and SAIFI for each outage. As outages occur, Gulf will also collect data by type of buried cable and type of pole. 2. ¾ Year | One time - $0 Annual – minimal | Not Applicable |
| FPUC | 1. FPUC is currently able to carry out this initiative. 2. Available now. | One Time - $0 Annual - $0 | Not Applicable |

*	The incremental cost impact is based on comparisons with the existing trimming program going forward.  “One Time” refers to first year set-up costs..  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 8 – Increased Coordination with Local Governments

Order Requirement:

1.	 Each utility should actively work with local communities year-round to identify and address issues of common concern, including the period following a severe storm like a hurricane and also ongoing, multihazard infrastructure issues such as flood zones, areas prone to wind damage, development trends in land use and coastal development, joint use of public right-of-way, undergrounding facilities, tree trimming, and long range planning and coordination.

2. 	Provide a timeline for implementation.

3.	Incremental plan costs.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million)* | Company Alternative Incremental Cost Impact ($ million)* |
| --- | --- | --- | --- |
| FPL | 1, The FPL Plan focuses initially on storm preparation, coordination and communication with External Affairs representatives working with county planners and post-storm communications FPL plans to implement: - On-going planning programs with External Affairs representatives working with local government officials. - A special e-mail program oriented to government officials and special audiences. - A new government update website. - A program called “community trouble reporting. - Community outreach teams to brief local government and customer groups. 2. No specific timeline for implementation of the entire plan is provided except for a general reference to May 2006 marking the start date for some programs. 3. Incremental costs are only provided for the training ($25k) and Wire Down/Priority 1 ($12k) and Communications ($100k). No methodology for cost estimates are provided. | One Time - $.1 Annual - $.012 | Not Applicable |
| PEF | 1. The PEF Plan provides an internal team composed of community relations, regulatory affairs and account management to coordinate Company planning with governmental activities. The activities include assigning specific staff to work with individual communities to identify opportunities throughout the year for improved preparedness, developing enhanced organization and planning, providing support and information for storm preparation and restoration, conducting an annual storm drill, conducting on-going activities such as planning workshops and town-hall type meetings at both state and county levels. 2. No specific timeline for implementation of the entire plan is provided except for a general reference 2006 marking the start date for the programs. 3. Incremental costs for the Plan are not provided. No methodology for estimating cost are provided. | One Time – No Response Annual – No Response | Not Applicable |
| TECO | 1. TECO’s Plan calls for building on past community involvement by including local government, fire, police and water officials in storm preparation workshops, including local government in local Emergency Operations Centers, increased vegetation management including government and consumer education, undergrounding planning and education, and damage reporting prior, during and after storms. 2. No specific timeline for implementation of the entire plan is provided except for a general reference to some of the programs having already started in 2006. 3. Only a general incremental cost for the overall plan is provided ($75,000). No methodology for estimating costs is provided. | One time - $0 Annual - $.075 | Not Applicable |
| GULF | 1. The Gulf Plan builds on existing programs of year round activities like workshops with community leaders, pre-hurricane planning with participation in all local government hurricane preparedness drills, exercises, information fairs by line clearing specialists and post hurricane programs to include timely news announcements to government officials, single point-of-contact personnel and a standing Emergency Operations Center staffed 24 hours a day. 2. Gulf’s Programs are currently ongoing. 3. No incremental costs are provided since the programs are considered already ongoing. No methodology for estimating costs is provided. | One Time - $0 Annual - $0 | Not Applicable |
| FPUC | 1. The FPUC Plan calls for interacting with local governments in each of the separate divisions of the Company, having personnel at local Emergency Operations Centers after each storm, and engaging in discussions with local government on both undergrounding and tree trimming issues as they arise. 2. No specific timeline for implementation of the entire plan since the program is simply a continuation of the activities that were carried out in 2005. 3 No incremental cost were listed with the exception of an estimated cost of $7,500 per event that FPUC staff attended. No methodology for estimating costs were provided. | One Time - $0 Annual - $0 | Not Applicable |

*	Incremental cost impact is calculated using 2005 as a base year.  “One Time” refers first year set-up costs.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.

Initiative 9 – Collaborative Research

Order Requirement:

1.	IOUs must establish a plan that increases collaborative research

2.	IOUs must identify collaborative research objective

3.	IOUs must develop collaborative plans that promote cost sharing

4.	IOUs must solicit municipals, cooperatives, educational and research institutions.

5.	IOUs must establish timeline for implementation.

6.	IOUs must identify their incremental costs necessary to fund the organization and perform the research.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) * | Company Alternative Incremental Cost Impact ($ million) * |
| --- | --- | --- | --- |
| FPL | 1. FPL Indicates support for the creation of a non-profit, member supported organization that coordinates all research efforts in the area of storm effects on utility infrastructures. 2. FPL did not enumerate research objectives. FPL did not identify any specific research projects. 3. FPL proposed a non-profit, member supported organization for researching storm effects on utility infrastructure with PURC as the host. FPL suggested a single coordinator of research efforts from each member utility, and proposes an organization which would pursue two types of research; membership funded research voted on by the majority of members, and individually funded research (not voted or funded by other utilities). 4. FPL states the IOUs will solicit participation from the municipal and rural electric cooperative utilities in addition to available educational and research organizations. 5. No timeline for implementation was provided. 6. For cost requirements, see column to the right. | One Time - $0 Annual - $05-$.10 | Not Applicable |
| PEF | Same as FPL. | One Time - TBD Annual – TBD | Not Applicable |
| TECO | Same as FPL. | One Time - TBD Annual – TBD | Not Applicable |
| GULF | Same as FPL. In addition, Gulf plans on continuing to participate as appropriate within Southern Company and its own R&D efforts. Gulf may also engage in R&D through a local university in Northwest Florida. | One Time - TBD Annual – TBD | Not Applicable |
| FPUC | Same as FPL. Commitment to fund research regarding hurricane winds and storm surge. Requires reasonable allocation of costs based on customers, net load, etc. | One Time - $0 Annual - $.025 | Not Applicable |

*	Incremental cost impact is calculated using 2005 as a base year.  “One Time” refers first year set-up costs.  “Annual” refers to annual incremental cost impact incurred each year beginning with the first year of implementation.  “TBD”“ is abbreviation for “To Be Determined.”

Initiative 10 – A Natural Disaster Preparedness and Recovery Program

Develop a formal Natural Disaster Preparedness and Recovery Plan that outlines the utility’s disaster recovery procedures if the utility does not already have one.

| Utility | Investor-Owned Electric Utility Plan to Comply with Order | PSC Incremental Cost Impact ($ million) | Company Alternative Incremental Cost Impact ($ million) |
| --- | --- | --- | --- |
| FPL | Disaster Preparedness/Recovery Plan already developed and filed . | Not Applicable | Not Applicable |
| PEF | Disaster Preparedness/Recovery Plan already developed and filed. | Not Applicable | Not Applicable |
| TECO | Disaster Preparedness/Recovery Plan already developed and filed. | Not Applicable | Not Applicable |
| GULF | Disaster Preparedness/Recovery Plan already developed and filed. | Not Applicable | Not Applicable |
| FPUC | Disaster Preparedness/Recovery Plan already developed and filed. | Not Applicable | Not Applicable |

Issued February 27, 2006, in Docket No. 060078-EI, In re: Proposal to require investor-owned electric utilities to implement ten-year wood pole inspection program.