217

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3                                      DOCKET NO. 030623-EI

4          In the Matter of:

5   COMPLAINTS BY OCEAN PROPERTIES, LTD.,

J.C. PENNEY CORP., TARGET STORES, INC.,

6   AND DILLARD'S DEPARTMENT STORES, INC.

AGAINST FLORIDA POWER & LIGHT COMPANY

7   CONCERNING THERMAL DEMAND METER ERROR.

_______________________________________/

8

9             ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

10               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

11

12                              VOLUME 2

13                        Pages 217 through 430

14   PROCEEDINGS:        HEARING

15   BEFORE:             COMMISSIONER J. TERRY DEASON

COMMISSIONER RUDOLPH "RUDY" BRADLEY

16                       COMMISSIONER CHARLES M. DAVIDSON

17   DATE:               Thursday, November 4, 2004

18   TIME:               Commenced at 9:35 a.m.

Concluded at 4:45 p.m.

19

PLACE:              Betty Easley Conference Center

20                       Room 148

4075 Esplanade Way

21                       Tallahassee, Florida

22   REPORTED BY:        TRICIA DEMARTE, RPR

Official FPSC Reporter

23                       (850) 413-6736

24   APPEARANCES:        (As heretofore noted.)

25

FLORIDA PUBLIC SERVICE COMMISSION

218

1                              I N D E X

2                              WITNESSES

3   NAME:                                                PAGE NO.

4   GEORGE BROWN

5        Continued Cross Examination by Mr. Hoffman      220

Redirect Examination by Mr. Hollimon            225

6

7   BILL SMITH

8        Direct Examination by Mr. Moyle                 229

Prefiled Direct Testimony Inserted              231

9        Cross Examination by Mr. Hoffman                251

Redirect Examination by Mr. Moyle               259

10

11   SIDNEY W. MATLOCK

12        Direct Examination by Mr. Keating               261

Prefiled Direct Testimony Inserted              264

13        Cross Examination by Mr. Moyle                  277

Cross Examination by Mr. Hoffman                287

14        Redirect Examination by Mr. Keating             290

15

EDWARD C. MALEMEZIAN

16

Direct Examination by Mr. Hoffman               293

17        Prefiled Rebuttal Testimony Inserted            297

Cross Examination by Mr. Hollimon               339

18        Redirect Examination by Mr. Hoffman             371

19

BILL GILMORE

20

Direct Examination by Mr. Hollimon              378

21        Prefiled Rebuttal Testimony Inserted            380

Cross Examination by Mr. Menton                 390

22        Redirect Examination by Mr. Hollimon            422

23

24   CERTIFICATE OF REPORTER                              430

25

FLORIDA PUBLIC SERVICE COMMISSION

219

1                              EXHIBITS

2   NUMBER:                                        ID.   ADMTD.

3   9         5/6/03 Letter                        224   228

4   6                                                    227

5   7                                                    227

6   10        Excerpts of Deposition Transcript

of B. Faircloth                      228   228

7

11        Excerpts of Deposition Transcript

8             of K. Herbster                       228   228

9   12        Excerpts of Deposition Transcript

of J. Teachman                       228   228

10

8                                                    228

11

13        Prefiled Direct Exhibits A-O of

12             B. Smith                             230   261

13   14        Correction Sheet to S. Matlock's

Prefiled Testimony and Exhibits      262   292

14

15        SWM-1 and SWM-2                      263   292

15

16        BG-1 through BG-4                    379   424

16

17        Deposition of J. DeMars              426   426

17

18        Deposition of C. Cain                426   426

18

19        Deposition of B. Faircloth           426   426

19

20        Deposition of H. Hutchinson          426   426

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

220

1                         P R O C E E D I N G S

2             (Transcript follows in sequence from Volume 1.)

3                            GEORGE BROWN

4   continues his testimony under oath from Volume 1:

5                     CONTINUED CROSS EXAMINATION

6   BY MR. HOFFMAN:

7        Q    Okay.  So you reached your conclusion in 2002 that

8   these meters supposedly were overregistering when FPL last

9   calibrated the meters, and this occurred right after the meter

10   test; correct?

11        A    That's what this is saying, yes.

12        Q    Well, this is your deposition testimony.

13        A    Yes, that's correct.

14        Q    Is that correct?

15        A    That is correct.  After I had talked with some

16   experts in the field, they assured me there was no other way.

17        Q    Okay.  And you reached this conclusion well before --

18   many months before you took the first deposition of an FPL

19   meter tester regarding FPL's meter testing and calibration

20   procedures; correct?

21        A    Yes, that is correct.

22        Q    And it was perhaps a year or so before Mr. Smith

23   educated you on meter design components and the intricacies of

24   how thermal demand meters work; correct?

25        A    That was well before I had any discussions with

FLORIDA PUBLIC SERVICE COMMISSION

221

1   Mr. Smith.  I had discussions with other experts.

2        Q    So the answer to my question is yes?

3        A    Yes.

4        Q    So you essentially came out early, if you will, with

5   a position of multiyear and ten-year refunds with FPL and

6   seeked (phonetic) to negotiate off of that position; correct?

7        A    That -- say that again, please.

8        Q    Yes.  You came out to FPL, you communicated to FPL in

9   2002, before this docket was even opened, a position that would

10   secure you the highest amount of money that these -- your

11   position that these meters had all been miscalibrated, and

12   thereafter, you sought to negotiate this case with FPL; isn't

13   that true?

14        A    What you're saying is true.  The difference being the

15   most reasonable thing to consider is that the meters were

16   miscalibrated.  If you may or may not recall that my contact

17   with Mr. Bob Armstrong was when the first meters we ever had

18   tested were tested in the field.  And Mr. Armstrong was

19   accepted by Florida Power & Light as a metering specialist,

20   that he followed all the various needs to do that testing.  His

21   testing matched Florida Power & Light's testing, and he is an

22   engineer, electrical engineer, was also an employee of Landis &

23   Gyr and assured me there was no way other than miscalibration

24   of these meters for them to go high.

25             MR. HOFFMAN:  Mr. Chairman, I'm going to move to

FLORIDA PUBLIC SERVICE COMMISSION

222

1   strike that response.  My question was whether he communicated

2   early with FPL a position of multiyear refunds and negotiated

3   off of that.  His explanation goes beyond that question, is

4   hearsay, and I move to strike it.

5             COMMISSIONER DEASON:  Okay.  There's an objection.

6             MR. HOLLIMON:  Well, he asked -- the question was

7   what's the basis of your statement, and he just supplied the

8   basis.

9             COMMISSIONER DEASON:  I'm going to allow the answer.

10   You may proceed, Mr. Hoffman.

11             MR. HOFFMAN:  Thank you, Commissioner.

12             COMMISSIONER DEASON:  Mr. Hoffman, how much more do

13   you have for this witness?

14             MR. HOFFMAN:  I probably have about 45 minutes.

15             COMMISSIONER DEASON:  Well, we need a break then.

16   We'll break for lunch.  Let's try to be back here at 1:30, if

17   we can.

18             (Lunch recess.)

19             COMMISSIONER DEASON:  Call the hearing back to order.

20   Mr. Hoffman, you were inquiring.  Oh, and just so that you

21   know, you have used 58 minutes of your allotted time.

22             MR. HOFFMAN:  I think I've curtailed it quite a bit,

23   Commissioner Deason.  I think I should be able to finish this

24   up in about 10 minutes.

25             COMMISSIONER DEASON:  Great.

FLORIDA PUBLIC SERVICE COMMISSION

223

1   BY MR. HOFFMAN:

2        Q    Mr. Brown, if you could, could you turn to your

3   rebuttal testimony?  On Page 8 of your rebuttal, beginning at

4   Line 20 through Page 9, Line 1 of your rebuttal, you state that

5   the before and after billing differential approach should be

6   used for the meters in this docket, and you support -- you cite

7   to a Florida statute.  Do you see that passage?

8        A    Say that again, please.

9        Q    Sure.  On Page 8 at Line 20 through Page 9, Line 1 of

10   your rebuttal, you state that the before and after billing

11   differential approach should be used for the meters in this

12   docket; is that correct?

13        A    Yes.

14        Q    Okay.  And you cite a Florida statute; correct?

15        A    Say that again, the last part.

16        Q    I'm sorry.  You cite a Florida statute in support of

17   your position.

18        A    That's correct.

19        Q    Isn't it true that FPL made this before and after

20   methodology available to you on behalf of your clients, and you

21   rejected that offer because FPL's proposal also included a

22   one-year refund?

23        A    Florida Power & Light -- that's correct.  We rejected

24   a portion of your offer.  That's correct.

25        Q    And you would agree that the customers who are not in

FLORIDA PUBLIC SERVICE COMMISSION

224

1   this docket to whom you draw a comparison received a one-year

2   refund from FPL together with the higher of the meter test or

3   the before and after kW demand billing approach; correct?

4        A    The customers that are not in this docket received,

5   that's correct.

6        Q    Okay.  I'm going to ask Mr. Menton to assist me here

7   and hand you a document.

8             MR. HOFFMAN:  Commissioner Deason, I'm handing out

9   copies of a letter dated May 6, 2003, from me to Mr. Brown and

10   would ask that that letter be marked for identification.

11             COMMISSIONER DEASON:  Exhibit 9.

12             MR. HOFFMAN:  Thank you.

13             (Exhibit 9 marked for identification.)

14   BY MR. HOFFMAN:

15        Q    Do you have that letter in front of you that's been

16   marked as Exhibit 9?

17        A    Yes, I do.

18        Q    Okay.  Mr. Brown, do you recall receiving this

19   letter?

20        A    Yes, I do.

21        Q    Is that your signature on Page 2 of this letter?

22        A    Yes, it is.

23        Q    Mr. Brown, if you turn to Page 17 of your rebuttal,

24   beginning with Line 16, and you go through Page 18 of your

25   testimony, that's where you talk about the issue of whether the

FLORIDA PUBLIC SERVICE COMMISSION

225

1   refund period for the J.C. Penney's account should include the

2   higher kWh charge under the GSD-1 rate; is that correct?

3        A    Let me read that, if I can.

4        Q    Okay.

5        A    That is correct.

6        Q    Are you aware that this J.C. Penney's account has

7   been on the GSD rate since September of 2003?

8        A    That's correct.

9        Q    And are you aware that they have not sought to

10   contract up to the GSLD-1 rate?

11        A    They have not opted to do that at this time.

12             MR. HOFFMAN:  Commissioner Deason, we have nothing

13   further.

14             COMMISSIONER DEASON:  Staff.

15             MR. KEATING:  No questions.

16             COMMISSIONER DEASON:  Commissioners.

17             Redirect.

18             MR. HOLLIMON:  Thank you.

19                        REDIRECT EXAMINATION

20   BY MR. HOLLIMON:

21        Q    Mr. Brown, you were asked some questions about

22   whether there's anything in the PSC rules that authorizes

23   before and after a refund calculation.  Do you recall that?

24        A    Yes, sir.

25        Q    Is there anything in the rules that prohibits before

FLORIDA PUBLIC SERVICE COMMISSION

226

1   and after?

2             MR. HOFFMAN:  I'm going to object, leading question.

3             COMMISSIONER DEASON:  The question is leading.  You

4   may need to rephrase, Mr. Hollimon.

5   BY MR. HOLLIMON:

6        Q    What do the PSC rules require in terms of how the

7   refund is calculated?

8        A    I don't have the rules right in front of me at the

9   present time.  I can't read it for you.  But its goal is to

10   make the customer whole or to refund to them what they were

11   overcharged.  And as far as I know, there is one rule that's at

12   the end of the section on refunds that does have to do with

13   when something can't be determined exactly, then you can use an

14   estimate back for the whole time period.

15        Q    Mr. Brown, you also were asked some questions about

16   the -- how you calculated your before period and your after

17   period for purposes of determining what the refund percentage

18   should be.  Do you recall that?

19        A    Yes, I do.

20        Q    Now, would you explain how you used the information

21   available to you to determine the after number?

22        A    Yes, I can.  In the example that Mr. Hoffman gave, I

23   was shown a history of 18 months of billing.  I took the 12

24   months prior to the billing, which would have been from

25   December to November, whatever it may be, I took the next 12

FLORIDA PUBLIC SERVICE COMMISSION

227

1   months after that period and then there were six additional

2   months.  I took the months that were from, I believe, January

3   through June and averaged the Januaries of '03 and '02 up

4   through June of averaging those months so that they were

5   comparative exactly of the month for month, not a 6-month

6   period or 18-month period compared to a 12-month period.

7             MR. HOLLIMON:  Thank you, Mr. Brown.

8             COMMISSIONER DEASON:  Okay.  Thank you, Mr. Brown,

9   for your testimony.  You may be excused.

10             (Witness excused.)

11             COMMISSIONER DEASON:  Exhibits.  Let's see, we have

12   prefiled Exhibits, I think, 6 and 7.  Are those moved?

13             MR. HOLLIMON:  Yes, move 6 and 7.

14             COMMISSIONER DEASON:  Without objection --

15             MR. HOFFMAN:  Commissioner, with respect --

16             COMMISSIONER DEASON:  You made objections earlier and

17   those rulings stand.  I'm going to admit 6 and 7.  And that

18   leaves Exhibits 8 and 9.

19             (Exhibits 6 and 7 admitted into the record.)

20             MR. HOFFMAN:  Commissioner, I do have an exhibit that

21   I need to offer in response to their exhibits.  They have

22   offered as part of composite Exhibit 6 the deposition

23   transcripts.  It's Exhibit 2 to Mr. Brown's direct testimony.

24   They have offered excerpts from the depositions of

25   Mr. Herbster, Mr. Faircloth, and Mr. Teachman, and we don't

FLORIDA PUBLIC SERVICE COMMISSION

228

1   object to that, but we do have the right under Rule 1.330(a)(4)

2   to introduce other parts of those depositions, and we wish to

3   offer those as exhibits as well.

4             COMMISSIONER DEASON:  Do you have copies of that?

5             MR. HOFFMAN:  Yes, sir.

6             COMMISSIONER DEASON:  Okay.  Please distribute that.

7   Mr. Hoffman, let's identify these.  Is there any particular

8   order?

9             MR. HOFFMAN:  Any order is fine, Commissioner.

10             COMMISSIONER DEASON:  Okay.  Well, then we'll begin

11   with Faircloth; that will be Exhibit 10.  Herbster will be 11

12   and Teachman, 12.

13             (Exhibits 10, 11, and 12 marked for identification.)

14             MR. HOFFMAN:  And we would move, Commissioners,

15   Exhibits 8 through 12.

16             COMMISSIONER DEASON:  Okay.  There's a motion to

17   admit Exhibits 8 through 12.  Any objection?

18             MR. HOLLIMON:  No objections.

19             COMMISSIONER DEASON:  Very well.  Hearing no

20   objection, show then that Exhibits 8 through 12 are admitted.

21             (Exhibits 8 through 12 admitted into the record.)

22             MR. HOFFMAN:  Thank you, Commissioner.

23             COMMISSIONER DEASON:  Okay.  I think we have one

24   other witness from the Customers at this point, Bill Smith.

25             MR. MOYLE:  I'm going to be handling Mr. Smith.

FLORIDA PUBLIC SERVICE COMMISSION

229

1                             BILL SMITH

2   was called as a witness on behalf of Ocean Properties, Ltd.,

3   J.C. Penney Corp., Dillard's Department Stores, Inc., and

4   Target Stores, Inc., and, having been duly sworn, testified as

5   follows:

6                         DIRECT EXAMINATION

7   BY MR. MOYLE:

8        Q    Please state your name and address for the record.

9        A    My name is Bill Smith.  My address is 33 South Easter

10   Island Circle, Englewood, Florida 34223.

11        Q    Have you caused direct testimony to be filed in this

12   docket?

13        A    Yes, I have.

14        Q    And have you caused exhibits to be filed along with

15   your direct testimony, Exhibits A through O?

16        A    Yes, sir, I have.

17        Q    If I asked you the questions as set forth in your

18   prefiled testimony today, would your answers to those questions

19   be the same?

20        A    Yes, sir.

21             MR. MOYLE:  I would ask that Mr. Smith's direct

22   testimony be inserted into the record.

23             COMMISSIONER DEASON:  Without objection?  Hearing

24   none, show that testimony inserted.

25             MR. MOYLE:  Okay.  And I would also ask that

FLORIDA PUBLIC SERVICE COMMISSION

230

1   Mr. Smith's exhibits be placed into the record.

2             COMMISSIONER DEASON:  Let's identify that.

3             MR. MOYLE:  I'm sorry.  Identify A through O maybe as

4   a composite exhibit.

5             COMMISSIONER DEASON:  Okay.  And this is attached to

6   the prefiled direct testimony?

7             MR. MOYLE:  Yes, sir.

8             COMMISSIONER DEASON:  Okay.  That will be composite

9   Exhibit 13.

10             (Exhibit 13 marked for identification.)

11             MR. MOYLE:  And I would ask that that composite

12   Exhibit 13 been placed into the record.

13             COMMISSIONER DEASON:  We'll wait until after

14   cross-examination and allow you to move it at that time.

15             MR. MOYLE:  Okay.

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

248

1   BY MR. MOYLE:

2        Q    Mr. Smith, have you prepared a brief summary of your

3   testimony?

4        A    Yes, sir, I have.

5        Q    Would you please provide it for the benefit of the

6   Commission at this time.

7        A    Hello, Commissioners.  My name is Bill Smith.  I am

8   testifying today about the meters that are the subject of this

9   docket, the TMT Duncan Landis & Gyr meter, my role in helping

10   design this type meter, my work history with Duncan Landis &

11   Gyr, and what I believe caused these meters to overregister

12   demand and when they started overregistering.

13             I'm an electrical engineer from Purdue University

14   where I graduated in 1961.  I worked for Duncan Landis & Gyr,

15   the manufacturer of these meters in dispute, from 1956 until

16   December 1972.  I continued to work in the fields of meters and

17   meter testing equipment my entire professional life until I

18   retired in 1995.  While at Duncan Landis & Gyr, my duties and

19   responsibilities included working on meter designs and working

20   in the area of quality control.  I was involved in designing

21   improvements to meters, including working with others on the

22   design of thermal demand meters like the ones in this docket.

23             Based upon my educational training in electrical

24   engineering, my familiarity with meters, including thermal

25   demand meters, my review of depositions and other filings made

FLORIDA PUBLIC SERVICE COMMISSION

249

1   in this case, I believe it likely that the meters in this

2   docket overregistered demand when first installed at the

3   customer's place of business and did not gradually begin

4   overregistering demand.

5             The thermal demand meter, compared to other meters,

6   is a relatively simple instrument tool -- measurement tool with

7   few critical parts.  I was not aware of thermal demand meters

8   gradually overregistering demand when I worked in quality

9   assurance at the meter manufacturer, Duncan Landis & Gyr.

10             Furthermore, FPL refused to allow me to inspect the

11   meters that are in this docket.  I believe it more likely that

12   given FPL's practice of testing the meters prior to installing

13   them that mistakes were made when testing or calibrating the

14   meters.  I became more convinced that the errors occurred prior

15   to installing the meters when I reviewed depositions of FPL

16   meter testers.  One FPL meter tester who tested and calibrated

17   many meters had never seen the Landis & Gyr manual which spells

18   out procedures for how to test and calibrate the thermal demand

19   meters that are in this docket.

20             FPL never used a meter test cover which the

21   manufacturer specifically recommends be used to improve meter

22   accuracy and efficiency.  Instead, FPL instructed its meter

23   testers to make adjustments quickly so as to not lose the heat

24   which helps make the meters accurate.  Rushing to make

25   adjustments is likely to result in error on occasion.  Another

FLORIDA PUBLIC SERVICE COMMISSION

250

1   FPL meter tester failed to compensate for backlash when

2   calibrating meters, contrary to the calibrating procedures

3   outlined in the manufacturer's manual.

4             FPL's written directions provided to meter testers

5   indicated that the meter test board should be left energized

6   for approximately ten minutes to check for proper calibration

7   after a meter has been adjusted when the manufacturer stated

8   that in rechecking a calibration the load on the meter must

9   remain constant for a minimum of 45 minutes before taking a

10   reading.  FPL's procedure of waiting ten minutes might have

11   saved time, but it affected accuracy and was inconsistent with

12   the recommended practice of the manufacturer.

13             I relate these things since it makes me believe it

14   much more likely that errors occurred in the meters' test shop

15   rather than in the field with the meters somehow gradually

16   overregistering demand.  I also reviewed customer billing

17   records to see how the customers' accounts changed once the

18   faulty meters were removed.  I've reviewed the records of one

19   account that provided a review of the account before a thermal

20   meter was installed, a review of the account while the thermal

21   meter was in place, and a review of the overregistering thermal

22   demand meter was replaced.  The data from this one particular

23   account showed a level of demand that increased when the

24   thermal demand meter was installed, remained steady, then

25   decreased when the thermal demand meter was removed.

FLORIDA PUBLIC SERVICE COMMISSION

251

1             My review of this data leads me to the conclusion

2   that the meters in dispute may have been overregistering for

3   longer than 12 months and I believe overregistering when they

4   were originally installed in the customer's business locations.

5   This concludes my summary.

6             MR. MOYLE:  The witness is available for

7   cross-examination.

8             COMMISSIONER DEASON:  Mr. Hoffman.

9             MR. HOFFMAN:  Thank you, Commissioner.

10                          CROSS EXAMINATION

11   BY MR. HOFFMAN:

12        Q    Good afternoon, Mr. Smith.

13        A    Good afternoon, sir.

14        Q    The meter testers that you were referring to in the

15   summary of your testimony, isn't it true that those meter

16   testers did not conduct the tests in the early 1990s on the

17   meters at issue in this docket?

18        A    I'm not sure when they worked at FPL.  Is that what

19   you're talking about?

20        Q    Yes.

21        A    I do not recall that.

22        Q    So you don't know one way or the other whether --

23        A    That's correct, sir.

24        Q    Okay.  Let me -- just as a point of clarification,

25   Mr. Smith, on Page 1 of your testimony on Line 18, you talk

FLORIDA PUBLIC SERVICE COMMISSION

252

1   about going to work for Duncan Landis & Gyr in 1958.  Now, just

2   as a point of clarification, Landis & Gyr did not purchase

3   Duncan until 1976; correct?

4        A    That's correct.

5        Q    Okay.  And during your time at Duncan, you worked on

6   test equipment; correct?

7        A    That is correct.

8        Q    And you also designed and built test equipment --

9        A    Yes, sir.

10        Q    -- and repaired test equipment?

11        A    Yes, sir.

12        Q    And the positions that you held after you left Duncan

13   that you outline on Page 1 of your testimony did not involve

14   thermal demand meters or testing or calibration of thermal

15   demand meters; true?

16        A    That's true.  But I believe there's a clarification

17   in the previous question.  I did more than just test equipment

18   and test equipment design while I was employed with Duncan

19   Electric.

20        Q    And since your retirement in 1996; is that right?

21        A    '95.

22        Q    '95.  Okay.  You have not been involved in any work

23   on thermal demand meter issues until you were retained by

24   Mr. Brown's consulting firm to testify in this case; correct?

25        A    That is correct, sir.

FLORIDA PUBLIC SERVICE COMMISSION

253

1        Q    Okay.  Now, the TMT model, which is the type of

2   thermal demand meter involved in this docket, was

3   first manufactured by Duncan in 1974 after you left the

4   company; true?

5        A    The thermal demand may be true, yes, sir.

6        Q    I'm sorry?

7        A    That may be true.  The design was certainly started

8   long before that.

9        Q    Okay.  But the TMT model, which is the type of model

10   of thermal demand meter at issue in this docket, was

11   first manufactured by Duncan in '74 after you left the company.

12        A    I do not argue with that sir, no.

13        Q    Okay.  As I understand it, Mr. Smith, the only meter

14   testing that you did when you were at Duncan was for quality

15   control of the test equipment, like a test rack; correct?

16        A    That is basically correct.

17        Q    It was not for calibration?

18        A    I was not hired as a meter calibrator and did not

19   perform as a meter calibrator.

20        Q    Okay.  On Page 2, Mr. Smith, of your testimony, you

21   state that you do not believe it's likely for the TMT model

22   thermal demand meter to gradually overregister demand.  Do you

23   see that?

24        A    Yes, sir.

25        Q    Okay.  You do agree, do you not, that these types of

FLORIDA PUBLIC SERVICE COMMISSION

254

1   meters can overregister demand due to imperfections in all of

2   the components?

3        A    Things are possible but not probable.  So if you're

4   asking me, is it possible?  Yes.  Is it probable?  No.

5        Q    And the very fact that there are adjustment screws on

6   the meters is because the meters can underregister or

7   overregister; correct?

8        A    The adjustment screws are put on the meter during the

9   design stage basically to offset variations that occur in the

10   design from meter to meter, and therefore, they can be

11   corrected to 100 percent accuracy with these screws.

12        Q    Okay.  But isn't it true that these adjustment screws

13   on the meters are there because these meters, in fact, can

14   underregister or overregister?

15        A    In the original design stage, yes, sir.

16        Q    Okay.  And you cannot say with certainty that a TMT

17   meter would not gradually overregister demand; correct?

18        A    That is correct.

19        Q    As I understand your testimony, you believe that

20   overregistration is more likely to occur from a step function

21   as opposed to a gradual occurrence; is that correct?

22        A    That is correct.

23        Q    And that step function could involve any number of

24   the components that are in a TMT meter; correct?

25        A    That is correct, sir.

FLORIDA PUBLIC SERVICE COMMISSION

255

1        Q    Now, when you were at Duncan, Mr. Smith, in your

2   experience there, it was not unusual to run into problems or

3   issues with the quality or the capability of the materials that

4   were used in building the meter; correct?

5        A    That is correct, sir, if you're talking about doing

6   testing on the materials to make sure that they were

7   satisfactory for manufacturing.

8        Q    And the practice would then be to make design

9   adjustments to address those issues with the materials or the

10   components; correct?

11        A    That is correct.

12        Q    But that did not mean that the components were not

13   subject to corrosion or breakdown once the meters were placed

14   into service; true?

15        A    Testing did indicate whether they would hold up for

16   many years of service under adverse conditions, yes, it did.

17        Q    So the components of the meters were still subject to

18   corrosion or breakdown once they were placed into service.

19        A    Yes.

20        Q    Now, you have a number of exhibits to your testimony.

21   You've attached a Landis & Gyr manual and a Sangamo manual.

22   Those contain a number of pages, do they not, instructing how

23   to repair and replace various parts or components of the meter,

24   don't they?

25        A    Yes, they do.

FLORIDA PUBLIC SERVICE COMMISSION

256

1        Q    And you would agree, would you not, that the TMT

2   meter has a built-in permanent sun shield?

3        A    Yes, it does.

4        Q    And isn't it true that there are a lot of

5   design-related reasons that can cause a meter to overregister

6   such as the wrong number of turns on the tertiary coil?

7        A    Yes.  But these should be discovered at calibration

8   time of meter qualification.

9        Q    And a meter can overregister due to the wrong number

10   of turns on the toroidal coil?

11        A    That is correct.  Again, it should be caught at

12   testing.

13        Q    And a meter can overregister because the magnetics

14   are different than they should have been, the housings are not

15   correct; is that true?

16        A    That's true.

17        Q    But again, that's why the adjustment screws are on

18   the meter?

19        A    Again, I would refer you to my original statement.

20   The basic reason for adjustment screws are to take out

21   inconsistencies of manufacture.

22        Q    But these adjustment screws are there to compensate

23   for problems that may arise from time to time with the tertiary

24   coil, with the magnetics, with the housings and so forth;

25   correct?

FLORIDA PUBLIC SERVICE COMMISSION

257

1        A    Only at time of manufacture.

2        Q    Not when they're out in the field?

3        A    No, sir.

4        Q    Okay.  Why are the adjustment screws on the meter

5   once the meters have been placed into service?

6        A    Basically because the utility wanted them there.

7   They did not necessarily trust the manufacturers to test

8   equipment to do things correctly, so they wanted some control.

9        Q    Do you have your deposition with you, Mr. Smith?

10        A    Yes, I do.

11        Q    Would you turn to Page 67 of your deposition.  Do you

12   have that in front of you, sir?

13        A    Yes.  Excuse me.  I'm looking at the wrong page.  67.

14        Q    Page 67.

15        A    Way in the back.  I have it, sir.

16        Q    Okay.  If you would just follow with me, Mr. Smith.

17   I'm going to start at Line 8 and read into the record the

18   deposition testimony that you provided through Line 17.

19             "Question:  What are some of the design reasons that

20   would cause a meter to run fast?

21             Answer:  Wrong number of turns on the tertiary coil,

22   wrong number of turns on the toroidal coil.

23             Question:  What else?

24             Answer:  Magnetics being different than it should

25   have been, but that's why they put adjustments on there so all

FLORIDA PUBLIC SERVICE COMMISSION

258

1   of -- can be compensated out."

2             Are you sticking with that testimony this afternoon?

3        A    Yes, sir.

4             MR. HOFFMAN:  I'm cutting a few out, Commissioner.

5   BY MR. HOFFMAN:

6        Q    Mr. Smith, the condition of not enough friction on a

7   maximum pointer, just by way of example, that black pointer

8   needle --

9        A    Yes, sir.

10        Q    -- these can cause a meter to overregister or

11   underregister; correct?

12        A    Since this allows the -- yes.  Let me explain.

13        Q    Sure.

14        A    Since this meter -- this hand could swing on a shaft

15   without enough friction.  Obviously, it could go to the right

16   or to the left, up scale, down scale.  It would have nothing to

17   do with the meter operation.

18        Q    Is it your testimony, Mr. Smith, that in connection

19   with this issue of backlash friction, that backlash friction is

20   very minor and that the effect of perhaps not removing backlash

21   on an overregistering meter is very small and cannot be

22   quantified?

23        A    I do not know the quantification, that is correct,

24   sir.

25        Q    Was my statement correct?

FLORIDA PUBLIC SERVICE COMMISSION

259

1        A    Yes, it is.

2        Q    Mr. Smith, isn't it true you have no direct evidence

3   that any of the meters in this docket overregistered demand due

4   to the affects of the sun?

5        A    Yes, sir.

6             MR. HOFFMAN:  No further questions.  Thank you,

7   Mr. Smith.

8             COMMISSIONER DEASON:  Staff.

9             MR. KEATING:  No questions.

10             COMMISSIONER DEASON:  Commissioners.

11             Redirect.

12             MR. MOYLE:  Just briefly.

13                        REDIRECT EXAMINATION

14   BY MR. MOYLE:

15        Q    Mr. Smith, based on your years of experience and your

16   involvement with thermal demand meters, do you believe it's

17   more likely than not that these meters were bad from the date

18   of installation as compared to gradually going bad over time?

19        A    That I do believe, sir.  Yes.

20        Q    And with respect to some of the causes that

21   Mr. Hoffman asked you about, you know, maybe this could have

22   happened, if you had been able to inspect the meters do you

23   think you would have been able to ascertain whether any of

24   those causes, some of those causes that Mr. Hoffman asked you

25   about had actually existed?

FLORIDA PUBLIC SERVICE COMMISSION

260

1             MR. HOFFMAN:  I'm sorry, Commissioner.  I'm going to

2   raise the same objection that was raised previously with this

3   issue of the ability to inspect.  The Customers filed a motion

4   to inspect the meters; it was denied.  They sought

5   reconsideration and that was denied.  So I don't think it's

6   relevant.

7             MR. MOYLE:  Maybe I can just make a proffer.

8             COMMISSIONER DEASON:  I think the record is clear.

9   You can move forward with your redirect.

10             MR. MOYLE:  I just want it to be clear from his

11   perspective that if he could have looked at that, that would

12   have made, you know, a difference.  He could have ruled some of

13   those things out.  If Mr. Hoffman is representing that he'll

14   agree to that for the purposes of a record, I'm fine.

15             COMMISSIONER DEASON:  You have proffered your opinion

16   as to what would have happened had that happened but that

17   didn't happen.  So let's move forward.  Okay?  You've made your

18   proffer.  It's in the record.

19             MR. MOYLE:  Okay.  I have nothing further.

20             COMMISSIONER DEASON:  Okay.  Exhibits.

21             MR. MOYLE:  We have --

22             COMMISSIONER DEASON:  Exhibit 13.

23             MR. MOYLE:  -- Exhibits A through O which you've

24   marked as composite Exhibit, I believe, 13.

25             COMMISSIONER DEASON:  That is correct.  You move

FLORIDA PUBLIC SERVICE COMMISSION

261

1   that.

2             MR. MOYLE:  We would like to move those in.

3             COMMISSIONER DEASON:  Without objection?  Hearing no

4   objection, show that composite Exhibit 13 is admitted.

5             (Exhibit 13 admitted into the record.)

6             COMMISSIONER DEASON:  Thank you, Mr. Smith, for your

7   testimony.  You may be excused.

8             (Witness excused.)

9             COMMISSIONER DEASON:  Staff witness is scheduled

10   next, I believe.

11             MR. KEATING:  I believe that's correct.  Staff would

12   call Mr. Sid Matlock.

13                          SIDNEY W. MATLOCK

14   was called as a witness on behalf of the Staff of the Florida

15   Public Service Commission and, having been duly sworn,

16   testified as follows:

17                         DIRECT EXAMINATION

18   BY MR. KEATING:

19        Q    Mr. Matlock, you have been sworn in already today; is

20   that correct?

21        A    Yes.

22        Q    Would you please state your name for the record.

23        A    My name is Sidney W. Matlock.

24        Q    And are you the same Sidney W. Matlock who prepared

25   prefiled direct testimony in this docket?

FLORIDA PUBLIC SERVICE COMMISSION

262

1        A    Yes, sir.

2        Q    And, Mr. Matlock, did you prepare Exhibits SWM-1 and

3   SWM-2 to your prefiled testimony?

4        A    Yes, sir, I did.

5        Q    Do you have any changes or corrections to make to

6   your prefiled testimony or exhibits at this time?

7        A    Yes, sir.  I have prepared a page of corrections

8   reflecting changes.  As filed, my testimony addressed one meter

9   that is not being addressed in this docket.  All but two of the

10   corrections to my testimony and exhibits are made to reflect

11   the correct list of meters.

12             MR. KEATING:  And, Commissioners, that list of

13   corrections was provided to the parties and to the court

14   reporter prior to the hearing.  We'd ask that that be marked

15   for identification.

16             COMMISSIONER DEASON:  It will be identified as

17   Exhibit 14.

18             (Exhibit 14 marked for identification.)

19   BY MR. KEATING:

20        Q    Mr. Matlock, other than noting the corrections you've

21   just identified, if I asked you the same questions included in

22   your prefiled testimony, would your answers be the same?

23        A    Yes, sir.

24             MR. KEATING:  Commissioner, staff asks that

25   Mr. Matlock's prefiled testimony be moved into the record as

FLORIDA PUBLIC SERVICE COMMISSION

263

1   though read.

2             COMMISSIONER DEASON:  Without objection, it shall be

3   so inserted.

4             MR. KEATING:  And staff also asks that his Exhibits

5   SWM-1 and SWM-2 be marked for identification.

6             COMMISSIONER DEASON:  Exhibit 15.

7             (Exhibit 15 marked for identification.)

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

275

1   BY MR. KEATING:

2        Q    Mr. Matlock, have you prepared a summary of your

3   testimony?

4        A    Yes.

5        Q    If you would.

6        A    Under the Commission rules, there's a multistep

7   process for determining whether a refund is due to a customer

8   and what amount is due to a customer whose meter is

9   overregistering the customer's actual usage.

10             First, he must test the meter against a standard to

11   determine whether the meter is overregistering beyond the error

12   limits allowed for that type of meter.  If so, the customer is

13   eligible for a refund.  For the meters in this case, the

14   Commission's rules establish a plus or minus 4 percent error

15   limit.  Second, you must determine a percentage of error to use

16   for purposes of calculating the proper refund amount.  Third,

17   you must determine the period of time for which the refund

18   should be calculated.  And finally, based on the results of the

19   second and third steps, you must calculate the refund due,

20   including interest.  My testimony addresses the first and

21   second steps in this process.

22             As I stated, the first step is to determine whether a

23   meter is overregistering beyond acceptable limits.  I recommend

24   that this be accomplished by testing each meter against a

25   standard while applying a level of demand to the meter that

FLORIDA PUBLIC SERVICE COMMISSION

276

1   reflects the peak kilowatt usage experienced on that meter in

2   its last 12 months of service.  The percentage of error would

3   then be calculated by dividing the difference between the

4   readings on the standard meter and the tested meter by the

5   full-scale reading on the meter.  You may hear this referred to

6   as the full-scale error.  Meters that exceed the 4 percent

7   error limit would then be eligible for a refund.  I believe

8   that this is consistent with the Commission's rules and is a

9   fair method of determining the maximum error that would have

10   likely been experienced by the customer.

11             The second step, as I previously mentioned, is to

12   determine the appropriate percentage of error to use for

13   purposes of calculating a refund.  I recommend that this be

14   accomplished by testing each eligible meter against a standard

15   while applying a level of demand to the meter that reflects the

16   average billing demand from the last 12 months of service.  The

17   percentage of error would then be calculated by dividing the

18   difference between the readings on the standard meter and the

19   tested meter by the reading on the standard meter.  You may

20   hear this referred to as the test point error.

21             The test point error would then be converted to a

22   correction factor that would be applied to the billing demands

23   for each month during the refund period.  The Commission's

24   rules are unclear when it comes to determining a percentage of

25   error for purposes of calculating a refund due to erroneous

FLORIDA PUBLIC SERVICE COMMISSION

277

1   demand readings.  However, I believe that the method I

2   recommend is consistent with the Commission's rules and is a

3   fair method of determining the meter error that would have

4   likely been experienced by the customer during the refund

5   period.  That concludes my summary.

6             MR. KEATING:  Staff tenders Mr. Matlock for cross.

7             COMMISSIONER DEASON:  Okay.  Which party wishes to go

8   first on this cross-examination?

9             MR. HOFFMAN:  I'd prefer to go last.

10             COMMISSIONER DEASON:  Okay.  Mr. Moyle.

11             MR. MOYLE:  Flip a coin.

12             COMMISSIONER DEASON:  You want to flip a coin?

13             MR. MOYLE:  Flip a coin, or odds or evens, scissor,

14   rock, paper.  I'll go ahead and go.

15             COMMISSIONER DEASON:  Okay.

16                          CROSS EXAMINATION

17   BY MR. MOYLE:

18        Q    Mr. Matlock, you had made a comment about the rules

19   being unclear.  Do you believe that the rules related to these

20   meters could be amended, changed, or updated to make them more

21   clear?

22        A    Yes, sir, I do.

23        Q    Would that be something that you would recommend as

24   somebody who's been with this Commission and familiar with

25   meters and meter testing, meter procedures, things like that?

FLORIDA PUBLIC SERVICE COMMISSION

278

1        A    I don't know that it would be necessary.  I don't

2   know that I would do that.  And I don't know that it's

3   necessary because that refund calculation is not something

4   that -- the way that I would do it is not something that our

5   rules prevent you from doing.  And I think it is consistent

6   with similar calculations that are carried out for kilowatt

7   hour meters.  And I don't know that it would be necessary to do

8   that to address these refunds.

9        Q    Okay.  You had made the comment about the rules don't

10   prevent you from doing that.  You've been in the room today,

11   have you not, and heard testimony about the before and after

12   approach that was used by FPL with respect to customers not in

13   this docket?

14        A    Yes, sir, I have heard that discussed.

15        Q    Are you aware of anything in the rules that would

16   prohibit the use of this before and after approach for a way of

17   determining meter error?

18        A    I don't -- there's not anything in the rules that say

19   to do it or not to do it.  The rules have a method of measuring

20   meter error.  And that's all that I have testified about.

21        Q    Okay.  And I looked at your testimony and I don't

22   have, you know, a tremendous amount with you, but on Line 20 of

23   Page 1, you indicated, the purpose of my testimony is to

24   explain the Commission's rules governing meter testing, meter

25   accuracy, refunds for inaccurate meters, and refund periods.

FLORIDA PUBLIC SERVICE COMMISSION

279

1   And, you know, we've heard testimony about what FPL did with

2   these meters and whatnot, and I was just trying to make sure

3   that from your perspective, being familiar with these rules,

4   that there was nothing in the rules that precluded FPL from

5   doing what they did with the before and after approach.  And

6   you would agree with me, there is nothing to prevent them from

7   doing that; correct?

8        A    I agree that there is nothing to prevent that.  We

9   first heard of that in an agreement that was made between the

10   customers and the utility.  And that was a -- it was a

11   negotiation.

12        Q    Who was that agreement with?  What customers?  Do you

13   know?  Or was it just a way -- FPL came to you and said, here's

14   how we propose to do it?

15        A    It was the customers who were represented by

16   Mr. Brown.

17        Q    The before and after approach?

18        A    Yes, sir.  It was in May of 2003.

19        Q    Okay.  And just so we're clear, Mr. Hoffman just used

20   an exhibit.  I think it was marked as Exhibit Number 9.

21             MR. MOYLE:  Can I approach the witness, and ask him

22   if this is what he's referencing with respect to the agreement?

23             COMMISSIONER DEASON:  Yes.

24             THE WITNESS:  Yes, sir.  This is what I'm

25   referencing.

FLORIDA PUBLIC SERVICE COMMISSION

280

1   BY MR. MOYLE:

2        Q    Were you a party to that discussion and that

3   agreement that's referenced in that document?  Were you

4   involved in those discussions?

5        A    I don't believe I would be considered a party, and

6   I'm not -- I wasn't involved in the discussions.  I just found

7   out that this agreement had been reached.

8        Q    I was going to ask you some questions about it if you

9   were in the room, but you weren't in the room; is that correct?

10        A    I wasn't in the room when the agreement was made.

11        Q    Okay.  Isn't it your understanding that FPL and

12   Mr. Brown on behalf of his customers agreed to test the meters

13   at 80 percent?

14        A    Yes, that was my understanding.

15        Q    Okay.  And you're not aware of anything that has

16   resulted in that agreement not being in place as we sit here

17   today, are you?  And that's still a deal as far as you're

18   concerned?

19        A    Yes, as far as I know that 80 percent test point is

20   still what is being used.

21        Q    Okay.  And with respect to your understanding about

22   what they agreed to, is it your understanding that there was an

23   agreement to use a before and after approach as well between

24   Mr. Brown and his customers and Florida Power & Light?  And I

25   can hand you the document if you need it.

FLORIDA PUBLIC SERVICE COMMISSION

281

1        A    As I recall, that method of calculating a percent

2   error to use was included in that agreement.

3        Q    Okay.  And then just if you know anything about this,

4   there's a sentence in the agreement that states as follows in

5   paragraph five, "Best efforts will be made by all parties to

6   settle all refunds in an expeditious manner; however, in the

7   event of a disputed claim that is not resolved by the parties,

8   no refund or credit shall be made pending final disposition of

9   the claim."  Do you have any information with respect to why

10   that sentence was inserted in this document?

11        A    No, sir, I don't.

12        Q    I asked you the leadoff question about are the rules

13   candidates for change and I think you indicated yes.  Some of

14   your testimony centers around 25-6.052(2)(a); correct?  And

15   this is the rule which requires meters to be accurate within

16   4 percent of full-scale when tested at any point between

17   25 percent to 100 percent of full-scale; correct?

18        A    Yes, sir, that's correct.  The wording of that rule

19   refers to error of registration of the demand meter.

20        Q    Right.

21        A    And it says that it does not -- it said that it

22   should not -- or the performance of the meter is acceptable if

23   that error of registration does not exceed 4 percent in terms

24   of full-scale value.  That's the actual exact wording of that.

25        Q    Okay.  And that's 25-6.052; correct?

FLORIDA PUBLIC SERVICE COMMISSION

282

1        A    (a).

2        Q    Okay.  Now, if I was reading your testimony properly

3   or correctly, the percentage of error changes depending on what

4   test point is selected; correct?

5        A    Yes, sir, that's true for -- that's generally true

6   for these meters that are in this docket.  The error of

7   registration increases measuring that error in kilowatts, and

8   as a result, that same error divided by the full-scale value of

9   the meter also increases.

10        Q    So am I correct, is it true that you could have --

11   let's say you tested the meter at 25 percent of full-scale,

12   that you could have an error reading that would be less than

13   4 percent, but if you moved up scale and tested it at

14   75 percent of full-scale value, that the error reading could

15   increase and be over 4 percent; correct?

16        A    Yes, sir, that is possible as it relates to these

17   meters.

18        Q    And that's sort of the basis for your suggestion and

19   say, hey, it's pretty critical as to where you test the meters,

20   what point on the scale; correct?

21        A    Yes, sir.

22        Q    Now, with respect to the rule that says that you can

23   test any point between 25 to 100 percent of full-scale, isn't

24   it true that customers when they're out there and they're using

25   electricity, that they're not going to be precisely at

FLORIDA PUBLIC SERVICE COMMISSION

283

1   25 percent or 30 percent?  I mean, they're going to vary with

2   respect to their usage; correct?  Isn't that partially why

3   you're making a recommendation of using their actual usage for

4   the test point?

5        A    Yes, sir, that's correct.

6        Q    And you're not advocating or urging or even believe,

7   do you, any sort of interpretation that would basically allow

8   for the following:  If you test the meter, say, at 25 percent

9   of full-scale and it's less than the 4 percent error point,

10   that you're done, that that's it?  As long as it tested once

11   at, say, anywhere between 25 and 100 percent, you know, the

12   meter is good to go.  That doesn't seem like a logical

13   interpretation of that rule, does it, to you?

14        A    I don't know that the rule as it's stated would

15   preclude that.  It's not the way I would do it if a customer's

16   load was greater than 25 percent if I were determining whether

17   or not the meter was accurate for his use.

18        Q    I understand.  I'm just trying to understand what you

19   believe the rule says with respect to the ability to test

20   between 25 and 100 percent.  I mean, obviously it's probably in

21   FPL's financial interest to test at a low point on the scale

22   for the reasons we just discussed, and conversely, it's in the

23   customer's interest to try to have it tested at a high point on

24   the scale.  You'd agree with that; correct?

25             MR. HOFFMAN:  I'm going to object to that question.

FLORIDA PUBLIC SERVICE COMMISSION

284

1   It's predicated on facts that are not in evidence.

2             COMMISSIONER DEASON:  Mr. Moyle, just rephrase your

3   question.

4             MR. MOYLE:  Okay.

5   BY MR. MOYLE:

6        Q    Would you agree that if FPL tested at 25 percent of

7   full-scale for all the meters, that they would have less meters

8   found to be in error as if they tested at 80 percent of

9   full-scale for meters based on your experience and testimony?

10        A    I don't think that that would -- I don't agree that

11   that would be to the utility's advantage to do that.

12        Q    Right.  But my question was, if they tested at

13   25 percent as compared to 80 percent, you would agree that

14   fewer meters would be found to be over 4 percent error;

15   correct?  We just talked about the proportional relationship.

16        A    Well, if all meters were like -- no, sir, I don't

17   agree.  If all meters were like these meters, there would be

18   fewer found to be in error.

19        Q    If you tested at a higher point in the scale, there

20   would be fewer found to be in error?

21        A    No, if you tested at a lower point.  Now, it's

22   outside my testimony, but we've heard that not all meters are

23   like these meters.

24        Q    Okay.  But this proceeding --

25        A    I also --

FLORIDA PUBLIC SERVICE COMMISSION

285

1        Q    I'm sorry.

2        A    I also don't agree that it's to a utility's advantage

3   to have inaccuracy among the meters that it uses.

4        Q    And I'm just asking you from a financial standpoint.

5   You know, I don't think it's the right thing; you don't think

6   it's the right thing.  But just from a standpoint of impact,

7   dollars and cents bottom line, if -- and I'm not suggesting

8   that FPL is motivated by that, but if somebody were, wouldn't

9   it benefit them to test at a lower point on the scale as

10   compared to a higher point on the scale with respect to these

11   thermal meters?

12        A    Well, I don't agree that it would benefit them

13   because they would not know whether a meter was inaccurate on

14   the high side or the low side at one end of the scale until the

15   meter was tested.  So I think it would be to their advantage to

16   do the right thing.  It would be to their advantage to know

17   what people are consuming and know that they're paying for what

18   they're consuming rather than to have inaccurate meters in use.

19        Q    And you agree that these rules should be interpreted

20   to treat customers fairly; correct?  That's sort of an

21   overlying tenent of these rules?

22        A    Yes, sir.

23             COMMISSIONER DEASON:  Mr. Moyle, I'm going to ask you

24   to wrap it up.  It's already been 15 minutes.

25             MR. MOYLE:  Okay.  I'm sorry.

FLORIDA PUBLIC SERVICE COMMISSION

286

1   BY MR. MOYLE:

2        Q    Just a couple more questions, and again this is on

3   this interpretation issue.  There's a rule that allows a

4   customer to seek independent tests; correct?

5        A    Yes, sir.

6        Q    And that independent test, there's nothing in that

7   rule that says a customer has to test at a particular point on

8   the scale; correct?  It just says you can go take an

9   independent test and test the meter.

10        A    I don't believe the test points are mentioned in that

11   rule.

12        Q    Okay.  Would that suggest to you that the better

13   interpretation of this rule is that the meter needs to test so

14   that it is less than 4 percent error at any point along the

15   scale, so that if you tested at 25 percent, it has to be less

16   than 4 percent; if you tested at 50 percent, it has to be less

17   than 4 percent; if you tested at 80 percent, it has to be less

18   than 4 percent; you know, at any point it has to be less than

19   4 percent because you have customers whose loads will vary?

20   Doesn't that seem like the most logical interpretation of that

21   rule to you?

22        A    If that were the way the rule --

23             COMMISSIONER DEASON:  Could you answer yes or no,

24   please.

25             THE WITNESS:  Yes, I believe that would be a clearer

FLORIDA PUBLIC SERVICE COMMISSION

287

1   statement.  Yes, sir.

2             MR. MOYLE:  Thank you.  I have nothing further.

3             COMMISSIONER DEASON:  Mr. Hoffman.

4                          CROSS EXAMINATION

5   BY MR. HOFFMAN:

6        Q    If you'd look at that rule, Mr. Matlock,

7   25-6.052(2)(a), does that rule state that the performance shall

8   be acceptable when the error does not exceed 4 percent when

9   tested at any point between 25 and 100 percent or when tested

10   at all points between 25 and 100 percent of full-scale value?

11             MR. KEATING:  Mr. Matlock, I'd like to interrupt and

12   ask if you have a copy of the rules in front of you to look at.

13             THE WITNESS:  Yes, sir.

14             MR. KEATING:  Okay.

15             THE WITNESS:  The rule says when tested at any point.

16   BY MR. HOFFMAN:

17        Q    Okay.  So the rule simply does not say that there is

18   to be tests at all points for performance purposes between

19   25 percent and 100 percent of full-scale value; correct?

20        A    That's correct.

21        Q    And the rule does not require more than one test if

22   you test a meter and the error of registration does not exceed

23   4 percent if you've tested at any point between 25 percent and

24   100 percent of full-scale value; correct?

25        A    That is correct for that rule, for Rule

FLORIDA PUBLIC SERVICE COMMISSION

288

1   25-6.052(2)(a).  There is another rule that I haven't -- this

2   rule wasn't highly discussed in my testimony, but it was

3   mentioned.  The rule is 25-6.056(4)(b), which states that a

4   meter is to be tested -- meters are to be tested when they are

5   suspected by the utility of being inaccurate or damaged.  So if

6   a meter is tested once, in 25-6.052(2)(a), if there was

7   evidence that that meter's result was not reflective of the

8   accuracy of that meter, another test would need to be

9   performed.

10        Q    Okay.  But in the typical situation where that event

11   is not present, if, for example, you test a thermal demand

12   meter at any point between 25 percent and 100 percent of

13   full-scale and the meter overregisters 2 percent, is there a

14   requirement under that rule to do a second test?

15        A    No, sir.

16        Q    You talked with Mr. Moyle a little bit about this

17   issue of the level of registration as you move up or down the

18   scale.  Do you recall those questions?

19        A    Yes, sir.

20        Q    Okay.  I think he asked you a question about if you

21   test at 25 percent of full-scale and have a 3 percent error,

22   then there was a question about if you move it up to 75 percent

23   of the scale.  Do you recall that?

24        A    Yes.

25        Q    And your testimony, as I understand it, is under that

FLORIDA PUBLIC SERVICE COMMISSION

289

1   scenario assuming that there was a 3 percent error at

2   25 percent, the test at 75 percent could produce an error

3   greater than 3 percent or less than 3 percent; correct?

4        A    Yes, sir, that's correct.

5             MR. MOYLE:  Which is it?  Greater or less than?  I'm

6   sorry.

7             COMMISSIONER DEASON:  No, he's saying it could be

8   either one and the witness agreed.

9   BY MR. HOFFMAN:

10        Q    Finally, Mr. Matlock, along sort of the same line.

11   You had some questions about whether it would be in someone's

12   financial interest, and I know there's no evidence of that in

13   this proceeding, but if you assume just for purposes of theory,

14   and I know that you don't accept this, that the level of error

15   did increase as you moved up the scale, and if you had more

16   underregistering meters than overregistering meters, what would

17   be the financial impact under that scenario?

18        A    If you had more underregistering meters as you moved

19   up the scale?

20        Q    Yes, sir.  If you had more underregistering meters

21   than overregistering meters and you accepted for purposes of

22   this question that the error increases as you move up the

23   scale.

24        A    It would depend on what the levels of usage were for

25   the various customers then.

FLORIDA PUBLIC SERVICE COMMISSION

290

1             MR. HOFFMAN:  Thank you, Mr. Matlock.  No further

2   questions.

3             COMMISSIONER DEASON:  Commissioners.

4             Redirect.

5             MR. KEATING:  Just a couple.

6                        REDIRECT EXAMINATION

7   BY MR. KEATING:

8        Q    Mr. Matlock, do you still have what was handed out as

9   Exhibit 9, the May 6th, 2003 agreement between FPL and George

10   Brown?

11        A    Yes, sir.

12        Q    Do you know whether this Commission, given that this

13   case has proceeded to hearing, can or should hold the parties

14   to this agreement?

15             MR. MOYLE:  Object to the extent it calls for a legal

16   conclusion.

17             THE WITNESS:  I don't know --

18             COMMISSIONER DEASON:  Wait.  I'm sorry.  Well, he

19   said he didn't know.

20             MR. MOYLE:  I just want the objection to the extent

21   it calls for a legal conclusion.

22             COMMISSIONER DEASON:  I understand.  Objecting, legal

23   conclusion.

24             MR. KEATING:  I believe Mr. Matlock was asked some

25   questions about this document before and whether certain

FLORIDA PUBLIC SERVICE COMMISSION

291

1   terms -- whether he understood that certain terms still apply.

2   I want to ask him whether he knows if they should apply -- I'm

3   sorry, whether we can apply them.

4             MR. MOYLE:  And my objection is just to the extent

5   that it calls for a legal conclusion about whether it's a

6   binding agreement.  He's free to answer with respect to what

7   his understanding is.

8             COMMISSIONER DEASON:  With that understanding, you

9   may answer the question.

10             THE WITNESS:  I don't know that we were ever in a

11   position to enforce this agreement should the agreement break

12   down.  We were told that certain things have been negotiated.

13   And I don't think that it would -- I don't know if it was up to

14   us to apply anything other than our rules in having these

15   disputes resolved in light of this agreement.

16             COMMISSIONER DEASON:  Let me ask this question.  Is

17   there anything in this agreement that is inherently

18   inconsistent with our rules?

19             THE WITNESS:  No, sir, I don't think that there was.

20   We found out about it shortly after this date or maybe on that

21   date, and I don't think it was operating outside the rules to

22   get things resolved.  It was just there were some things in it

23   that our rules didn't cover or that our rules didn't sanction.

24   And it was a way to reach a conclusion if the agreement held

25   up.

FLORIDA PUBLIC SERVICE COMMISSION

292

1   BY MR. KEATING:

2        Q    Just one more question.  Mr. Matlock, is there

3   anything that you are aware of in the Commission's rules that

4   would suggest the use of either a percentage of error

5   determined by a meter test or a percentage of error based on a

6   comparison of meter readings before and after meter

7   replacement?  Is there anything in the rules that leads you to

8   believe that one of those two methods is preferred under the

9   Commission's rules?

10        A    Well, I think the rules are -- I think the rules

11   would use a test result, and that's as far as the rules would

12   go.  The other way of calculating a percent revision to a

13   customer's bill is -- when it's used is greater than what the

14   test result gives you.  So I don't know of anything.

15             MR. KEATING:  Thank you.

16             COMMISSIONER DEASON:  Okay.  Exhibits.

17             MR. KEATING:  Staff would move Exhibits 14 and 15.

18             COMMISSIONER DEASON:  Without objection, show that

19   Exhibits 14 and 15 are admitted.

20             (Exhibits 14 and 15 admitted into the record.)

21             COMMISSIONER DEASON:  Thank you, Mr. Matlock.  You

22   maybe excused.

23             (Witness excused.)

24             COMMISSIONER DEASON:  Mr. Hoffman, you may call your

25   next witness.

FLORIDA PUBLIC SERVICE COMMISSION

293

1             MR. HOFFMAN:  We call Ed Malemezian.

2                        EDWARD C. MALEMEZIAN

3   was called as a witness on behalf of Florida Power & Light

4   Company and, having been duly sworn, testified as follows:

5                         DIRECT EXAMINATION

6   BY MR. HOFFMAN:

7        Q    Would you please state your name and business

8   address.

9        A    My name is Ed Malemezian, 8009 Southwest Yachtsmans

10   Drive in Stuart, Florida.

11        Q    And by whom are you employed?

12        A    Ed Malemezian Consulting.

13        Q    And your position?

14        A    I am the president and principal.

15        Q    Mr. Malemezian, have you prepared and caused to be

16   filed 39 pages of prefiled rebuttal testimony in this

17   proceeding?

18        A    Yes, I have.

19        Q    Do you have any changes to your prefiled rebuttal

20   testimony?

21        A    Yes, I do.

22        Q    Could you outline that change?

23        A    Yes.  I have one change on Page 27, Line 2, where I

24   talk about FPSC Rule 25-6.052(2)(a).  I'd like to add (4) to

25   that sentence.  And that is the only change I have.

FLORIDA PUBLIC SERVICE COMMISSION

294

1        Q    With that change, if I asked you the questions

2   contained in your prefiled rebuttal testimony, would your

3   answers be the same?

4        A    They would.

5             MR. HOFFMAN:  Commissioner Deason, I would ask that

6   Mr. Malemezian's prefiled rebuttal testimony be inserted into

7   the record as though read.

8             MR. HOLLIMON:  I have an objection.

9             COMMISSIONER DEASON:  Without objection, it shall be

10   inserted.

11             MR. HOLLIMON:  I'm sorry.  I have an objection.

12             COMMISSIONER DEASON:  Oh, you have an objection.  I

13   thought you said you hadn't.  I guess that was just wishful

14   thinking.  Okay.  State your objection.

15             MR. HOLLIMON:  My objection is to the opinion

16   testimony provided by this witness with regard to issues that

17   fall under the engineering field of material science, and

18   specifically Page 12, Line 3 through Page 17, Line 2, and

19   Page 18, Lines 6 through 11.  This witness admits in his

20   testimony that he's not an expert in material science and yet

21   he's rendered multiple opinions with regard to that particular

22   engineering discipline.

23             COMMISSIONER DEASON:  What was the second part of

24   your -- Page 18, what lines?

25             MR. HOLLIMON:  Line 6 through 11.

FLORIDA PUBLIC SERVICE COMMISSION

295

1             COMMISSIONER DEASON:  6 through 11.

2             MR. HOFFMAN:  What was the first one, Mr. Hollimon?

3             MR. HOLLIMON:  It was Page 12, Line 3 through

4   Page 17, Line 2.

5             COMMISSIONER DEASON:  Okay.  There's been an

6   objection.  Do you care to respond to the objection?

7             MR. HOFFMAN:  Yes, sir.  As he outlines in his

8   testimony, Mr. Malemezian has an electrical engineering degree.

9   He began his career with FPL in 1971 and has served in a number

10   of capacities involving metering.  He has served as the meter

11   superintendent for Southern Division Meters and has

12   approximately 26 years in every aspect of meter operations,

13   meter testing, meter processes, meter procedures, and the

14   workings of the components of these thermal demand meters.

15             His testimony, Commissioners Deason, goes straight to

16   and directly to the impacts on the characteristics of the

17   components of these meters which he has worked with for roughly

18   26 years.  He has spoken over those 26 years many times with

19   the manufacturer about these components.  He has observed and

20   experienced on numerous occasions problems with these

21   components.  And the fact of the matter is one does not have to

22   be a metallurgist to be qualified to render an opinion as to

23   whether the characteristics of these components of these

24   meters, that he has probably more experience than anyone in

25   this state with, whether they can change over the course of

FLORIDA PUBLIC SERVICE COMMISSION

296

1   time.  So we think that he is perhaps the most qualified person

2   that we could possibly produce to address the issue of whether

3   the characteristics of the many components in this meter can

4   change.

5             COMMISSIONER DEASON:  I'm going to overrule the

6   objection, testimony found on Page 13, Lines 14 through 18,

7   allow this witness to testify on this subject, and any further

8   question about this just falls to the weight that the

9   Commission would give to this testimony.  So that objection is

10   overruled.  The testimony is inserted into the record in its

11   entirety as corrected.

12             There are no exhibits attached to his testimony; is

13   that --

14             MR. HOFFMAN:  No, sir, there is not.

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

336

1             COMMISSIONER DEASON:  Is there a summary?

2             MR. HOFFMAN:  Yes, sir.

3   BY MR. HOFFMAN:

4        Q    Have you prepared a summary of your rebuttal

5   testimony?

6        A    Yes, I have.

7        Q    Could you please provide that to the Commission?

8        A    Yes, I will.  The purpose of my testimony is to

9   respond to certain assertions made in the direct testimonies of

10   Mr. George Brown of Southeastern Utility Services and Mr. Bill

11   Smith.  In addition, my testimony will discuss the method

12   proposed in the direct testimony of Mr. Sidney Matlock of the

13   FPSC in determining the percent error to be used in calculating

14   customer refunds or backbills.  I will try to highlight certain

15   parts of my testimony.

16             George Brown testifies that at the time the meters

17   began to overregister can be established as the time FPL last

18   calibrated the meters.  He testifies there is virtually no

19   physical mechanism that can result in these meters gradually

20   overregistering demand.  I disagree.  Thermal demand meters are

21   devices with numerous components.  Each one of these components

22   that go into the thermal meter is critical to its proper

23   operation.  Changes in the characteristics of any one of these

24   components will affect demand registration.  Many of the

25   components are mechanical in nature and subject to some wear,

FLORIDA PUBLIC SERVICE COMMISSION

337

1   tear, or malfunction.  If that were not the case, then Landis &

2   Gyr would not have found it necessary to include so many pages

3   in Bulletin 841 on how to repair or how to replace them.

4             As an engineer, I know that all mechanical components

5   are constructed of materials, and that regular and continued

6   temperature cycling such as that which occurs under the cover

7   of meters accentuate changes in the characteristics of these

8   materials.  It is impossible to predict which changes occurred

9   and when they did.  If Landis & Gyr could have made a meter

10   with perfectly made parts and with parts that never change

11   characteristics, they could have and they would have left off

12   the adjustment screws.  These calibration mechanisms are there

13   to allow the meter to be brought back within calibration limits

14   after the parts have changed.

15             My testimony discusses the fact that six, six of the

16   14 meters in this docket were never calibrated by FPL.  This

17   fact eliminates Mr. Brown's theory that miscalibration is the

18   cause of overregistration.  FPL's thermal meter and calibration

19   processes comply with manufacturer's recommendations.  Let me

20   address three of the issues.

21             Landis & Gyr Bulletin 841 provides two methods for

22   calibrating meters.  The practice employed by FPL involves

23   quickly removing the cover and the other involves the use of a

24   special test cover.  Landis & Gyr takes a very conservative

25   approach in suggesting 45 minutes be required for stabilization

FLORIDA PUBLIC SERVICE COMMISSION

338

1   after adjustments are made.  Ten minutes was established by FPL

2   as being more than adequate for this verification test.  FPSC

3   rules and FPL's Commission-approved test procedures authorize

4   testing at any point between 25 and 100 percent of full-scale

5   value.  The suggestion in Landis & Gyr's Bulletin 841 certainly

6   do not take precedence over FPSC rules.

7             The effects of heating from solar radiation on demand

8   registration are really very straightforward and simple to

9   understand.  FPL has investigated this issue and found that

10   this external heating either has no effect or underregistration

11   on the meters.

12             Turning to Mr. Matlock's testimony, he proposes the

13   use of error at the meter test point to calculate refunds.  His

14   proposal is inconsistent with the test requirement provided by

15   Rule 25-6.052(2) which states that the error of registration is

16   defined as a percentage of full-scale value.  Mr. Matlock also

17   suggests calculating the customer's billing demand from the

18   billing cycles contained in the refund or backbill period

19   versus FPL's present method which uses the 24 months prior to

20   the meter change.  Both methods are similar and both are

21   intended to select a demand test point reflective of the

22   customer's actual demand usage prior to the meter change.  That

23   concludes my summary.

24             MR. HOFFMAN:  Thank you, Mr. Malemezian.  He's

25   available, Commissioner Deason, for cross.

FLORIDA PUBLIC SERVICE COMMISSION

339

1             COMMISSIONER DEASON:  Mr. Hollimon.

2                          CROSS EXAMINATION

3   BY MR. HOLLIMON:

4        Q    Good afternoon, Mr. Malemezian.

5        A    Good afternoon.

6        Q    Mr. Malemezian, you've been here all day, haven't

7   you?

8        A    Yes, I have.

9        Q    Okay.  Do you recall some testimony with Mr. Bromley

10   when he was being examined about the meter that brought the

11   whole thermal demand meter issue to the attention of Florida

12   Power & Light?

13             MR. HOFFMAN:  Objection.  That's outside the scope of

14   his rebuttal.

15             MR. HOLLIMON:  Well, I think if you give me a chance

16   to follow up --

17             COMMISSIONER DEASON:  I'm sorry.  Finish your

18   objection.

19             MR. HOFFMAN:  Commissioner, I think that's clearly

20   within the scope of Mr. Bromley's testimony and it's a question

21   for him, but that's outside the scope of his prefiled rebuttal.

22             COMMISSIONER DEASON:  Your response.

23             MR. HOLLIMON:  I simply was trying to lay the

24   predicate, as I've learned, for a question that I was about to

25   ask him.  That's all I was trying to establish.

FLORIDA PUBLIC SERVICE COMMISSION

340

1             COMMISSIONER DEASON:  I'll give you that latitude.

2   Please proceed.

3   BY MR. HOLLIMON:

4        Q    So, Mr. Malemezian, you were present when Mr. Bromley

5   testified, were you not, sir?

6        A    Yes, I was.

7        Q    And are you familiar with the meter that he described

8   as the meter that brought the whole thermal demand meter issue

9   to FPL's attention?

10        A    Yes, I am.  I'm not sure I would characterize it that

11   way, but, yes, I am.  I have some knowledge of that, yes.

12        Q    I believe in your summary you said that with regard

13   to the issue of sunlight, it's very simple and straightforward

14   and simple to understand; is that correct?

15        A    I did say that, yes.

16        Q    And that there was some investigation done by Florida

17   Power & Light and it demonstrated a consistent result; is that

18   correct?

19        A    Yes, they did do that.

20        Q    Now, how do you explain the fact that the meter that

21   Mr. Bromley discussed had the exact opposite result?

22        A    I would characterize that as an anomaly in that one

23   meter.  FPL tried very diligently to reproduce that effect.

24   And in testing 150 meters after the fact looking for that

25   specific type of reaction, they clearly didn't find it on a

FLORIDA PUBLIC SERVICE COMMISSION

341

1   single other meter.

2        Q    Mr. Malemezian, in your testimony you refer to the

3   ANSI C12 family of standards as the Bible for metering

4   requirements; isn't that correct?

5        A    I do, yes.

6        Q    While you were employed by FPL, did FPL consider

7   these standards to be the Bible?

8        A    I think that's a correct characterization, yes.

9        Q    Does FPL follow the recommendations of the ANSI

10   C12.1 with regard to metering issues?

11        A    Yes, they do where they are appropriate.

12        Q    So sometimes the Bible is not appropriate?

13        A    Sometimes other rules and other requirements take

14   precedence over the ANSI requirements, yes.

15        Q    So are the rules a better technical standard than

16   ANSI?

17        A    Are the rules as in the PSC rules?

18        Q    Correct.

19        A    The --

20             MR. HOFFMAN:  Excuse me.  I'm going to object.  The

21   question is ambiguous.  I just don't know what rules of the

22   Commission Mr. Hollimon is referring to.

23             COMMISSIONER DEASON:  Okay.  Could you specify,

24   Mr. Hollimon?

25   BY MR. HOFFMAN:

FLORIDA PUBLIC SERVICE COMMISSION

342

1        Q    I'm referring to the rules that you mentioned in your

2   prior response, but in particular, I'm referring to the PSC

3   rules that relate to how you test meters.  And the question is

4   whether the ANSI standard is a better technical resource than

5   the PSC rules with regard to meter testing.

6        A    I would contend that the -- I think the answer to the

7   question is yes.

8        Q    Thank you.

9        A    And I would contend that the Florida PSC rules have a

10   requirement that requires Florida Power & Light and all other

11   investor-owned utilities to provide a test plan.  And the test

12   plan is the resource and the technical document that describes

13   all of the technical details of meter testing.  And so by the

14   fact that the FPSC rules require that that document be prepared

15   and submitted and approved by the Commission and the Commission

16   staff, I would say that the FPSC rules do in fact provide

17   excellent technical guidance.

18        Q    Mr. Malemezian, in your testimony you take issue with

19   the testimony of Mr. Brown and Mr. Smith that thermal demand

20   meters are relatively simple and pretty straightforward in

21   their design operation, do you not?

22        A    I do, yes.

23        Q    Isn't it true, Mr. Malemezian, that in your

24   experience with thermal demand meters while you were employed

25   with FPL was that thermal demand meters are fairly simple

FLORIDA PUBLIC SERVICE COMMISSION

343

1   devices?

2        A    Yes.  I would characterize thermal demand meters as

3   very simple devices, but being simple devices doesn't mean that

4   there are not complex mechanisms and complex interactions that

5   are dependent on proper operation of parts, components,

6   materials being stable and so forth.  Simple devices can have

7   such similar reactions to changes.

8        Q    Do you recall being deposed on September 14th, 2004?

9        A    Yes, I do.

10        Q    Do you have a copy of your deposition?

11        A    Yes, I do.

12        Q    I'm going to read into the record on Page 21,

13   beginning on Line 4, it says, "During the time that you worked

14   for Florida Power & Light, what was your experience with

15   thermal demand meters?"

16             And your response was, "Florida Power & Light used

17   thermal demand meters as its primary measurement of demand on

18   commercial industrial customers.  Florida Power & Light was

19   very happy with the performance of those demand meters and

20   throughout the years got very good results from them.  They

21   were fairly simple devices.  They were fairly reliable, fairly

22   stable devices.  They were certainly much better than any

23   alternatives that were offered in the industry in the early

24   years."

25             Do you stand by that testimony?

FLORIDA PUBLIC SERVICE COMMISSION

344

1        A    I do, yes.

2        Q    Now, in your prefiled testimony, you relied upon the

3   Sangamo "Facts About Demand" paper; is that correct?

4        A    I did make some references in reading through that,

5   yes.

6        Q    You relied upon it in forming your testimony, did you

7   not?

8        A    Yes, if that's the definition of being -- of relied

9   upon it.  Yes, I've reviewed it.

10        Q    Well, let's turn to Page 212 of your deposition.

11        A    212?

12        Q    Correct.  We're going to refer -- oh, I'm sorry.

13   Actually, it begins on the bottom of Page 211.  The last line

14   on Page 211 I'm going to read into the record.

15             "In response to some of Ms. Smith's questions, you

16   talked about the Sangamo paper and the Jenny paper.  Do you

17   recall that?"

18             Your answer is yes.

19             "Did you rely upon these documents to formulate your

20   testimony?"

21             "Answer:  Yes, I read them.  Yes.  And they were

22   input into my testimony.  Yes.

23             Question:  So you relied upon them?

24             Answer:  As I relied on lots of information, yes.

25             Question:  You found them authoritative?

FLORIDA PUBLIC SERVICE COMMISSION

345

1             Answer:  I found that they had useful information in

2   them, yes.

3             Question:  The kind of documents that an expert would

4   rely upon?

5             Answer:  Yes."

6             Do you stand by that testimony?

7        A    I do.

8             MR. HOLLIMON:  May I approach?

9             COMMISSIONER DEASON:  Yes.

10   BY MR. HOLLIMON:

11        Q    Can you identify the document that has been handed to

12   you?

13        A    Yes.  This is the Sangamo "Facts On Demand" Bulletin

14   that you asked me about in my deposition.

15        Q    Okay.  And, Mr. Malemezian, if you'll turn to the

16   page Bates numbered 100 TDM.

17        A    Yes, I'm there.

18        Q    If you'll read the fourth paragraph into the record,

19   please.

20        A    "The excellent field accuracy of thermal meters is,

21   in part, a result of the simplicity of design (only one moving

22   part).  Careful selection, matching, and aging of the bimetal

23   coils are other factors of prime importance.  Compensation for

24   fluctuations of ambient temperatures (sun shield, enclosure

25   design, deflection adjustment) give stable accuracy in all

FLORIDA PUBLIC SERVICE COMMISSION

346

1   installations."

2        Q    And if you'll turn to the next page, it's 101 TDM.

3        A    Yes.

4        Q    Do you see that?

5        A    I do.

6        Q    And under the testing and maintenance, would you read

7   the last sentence in the first paragraph, please.

8        A    "For example" --

9        Q    No.  "This sustained."

10        A    Pardon?

11        Q    The second sentence in the first paragraph under

12   testing and maintenance.

13        A    Testing and maintenance, the second sentence.

14   "Thermal meters can be tested," is that the sentence?

15        Q    No.  "This sustained accuracy."  Do you see that

16   second sentence, first paragraph?

17        A    "This sustained accuracy is the result of the

18   inherent design and the fact that thermal meters have only one

19   moving part."

20        Q    Now, in this document, what is the recommendation in

21   terms of the test point at which these meters should be tested,

22   thermal demand meters?

23        A    I don't recall.

24        Q    If you'll look in the fourth paragraph under testing

25   and maintenance, would you read the third sentence into the

FLORIDA PUBLIC SERVICE COMMISSION

347

1   record?

2        A    The fourth paragraph?

3        Q    Yes.  The third sentence beginning with, "The

4   meters."

5        A    "The meters to be tested are connected in series with

6   the standard meter and a load of 3/4 scale or higher applied."

7        Q    Now, what's your opinion as to why this authoritative

8   document states that testing should be conducted at 3/4 scale

9   or higher?

10        A    I do not know why they put that comment in there.

11        Q    Okay.  If you'll turn to the next page, 102.  And if

12   you'll read into the record the second to last paragraph,

13   please.

14        A    "Since the only moving part, the bimetal shaft, moves

15   slowly on polished stainless steel pivots, no lubrication is

16   required on any part of the thermal meter.  The bimetal coils

17   will remain stable indefinitely because of the aging processes

18   performed before they are assembled in the meter.  The heating

19   elements are precisely matched during manufacture and do not

20   require further attention."

21        Q    Okay.  Earlier when we were referring to 3/4 scale,

22   that's the same thing as 75 percent of scale; is that correct?

23        A    Yes, it is.

24        Q    If you'll turn to 112 TDM, please.  Under the

25   question that's Number 23, do you see that?

FLORIDA PUBLIC SERVICE COMMISSION

348

1        A    I do.

2        Q    Would you read the second paragraph, please, into the

3   record.

4        A    The thermal meters are available?

5        Q    Yes.

6        A    "Thermal demand meters are available with a dual

7   range feature that is easily changed in the field.  This

8   feature provides extra demand measurement capacity and better

9   accuracy by keeping the demand reading in the upper half of the

10   scale as loads increase.  Again, recalibration is not necessary

11   on Lincoln meters with a range change."

12        Q    Now, why is it that better accuracy occurs when the

13   demand reading is kept in the upper half of the scale?

14        A    The effects of meter reading errors are less of a

15   percentage of the overall reading of the meter, the error

16   that's introduced by reading of the meter.

17        Q    Now, is that true if you're talking about full-scale

18   error?

19        A    It's true if you're talking of any kind of error.

20   The higher you are in the scale, the less the uncertainty, and

21   the reading is a percentage of the overall reading that you're

22   taking.

23        Q    Now, Mr. Malemezian, the meters that are in this

24   docket were all manufactured in accordance with ANSI standards,

25   were they not?

FLORIDA PUBLIC SERVICE COMMISSION

349

1        A    My understanding is, yes, they were.

2        Q    Now, are you familiar with a standard ANSI C12.5?

3        A    Yes, I am.

4        Q    And doesn't that standard state that thermal demand

5   meters shall be substantially constructed of good materials in

6   a workmanlike manner with the objective of attaining stability

7   of performance over long periods of time and over wide ranges

8   of operating conditions with a minimum of maintenance?

9        A    It does say that.  But remember that the word it uses

10   is they are to be designed with the objective of attaining that

11   stability.  Attainment of an objective is not always possible.

12        Q    Mr. Malemezian, you have a significant amount of your

13   testimony that goes to the physical characteristics of the

14   components in thermal demand meters and that they're subject to

15   change over time due to temperature cyclings.  Do you recall

16   that?

17        A    Yes, I do.

18        Q    Isn't it true there's a specific engineering

19   discipline that focusses on the physical characteristics of

20   materials and the effects of stress on these characteristics?

21        A    I believe there is, yes.

22        Q    And isn't it true that discipline is known as

23   material science?

24        A    I believe that's correct, yes.

25        Q    And isn't it true you have no training in material

FLORIDA PUBLIC SERVICE COMMISSION

350

1   science?

2        A    I have no expert training in that.  As an engineer,

3   you take courses in that as part of your undergraduate work,

4   and I did have some of those courses.

5        Q    But you're not an expert -- you don't consider

6   yourself to be an expert in material science, do you?

7        A    No, I do not claim to be an expert.

8        Q    You're a Florida professional engineer, aren't you?

9        A    Yes, I am.

10        Q    As a matter of fact, on the very front of your

11   testimony it says, Ed Malemezian, P.E., doesn't it?

12        A    It does say that, yes.

13        Q    And as a Florida professional engineer, what

14   engineering disciples do you hold yourself out to be competent

15   in?

16        A    Electrical engineering.

17        Q    You don't hold yourself out to be competent in

18   material science, do you, sir?

19        A    Not as an expert, no.  I mean, I will say that I

20   don't feel that I need to be an expert in material science in

21   order to render opinions on the changes and characteristics

22   that occur in meters.  Having been -- as Mr. Hollimon (sic)

23   pointed out, my background is very extensive, 26 years at

24   Florida Power & Light dissecting many, many meters, following

25   up on problems and issues with those meters, working with

FLORIDA PUBLIC SERVICE COMMISSION

351

1   manufacturers, including Landis & Gyr.  You get to learn an

2   awful lot about the interaction of those components and the

3   changes in material characteristics that can take place, and I

4   don't feel I have to understand the nitty-gritty details of all

5   of the physics involved there in order to render opinions and

6   discussion on how those changes can affect --

7        Q    We're going to get to that, Mr. Malemezian.  Let's

8   just hold on for a second.

9             The meters in this docket are all 1V thermal meters;

10   is that correct?

11        A    Yes, they are all 1V thermal demand meters.

12        Q    Now, isn't it true that you have no specific

13   experience with investigating 1V thermal demand meters with

14   regard to changes and characteristics of their components?

15        A    That's not true, no.  In my years of experience at

16   Florida Power & Light, I was involved with investigations into

17   the changes in accuracy and calibration that ultimately was

18   tracked down to changes in the characteristics of many meters.

19   These investigations probably were the hundreds or the

20   thousands of meters.  Included in that batch of meters that I

21   experienced in this 26 years were thermal demand meters and

22   were thermal demand meters of the 1V type, but I cannot

23   associate to you today that a specific issue or problem I can

24   remember back that was specifically attributed to a 1V meter.

25        Q    So the answer to my question is yes?  You have no

FLORIDA PUBLIC SERVICE COMMISSION

352

1   specific examples of investigations into 1V thermal demand

2   meters?

3        A    The answer to your question is yes, with the

4   explanation that I gave.

5        Q    Okay.  Now, isn't it true that you've also never had

6   any discussions with thermal demand meter manufacturers about

7   changes in component characteristics?

8        A    No, that's not true.  I believe that through the

9   years at Florida Power & Light there were issues associated

10   with thermal demand meters and that Landis & Gyr, the

11   manufacturer of these meters, was the primary supplier to

12   Florida Power & Light for many years.  And through those years

13   there were numerous discussions on why meters behaved and

14   performed the way they did.  And changes in characteristics of

15   materials certainly were part of those discussions.

16        Q    But you can't recall any specific discussion you ever

17   had with that regard?

18        A    That's correct.

19        Q    Okay.  Mr. Malemezian, have you examined, personally

20   examined the meters that are in this docket?

21        A    Describe to me -- explain to me what you mean by

22   examine.

23        Q    Have you looked at them?

24        A    Have I looked at them?  I do not believe I have.

25        Q    Did you ask Florida Power & Light to let you look at

FLORIDA PUBLIC SERVICE COMMISSION

353

1   them?

2        A    I do not believe I did, no.

3        Q    So you don't have any idea whether or not any of the

4   component characteristic changes you've testified to have

5   actually occurred?

6        A    I do not.  But again, relying on my very extensive

7   experience I don't need to understand the specific mechanisms,

8   the specific characteristics that occurred in these particular

9   14 meters to understand that these materials are tightly

10   integrated into the chain of accuracy and performance and

11   stability of these meters.  I did not feel that I needed to

12   examine them.  And further, a casual examination -- preserving

13   the integrity of the meters, which FPL felt was important, that

14   casual observation and looking at them would not have led me to

15   conclude anything specific about these particular meters.

16        Q    Mr. Malemezian, you've also never tested meter

17   components for changes in material characteristics, have you?

18        A    No, I have not personally.  However, I have been

19   intimately involved with manufacturers like Landis & Gyr who

20   did do that for Florida Power & Light and been witness and

21   beneficiary of the results of those investigations.

22        Q    And have you ever been informed by Landis & Gyr that

23   the material characteristics in thermal 1V demand meters

24   changed characteristics?

25        A    Again, not specific to a particular 1V thermal demand

FLORIDA PUBLIC SERVICE COMMISSION

354

1   meter.  However, that discussion has taken place, again,

2   through the years numerous times on general populations of

3   meters of which the 1V is a party to or a member of, and I

4   cannot tell you specifically this discussion was on this 1V

5   meter.

6        Q    Mr. Malemezian, you testify that it's reasonable to

7   expect the physical characteristics of bimetal coils in thermal

8   demand meters to change over time; isn't that correct?

9        A    I did say that, yes.

10        Q    And isn't it true that the choice of materials used

11   to construct a bimetal coil would have a significant bearing on

12   whether or not a material's characteristics will change over

13   time?

14        A    Yes, that is true.

15        Q    And this would also be true for all the other

16   components in thermal demand meters?

17        A    That is true, yes.

18        Q    And let me make sure I understand something.  You've

19   never designed a thermal demander meter, have you?

20        A    No, I have not.

21        Q    You've never been through the design process for a

22   demand meter component?

23        A    No, I have not.

24        Q    You've never specified the materials that will be

25   used in the demand meter?

FLORIDA PUBLIC SERVICE COMMISSION

355

1        A    No, I have not.

2        Q    You've never selected materials for a demand meter?

3        A    No, I have not.

4        Q    You have no idea what the manufacturer's design

5   specifications are for the thermal demand meters in this

6   docket?

7        A    No, I don't.  And I don't feel that I need to.

8        Q    Now, I'm going to go back to the bimetal coils for a

9   second.  You don't know what type of materials are used in

10   those coils, do you, sir?

11        A    I do not.

12        Q    And you have no idea what the physical properties of

13   those coils are?

14        A    I do not.

15        Q    Isn't it true that it's a standard engineering

16   practice to -- in engineering design to build in what's known

17   as a factor of safety?

18        A    Yes, it is.

19        Q    And isn't it also true that the purpose of the factor

20   of safety is to account for uncertainties in the design

21   process?

22        A    Uncertainties in the design process, uncertainties in

23   the materials that are being used, uncertainty in manufacturing

24   tolerances and capabilities.  All of those things are a

25   result -- or are a goal of safety margins that are designed in.

FLORIDA PUBLIC SERVICE COMMISSION

356

1   However, again, years of experience has led me to see firsthand

2   that when you get bad materials and materials behaving in a

3   fashion that were not part of your original design objectives,

4   that margins of safeties are not adequate for preventing

5   changes.

6        Q    Now, Mr. Malemezian, you also testify that we're not

7   in a perfect world; isn't that correct?

8        A    I did say that, yes.

9        Q    Now, isn't, in fact, the whole purpose of a factor of

10   safety to compensate for the fact that we're not in a perfect

11   world?

12        A    It is.  And the practical reality of it is you can

13   never design a margin of safety to prevent the totally

14   unexpected circumstances from happening.  And that's what I

15   refer to as we do not live in the perfect world and such the

16   margins of safety cannot cover all of the situations.

17        Q    You just said that you can't use a factor of safety

18   that would compensate for totally unexpected circumstances; is

19   that correct?

20        A    That is correct.

21        Q    Now, you also testified that it's entirely reasonable

22   to expect that these kind of conditions, the changing in

23   characteristics, will occur in these meters; isn't that

24   correct?

25        A    I did say that, yes.

FLORIDA PUBLIC SERVICE COMMISSION

357

1        Q    So isn't that exactly the type of change that a

2   factor of safety then is actually perfect to protect for?

3        A    Yes, it is the intention of a factor of safety.

4   However, to design a margin of safety adequate to protect you

5   under all of these circumstances, you couldn't afford -- you

6   would not be able to afford the resulting meter or any kind of

7   device that would be perfectly stable and safe to use.

8             MR. HOLLIMON:  May I approach?

9             COMMISSIONER DEASON:  Yes.

10   BY MR. HOLLIMON:

11        Q    I'm going to hand you something.  Mr. Malemezian, can

12   you identify what I've handed you?

13        A    Yes.  This is the "Marks' Standard Handbook For

14   Mechanical Engineers."

15        Q    Now, Mr. Malemezian, is that an authoritative text?

16        A    Yes, I believe it is.

17        Q    Is it the kind of text that an expert would rely

18   upon?

19        A    Yes.

20        Q    I've tabbed a page that's 5-20.  Would you turn to

21   that, please.

22        A    Yes.  I have it here.

23        Q    And under the column that says, "Design Stresses,"

24   I'd like for you to read into the record the second paragraph,

25   please.

FLORIDA PUBLIC SERVICE COMMISSION

358

1        A    "The design stress is determined by dividing the

2   applicable material property -- yield strength, ultimate

3   strength, fatigue strength -- by a factor of safety.  The

4   factor should be selected only after all uncertainties have

5   been thoroughly considered.  Among these are the uncertainty

6   with respect to the magnitude and kind of operating load, the

7   reliability of the material from which the component is made,

8   the assumptions involved in the theories used, the environment

9   in which the equipment might operate, the extent to which

10   localized and fabrication stresses might develop, the

11   uncertainty concerning causes of possible failure, and the

12   endangering of human life in case of failure.  Factors of

13   safety vary from industry to industry, being the result of

14   accumulated experience with a class of machines or a kind of

15   environment.  Many codes, such as the ASME code for power

16   shafting, recommend design stresses found safe in practice."

17        Q    Now, Mr. Malemezian, isn't it true that by choosing

18   materials and incorporating an appropriate factor of safety,

19   it's possible to design a bimetal coil such that the integrity

20   and physical characteristics of the coil could be assured for a

21   long period of time?

22        A    If it were a perfect world, that would be a true

23   statement.  Again, my years of operating experience has shown

24   me that materials crop up that get selected, that get built

25   into meters that are unexpected and cause problems later beyond

FLORIDA PUBLIC SERVICE COMMISSION

359

1   what a margin of safety would be able to cover you for.

2        Q    Okay.  I want you to turn to deposition Page 36,

3   please, Line 8.  Let me know when you're there.  I'm going to

4   read into the record the question beginning on Line 8.

5             "Wouldn't it be possible to design a coil by choosing

6   the materials and the factor of safety such that the integrity

7   and physical characteristics of the coil could be assured for a

8   long period of time?"

9             "Answer:  If you define the bounds of what that

10   margin of safety is, I suppose yes."

11             Do you stand by that testimony?

12        A    Yes.

13        Q    Now, you don't know what materials the bimetal coils

14   for the meters in this docket are constructed of, do you, sir?

15        A    No, I don't.  And as I've explained, I don't feel

16   that I need to know that --

17        Q    And you don't know what any of the physical

18   properties of these materials are, do you?

19        A    And again, no.  I don't feel that I need to know that

20   to understand that changes do occur.

21        Q    And you don't have any idea what the factor of safety

22   that was used by Landis & Gyr in designing these meters is, do

23   you?

24        A    No, I don't.  And again, I don't feel that I need to

25   know that.

FLORIDA PUBLIC SERVICE COMMISSION

360

1        Q    And just to make sure, you haven't performed any

2   physical testing on any of the meter components that you have

3   identified as being subject to change; is that correct?

4        A    Not personally.  But again, I reflect back -- or I

5   remind you of my earlier comments that having been involved

6   with the dissection and investigation of literally hundreds or

7   thousands of meters that have changed characteristics, the

8   change in the characteristics of materials is always very, very

9   high up on the list of causes that the manufacturers have

10   identified to us.

11        Q    And those meters that you're talking about that

12   change characteristics, those were the kilowatt hour

13   registration meters, weren't they?

14        A    The majority of them were, yes.  But they are

15   constructed of materials, steels, metals, various components,

16   springs, bearings, greases, all of the same kinds of things

17   that are at play in my testimony on the things that can change

18   thermal demand meters -- change in thermal demand meters.

19        Q    Now, Mr. Malemezian, even if we assume that some

20   physical characteristic of a bimetal coil changed, you don't

21   have any idea what effect that would have on demand

22   registration, do you, sir?

23        A    The effect of a change in the characteristics of a --

24   no, I do not.  The change in the characteristics of the bimetal

25   coil could cause a meter to overregister or underregister

FLORIDA PUBLIC SERVICE COMMISSION

361

1   depending on the direction of the change and into -- and which

2   bimetal coil, whether it was a driving element or the retarding

3   element, in the meter.

4        Q    And so for the meters in this docket, you don't know

5   if any changes occurred; correct?

6        A    Repeat the question, please.

7        Q    For the meters in this docket, you don't know if any

8   changes actually occurred to these bimetal coils?

9        A    No, I do not.

10        Q    So you can't possibly know what the effect of any

11   such change that you don't know about would be?

12        A    That's correct.

13        Q    Now, you've also testified the physical

14   characteristics of the calibration and zero adjustment springs

15   are subject to change; is that correct?

16        A    Yes.

17        Q    And what material are these springs made from?

18        A    Again, I don't feel that I need to know that.

19        Q    Okay.  You don't know?

20        A    I do not know.

21        Q    And what's the spring constant on some of these

22   springs?

23        A    I do not know.

24        Q    What's the density of the material?

25        A    I do not know.

FLORIDA PUBLIC SERVICE COMMISSION

362

1        Q    What's the coefficient of expansion?

2        A    I do not know.

3        Q    What's the thermal connectivity?

4        A    I do not know.

5        Q    What's the melting temperature?

6        A    Do not know.

7        Q    What's the modulus of elasticity?

8        A    Do not know.

9        Q    What's the yield stress?

10        A    Do not know.

11        Q    What's the ultimate stress?

12        A    Do not know.

13        Q    Those are all basic properties of metals, are they

14   not?

15        A    They are.  But again, my comment is I don't feel that

16   I need to know that to understand that they do change.  I've

17   had reports from those experts that do know about those things

18   tell me on other meters, other investigations that those -- all

19   of those things are, in fact, in play and subject to change.

20        Q    Now, Mr. Malemezian, for all the other components of

21   the meters that you've identified as being subject to changing

22   characteristics, if I asked you the same series of questions

23   about what the type of material is and what their material

24   properties are, would your answer be that you don't know what

25   the types and properties of the materials are?

FLORIDA PUBLIC SERVICE COMMISSION

363

1        A    Depending on the questions you ask me, if they are

2   the questions in my testimony, then the answer would be yes,

3   they would be the same.  My answer would be the same.

4        Q    Have you ever personally observed in a Landis & Gyr

5   thermal demand meter, a 1V meter, any change, a physical

6   characteristic of a meter component?

7        A    Yes, I have.  The issues associated with the thermal

8   grease.  I personally witnessed changes in the viscosity of the

9   grease both in a lessening of viscosity and in increase in

10   viscosity manifesting itself in changes of the performance of

11   the damping assembly of the meter.

12        Q    Now, is that for a TR meter or a TMT meter?

13        A    The majority of the changes that I saw were in

14   regards to the TR meter, and the grease used in the TMT meter

15   is the same type of grease.

16        Q    Now, Mr. Malemezian, would you agree with me that for

17   all these meters and all the components in these meters that by

18   choosing appropriate materials and by choosing appropriate

19   factors of safety, that it's possible to design these

20   components such that you could expect that the normal operation

21   of the meter would have no effect on the characteristics of

22   these materials?

23        A    Could you repeat the question?

24        Q    Yes.  Would you agree with me that if you choose

25   appropriate materials and choose appropriate factors of safety,

FLORIDA PUBLIC SERVICE COMMISSION

364

1   that it's possible to design the components in this meter such

2   that under normal operating conditions, the normal operation of

3   the meter would have no effect on the characteristics of the

4   springs -- excuse me, of the components in the meter?

5        A    Yes.  I would agree with that statement to the degree

6   that, again, we're in this perfect world and that the margins

7   of safety are adequate to protect the changes in

8   characteristics.  But again, my firsthand experience shows me

9   that materials crop in to meters and get built in that are not

10   expected and, therefore, exceed the margin of safety that the

11   designs you're describing would protect you from.

12        Q    Mr. Malemezian, you've testified about changes in

13   conductivity of electrical connections in these meters; is that

14   correct?

15        A    Yes, I did.

16        Q    And in the soldered joints in these meters?

17        A    Yes.

18        Q    Now, isn't it true, Mr. Malemezian, that by simply

19   removing the meter cover, that the condition of these

20   connections and the soldered joints can be quickly and easily

21   checked?

22        A    Yes.  The majority of them are readily accessible by

23   removing of the cover.  However, as I think Mr. Bromley

24   mentioned, that we, Florida Power & Light intended to preserve

25   the integrity for future testing and retesting.  Breaking the

FLORIDA PUBLIC SERVICE COMMISSION

365

1   seal and recovering the cover of the meter removes some degree

2   of certainty from the resulting meter.  Further, in the

3   checking of the thermal demand meter and the electrical

4   connections, as you described, while the majority of them would

5   be then readily accessible or accessible with the cover

6   removed, there are, in fact, some that are down deep within the

7   bowels of the meter that would require further disassembly to

8   get to and reach.

9        Q    But you could check the majority of these electrical

10   connections that you refer to in your testimony quickly and

11   easily by simply removing the cover?

12             MR. HOFFMAN:  I'm going to object, Commissioner

13   Deason.  Again, we're starting to go down the road of examining

14   the meters.  That request was made and has been denied.  So I

15   would object to the relevancy.

16             COMMISSIONER DEASON:  I'll take that question to mean

17   it's more of a general question concerning these type meters,

18   not the ones that are in question, but how you could go about

19   doing it.  I'm going to allow the question.

20             THE WITNESS:  Repeat it, please.

21   BY MR. HOLLIMON:

22        Q    That a majority of the electric connections and

23   soldered joints inside 1V thermal demand meters can be easily

24   and quickly checked simply by removing the meter cover and

25   performing the test.

FLORIDA PUBLIC SERVICE COMMISSION

366

1        A    Yes, that is correct.  As I expressed, you would have

2   to remove the cover to do those tests.

3        Q    And isn't it also true that by performing this check

4   and this test, that you would not affect the future performance

5   of the meter?

6        A    Unless you -- no, that's not necessarily true.  If

7   you selected a meter that applied more current than was

8   appropriate, it could, in fact, affect the further

9   repeatability of the testing.

10        Q    But if you select the right meter and perform the

11   test correctly, it shouldn't affect the future performance of

12   the meter.

13        A    That's a correct statement, yes; again, with the

14   caveat that you had to remove the cover to do that.

15        Q    And also, by removing the meter cover and performing

16   this test, you wouldn't affect the integrity of the meter,

17   would you?

18        A    Define integrity.

19        Q    Well, the ability of the meter to be used in service

20   and to be repeatable when it's tested.

21        A    You would remove a degree of certainty that the meter

22   has not been altered in any fashion by taking the cover off.

23   So the answer was I think the integrity would be compromised.

24        Q    And isn't it standard practice of Florida Power &

25   Light to remove meter covers when they calibrate meters?

FLORIDA PUBLIC SERVICE COMMISSION

367

1        A    When they calibrate meters, yes.  We're talking about

2   testing meters here, not calibrating meters.

3        Q    Mr. Malemezian, in your testimony you talked about a

4   lot of these components that could experience a change in

5   physical conditions or that might, and that these changes might

6   affect the calibration of the meters; is that correct?

7        A    Yes.

8        Q    But for the meters in this docket, you've never

9   actually observed any of these conditions actually considering?

10             MR. HOFFMAN:  Objection, asked and answered.

11             COMMISSIONER DEASON:  I believe it has been asked and

12   answered.

13   BY MR. HOLLIMON:

14        Q    Isn't it true, Mr. Malemezian, that your testimony is

15   based on the supposition the changes to physical

16   characteristics may occur and not based on any factual evidence

17   that any such changes have actually occurred?

18        A    I don't believe that's true in that my years of

19   experience leads me to believe that these changes occur

20   regularly and are certainly possible and explain why a meter

21   that has been in service over time has, in fact, changed its

22   calibration.

23        Q    Now, I'm talking about the meters that are in this

24   docket, Mr. Malemezian.  And I want to know what's the factual

25   evidence that you have that any of these changes have actually

FLORIDA PUBLIC SERVICE COMMISSION

368

1   occurred.

2        A    I can cite solely the fact that six of these meters

3   that Florida Power & Light installed in the early '90s were

4   never calibrated by Florida Power & Light.  And so if they

5   were -- and the test records indicate that they had zero error

6   when they were installed, and roughly ten years later, they're

7   removed from service and they do, in fact, have calibration

8   errors in them, the only explanation for that is that something

9   within the meter has, in fact, changed.

10        Q    Is it possible that the meter test report is wrong?

11        A    Is it possible?  Yes.  Is it likely?  No.

12        Q    Well, would that provide another explanation for why

13   when retested ten years later you see this miscalibration?

14        A    It could.  However, again, on these six meters in

15   particular, I think Mr. Bromley explained that these meters

16   were purchased new from Landis & Gyr.  They were tested by

17   Landis & Gyr, calibrated by Landis & Gyr.  Landis & Gyr shipped

18   them.  They had zero error.  Some months later, the meters were

19   received by Florida Power & Light, tested by Florida Power &

20   Light, and found to have zero error, confirming what the

21   manufacturer had sent them out as.  And so for Landis & Gyr and

22   Florida Power & Light to have made identical errors in both

23   sign, direction, and magnitude for the testing that they did on

24   these six meters is extremely unlikely.

25        Q    Now, Mr. Malemezian, you have no personal knowledge

FLORIDA PUBLIC SERVICE COMMISSION

369

1   about any calibration testing that Landis & Gyr did for the six

2   meters you referred to, do you, sir?

3        A    No firsthand personal knowledge of those six.

4        Q    Mr. Malemezian, are you being compensated by FPL for

5   your testimony today?

6        A    Yes, I am.

7        Q    What's your compensation rate?

8        A    $250 an hour.

9        Q    And as I understand it, your business is a one-man

10   consulting firm; is that correct?

11        A    Yes, it is.

12        Q    And virtually all of your work is with utilities and

13   utility suppliers; is that correct?

14        A    I think that's a fair characterization, yes.

15        Q    So that's where your bread and butter comes from?

16        A    Yes, it is.

17        Q    Now, prior to your engagement by FPL, you were

18   contacted by Mr. Brown about a potential engagement, were you

19   not?

20        A    Yes, I was.

21        Q    For this matter?

22        A    Yes.  Mr. Brown asked if I would be interested in

23   helping him with this.

24        Q    And as I understand, you declined Mr. Brown because

25   you would not engage in any situation that would put you at

FLORIDA PUBLIC SERVICE COMMISSION

370

1   odds with utility customers; is that correct?

2        A    I think that's pretty much what I told him, yes.

3        Q    And you told Mr. Brown you would not accept any

4   engagement against FPL or any other utility; is that correct?

5        A    I believe those were my words, yes.

6        Q    So I guess you don't want to take any actions that

7   would interfere with your bread and butter, do you?

8        A    I'm not sure that's so.  I certainly would take

9   actions that I felt were appropriate.

10        Q    I guess you wouldn't want to take any actions --

11   well, you wouldn't want to accept a representation adverse to

12   FPL; is that right?

13        A    What I explained to Mr. Brown is I would not take on

14   assignments by folks that were going against FPL.  However, if

15   in maybe working for FPL that I uncovered or discovered

16   something that was unfavorable to them, my duty would be to

17   disclose and report that kind of activity.

18        Q    And so in this case did you discover anything

19   unfavorable to FPL?

20        A    Not in any of the issues I can think about sitting

21   here right now.

22        Q    But you never looked at the meters, did you?

23        A    Again, I didn't feel I needed to do that to

24   understand what was going on.  My years of experience have told

25   me what mechanisms were at play, and I didn't feel that I

FLORIDA PUBLIC SERVICE COMMISSION

371

1   needed to nor was it prudent to because of the fact that they

2   were sealed or held for litigation purposes.

3             MR. HOLLIMON:  That's all we have.

4             COMMISSIONER DEASON:  Staff.

5             MR. KEATING:  No questions.

6             COMMISSIONER DEASON:  Commissioners.

7             Redirect.

8             MR. HOFFMAN:  Thank you, Commissioner.

9                        REDIRECT EXAMINATION

10   BY MR. HOFFMAN:

11        Q    Mr. Malemezian, Mr. Hollimon asked you a number of

12   questions that dealt with the details of the materials in

13   thermal demand meters.  Do you recall those?

14        A    Yes, I do.

15        Q    And I think that you acknowledged more than once that

16   you're not -- you don't view yourself to be an expert in

17   material science; correct?

18        A    That is correct.

19        Q    Well, if you're not an expert in material science,

20   can you explain on what basis you have provided your opinion

21   that the characteristics of the components of these thermal

22   demand meters can change?

23        A    Yes, I think I can.  It relates back to my

24   engineering training that sets the tone for creative problem

25   solving and thinking, some basic course work.  But then the

FLORIDA PUBLIC SERVICE COMMISSION

372

1   bulk of my opinions and testimony revolves around my 26 years

2   involved in metering at Florida Power & Light, all aspects of

3   metering, from superintendent of a field operation of a meter

4   shop similar to Florida Power & Light's meter test center, a

5   standards laboratory, field operations involving related

6   activities to metering, being responsible for meter

7   engineering, having frequent and regular discussions with

8   manufacturers like Landis & Gyr, the other suppliers of

9   metering devices, having been personally involved in

10   investigations of problems and issues having to do with the

11   accuracy of meters, the long-term stability of meters; as I

12   said, literally hundreds and hundreds, if not thousands, of

13   those kinds of investigations over that 26 years.  And as I

14   described, many of those investigations lead you right to

15   materials and changes in the characteristics of those

16   materials.

17             And so I don't feel that I need to understand the

18   nitty-gritty details of all of the constants involved and the

19   strengths involved to realize as an engineer that those

20   materials do change, they are built into these meters, and

21   margins of safety are not adequate to protect against the

22   unexpected.  And so it's just years and years of experience

23   being an expert and being very familiar with those workings of

24   meters to render the opinions that I've given here.

25        Q    You were asked by Mr. Hollimon -- thank you,

FLORIDA PUBLIC SERVICE COMMISSION

373

1   Mr. Malemezian.  You were asked by Mr. Hollimon twice, at least

2   twice about your experience in investigating components of 1V

3   meters.  And when you were asked that the first time, I believe

4   your answer was yes and you provided a response.  And then when

5   he asked you the question again I believe you said not quite.

6   So I think the record is unclear.  So I would like to ask you

7   to explain what experience you have, if any, in investigating

8   the components of 1V meters.

9        A    Yes, I can take a stab at that.  My experience with

10   1V meters, I feel very comfortable in saying that in the years

11   of dissecting and following through with problems on meters,

12   the 1V thermal meter, the TMT that is the type of meter

13   involved in this docket, was a meter that was included in this

14   broad umbrella of the hundreds and thousands of investigations

15   that I was involved in.

16             The materials that were in those meters were

17   certainly similar to the materials in other meters.  But what I

18   can't say and I don't want to go on record as saying is I can

19   remember on a specific date on a specific instance this problem

20   with the 1V thermal meter.  I mean, we're going back over 25 or

21   30 years of experience, and I cannot in good faith relate to

22   you that specific.  But I feel that my experience is so broad

23   that it absolutely included 1V thermal meters.

24        Q    Thank you.  You also stated in response to a question

25   from Mr. Hollimon that you had not examined the meters at issue

FLORIDA PUBLIC SERVICE COMMISSION

374

1   in the docket and that a casual examination would not reveal a

2   change in components.  Why is that?

3        A    Well, because the changes that we're looking for that

4   I'm describing are very subtle.  Most of the changes in the

5   materials that we're looking for in order to properly test for

6   would require a destructive test.  The bimetals are in

7   housings.  To do a test and see if the characteristics haven't

8   changed, you have to totally disassemble the meter and that

9   would destroy the future capability to test them at some other

10   point perhaps, as Mr. Matlock had indicated in his testimony.

11             The changes that we're looking for are very, very

12   subtle.  They're in the ranges of percent, and they're probably

13   well within the design specifications of those materials.

14             The second reason or another reason why we have not

15   investigated them, Florida Power & Light does not have the

16   wherewithal to do those very sophisticated types of tests.

17   Further, Landis & Gyr, the supplier of these meters, stopped

18   manufacturing them 12 or 13 years ago.  All of the equipment,

19   the test equipment, the fixtures, and even the people and the

20   expertise that had the familiarity to do this testing are no

21   longer there.  So it would be very difficult to even find

22   anybody that was capable of doing a test.  And other than the

23   curiosity of probably understanding what was going on here,

24   there really isn't a good reason to do the test and to find a

25   specific cause.

FLORIDA PUBLIC SERVICE COMMISSION

375

1             If you could find a single cause, probably there's

2   multiple causes here, those only come into importance if you

3   are continuing to buy these meters in the future so that the

4   manufacturer could correct the manufacturing problem, a

5   materials problem and not build that into future meters.

6   That's not the case here.  So there is not a lot of reason to

7   do this.

8        Q    Mr. Hollimon asked you a number of questions

9   regarding the utilization of a factor of safety.  Do you recall

10   those questions?

11        A    Yes, I do.

12        Q    What effect would the utilization of a factor of

13   safety in the design of a thermal demand meter have on whether

14   the components of the meters can change and cause

15   overregistration over a period of time?

16        A    The higher the factor of safety the less likely those

17   changes are to occur would occur over time.  However, as I

18   described, that my experience again has led me to see firsthand

19   that materials get manufactured into meters that are for some

20   reason in excess of the specifications, they somehow find

21   theirselves (phonetic) into the manufacturing process and

22   manifest themselves in problems later.  And I've seen numerous

23   examples of that kind of situation at Florida Power & Light.

24   Factors of safety are there, meters are designed, but something

25   unusual happens and all of a sudden you've got a problem, you

FLORIDA PUBLIC SERVICE COMMISSION

376

1   know, years down the road.

2        Q    If you could, Mr. Malemezian -- I think this is my

3   last question -- you were handed an exhibit or document, excuse

4   me, by Mr. Hollimon.  It was the Sangamo document, the

5   first page says, "Facts About Demand Metering."

6        A    Yes.

7        Q    Do you have that?

8        A    I do.

9        Q    And Mr. Hollimon asked you a question or two from a

10   statement on Page 101 TDM of that document in the last

11   paragraph, the third sentence.  And if you could turn to that.

12        A    Yes, I have it.

13        Q    That passage states, "The meters to be tested are

14   connected in series with the standard meter and a load of 3/4

15   scale or higher applied."  And I think that you stated that the

16   3/4 scale means 75 percent; correct?

17        A    That's correct, yes.

18        Q    Does this document state whether or not this

19   statement is made by Sangamo in connection with a 3.5 or a

20   7.0 scale?

21        A    It makes no reference to that, no.

22        Q    Okay.  And what would a 75 percent test on a

23   3.5 scale be?  75 percent?

24        A    75 -- 3.5 or roughly 3.

25        Q    And what would it be if a 75 percent demand was

FLORIDA PUBLIC SERVICE COMMISSION

377

1   placed on a 7.0 scale?

2        A    Same calculation, 75 percent of 7 and so you're

3   talking roughly 6.

4        Q    Wouldn't it equate to half of the 75 percent?

5        A    Yes.

6             MR. HOFFMAN:  No further questions.

7             COMMISSIONER DEASON:  Thank you, Mr. Malemezian.  You

8   may be excused.

9             (Witness excused.)

10             MR. HOLLIMON:  Commissioner, I have just one redirect

11   on the very last question that was asked.

12             MR. HOFFMAN:  I'm going to object to that.

13             MR. HOLLIMON:  I'm sorry.  That's fine.

14             COMMISSIONER DEASON:  No, I think we're concluded.  I

15   believe we're down to the last witness; is that correct?

16             MR. MOYLE:  Yes, sir.

17             COMMISSIONER DEASON:  Let me inquire.  How much

18   cross-examination do we anticipate?

19             MR. MENTON:  Commissioner Deason, after hearing

20   Mr. Bradley earlier, I've tried very hard to pare it down.  So

21   I would say 30 to 45 minutes.

22             COMMISSIONER DEASON:  Do you guys need a break or no?

23   All right.  We're going to roll.

24             Okay.  Mr. Moyle, you may call your witness.

25             Just a second.  Before we do, I better need to check

FLORIDA PUBLIC SERVICE COMMISSION

378

1   with the court reporter.  Are you okay?

2             THE COURT REPORTER:  I'm fine.

3             COMMISSIONER DEASON:  We can break if you'd like.

4   You're okay?

5             THE COURT REPORTER:  I'm okay.

6             COMMISSIONER DEASON:  Okay.  We're going to roll.

7             MR. MOYLE:  Mr. Gilmore will be the next witness, and

8   Mr. Hollimon will put him on.

9                            BILL GILMORE

10   was called as a witness on behalf of Ocean Properties, Ltd.,

11   J.C. Penney Corp., Dillard's Department Stores, Inc., and

12   Target Stores, Inc. and, having been duly sworn, testified as

13   follows:

14                         DIRECT EXAMINATION

15   BY MR. HOLLIMON:

16        Q    Would you please state your name and address.

17        A    My name is Bill Gilmore.  My address is 11850

18   Southwest 81st Road, Miami.

19        Q    Have you prepared and caused to be filed rebuttal

20   testimony plus Exhibits 1 through 4?

21        A    Yes, I have.

22        Q    Do you have any changes to this rebuttal testimony?

23        A    No, I do not.

24        Q    If I asked you the questions in your rebuttal

25   testimony today, would your answers be the same?

FLORIDA PUBLIC SERVICE COMMISSION

379

1        A    Yes.

2             MR. HOLLIMON:  I'd ask that Mr. Gilmore's testimony

3   be moved into the record.

4             COMMISSIONER DEASON:  Without objection, show the

5   testimony inserted.

6             MR. HOLLIMON:  I'd also ask that the Exhibits

7   1 through 4 be entered into the record as a composite exhibit.

8             COMMISSIONER DEASON:  We will identify the exhibits

9   as Composite 16, and I'll allow you to move them after

10   cross-examination.

11             (Exhibit 16 marked for identification.)

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

388

1   BY MR. HOLLIMON:

2        Q    Mr. Gilmore, have you prepared a summary?

3        A    Yes, I have.

4        Q    Would you please present that.

5        A    Yes.  I'm testifying today about the history of the

6   meters that are subject to this docket and my analysis of that

7   history and also the results that cannot logically be drawn

8   from the analysis.  Also, I'm addressing the testimony of PSC

9   Commission staff Sid Matlock and his analysis.

10             I'm an engineer from Georgia Tech with an MBA from

11   the University of Florida.  I've spent 20 years with Florida

12   Power & Light and after that was a consulting engineer for ten

13   years.  During that time and at FPL, I learned the techniques

14   that I'm describing here and used them scores of times at FPL

15   and at many other large companies throughout the United States

16   and Great Britain.

17             My analysis is based on the fact that kilowatt hours

18   and kilowatt demand are related and typically go up or down

19   together not exactly but very close.  I tested this

20   relationship by conducting a correlation analysis.  This

21   correlation confirmed that there is a statistical positive

22   relationship between kilowatt hour and consumption -- kilowatt

23   consumption and demand.  The reason I did this, because I'm

24   trying to see over the years if there is a change in these

25   meters.  The problem with checking that is over the years,

FLORIDA PUBLIC SERVICE COMMISSION

389

1   typically at any location you do have a slight increase in

2   demand.  And you might consider that that would be some type of

3   a meter issue until you look and see that the kilowatt hours is

4   also going up at about the same rate.  So my analysis tries to

5   take that out, and I use a ratio of demand and kilowatt hours

6   and chart that using control charts over a period of time.

7   That way I can determine if the demand is actually changing in

8   relationship to the kilowatt hour usage.

9             I constructed control charts to determine if there

10   has been a change here.  The control charts I submitted measure

11   whether or not there was a statistically significant change in

12   the demand kWh ratio over time.  And if there is a point or

13   points outside the control limits, you can conclude that

14   something significant has occurred; otherwise, you cannot

15   necessarily conclude that.

16             Not all my charts are telling.  However, for most,

17   there's an obvious change in this ratio only when the new meter

18   was installed.  There is not a gradual change which might be an

19   indication of a meter slowly beginning to run out of tolerance.

20   So if the meter is running out of tolerance at test time and it

21   did not go bad over time, there's no indication of that, I'm

22   saying that it must have been out of tolerance when it was

23   installed.

24             Also, in my testimony I responded briefly to

25   Mr. Matlock's testimony regarding Rule 25-6.052(2)(a) that

FLORIDA PUBLIC SERVICE COMMISSION

390

1   requires that a thermal demand meter must be accurate to within

2   4 percent of full-scale when tested at any point between 25 and

3   100 percent.  And I'm actually questioning there the definition

4   of any and whether that means all or just one location.  That

5   was the extent of my testimony.  And that's my summary.

6             MR. HOLLIMON:  We tender this witness for cross.

7             COMMISSIONER DEASON:  Mr. Menton.

8             MR. MENTON:  Thank you, Commissioner.

9                          CROSS EXAMINATION

10   BY MR. MENTON:

11        Q    Good afternoon, Mr. Gilmore.  Steve Menton

12   representing FPL.  You do not have a degree in statistics, do

13   you?

14        A    No, sir, I do not.

15        Q    And you do not belong to any professional or academic

16   organizations related to statistics or statistical analysis, do

17   you?

18        A    No, sir, I do not.

19        Q    And you have never before testified before this

20   Commission or in any judicial or administrative proceeding

21   regarding statistical analysis, have you?

22        A    This is the first time.

23        Q    Now, I understand from your testimony that you are

24   principal and vice president of Southeastern Utility Services,

25   Inc.

FLORIDA PUBLIC SERVICE COMMISSION

391

1        A    That is correct.

2        Q    And that's SUSI, as we've referred to it sometimes

3   here?

4        A    Yes, sir.

5        Q    And you started with SUSI in 2003?

6        A    Approximately, yes.

7        Q    And that was basically after all of the thermal

8   demand meters in this case had been switched out; isn't that

9   right?

10        A    I think so.

11        Q    And isn't it true, Mr. Gilmore, that 99 percent of

12   your work with SUSI has been related to FPL thermal demand

13   meters?

14        A    No, sir, that is not true, not any longer.

15        Q    Well, at the time that I took your deposition back on

16   September 9th, 2004 that was correct; isn't that right?

17        A    I think I testified to that.  During this later

18   time -- I haven't been there very long.  During this later time

19   I've done mostly other things.

20        Q    So you do not disagree that as of September 9th,

21   2004, a couple months ago, 99 percent of your work with SUSI

22   had been related to FPL thermal demand meters?

23        A    Yes, sir.

24        Q    Now, Mr. Gilmore, isn't it true that the bulk of your

25   compensation is based on the profits of SUSI?

FLORIDA PUBLIC SERVICE COMMISSION

392

1        A    If SUSI does not make money, I don't make money.

2        Q    Well, isn't it correct that you draw a nominal salary

3   only from SUSI?

4        A    That's correct.

5        Q    And the bulk of your compensation is based upon the

6   profits of the company.

7        A    It's based partially on the profits of the company

8   and partially on my own activities.

9        Q    And SUSI, I think Mr. Brown has already testified,

10   has a contingency fee arrangement with its clients regarding

11   payment if it is successful in achieving refunds in this

12   proceeding; correct?

13        A    I think that was his testimony.

14        Q    And as a principal of SUSI, you stand to benefit

15   financially if the refunds in this case are extended beyond the

16   one year provided in the rule; correct?

17        A    Yes.

18        Q    Could you please refer to your Exhibit BG-2.

19        A    Could you tell me what that is?

20        Q    It's the backup data for the billing data that you

21   put together.

22        A    Okay.

23        Q    And this is a composite exhibit of billing data for

24   the meters that are at issue in this docket; correct?

25        A    BG-2?

FLORIDA PUBLIC SERVICE COMMISSION

393

1        Q    Yes.

2        A    Yes, sir.

3        Q    And take a look at the first page of that composite.

4        A    What store is that?

5        Q    Target State Road 7.

6        A    Yes.

7        Q    This is the Target store in Boca; correct?

8        A    Yes, sir, on State Road 7.

9        Q    Now, that store is not actually included in this

10   docket; isn't that right?

11        A    I'm not aware of that, sir.

12             MR. MENTON:  Commissioner Deason, if I might, this is

13   the Target store that was referred to earlier, the Target Boca

14   store, and there are two portions -- or actually three portions

15   of his testimony that refer to the Target store in Boca which I

16   believe is not part of this docket and should be stricken from

17   the exhibit.  And specifically it's Page 1 of BG-2 here.  And

18   then going back to his next exhibit, which is BG-3, which is a

19   composite exhibit that has the control charts and the tables

20   that were used in preparing the control charts, the first two

21   pages of that exhibit also relate to the Target store on State

22   Road 7.

23             And then in addition to that, if you look at his

24   testimony on Page 6, that is the -- beginning on Line 19 and

25   carrying over to Page 7, he uses this particular store as an

FLORIDA PUBLIC SERVICE COMMISSION

394

1   exhibit.  So I would move to strike those portions of his

2   exhibits and testimony as they relate to a meter that is not at

3   issue in this docket.

4             COMMISSIONER DEASON:  Mr. Hollimon.

5             MR. HOLLIMON:  Yes, Commissioner Deason.  I assume we

6   can handle this the way we handled the earlier issue.  That

7   would be fine with us.

8             COMMISSIONER DEASON:  The record reflects that the

9   Customers acknowledge that this particular meter is not subject

10   to further determination by this Commission as to a refund, and

11   so I'll just let the record reflect that.  And there's no need

12   to go through the exercise of striking portions of exhibits or

13   portions of prefiled testimony.

14             MR. MENTON:  And just one other area where it does

15   show up on Exhibit 4 as well.  It's the first one in Line 4 of

16   his exhibits.

17             COMMISSIONER DEASON:  Very well.

18             MR. MENTON:  Thank you, sir.

19   BY MR. MENTON:

20        Q    Mr. Gilmore, on Page 4 of your testimony, you

21   indicate that one of the assumptions that you made in your

22   analysis was that there is a relationship between consumption

23   and demand; correct?

24        A    Yes, sir.

25        Q    And to conduct your analysis, you calculated a ratio

FLORIDA PUBLIC SERVICE COMMISSION

395

1   of demand to consumption utilizing maximum demand to total

2   kilowatt consumption for a given period; correct?

3        A    Would you repeat that?  I want to make sure.

4        Q    To conduct your analysis, you calculated a ratio of

5   demand to consumption utilizing maximum demand to total

6   kilowatt consumption for a given period.

7        A    Yes.

8        Q    Would you please refer to your Exhibit BG-1.

9        A    For what store?

10        Q    BG-1.

11        A    Oh, BG-1.  Okay.  Yes.

12        Q    And this exhibit purports to reflect the extent to

13   which there is a correlation between demand and consumption for

14   each of the meters in question as well as the Target Boca that

15   we talked about earlier; correct?

16        A    That's correct.

17        Q    In other words, whether or not there was the ratio

18   that you've utilized actually shows a relationship between

19   demand and consumption.

20        A    That's correct.

21        Q    Now, on Page 6, Lines 5 through 6 of your testimony,

22   you indicate that you believe a correlation of .70 would be

23   considered a strong correlation; correct?

24        A    Yes, that's a very strong correlation.

25        Q    Now, even if we accept all of the other aspects of

FLORIDA PUBLIC SERVICE COMMISSION

396

1   your approach, and I'm going to talk about some of the problems

2   that we see with it in a minute, but even if we accept all of

3   the other aspects of your approach, when the correlation is

4   below .7, you would agree that it's harder to draw any

5   conclusions from the data; isn't that right?

6        A    Harder, but not out of the question.

7        Q    So it is harder.  All right.

8             Now, let's take a look at your Exhibit BG-1.

9        A    Okay.

10        Q    Four of the meters that you've listed on here,

11   Delray, Target Hollywood, J.C. Penney Naples, and Dillard's

12   Coral Springs, the correlation that you calculated is well

13   below the .70 figure that you reference in your testimony;

14   correct?

15        A    A correlation -- the reason I can't answer yes or no

16   is the definition of well below.  The correlation could be

17   anywhere from minus one to plus one.

18        Q    Okay.  For Dillard's Coral Springs it's .33?

19        A    Yes.

20        Q    Okay.  And J.C. Penney Naples is .48?

21        A    Yes.

22        Q    Okay.  Now, for some of these where the correlation

23   was below the standard of .7 that you had referenced, you made

24   some footnotes here off in the right-hand column.  Do you see

25   that?

FLORIDA PUBLIC SERVICE COMMISSION

397

1        A    Yes.

2        Q    And if you would take a look at Note 3, which relates

3   to the J.C. Penney's Naples store, down below here you have a

4   little explanation as to -- well, why don't you just read us

5   what your Footnote 3 says.

6        A    Number 3.  Underlying data is suspect.  For example,

7   in 1994, there are four consecutive months (April through July)

8   where the demand is 480, even though the kilowatt hour

9   consumption increases from 189,000 to 248,000.

10        Q    Okay.  So you're saying that the 1994 data for J.C.

11   Penney's Naples is suspect and, therefore, that that might

12   provide an explanation for why the correlation isn't as great

13   as you were hoping it to be; correct?

14        A    That's a possible explanation, that's correct.

15        Q    Would you please refer to Exhibit 3, Page 11.

16        A    What store is that?

17        Q    It's the J.C. Penney's Naples that we just

18   referenced.  I'm sorry, it's Exhibit 2 in the billing data.

19        A    Exhibit 2?

20        Q    Yes.

21        A    Page 11?

22        Q    Yes.

23        A    I have it.

24        Q    Okay.  So this is the meter that you were just

25   talking about where the data for 1994 was supposedly suspect;

FLORIDA PUBLIC SERVICE COMMISSION

398

1   correct?

2        A    Yes.

3        Q    Okay.  If you look at the billing data, the billing

4   data doesn't even pick up until 1996, does it?

5        A    That's what it shows, sir.

6        Q    Okay.  So there is no data for 1994 as referenced in

7   your footnote for Number 3 back on BG-1; isn't that right?

8        A    Yes, sir, there is data.  It's just not here.

9        Q    You have data for J.C. Penney's Naples prior to 1996?

10        A    I want to make sure I look at the right one.  I have

11   a lot of them here.

12             Okay.  I was looking at the wrong one.  Yes, that is

13   correct, there is no data for that.

14        Q    So the footnote in your Exhibit BG-1 does not provide

15   any explanation for why the correlation for this meter is below

16   the .70 that you have identified as constituting a strong

17   correlation; isn't that right?

18        A    You're going to have to repeat.  Say that again.

19        Q    Well, the point is, is that the footnote that you

20   have here, Number 3, that purports to explain why there might

21   not be a correlation is, in fact, not correct because there is

22   no 1994 data that it could be in error as you referenced in

23   this footnote; correct?

24        A    Yes, sir.  That's an error.

25        Q    And you don't have any explanation for why the

FLORIDA PUBLIC SERVICE COMMISSION

399

1   correlation for the Dillard's Coral Springs would be .33, do

2   you?

3        A    I have some suspicions, but I have no data.

4        Q    Okay.  In your Exhibit BG-1 here that purports to

5   show the correlation for the various meters, you don't have

6   Dillard's Port Charlotte listed on here, and that's one of the

7   meters that's in this docket; isn't that right?

8        A    No, sir, I do not.

9        Q    So you haven't provided us with any information

10   regarding the correlation for that meter that is in this

11   docket; correct?

12        A    That's correct.

13        Q    Okay.  Mr. Gilmore, would you take a look at the

14   control charts which are included as part of your Exhibit BG-3.

15   Let's basically move to Exhibit BG-3.

16        A    Okay.  Any one specific?

17        Q    Yes.  Let's take a look at the Port Charlotte control

18   chart.

19        A    Port Charlotte Dillard's?

20        Q    Target, Target Port Charlotte, which is about halfway

21   through --

22        A    I'm sorry, what did you say?  Target Port Charlotte?

23        Q    Target Port Charlotte control chart, which is about

24   halfway through your exhibit pack.  The pages aren't numbered,

25   I'm sorry.

FLORIDA PUBLIC SERVICE COMMISSION

400

1        A    Target Port Charlotte.

2        Q    And this is one of the exhibits that you have

3   presented to the Commission to demonstrate your theory that

4   somehow some of these meters are, quote, out of control; is

5   that right?

6        A    That's part of the reason I submitted it.

7        Q    Okay.  And by out of control, that means that it

8   falls below the lower control limit; is that right?

9        A    Yes.

10        Q    Okay.  And the control limits -- if a meter falls

11   within the control limits, that essentially means that any

12   variation that occurs can be explained by natural chance; isn't

13   that right?

14        A    Well, it's somewhat the opposite of that.  If it

15   falls in there, you cannot conclude that it has a specific

16   cause other than natural variation.

17        Q    Well, let's look at Target Port Charlotte for a

18   second here.

19        A    Okay.

20        Q    The next page is the page that is used to calculate

21   the lines that are reflected on the chart; is that right?

22        A    That is correct.

23        Q    If you look at the chart, the following page behind

24   the chart for Target Port Charlotte, you have calculated a mean

25   for this meter of 2.49; correct?

FLORIDA PUBLIC SERVICE COMMISSION

401

1        A    That's correct.

2        Q    And you have calculated a lower control limit of

3   2.349; correct?

4        A    That is correct.

5        Q    Let's go back to the chart and take a look at the

6   chart that you have for this exhibit.  This exhibit would seem

7   to reflect a mean of 2.549 roughly, wouldn't it?

8        A    It's over 2.5, yes.

9        Q    And the control limit on your chart is 2.45 or above;

10   correct?

11        A    Yes, sir, that's correct.

12        Q    Well, if we had actually graphed the control limits

13   that you had calculated here with a lower control limit of

14   2.349, you would agree that this meter would be in control;

15   isn't that right?

16        A    No.  Actually, I would agree that I don't have the

17   right data corresponding to this.

18        Q    Now, which is wrong?  The chart or the calculating

19   data that you have behind the chart?

20        A    I'm not quite sure.

21        Q    Mr. Gilmore, you would agree that there are a number

22   of items that could impact upon a customer's electrical usage

23   and kilowatt demand consumption; correct?

24        A    That's correct.

25        Q    For example, weather, change in usage, equipment

FLORIDA PUBLIC SERVICE COMMISSION

402

1   deterioration, installation failures, changes in business

2   practices, conservation, all of those could have an impact upon

3   either or both of a customer's electrical usage in kilowatt

4   demand consumption; correct?

5        A    Yes.  But some of those you mentioned would have a

6   very small effect and some would have a very large effect --

7   could have a large effect.

8        Q    Okay.  Now, we've already talked a little bit about

9   what it means for a control chart to be, quote, in control, and

10   that means that the variation conforms to a statistical pattern

11   that might reasonably be produced by chance causes.  Is that a

12   fair statement?

13        A    Again, you cannot conclude that any of the variation

14   is not chance cause.  It's sort of the negative to what you

15   said.

16        Q    Well, when a sample is out of control, so to say,

17   when it falls below the control limits, it's not possible to

18   trace the variation to any particular cause, is it?

19        A    Not from the control chart itself.  That is a flag to

20   say something is out of control, and you go back and look at

21   the data and the circumstances to determine what it was.

22        Q    But you can't draw a conclusion from a control chart

23   as to what the particular cause is in any situation, can you?

24        A    Without further data, you cannot.

25        Q    Now, going back to your Exhibit BG-2, as reflected on

FLORIDA PUBLIC SERVICE COMMISSION

403

1   your BG-2, you had at least five months of data for the year

2   2004 at the time you prepared your analysis; correct?

3        A    Had at least what?  I'm sorry.

4        Q    You had at least five months of data for the year

5   2004 at the time you prepared your analysis.

6        A    Yes, I did.

7        Q    And there was additional 2004 data available

8   subsequent to the preparation of your testimony; isn't that

9   right?

10        A    Yes, sir.

11        Q    And you have not included any of the 2004 data as

12   part of your control charts, have you?

13        A    No, sir, I would never do that.

14        Q    Okay.  And you haven't done any analysis of the 2004

15   data, have you?

16        A    Yes, sir, I have.

17        Q    Well, do you recall during your deposition when I

18   took it back on September 9th I asked you that question?

19        A    Yes, sir, that was two months ago.

20        Q    Two months ago.  So at the time that I took your

21   deposition, you had not done any analysis of the 2004 data,

22   have you?

23        A    No, I had not.  It would have been improper to do so.

24        Q    And you did not at the time we took your deposition

25   provide us with any benefit of your insight into what the 2004

FLORIDA PUBLIC SERVICE COMMISSION

404

1   data might show, did you?

2        A    You have to have all four seasons in the data before

3   it counts, before it means anything.

4        Q    And when I asked you at your deposition on September

5   of this year whether the 2004 data was consistent with the

6   analysis that you presented in your testimony, you couldn't

7   answer that question, could you?

8        A    At the time I could not.

9        Q    So the analysis that you've presented with respect to

10   your charts here, it only shows in certain situations there was

11   one year that seemed to change after the meter change out; is

12   that right?

13        A    You're going to have to repeat that.  I'm sorry.

14        Q    Well, maybe I'll skip that one and move on.  I'm

15   going to try to skip over and speed up, so we can get finished

16   here.

17             Would you agree with me that knowledge of the

18   behavior of chance variations is the foundation on which

19   control chart analysis rests?

20        A    You're going to have to repeat that again.  I'm

21   having trouble hearing you.

22        Q    Knowledge of the behavior of chance variations is the

23   foundation on which control chart analysis rests.

24        A    I'm not sure it's a foundation, but it's certainly

25   part of it.

FLORIDA PUBLIC SERVICE COMMISSION

405

1        Q    So you don't disagree that that's a very important

2   component of any controlled chart analysis; correct?

3        A    No, I do not.

4        Q    And you would agree that the more data points that

5   are utilized in a controlled chart analysis, the better you are

6   able to draw any conclusions from it; isn't that right?

7        A    Good and more good and appropriate data makes your

8   analysis better, but more data if it's not appropriate or wrong

9   data does not help you.

10        Q    Well, when you use these data points on here, these

11   are the points that you're utilizing to calculate the mean in

12   the upper and lower control limits; correct?

13        A    Yes, sir.

14        Q    And from a statistical standpoint, isn't it better to

15   have more data to include to draw those kinds of lines, the

16   mean and the upper and lower control limits, rather than less

17   that?

18        A    Yes, sir.  But we went back to the extent of records.

19   We used all the data available.

20        Q    Well, you had the ability to do a monthly analysis of

21   this data, did you not?

22        A    Yes, sir.  But I'm not understanding why I would want

23   to do that, why would anyone want to do that.

24        Q    Well, you did not do an analysis of the monthly data,

25   did you?

FLORIDA PUBLIC SERVICE COMMISSION

406

1        A    You mean comparing January to February and then

2   February to March?

3        Q    Yes, sir.  You could calculate a demand ratio for

4   every month for every year in which you had this data, and you

5   could use that to calculate control limits, calculate a mean

6   and to do an analysis; isn't at right?

7        A    If you did that, you would insert seasonal variation

8   in the ratio, and the ratio has a seasonal variation.

9        Q    Could you answer my question first; then you can

10   explain.

11        A    Could you mathematically do it?

12        Q    Yes.

13        A    Yes, I can take the calculator out and do it.  Yes,

14   sir, I could.

15        Q    And if you did that, you would be using a lot more

16   individual data points from which you would be drawing your

17   mean and from which you would be drawing your upper and lower

18   control limits; correct?

19        A    You have more numbers, yes, sir.

20        Q    By aggregating 12 months' worth of data into a single

21   point, which is what you've done here with your analysis; isn't

22   that right?

23        A    Yes, sir, I have.

24        Q    You are not able to determine whether in any

25   particular year there were any abnormal or unusual seasonal

FLORIDA PUBLIC SERVICE COMMISSION

407

1   variations; correct?

2        A    I put 12 months in, yes, sir.  No, sir, I could not.

3   I put the 12 months in specifically to avoid seasonal

4   variations.  We all know we have seasonal variations.  We

5   weren't looking for seasonal variations.  We were looking from

6   year to year change.

7        Q    But you only have one year after the change, so how

8   can you draw any conclusions from one year's worth of

9   post-data?

10        A    You can draw two different conclusions possibly if

11   the chart shows it.  One is all the points before the meter

12   change out are in control.  There's no evidence of any slow

13   change.  Two, there is for the year after a significant change,

14   and you'd say now what caused that change?  What was the

15   difference between this year and all the rest?

16        Q    Mr. Gilmore, you had information that told you when

17   these meters were actually removed; isn't that right?

18        A    Yes, sir.

19        Q    Did you do any analysis of what happened in the

20   months immediately after the meters were removed and compared

21   those to the months in the prior years to see whether there was

22   any change?

23        A    That's in here.

24        Q    Where is the monthly data --

25        A    The monthly, it's not.  It's aggregated.

FLORIDA PUBLIC SERVICE COMMISSION

408

1        Q    Okay.  You never did an analysis of what happened.

2   Let's take, for example, a meter that was removed in November

3   of '02, which is when a lot of these meters were removed.

4        A    Right.

5        Q    You never looked at whether or not the demand ratio

6   in December of '02 was different than the demand ratio in

7   December of '01.  You never looked at whether January '02 was

8   different.  You didn't look if February '02 was different.  You

9   didn't look at whether March or April was different, did you?

10        A    Yes, sir, I did do some preliminary on that.

11        Q    Mr. Gilmore, during your deposition I asked you that

12   question, did I not?

13        A    Not exactly like that.

14        Q    I asked you whether you had done any monthly

15   analysis, did I not?

16        A    Yes, sir.  I thought you meant, say, January to

17   February to March to April.

18        Q    Well, during your deposition when I asked you whether

19   you had done any monthly analysis, you told me that you had

20   not; isn't that right?

21        A    I have no meaningful analysis to provide.

22        Q    So if you're using yearly analysis, if there was a

23   sudden drop-off six months after the meter changed out, we

24   wouldn't be able to tell that from the data or the information

25   that you've presented, would we?

FLORIDA PUBLIC SERVICE COMMISSION

409

1        A    If you're talking about -- yes, I'm sorry.  No,

2   you'll not be able to change -- show dramatic changes.  It's an

3   average, comparing years to years.

4        Q    And you wouldn't be able to tell when in a particular

5   year the data may have changed even if it did change, would

6   you?

7        A    No, sir.  This is yearly data.

8             MR. MENTON:  Commissioner, just give me a couple more

9   minutes.  I'll try to skim through this.

10   BY MR. MENTON:

11        Q    Mr. Gilmore, are you familiar with Professor

12   Shewhart?

13        A    Yes, sir.

14        Q    Professor Shewhart is kind of considered the guru of

15   control charts, is he not?

16        A    He's definitely one of the authorities.

17        Q    Let me read you a quote from Professor Shewhart and

18   see whether you agree with this or not.  "It has also been

19   observed that a person would seldom, if ever, be justified in

20   concluding that a state of statistical control of a given

21   repetitive operation or production process has been reached

22   until he had obtained, under presumably the same essential

23   conditions, a sequence of not less than 25 samples of size

24   4 that are in control."

25             MR. HOLLIMON:  Objection.  Can we have that given to

FLORIDA PUBLIC SERVICE COMMISSION

410

1   the witness and get some foundation for that?

2             MR. MENTON:  Your Honor, this came from a Web site

3   that Mr. Gilmore cited me to as part of the information that he

4   relied upon in developing his testimony.  And it's a quote from

5   Professor Shewhart who is a recognized authority in the area.

6             THE WITNESS:  I'm familiar with the quote.

7   BY MR. MENTON:

8        Q    You are familiar with the quote?

9        A    Yes, I am.

10        Q    You don't disagree that a sequence of not less than

11   25 samples of size 4 should be in control before you draw any

12   conclusions with respect to a control chart; isn't that right?

13        A    Yes, sir, I disagree with that because of the way it

14   has been used over the many years since Dr. Shewhart made the

15   statement.  You will see authorities, people who know control

16   charts much better than I, using available data when they have

17   6, 7 points.  They acknowledge the fact that they don't have as

18   many points as they would like, but they could use it.  And

19   it's not considered bad data.  It's just you would like to have

20   more.

21        Q    And let me ask you to continue on with that page that

22   Mr. Hoffman has now handed you.  The last sentence there which

23   quotes from Quesenberry, who is another well-respected expert

24   in the area of control charts; isn't that right?  Could you

25   read that last sentence into the record, please.

FLORIDA PUBLIC SERVICE COMMISSION

411

1        A    "It's important to note that control" --

2        Q    No, just the last sentence beginning with when.

3        A    "When the control limits are not computed from a

4   large amount of data, the actual properties might be quite

5   different from what is assumed."

6        Q    Do you agree or disagree with Professor Quesenberry's

7   statement there?

8        A    Yes, sir, I agree.  It's well known that you need

9   more -- the more data, the better.  But I would add, you would

10   not put in irrelevant data to allow you to have more.

11             MR. MENTON:  Just a couple more points, Commissioner.

12   I'll try to speed up here.

13   BY MR. MENTON:

14        Q    You would agree, Mr. Gilmore, that there is no

15   general statistical principle that would allow you to discard

16   data that you don't like; isn't that right?

17        A    No.  I'm sorry.  Would I agree?  I agree that I know

18   of no statistical concept that says you can under this exact

19   circumstance throw out data that is suspect or something.

20        Q    Well, one of the reasons for doing a statistical

21   analysis is try to make sense of the world of data that you've

22   accumulated; isn't that right?

23        A    Yes, sir.

24        Q    So you can't just willy-nilly discard data that you

25   don't like; isn't that accurate?

FLORIDA PUBLIC SERVICE COMMISSION

412

1        A    You would never do it willy-nilly, but there are many

2   cases where -- that you analyze aberrations in data, try to

3   come up a reasonable cause for it, mark it as being this is

4   probably the cause, and take it out of your sample.

5        Q    Well, and that's what you did in connection with some

6   of the charts that you have presented to the Commission today;

7   isn't that right?

8        A    Yes, sir.  There was some data that we just plain did

9   not understand.  We used the data from FPL.  We used what we

10   got --

11        Q    Okay.  And then some of that data you excluded when

12   you prepared your charts and your analysis for your testimony;

13   correct?

14             MR. HOLLIMON:  Excuse me.  Can we let the witness

15   answer, complete his answers?

16             MR. MENTON:  I'm sorry.

17             THE WITNESS:  Yes, sir, once or twice.  Maybe you

18   could point out more than that, but once or twice we took out

19   certain data that was consecutive meter reads.

20   BY MR. MENTON:

21        Q    But there was no fixed standard that you utilized in

22   determining to exclude data, was there?

23        A    No, sir.  If somebody else did it, they might take

24   out more.

25        Q    So it was a subjective standard that you applied in

FLORIDA PUBLIC SERVICE COMMISSION

413

1   certain instances to exclude data as you were preparing your

2   testimony for this Commission.

3        A    Yes, sir.

4        Q    Now, for example, for Target Hollywood, you did not

5   use the data for 1994; isn't that right?

6        A    That's correct.

7        Q    And that data, if included, would have significantly

8   impacted upon the mean and the control limits that you would

9   have projected; isn't that correct?

10        A    I'm looking at the data, sir.

11        Q    And this is Page 6 of Exhibit 2.

12        A    Yes, sir, that was a subjective call on my part to --

13   when I scratched my head long enough in looking at the data, I

14   said, I don't understand it, how it could be this way.

15        Q    And as I understood your testimony at your deposition

16   when I asked you, it was because you had consecutive demand

17   readings of the same number, and therefore, you used that as a

18   basis to exclude the 1994 data when you calculated your mean

19   and your control limits; is that right?

20        A    Yes, sir.  In other places there's also multiple

21   readings, and this one just stuck out.

22        Q    Okay.  So, for example, in '94 there's several

23   readings of -- demand readings of 480.  So you used that as a

24   basis to exclude that data; correct?

25        A    Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

414

1        Q    But isn't it true, Mr. Gilmore, that for that same

2   meter if you look at the data for 1996, for 1997, for 1999, and

3   for 2001, there are identical situations which you did not

4   exclude when you did your analysis?

5        A    If they were identical, I wasn't aware of it.  I

6   thought I was picking out the worst cases.

7        Q    And it's because in 1994 you had four consecutive

8   480 readings of demand from the months of July -- or I guess

9   this is upside down, but it would be from April through July;

10   correct?

11        A    Yes, sir.

12        Q    Okay.  But if you look at 1997, if you look at March

13   through September, you had even more months with the same

14   consecutive demand reading, and you did not exclude that data,

15   did you?

16        A    I probably should have taken that one out too.

17        Q    And you could have done the same thing in '99, and

18   you could have done the same thing in 2001, and you could have

19   done the same thing in 1996 if you were being consistent; isn't

20   that right?

21        A    I was trying to use the best data available.  If I

22   was inconsistent, it was not an intent.

23        Q    Well, and you did this in other instances as well,

24   didn't you?  For Target in Venice, you excluded the data for

25   the year 2001; isn't that right?

FLORIDA PUBLIC SERVICE COMMISSION

415

1        A    Yes, sir.

2        Q    Okay.  And the basis was because there were three

3   months where the meter reading was the same in May, June, and

4   July, and so you excluded 2001 data.

5        A    Just one second.  Also, the multiple readings of

6   576 in 2000 --

7        Q    But you didn't exclude 2000.

8        A    I excluded the 12 months labeled 2001.  These

9   12-month periods are not calendar periods.  They're 12-month

10   periods on each one.

11        Q    Well, let me just ask you this way, see if I can

12   speed it up.

13             You would agree that if you had included the 2001

14   data for the Target Venice store, it would have significantly

15   impacted upon the mean and the control limits that you have

16   included -- or that you would have calculated; is that fair?

17        A    I took those data points out before I even calculated

18   it.  I don't know.

19             MR. MENTON:  Commissioner Deason, I have just one

20   last area that I'll get into, and I'll try to make this brief.

21   This, I think, is going to end up in a brief proffer, but I

22   wanted to lay a couple of questions as a predicate and then

23   I'll come back to it.  But this is the last issue.

24   BY MR. MENTON:

25        Q    Mr. Gilmore, referring back to your

FLORIDA PUBLIC SERVICE COMMISSION

416

1   Exhibit B-2 (sic), you utilized those numbers, as we've already

2   talked about, to calculate the ratio which was then used to

3   calculate the control limits and the mean; is that right?

4        A    B-2 is the raw data.  Right.

5        Q    And you annualized that data, and then you calculated

6   the mean and the control limits; is that right?  Well, let me

7   back up.

8             You calculated the ratio based upon annualized data,

9   and that's a straight mathematical calculation; right?

10        A    That's correct.

11        Q    And you could take the monthly data, as I think we've

12   already talked about, and run the ratio calculation very

13   simply.  It's a straight mathematical calculation; correct?

14        A    Are you referring to month-by-month?

15        Q    Month-by-month.

16        A    You could do it by day if you like.  Yes.

17        Q    And we've got the monthly data here in BG-2 which

18   shows each of the readings for each of the months for all of

19   the years in question for each of the meters.

20        A    Right.

21        Q    And so you can calculate that across very easily to

22   determine what the monthly ratio would be; correct?

23        A    Yes.

24        Q    And then you could take the monthly calculation and

25   project that onto a chart calculating the mean, and you could

FLORIDA PUBLIC SERVICE COMMISSION

417

1   calculate control limits very simply using the monthly data;

2   isn't that right?

3        A    You could do it mathematically, but I don't know that

4   it would be of any value to you.

5        Q    But you don't know because you haven't done the

6   analysis, have you?

7        A    No.  I would not do it that way.  I would not

8   recommend anyone else do it that way either.

9             MR. MENTON:  Commissioner Deason, if I might.  The

10   reason I just asked those last questions is, Mr. Gilmore's

11   analysis that we've heard about today was presented to us for

12   the first time as rebuttal testimony.  We have moved to strike

13   that analysis since it was not included as part of the

14   Customers' case in chief, and that motion was denied.  And we

15   certainly respect that ruling.  But because we didn't have an

16   opportunity to submit any rebuttal testimony because it wasn't

17   presented in the case in chief, we were a little bit handcuffed

18   in order to try to respond to some of the analysis that he's

19   presented here.

20             I would like to present as a composite exhibit, we

21   have done those monthly ratio calculations, and we have plotted

22   those onto a graph, and I would like to submit those.  Again, I

23   think it's a straight mathematical calculation.  I'm not going

24   to belabor the Commission today by going through with him each

25   of the months and trying to calculate it.  I just think in our

FLORIDA PUBLIC SERVICE COMMISSION

418

1   proposed order we can make some references to it.  And

2   alternatively, we would just like to proffer it for the record

3   if -- whatever you like.  But let me pass those out.

4             I have provided these just a couple of days ago to

5   Mr. Hollimon, and I know they haven't had an opportunity to

6   fully run all those calculations.  But it's a straight -- I

7   mean, all you need is a little calculator.  You can actually

8   get a computer program to run that stuff.

9             MR. HOLLIMON:  Commissioners, we would object to

10   entry of some exhibit prepared by counsel for FPL.  If they

11   wanted to have surrebuttal, they could have moved for

12   surrebuttal; they did not do that.  We have no opportunity to

13   cross-examine the person that prepared this particular

14   document.  And I have been provided a copy of it, but from the

15   information contained in that exhibit, there's no way to

16   determine how, in fact, the graphical analysis was conducted.

17             As I understand it, it's a computer program that you

18   push the button and all this internal whirring goes on and you

19   get a result, but that doesn't help me understand what the

20   process was that was used as opposed to Mr. Gilmore's testimony

21   where all the information necessary to understand the

22   calculations and the plotting of the graphs is presented in his

23   testimony.  Mr. Gilmore is available and is being

24   cross-examined.  We don't have a similar opportunity with

25   regard to the information that Mr. Menton has now proffered.

FLORIDA PUBLIC SERVICE COMMISSION

419

1             COMMISSIONER DEASON:  Mr. Menton.

2             MR. MENTON:  Commissioner Deason, if I might.  The

3   composite exhibit that I just handed to you, actually there are

4   two documents related to each of the meters in question.  The

5   first document takes the data from Mr. Gilmore's Exhibit Number

6   2, which is all of the billing data, the kilowatt and the

7   demand readings, and then is a straight mathematical

8   calculation.  You can sit there and do each one line by line.

9   And I think it's a matter that can appropriately be officially

10   recognized by the Commission because under the evidence code --

11   or information that is easily verifiable can be taken --

12   judicial notice can be taken of that.  So I would submit that

13   the first document that I've presented there is a straight

14   mathematical calculation that can be easily verified.

15             The second one is just a plot of that data.  Now, on

16   that plot, on the graphs, there are -- there's a mean, which

17   again is a very straight mathematical calculation of all the

18   data which I don't think can really be contested.  And the

19   control limits, I would agree, the control limits are part of a

20   computer program.  And again, I don't think it's a

21   controversial issue.  It's just a matter of whether you use a

22   sigma 2 or a sigma 3, and the computer will calculate it for

23   you.  But I will not make any arguments based upon that.  I

24   would proffer it for the record just to demonstrate what we

25   would have presented as rebuttal testimony if this had been

FLORIDA PUBLIC SERVICE COMMISSION

420

1   presented in the Customers' case in chief.

2             COMMISSIONER DEASON:  Mr. Keating.

3             MR. KEATING:  I was afraid you were going to look

4   over here.

5             COMMISSIONER DEASON:  It's late in the day.

6             MR. KEATING:  It's late in the day.  And I understand

7   FPL's dilemma and that this was presented in rebuttal

8   testimony.

9             COMMISSIONER DEASON:  You need to get out your coin

10   and flip it?  I'm just kidding.  I'll make the ruling, okay,

11   without advice unless --

12             MR. KEATING:  To be honest, I'm not real sure how to

13   handle it right now.

14             MS. HELTON:  May I have a minute to confer with

15   Mr. Keating?

16             COMMISSIONER DEASON:  Surely.

17             COMMISSIONER DAVIDSON:  Someone from legal knew how

18   to handle it when they advised me how to rule on the order.

19             MR. KEATING:  Commissioners, what staff would

20   recommend is that you accept it as a proffer, but for purposes

21   of admitting into the record, we do not believe it should be

22   admitted into the record.

23             FPL did move to strike portions of Mr. Gilmore's

24   testimony that included this analysis on the grounds that it

25   was improper rebuttal.  The Prehearing Officer ruled that it

FLORIDA PUBLIC SERVICE COMMISSION

421

1   was proper rebuttal.  There wasn't a request for surrebuttal,

2   which this essentially amounts to, but I think it's appropriate

3   for a proffer.

4             COMMISSIONER DEASON:  We will accept it as a proffer.

5   I agree, it should not be in the record.  It borders on the --

6   how should I say?  It's not customary to engage in this type of

7   activity, the sponsoring of such massive documents without a

8   witness actually taking the stand.

9             I would note, however, that to the extent your

10   representation is correct, that it is simply a massive amount

11   of calculations, simple calculations done with data that is

12   already in the record, you may wish to take an example and

13   maybe you could highlight that some way in your brief.  I'm not

14   sure.  I'm not recommending that you do that.  But I'm

15   uncomfortable at this point wholesale admitting all of this

16   information in the record.  And so certainly you can proffer

17   it, but we will not even identify it as an exhibit, and it will

18   certainly not be part of the record.

19             MR. MENTON:  Thank you, sir.

20             COMMISSIONER DEASON:  Does that conclude your

21   cross-examination?

22             MR. MENTON:  Yes, sir.

23             COMMISSIONER DEASON:  Staff.

24             MR. KEATING:  Staff has no questions.

25             COMMISSIONER DEASON:  Commissioners.

FLORIDA PUBLIC SERVICE COMMISSION

422

1             Redirect.

2             MR. HOLLIMON:  Yes.  Thank you, Commissioners.

3                        REDIRECT EXAMINATION

4   BY MR. HOLLIMON:

5        Q    Mr. Gilmore, you were asked several questions about

6   conducting an analysis with 2004 data.  Do you recall that?

7        A    Yes, I do.

8        Q    And why didn't you do an analysis with 2004 data in

9   September of 2004?

10        A    For the data to be meaningful, you need all four

11   seasons into your data points.  If you don't do that, you're

12   comparing summer to winter, and the usage patterns and the

13   ratio are different.  The ratio is lower in one season and

14   higher in another.  I have to figure out which way to do that.

15   That's common.  But if you take all four seasons and put them

16   together, then you have the average for the year.  If you did

17   it for four or five months, you don't -- you have half a year.

18   So you have half a data point.

19        Q    Since September of 2004 has enough time passed where

20   you have additional data of the correct magnitude?

21        A    Yes, sir.  Two of them actually have over two years

22   of data.

23             MR. MENTON:  Commissioner Deason, I'm not sure where

24   we're going with this, but I think, as we've already

25   established in the cross, he did not have any such analysis

FLORIDA PUBLIC SERVICE COMMISSION

423

1   available at the time of his deposition.  And if they're

2   attempting to back door that now, then I would certainly

3   object.

4             COMMISSIONER DEASON:  You're not trying to back door

5   anything, are you, Mr. Hollimon?

6             MR. HOLLIMON:  Absolutely not.  I mean, I believe the

7   door was wide open when on cross-examination he was asked about

8   whether or not he had analyzed 2004 data and whether he had

9   done any additional analysis since --

10             COMMISSIONER DEASON:  You're not trying to introduce

11   any new analysis at this point though, are you?

12             MR. HOLLIMON:  No.  I'm simply trying to make the

13   record clear about what he's done since his deposition occurred

14   and why he has done what he's done since his deposition

15   occurred.

16             MR. MENTON:  It sounds to me like he's trying to back

17   door some analysis that we've never been presented with.

18             COMMISSIONER DEASON:  Mr. Hollimon, I'm going to ask

19   you to proceed with your redirect and leave this particular

20   line.

21             MR. HOLLIMON:  Okay.

22   BY MR. HOLLIMON:

23        Q    Mr. Gilmore, why did you choose to do a yearly

24   analysis instead of a monthly analysis?

25        A    Monthly analysis compares month to month to month,

FLORIDA PUBLIC SERVICE COMMISSION

424

1   and it's somewhat meaningless to compare a month in the fall

2   and a month in summer and a month in the winter.  We know

3   there's a lot of seasonal variation there and having nothing to

4   do with anything except the weather changes.  We know it's

5   there, but we're not trying to capture that.  We're trying to

6   capture long-term changes, if they exist, from over a long

7   period of time.

8             If I were interested in the variation from year to

9   year, I would do that -- I mean, from month to month, I could

10   do that.  I could do that, as I said, from day to day with the

11   proper data.  It wouldn't have any meaning, but I could sure

12   have a lot of data points.

13             MR. HOLLIMON:  Thank you, Mr. Gilmore.

14             COMMISSIONER DEASON:  Okay.  Exhibits.

15             MR. HOLLIMON:  Yes.  We'd move Exhibit 16.

16             COMMISSIONER DEASON:  Yes.  Without objection, show

17   that Exhibit 16 is admitted.

18             (Exhibit 16 admitted into the record.)

19             COMMISSIONER DEASON:  Thank you, Mr. Gilmore.  You

20   maybe excused.

21             (Witness excused.)

22             COMMISSIONER DEASON:  That's the last witness.

23             Staff, any final matters?

24             MR. KEATING:  I believe it would be appropriate to

25   establish a due date for post-hearing briefs from the parties.

FLORIDA PUBLIC SERVICE COMMISSION

425

1   The CASR for this docket currently indicates that those briefs

2   should be due December 6th, and staff proposes that we use that

3   date.

4             COMMISSIONER DEASON:  Any objection to briefs being

5   filed on the 6th of December?

6             MR. HOLLIMON:  That's fine.

7             COMMISSIONER DEASON:  Okay.  Very well.  Anything

8   else?

9             MR. MOYLE:  We have just a couple of matters.

10   Mr. Hoffman and I had discussed -- the Customers had listed

11   some additional witnesses that they wanted to use at this

12   hearing, FPL employees that we took a deposition of.

13   Mr. Hoffman and I reached an agreement that in lieu of calling

14   them as adverse witnesses live we would just introduce their

15   depositions.  So I have the depositions of Mr. DeMars,

16   Mr. Cain, Mr. Faircloth, and Mr. Hutchinson that I'd like to

17   put into the record.

18             COMMISSIONER DEASON:  Okay.  We'll identify the

19   depositions as exhibits.  We'll take them one at a time.

20             MR. MOYLE:  Okay.  I think Mr. DeMars can be 17.

21             COMMISSIONER DEASON:  It will be identified as 17.

22             MR. MOYLE:  Mr. Cain as 18.

23             COMMISSIONER DEASON:  Exhibit 18.

24             MR. MOYLE:  Mr. Faircloth as 19.

25             COMMISSIONER DEASON:  19.

FLORIDA PUBLIC SERVICE COMMISSION

426

1             MR. MOYLE:  And Mr. Hutchinson as 20.

2             COMMISSIONER DEASON:  Exhibit 20.

3             (Exhibits 17 through 20 marked for identification.)

4             MR. MOYLE:  And there is one other matter that I'm

5   not clear on.

6             COMMISSIONER DEASON:  There is agreement that these

7   depositions can be entered into the record?

8             MR. HOFFMAN:  Yes, sir.

9             COMMISSIONER DEASON:  Show then that Exhibits 17

10   through 20 are admitted.

11             (Exhibits 17 through 20 admitted into the record.)

12             MR. MOYLE:  Earlier during the proceeding I had made

13   an effort to try to get in some contracts that are in another

14   proceeding, and you ruled that that was not appropriate.  And I

15   think I made a proffer.  As Mr. Menton just did with his

16   proffer, he provided copies of the document.  I don't want to

17   prejudice myself in any way by not providing copies of the

18   document as a proffer.  And I'd like to provide copies as a

19   proffer at this point, if I could.

20             COMMISSIONER DEASON:  You may do so.

21             MR. HOFFMAN:  Commissioner Deason, Mr. Menton informs

22   me that he's got a hearing at DOAH that's scheduled for

23   December 6th, and he is going to be assisting me on this brief.

24   In light of that, if there's no objection, I would ask that

25   instead of December 6, that post-hearing briefs be established

FLORIDA PUBLIC SERVICE COMMISSION

427

1   to be filed by December 16.

2             COMMISSIONER DEASON:  When is this scheduled to go to

3   agenda conference?

4             MR. KEATING:  On the CASR right now we've got it

5   scheduled to go to agenda conference on January 18th.  The only

6   time limits on taking this to agenda and getting a decision, I

7   believe, are a 90-day limit set forth in Chapter 120 of the

8   Florida Statutes.  There's some flexibility there with that

9   date.

10             COMMISSIONER DEASON:  I'm sorry.  The 90-day what?

11             MR. KEATING:  There's a 90-day time limit in the

12   Florida Statutes for rendering an order following hearing.

13             COMMISSIONER DEASON:  I never knew that.  Is that

14   new?  Wow.  I guess we've always been so efficient we've never

15   mopped up on the 90 days.  When does the 90 days expire?

16   90 days from today?

17             MR. KEATING:  I believe that's how we've interpreted

18   it.  It's not something that's ever come into play, I'll say

19   that.

20             COMMISSIONER DEASON:  So how many days do you need to

21   write the order?  It depends on what we decide.  Okay.  Well, I

22   guess I'll just ask the question to staff.  Is there an

23   objection to changing the briefing schedule from December the

24   6th to the 16th?

25             MR. KEATING:  I don't think we'd have any objection

FLORIDA PUBLIC SERVICE COMMISSION

428

1   to that, and I think we could still get this to an agenda.  I

2   don't have the agenda schedule in front of me, but if there's

3   one in late January, we could probably --

4             COMMISSIONER DEASON:  There's an agenda on the 18th

5   of January, and then the next agenda is the 1st of February.

6   The 1st of February may be giving you just a short amount of

7   time before this magical 90 days expires.

8             MR. KEATING:  And if the parties don't have any

9   objection to allowing me a little more time to write an order

10   beyond that 90 days, I think --

11             COMMISSIONER DEASON:  Well, I'm sure Mr. Hoffman

12   wouldn't because it's his request.

13             MR. HOFFMAN:  That's true.

14             COMMISSIONER DEASON:  Mr. Moyle, whatever input you

15   have in this --

16             MR. MOYLE:  Mr. Menton has another professional

17   obligation; we respect that.  And we would be willing to

18   accommodate a pushback of the filing date of the brief filing

19   date.

20             COMMISSIONER DEASON:  So if it becomes necessary to

21   put this on the February 1st agenda, you'd agree to give staff

22   some latitude in actually writing the order, perhaps some

23   additional time, if necessary.

24             MR. MOYLE:  Yes, that's fine.  I guess it would be

25   decided in that agenda, and then the order would come out

FLORIDA PUBLIC SERVICE COMMISSION

429

1   shortly after that.

2             COMMISSIONER DEASON:  Is that amenable to staff?

3             MR. KEATING:  Yes.

4             COMMISSIONER DEASON:  Okay.  Well, then we can change

5   the briefing schedule then from December the 6th to December

6   the 16th.

7             MR. HOFFMAN:  Thank you, Commissioner.

8             COMMISSIONER DEASON:  Okay.  Anything further?

9   Hearing nothing before we conclude, I just want to thank the

10   parties for being mindful of the time constraints we've worked

11   under.  I think we've covered a lot of ground in a short period

12   of time, but we've done it efficiently and thoroughly.  I think

13   we've had a thorough airing of the issues.  I appreciate the

14   thorough and expeditious way in which you conducted your

15   cross-examination.  I want both parties to know that you

16   concluded your cross-examination well below the three-hour

17   limit, both parties did, both sides.  And staff, your

18   cross-examination was the best I'd ever heard.

19             MR. KEATING:  I don't know if that's a compliment.

20             COMMISSIONER DEASON:  Just being facetious.  With

21   that, this hearing is adjourned.

22             (Hearing concluded at 4:45 p.m.)

23                              - - - - -

24

25

FLORIDA PUBLIC SERVICE COMMISSION

430

1   STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2   COUNTY OF LEON      )

3

I, TRICIA DeMARTE, RPR, Official Commission Reporter,

4   do hereby certify that the foregoing proceeding was heard at

the time and place herein stated.

5

IT IS FURTHER CERTIFIED that I stenographically

6   reported the said proceedings; that the same has been

transcribed under my direct supervision; and that this

7   transcript constitutes a true transcription of my notes of said

proceedings.

8

I FURTHER CERTIFY that I am not a relative, employee,

9    attorney or counsel of any of the parties, nor am I a relative

or employee of any of the parties' attorneys or counsel

10   connected with the action, nor am I financially interested in

the action.

11

DATED THIS 15th DAY OF NOVEMBER, 2004.

12

13

___________________________________________

14                         TRICIA DeMARTE, RPR

FPSC Official Commission Reporter

15                           (850) 413-6736

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION