130

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3                                           DOCKET NO. UNDOCKETED

In the Matter of

4

ELECTRIC UTILITY INFRASTRUCTURE

5   WORKSHOP.

________________________________/

6

7

8

9

10

11

12             ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

13               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

14

15                              VOLUME 2

16                        Page 130 through 279

17

PROCEEDINGS:        Electric Utility Infrastructure

18                       Staff Workshop

19   DATE:               Monday, January 23, 2006

20   TIME:               Commenced at 9:10 a.m.

Concluded at 5:41 p.m.

21

PLACE:              Betty Easley Conference Center

22                          Room 148

4075 Esplanade Way

23                       Tallahassee, Florida

24   REPORTED BY:        JANE FAUROT, RPR

Official FPSC Reporter

25                       (850) 413-6732

FLORIDA PUBLIC SERVICE COMMISSION

131

1                               I N D E X

2                                                      PAGE

3   PRESENTATIONS BY:

4        MICHAEL SPOOR                                 132

5        DAVID McDONALD                                181

6        ALAN SHAFFER                                  215

7        PAUL DAVIS                                    234

8        CHRISTIE MIREE                                250

9        MARK CUTSHAW                                  271

10        MICHELLE HERSHEL                              275

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

132

1                        P R O C E E D I N G S

2             (Transcript continues in sequence from Volume 1.)

3             MS. HELTON:  We have heard from the local governments

4   and some technical experts during the morning session, and now

5   we're going to turn to the utilities to hopefully learn some

6   things about what has happened in the state the last couple of

7   years, at least, and to hear what ideas they might have for

8   mitigating any future damage in the next upcoming storm seasons

9   that unfortunately we have been told could be just as bad if

10   not worse than the ones we have had the last two years.

11             We are not going to keep a tight time frame this

12   afternoon like we did this morning.  We have asked the

13   utilities to work among themselves to kind of decide how much

14   time they each needed, but we are also not going to be perhaps

15   as polite as we were to the presenters this morning in that we

16   envision interrupting you and asking questions as you are going

17   along.  I think that that might give us a little bit more

18   meaningful dialogue.

19             So first up is Michael Spoor with Florida Power and

20   Light.

21             MR. SPOOR:  Thank you.  Good afternoon, everyone.

22             Before I get started, actually, on the Florida Power

23   and Light presentation, I would like to just say a couple of

24   opening remarks on behalf of all of the IOUs.  As was

25   mentioned, my name is Michael Spoor.  I'm the Director of

FLORIDA PUBLIC SERVICE COMMISSION

133

1   Distribution System Performance for Florida Power and Light.

2   I'm responsible for distribution reliability and hardening and

3   emergency preparedness.

4             A couple of points that I do want to make in regards

5   to, again, on behalf of all the invest-owned utilities.  First,

6   we recognize the impacts of the 2004 and 2005 hurricanes on

7   Florida's electrical system.  And, more importantly, the

8   impacts it has had on our customers and actually the

9   communities that we, ourselves, live in.  Because of this, it

10   is time to take a fresh look at these ideas.  And so,

11   therefore, all of the IOUs endorse this effort and agree that

12   it is critical for Florida's economic vitality and the security

13   moving forward.

14             We compliment the PSC and Staff for undertaking this

15   effort, and certainly appreciate the opportunity to participate

16   in today's workshop and any activities that may be happening

17   moving forward.  Florida's investor-owned utilities have

18   extensive experience and are ready to actively and

19   constructively help evaluate infrastructure alternatives that

20   work for Florida.  For this process to ultimately provide the

21   best results, we must take time to understand all of the facts

22   and options to ensure that whatever changes we make are truly

23   for the better.

24             So now I would like to speak specifically about FPL.

25   With me here today are some of our technical engineers from

FLORIDA PUBLIC SERVICE COMMISSION

134

1   both our transmission and distribution groups if there is, by

2   chance, a question that I may not be able to answer that they

3   may be in a better position to answer.  In addition to my

4   presentation today, the staff had asked a series of questions

5   in advance of this workshop which I believe we provided

6   detailed responses already in advance.

7             MS. HELTON:  Let me say, I think those responses have

8   been handed out today and also are available on the web.  And I

9   have learned, since I made an announcement this morning that

10   everything was available on the website as of this morning,

11   that wasn't exactly true.  We are having some technical

12   difficulties with Gulf Power's presentation, not because of

13   what Gulf Power gave to us, but because we are just having

14   computer issues that are larger than that.  So hopefully by

15   tomorrow Gulf Power should be up, as well.

16             MR. SPOOR:  I want to first start out by providing

17   some specifics about our service territory in Florida.  We have

18   facilities along the east coast from Georgia all the way down

19   through Miami-Dade County.  And on the west coast, we serve

20   just below Tampa all the way down through Naples and Fort

21   Myers.  We have a growing system.  In fact, for the last

22   several years we have been adding over 100,000 customer

23   accounts to our service territory.  We have a very large

24   infrastructure, which includes over 68,000 transmission

25   structures, over 800,000 distribution transformers, and over

FLORIDA PUBLIC SERVICE COMMISSION

135

1   one million distribution poles that serve 4.3 million customer

2   accounts in the state.

3             My presentation today will cover our experiences from

4   the 2004 hurricane season and how those storms impacted our

5   infrastructure and customers.  Next I'll talk about some

6   lessons that we learned from the '04 season, specifically ones

7   that we were able to apply to the 2005 season.  Following that,

8   I will cover this past year's experiences and certainly, again,

9   how it impacted our system and our customers.  What lessons we

10   might have learned already from the 2005 season, but more

11   importantly, what are the next steps that we need to take in

12   this initiative.

13             I think it's important to start, first, by providing

14   a recap, certainly going back to last season, or the '04 season

15   in terms of hurricanes.  We believe this approach will only

16   work if, first, we recognize where we have been, where we are,

17   and then certainly where we need to go.

18             In 2004, FPL's service territories were impacted by

19   three direct hits by hurricanes.  The first was Hurricane

20   Charley made landfall on the west coast of Florida on August

21   13th, 2004, as a Category 4 with winds of 145 miles an hour.

22   The hurricane force winds spread out over 60 miles and tropical

23   storm force winds were 210 miles wide.  Charley was a

24   fast-moving storm.  It impacted not only our west coast with

25   hurricane force winds, but also exiting near Daytona Beach

FLORIDA PUBLIC SERVICE COMMISSION

136

1   still as a strong hurricane.

2             Not soon after we completed our restoration efforts

3   for Charley, we were again impacted by a second hurricane,

4   Hurricane Frances, which made direct landfall in our Treasure

5   Coast area.  Again, Frances was a very large hurricane.

6   Hurricane force winds were spreading out over 145 miles and

7   tropical storm force winds 345 miles wide.  In essence, our

8   entirely 27,000 square mile service territory was impacted by

9   this hurricane.

10             Not only was it a big hurricane, but it was a

11   slow-moving hurricane.  In fact, some of us that were involved

12   with it wondered if it was ever going to move off us.  Well,

13   thank God it did 60 hours later, so we could effectively begin

14   our restoration efforts.

15             The last hurricane of the '04 season that had direct

16   impact on us was Hurricane Jeanne, which made landfall in

17   almost the exact area as Hurricane Frances did just a few weeks

18   earlier.  Again, hurricane force winds extended 125 miles out

19   with tropical storm force winds at 315 miles wide.

20             Again, as part of the materials we have provided

21   already in advance we furnished maps that break down the

22   equipment repaired by FPL management area and/or region.  This

23   slide here shows a cumulative summary of all the equipment we

24   repaired for the three 2004 hurricanes for the entire T&D

25   infrastructure.  I don't want to necessarily highlight or go

FLORIDA PUBLIC SERVICE COMMISSION

137

1   through the entire list, but there are a couple that I would

2   like to highlight for everyone here today.

3             First is in terms of distribution poles.  Just over

4   10,000 poles out of the one million that we have in our service

5   territory were replaced through all three hurricanes in the '04

6   season.  This represents about one percent of the million poles

7   that we have in our pole population.

8             Our analysis after the hurricanes determined that the

9   majority of these poles broke due to falling trees and flying

10   debris, certainly a significant factor.  Keep in mind that

11   these three hurricanes did have limited storm surge.  In

12   essence, these were hurricanes that certainly had high winds,

13   but at least our service territory did not see the typical

14   impacts that you may have involving storm surge.  I believe one

15   of the IOUs later today may be able to share a different

16   experience that they had in terms of storm surge on their

17   electrical grid.

18             For our transmission system, less than one percent of

19   the over 68,000 structures replaced were replaced during all

20   three hurricanes, with less than .1 percent of these structures

21   being replaced at any one storm.  Although, as you can see on

22   this slide there was some substation equipment that was

23   replaced, none of the substations were damaged to the extent

24   that they were inoperable for the storms.

25             As has always been the practice at FPL, after the

FLORIDA PUBLIC SERVICE COMMISSION

138

1   2004 hurricane season we conducted a thorough lessons learned

2   assessment to not only identify what we did well, but more

3   importantly what lessons and what things we needed to do to

4   improve on our performance moving forward.  To help us with

5   this effort, we hired a third-party consultant to assist in

6   evaluating our system performance as well as our restoration

7   processes.  A copy of their report that they completed again

8   has been provided to staff as part of our advance responses to

9   the questions that you had asked.

10             Some of their key findings, though, were that FPL met

11   or exceeded standard utility restoration practices.  FPL's

12   distribution, transmission, and substation facilities performed

13   well, and their comment, concluding comment was that they

14   believed that no other North American-based utility that they

15   were familiar with had restoration plans and practices in place

16   that could have successfully restored customers in a six-week

17   time frame after three major back-to-back disasters.

18             They did provide recommendations in terms of

19   opportunity for improvement, which several have been

20   implemented in time for this past 2005 season.  Some of the key

21   ones are listed here.  Specifically, certainly communicating

22   with our customers in terms of estimated time of restoration,

23   providing them better information at a lower level in terms of

24   when they can expect to have their service restored.

25             Secondly, establishing a better partnership with the

FLORIDA PUBLIC SERVICE COMMISSION

139

1   local EOCs to identify the critical infrastructure that is key

2   to bringing up on the front end of these hurricanes to get the

3   communities back up and running.

4             Lastly, was certainly a key one, which was to

5   establish partnerships in terms of resources.  You heard

6   earlier today from a representative from EEI the criticalness

7   of mutual aid assistance.  This was a key enhancement to

8   continue to leverage those alliances with other utilities.

9             In addition to the third-party consultant review, we

10   also conducted our own internal reviews.  For distribution,

11   although we believe we had good data after the '04 season, we

12   recognized that there was an opportunity to obtain even better

13   data.  So one of the key learnings that we had was the

14   development of what we called forensic teams, which were, in

15   essence, our product engineers being able to go out immediately

16   after a storm has passed, when it's safe, to gather firsthand

17   information on the ground, if you will.  And you will see later

18   where that has been a critical feed to our analysis after the

19   '05 season.

20             For our transmission and substation system, there

21   have been several initiatives that are or have been

22   implemented.  Again, several of those details have been

23   provided in advance to the responses to the questions that were

24   asked by Staff.  It's important to emphasize that these parts

25   of our transmission systems that did have activities completed

FLORIDA PUBLIC SERVICE COMMISSION

140

1   after the '04 season actually performed quite well for the '05

2   storm season.

3             In 2005, there were four hurricanes that actually

4   impacted our service territory, two with the outer bands

5   sweeping across our service territory, which were Dennis and

6   Rita, and certainly having an impact on our customers, and then

7   two direct hits.

8             On the evening of August 25th, Hurricane Katrina made

9   landfall near the Broward/Miami-Dade line.  It made landfall

10   with hurricane force winds of 80 miles an hour which intended

11   over most of Southern Florida, which happens to be our most

12   densely and highest populated areas.  Tropical storm force

13   winds extended out 160 miles.

14             Hurricane Wilma, which became a hurricane on October

15   18th, grew in strength to a Category 5 on October 19th,

16   registering the lowest central pressure ever, and therefore the

17   most powerful hurricane on record in the Atlantic basin.  It

18   made landfall on the southwest coast of Florida near

19   Marco Island on October 24th as a strong Category 3.  It

20   crossed the state quickly and exited just north of Palm Beach

21   as a Category 2 hurricane.  Hurricane force winds again

22   extended out 125 miles from the center and tropical storm force

23   winds out over 200 miles.

24             In addition to impacting our customers on the west

25   coast, Wilma also impacted our customers in the tri-county

FLORIDA PUBLIC SERVICE COMMISSION

141

1   area, Palm Beach, Broward, Miami-Dade.  Although Hurricane

2   Wilma was not the strongest hurricane ever to hit our service

3   territory, I believe many of us believe it was certainly one of

4   the most challenging to provide restoration to our customers.

5             Again, in our written responses we have provided the

6   equipment that we replaced at a regional or management area for

7   the 2005 season, and here are the cumulative totals.  Again,

8   there are just a couple that I would like to highlight.  The

9   first being that just under 13,000 distribution poles, or again

10   around one percent of our total one million poles were in need

11   of replacement with the cumulative of the hurricanes of 2005.

12   This is both for FPL and non-FPL poles.

13             For our transmission system, no structures needed to

14   be replaced during Hurricane Katrina and those structures that

15   were replaced as a result of Hurricane Wilma were located in

16   the center part of the state near Belle Glade, with the

17   majority of the damage occurring on just a few line sections.

18             Just as in 2004, minimal substation equipment needed

19   to be replaced, however, eight of the substations, or 1.5

20   percent of the total substations were inoperable for a short

21   period of time after Wilma until this equipment could be

22   replaced.

23             Just as we did in 2004, we again have begun an

24   exhaustive and comprehensive lessons learned to really review

25   and understand how we can improve moving forward.  Immediately

FLORIDA PUBLIC SERVICE COMMISSION

142

1   following the restoration effort, we retained an

2   internationally recognized outside consulting firm, KEMA, to

3   perform a review of the FPL facilities after Wilma to better

4   understand if the transmission and distribution systems

5   performed appropriately.

6             Earlier today, just before lunch, you heard from

7   Doctor Richard Brown with KEMA, who led this effort.  The key

8   areas that KEMA evaluated as part of our review are shown here

9   on this slide.  This review is not only covering the

10   infrastructure performance, but it also reviewed our standards

11   and compliance with the NESC, which there has been some

12   discussion this morning about, the quality of the poles that we

13   purchased, our pole maintenance practices, as well as an

14   industry benchmark with other utilities that may be subject to

15   areas of impact from hurricanes.

16             KEMA utilized an extensive amount of data, including

17   the forensics data I highlighted before, to draw their

18   conclusions and issue their final report.  That final report

19   was completed just over a week ago, and we have included it not

20   only as part of our direct testimony in a docketed matter, but

21   also I believe there are copies that have been presented here

22   today, as well.

23             The key finding of the KEMA report was that FPL's

24   transmission, substation, and distribution systems are designed

25   to meet or exceed all safety standard requirements, and during

FLORIDA PUBLIC SERVICE COMMISSION

143

1   Wilma performed as expected and in accordance with FPL's

2   standards.  In fact, they recognized that FPL's distribution

3   standards require poles that are 50 percent stronger than

4   required by the NESC.

5             As I mentioned, the final KEMA report was just

6   completed a week ago, barely two months after we completed

7   restoration efforts for Hurricane Wilma.  We are now in the

8   process of reviewing those findings.  More importantly, we are

9   now in the process of what we consider entering the next phase,

10   and that next phase is about further exploration to harden our

11   infrastructure.

12             As I showed you earlier before, the system

13   performance after the '04 and '05 hurricane seasons, both of

14   which were unprecedented, recognize or showed that our system

15   performed well.  But as we have been saying here today, if

16   indeed the weather has changed, so must we.

17             We are currently in the process of now working with

18   KEMA to provide assistance in developing what we are calling a

19   hardening road map.  And what this is really about is to what

20   extent do we want to harden the system, where we are now, and

21   the steps that we must take to get there.  There has been some

22   talk this morning that, you know, there is no silver bullet.

23   It would be great to have one.

24             However, we do believe that there are opportunities

25   that we must explore.  We must keep in mind that although there

FLORIDA PUBLIC SERVICE COMMISSION

144

1   is no single answer, that we must evaluate several items, some

2   of which Doctor Brown mentioned, many of which are listed here,

3   as just examples of areas that we must explore.  In essence, we

4   have to take the probabilistic benefit of what some of these

5   items may do and certainly evaluate that against the cost.

6   Additionally, this will be a long process.  I think this

7   morning it was highlighted, we certainly through this process

8   need to determine what we can do in the short-term and then

9   what we can do in the long-term, and we support that approach.

10             FPL believes this is the right thing to do.  If

11   indeed, again, we are entering a period of heightened hurricane

12   activity, we must take a fresh look at these ideas.  We at FPL

13   assure you that we will continue to support these efforts and

14   we will share our plans as we continue to develop them in the

15   coming weeks and months.

16             That concludes my formal presentation.

17             MS. HELTON:  Mr. Spoor, I think that we have some

18   questions for you.

19             Mr. Trapp.

20             MR. TRAPP:  Mr. Spoor, I'm Bob Trapp of the Economic

21   Regulation Section.  I just have a few questions I would like

22   to direct your way, if I could.

23             MR. SPOOR:  Certainly.

24             MR. TRAPP:  Staff has looked at residential rates

25   being charged by Florida Power and Light, and we note that the

FLORIDA PUBLIC SERVICE COMMISSION

145

1   transmission component in the residential rates is roughly 4.3

2   percent total rates.  We notice that distribution is about 15.8

3   percent total rates, so together we are only talking about 20

4   percent of the bill being represented by transmission and

5   distribution costs to the typical residential customer.  So

6   that means that 80 percent of the system cost is going into

7   power plants and fuels for those power plants.  Can you give me

8   some assurance or some feel that because you are only

9   20 percent of the dog, that you are giving the appropriate wag?

10             MR. SPOOR:  Sure.  I think that is a fair question.

11   And certainly I don't mean to stand up here and understand

12   everything about our rate structures, I will certainly leave

13   that to our rate structure department.  In terms of investment,

14   though, as we have stated before, we have been investing in our

15   system.  Certainly I think since 1998 we have invested over one

16   billion dollars alone in just the distribution infrastructure.

17   So we believe we are making the appropriate investments for the

18   world that we have lived in in terms of normal reliability.

19             Now, again, certainly as I mentioned, with the

20   weather changing, as it has changed we acknowledge that we must

21   take a fresh look in terms of what we are doing to our system.

22   So I recognize certainly that, you know, and certainly when we

23   develop our plans in the coming weeks and months, that we will

24   be looking at all avenues in terms of what we are currently

25   doing and then just certainly as important what we need to do

FLORIDA PUBLIC SERVICE COMMISSION

146

1   in the future.

2             MR. TRAPP:  What about maintenance costs, have they

3   been on the increase?  Have your budgets reflected increased

4   commitment to maintenance in the field for distribution in

5   particular, and also transmission?

6             MR. SPOOR:  I can't speak for the transmission side,

7   but certainly in distribution.  In fact, I know just this year

8   alone our vegetation budgets, I believe, are increasing in the

9   magnitude of 20 percent over what they were even last year,

10   which has already been increasing.  So, in terms of investing

11   in our infrastructure, we certainly have been investing

12   dollars, yes, sir.

13             MR. TRAPP:  But how long has that commitment taken

14   place?  Has it just been the last two years as a result of

15   these hurricanes, or how does it compare to budgets ten years

16   ago?  Are we keeping up with at least inflation?

17             MR. SPOOR:  Well, again, I can't speak for some of

18   the funding levels ten years ago, but I can tell you dating

19   back as far as 1998 when we made a concerted effort to improve

20   our reliability, centralizing our efforts, and certainly doing

21   a more targeted approach in terms of how we can best spend our

22   money to get the biggest bang for our buck on our system, I can

23   tell you each and every year I believe those level of

24   investments have certainly been to a level that, again, as you

25   look at our performance, has certainly helped in our

FLORIDA PUBLIC SERVICE COMMISSION

147

1   estimations.

2             Again, that is not to say moving forward do we need

3   to explore other opportunities, I think my opening comments, as

4   I said, I think we certainly welcome the opportunity to work

5   with staff to understand if, indeed, there are things we can

6   do, again, to get the biggest bang for our buck.

7             MR. TRAPP:  In terms of some of the speakers this

8   morning, we heard from -- let me look at my agenda.  We heard

9   from Mayor Castro of Dania Beach, who offered what sounded to

10   me like good business practice feedback from the local

11   community that you serve.  Some actual input from your

12   customers and the opportunity to work one-on-one with them to

13   pre-identify such things as vegetation management, discuss

14   openly undergrounding, hardening issues, and things of that

15   nature, and she indicated that she had put a proposal forward

16   to Florida Power and Light.  Are you familiar with that

17   proposal?

18             MR. SPOOR:  I'm personally not familiar with that

19   proposal, but I can tell you when she was talking I was taking

20   notes.  And I'm sure if I don't reach out to her quickly,

21   somebody from FPL, if they haven't already, certainly will.  I

22   concur.  I think she had some great ideas in terms of working

23   with the local communities in that area.

24             MR. TRAPP:  In addition to the community of Dania

25   Beach, could I ask you to look more globally up and down your

FLORIDA PUBLIC SERVICE COMMISSION

148

1   east and west coast and perhaps look at the concept of better

2   coordination/cooperation and get some input from those people?

3             MR. SPOOR:  Certainly.  I know other communities that

4   we are certainly engaged in conversation with and wanting to be

5   great working partners with them to ultimately improve things

6   moving forward.

7             MR. TRAPP:  We also heard from the universities, and

8   there seems to be a lot more than I thought was going on in

9   terms of data collection with respect to coastal and inland

10   wind speeds and the effects on structures within the state.

11   What is Florida Power and Light doing in the area of working

12   with the educational community?

13             MR. SPOOR:  Well, I believe Doctor Domijan from the

14   University of South Florida highlighted a project that we have

15   been engaged with them.  It is really a research and

16   development program.  To date, that has really kind of taken a

17   look at weather in terms of what it means to our day in/day out

18   reliability.  Certainly, a question that can be asked is can

19   that be expanded to times of hurricanes?  And although I don't

20   know if the definitive answer is yes, it is certainly an area

21   of exploration.

22             MR. TRAPP:  I think Doctor Gurley outlined a program

23   that he is doing primarily in conjunction with the Department

24   of Community Affairs that is testing the impact of wind speeds

25   on building codes within Florida, and it just occurred to me

FLORIDA PUBLIC SERVICE COMMISSION

149

1   that if the University of Florida can do wind tunnel tests on

2   models of residential homes, why can't they do the same thing

3   for poles and lines.  Have you explored that?

4             MR. SPOOR:  We have not explored that particular

5   option.  But certainly, again, it was a very compelling

6   presentation and certainly an area of exploration.

7             MR. TRAPP:  I know that there are certain rivalries

8   that occur within the colleges within the Florida system, but

9   it seems even the University of Miami might have something to

10   offer in terms of --

11             MR. SPOOR:  We actually do have -- in addition, as

12   Doctor Domijan had highlighted, even when he was at UF we were

13   still working on the project with them, and now he has moved to

14   the University of South Florida.  We actually even have another

15   program that -- again, not necessarily related to hurricanes,

16   but in terms of weather, with FSU.  So we do certainly try to

17   support and work with the local talent that we have in our

18   universities across the state.

19             MR. TRAPP:  I think my staff has probably more

20   in-depth reaching questions, but I had just a couple overall,

21   and I think Connie wants to ask one before I turn it over to

22   staff, or before Mary Anne turns it over, Madam Chair.

23             I am a little concerned -- I want to ease my mind --

24   of are we just focusing on what has occurred in the last two

25   years because of the hurricanes, or are we constantly aware of

FLORIDA PUBLIC SERVICE COMMISSION

150

1   the problems of reliability, and concerns, and impact of

2   reliability on the citizens of Florida?  And I wondered if you

3   could speak briefly on what that does Power and Light really do

4   in terms of being out there, looking at issues such as how do

5   you inspect your poles on a normal routine basis, how do you

6   inspect your lines on a routine normal basis, how do you

7   address vegetation issues?  Could you give me just kind of a

8   brief overview of what is normal before we talk about what

9   maybe we need to react in terms of extra normal for hurricanes?

10             MR. SPOOR:  Normal in terms of -- I mean, I guess if

11   I understand your question correctly, you know, it is part of

12   our annual reliability plans.  They are made up of several

13   components that we believe touch our infrastructure in terms of

14   the conductors, the vegetation.  Again, we do not have just one

15   program that would address one part of our system.  It is

16   really a portfolio of reliability initiatives that we have been

17   deploying, executing, tracking for several years now.

18             So in terms of what we are doing for reliability, I

19   do believe we have those types of programs.  I don't know if

20   there is one specific that you would like me to respond to, but

21   I guess my comment is, again, it is not just one specific

22   reliability initiative that we have.  We believe we have a

23   fairly robust portfolio, if you will, of reliability

24   initiatives not only dealing with our overhead infrastructure,

25   but also our underground infrastructure.  We invest a lot

FLORIDA PUBLIC SERVICE COMMISSION

151

1   annually on maintaining our underground infrastructure in terms

2   of replacing aged cable, injecting aged cable, so there are

3   several things that we do, we believe, to touch our

4   infrastructure.

5             MS. KUMMER:  This is Connie Kummer with the

6   Commission staff.  There are just a couple of points I wanted

7   to raise.  You made the statement several times that FPL had

8   met the standards.  We heard this morning that as a

9   non-engineer, to me it sounded like standards are really kind

10   of a moving target.  We heard that loading on the poles makes a

11   difference, weather makes a difference, combination of things.

12   When you say "meet standards," are you looking at something

13   other than just the bare pole sitting out there when you

14   evaluate whether you meet the standards?

15             MR. SPOOR:  It is a good question.  When I reference

16   or make a comment in terms of meeting standards that is as we

17   build our system.  So that would be including those

18   attachments, the equipment we may hang on the poles in terms of

19   are we meeting the standards end state, or once everything is

20   built, if you will.

21             MS. KUMMER:  And given that we still are having some

22   problems, have you looked at whether or not the standards ought

23   to be changed, ought to be increased?  I note that you said

24   some of them are built to 50 percent greater.  Have you

25   explored that as a possibility?

FLORIDA PUBLIC SERVICE COMMISSION

152

1             MR. SPOOR:  We certainly believe that, again,

2   although there is no silver bullet, I think it is an area that

3   we will look at.  You know, I think part of what we are

4   concerned with, that it is not going to be just about a design

5   change, though.  Certainly, and, again, I welcome the comments

6   from some of the community leaders today, specifically the

7   Mayor of Dania Beach.  It is about how our system coincides, if

8   you will, with vegetation management in their communities.

9             Although putting stronger poles in, more poles,

10   shorter spans could ultimately be some of the solutions or part

11   of the things that we could consider to harden the system, we

12   also must recognize that, you know, a robust vegetation

13   management program, and that is not just necessarily the

14   utility trimming more trees, but it is certainly promoting our

15   right tree/right place, making sure that, again, both the

16   standards and where we build our system in terms of vegetation

17   that they both can coexist.

18             MS. KUMMER:  And the last question.  You mentioned on

19   your last slide, I think, that you are working to develop a

20   road map.  Do you have a timetable when you expect that to be

21   in some kind of concrete form?

22             MR. SPOOR:  We have not mapped out the time frame.  I

23   know that we are -- just as we did with the final KEMA report

24   that just came out, we are fast-tracking that as quickly as

25   possible.  I think all of the IOUs recognize that June 1 is

FLORIDA PUBLIC SERVICE COMMISSION

153

1   right around the corner.  So in terms of things that we may be

2   able to do this year and things we may be able to do longer

3   term, we recognize it is of an urgent nature.

4             MS. HELTON:  Bill, did you have --

5             MR. McNULTY:  Yes, I believe both myself and Jim

6   Breman from staff have questions.  And there may be additional

7   questions, as well.

8             MS. HELTON:  And I want to remind the audience, if

9   you have any questions, if you would please put them on the

10   index cards so that Staff can ask them.

11             MR. McNULTY:  Good afternoon, Mr. Spoor.  I have just

12   a few questions.

13             One of them has to do with the response to a data

14   requests that went out related to this workshop, and I think

15   the very first question is actually covered in your

16   presentation, which is the damages that were done and the

17   various facilities that were replaced as a result of the

18   storms.

19             And I guess a general question I would have is that

20   is all good information to have.  We see that it looks like the

21   preponderance of the data would indicate that distribution was

22   the larger infrastructure hit, but that transmission had an

23   important part of the storms, the recent storms, at least for

24   2005, and I'm sure for 2004, as well.

25             I guess my basic question is to what extent does data

FLORIDA PUBLIC SERVICE COMMISSION

154

1   exist to be able to look at the time frames for the

2   restorations of the different types of components.  For

3   instance, you had major transmission structures that were down,

4   and you had to restore those, and the priority listing as we

5   know from your data responses says that you have to get your

6   transmission up first and then you have to move down the line.

7   I'm wondering if there is a possibility of data that the

8   utilities have, and FPL in this case has that would say we can

9   create a Gantt chart, some sort of a schedule that would show

10   how long it took to get transmission back up and running, how

11   long it took to get, you know, transmission substations, and

12   then all the way down the line, all the way to the service

13   drops to see if there is a blockage there.  Some sort of

14   bottleneck that says, you know, we have these thousands of

15   people from around the country that are in our service

16   territory working right now and our real bottleneck is this.

17             First of all, I want to kind of get a sense,

18   generally, if you know if there is a bottleneck?  And then,

19   secondly, what kind of data would there be to support reviewing

20   that type of analysis?

21             MR. SPOOR:  Yes.  In terms of whether there is a

22   bottleneck or not, I'm not aware of any that exists in terms of

23   the restoration process.  In terms of whether that data exists,

24   it is something we would just have to take a look at.  I mean,

25   certainly the way we approach these storms in terms of

FLORIDA PUBLIC SERVICE COMMISSION

155

1   restoration priorities, first and foremost our strategy is to

2   certainly get the generation and transmission systems back up

3   first and foremost, and then certainly working down to the

4   lower level devices.

5             You know, it has always been about restoring power to

6   the critical infrastructure in parallel to restoring power to

7   the parts of our system that can restore power to the most

8   amount of customers in the quickest and safest way.  So it's

9   certainly something we would have to look at in terms of data

10   availability.

11             MR. McNULTY:  And the reason I mention that is

12   because then that could help us focus on the type of equipment

13   that we would need to find the solutions for.  Again, we have

14   heard the sentiment several times today there is no silver

15   bullet, but there certainly has to be areas to focus on.  The

16   obvious thing that the eye is attracted to is 10,000 poles

17   down.  But I'm wondering if there might be something to be

18   learned from if you have inventory data that says on day one

19   after the storm X number of transmission poles went out and

20   were replaced, and day two, and so forth, and so you can look

21   at and see on a day-by-day basis.  That would be a data need

22   that I think that staff would like to review for the purposes

23   of seeing is there a bottleneck and how can we, you know, move

24   on from there to learn more about that bottleneck if there is

25   one.

FLORIDA PUBLIC SERVICE COMMISSION

156

1             MR. SPOOR:  Yes.  I guess I would -- and certainly it

2   is something we can look into.  Again, the term bottleneck, I

3   think, you know, our restoration plans, we certainly have

4   effectively been able to apply the resources, all of these

5   resources, as you mentioned, from around the country as they

6   come in to make them the most productive work force possible to

7   restore power to our customers.

8             MR. McNULTY:  Right.  And, of course, the idea being

9   that if it is replaced in a nonstorm sort of environment, the

10   costs for that go down.  And, of course, then you also avoid

11   the outages, and that is the obvious concern there.

12             I think we heard a couple of times this morning, I

13   think Commissioner Falcone, and then expressed again by Schef

14   Wright the concern about, you know, what really affects the

15   reliability of the system, is it most distribution or

16   transmission, and that sort of thing.  And I wondered if FPL

17   had done any studies on that?

18             MR. SPOOR:  Studies in terms of, I'm sorry?

19             MR. McNULTY:  There was the question about

20   reliability, the impacts of reliability versus the

21   transmission, versus the distribution segments; and

22   undergrounding, the undergrounding versus

23   transmission/distribution, and which one of those affects

24   reliability more.  He said that he could find no information on

25   the reliability issues there.  I was wondering if you had any

FLORIDA PUBLIC SERVICE COMMISSION

157

1   information to share on that.

2             MR. SPOOR:  Well, one of the difficulties, I think,

3   and, again, we continue to try to do that analysis in terms of

4   reliability differences, if they may exist, between overhead

5   and underground.  And part of that challenge is certainly you

6   first have to define, you know, what is underground versus what

7   is overhead.  I believe there was a slide from Doctor Brown

8   just before lunch that mapped out, you know, certainly you can

9   have parts of your system overhead, parts of your system

10   underground.  You may have underground service in your

11   subdivision, but the lines that are feeding into those

12   subdivisions may be overhead.  So to delineate, to say what

13   part of the system that is overhead, how is that performing

14   versus underground, we have not completed that analysis to be

15   able to say conclusively what that is telling us.

16             Again, a lot of that has to do with the hybridness,

17   if you will, of our system in that you may have an overhead

18   feed and you may also have part of the system that's ultimately

19   getting all the way down to your meter as underground.

20             MR. McNULTY:  Is there a way to study the system such

21   that there may be pure overhead, pure underground and make

22   comparisons of those two different scenarios?

23             MR. SPOOR:  We certainly would have to take a look at

24   that, if indeed those pure examples, as you highlighted, exist.

25             MR. McNULTY:  Okay.  Additionally this morning we

FLORIDA PUBLIC SERVICE COMMISSION

158

1   heard from Homac manufacturing and their idea about breakaway

2   connectors.  And I wondered at that time, you know, to what

3   extent FPL had analyzed those.  It seemed like another example

4   of where is the bottleneck.  There must have been thousands of

5   service drops that had to be replaced.  How important is that

6   type of technology a solution for the two concerns that we are

7   here for today, which is storm costs and storm restoration

8   time?

9             MR. SPOOR:  Well, that particular prototype we have

10   not been engaged actively with Homac.  Of course we do do a lot

11   of business with Homac, as they highlighted in terms of

12   connectors.  It is certainly one that I think we need to

13   consider, again, in terms of new materials.  I believe part of

14   anything we do moving forward, hardening can certainly be

15   defined as mitigating the impacts that a hurricane may have.

16   And certainly that, to me, was an example of a mitigating type

17   of strategy.

18             In essence, you may not necessarily be able to

19   prevent entirely what the hurricanes are going to do to your

20   system, but, in essence, if you can mitigate the damage that

21   they are causing to that with this breakaway connector that he

22   talked about, it is certainly something that I think we would

23   be open to look at as a possible solution.

24             MR. McNULTY:  An additional question I had is on your

25   wood pole databases.  I understand that the company is in the

FLORIDA PUBLIC SERVICE COMMISSION

159

1   process of developing a database that will eventually

2   incorporate the salient data such as vintage and pole type and

3   so forth throughout their service territory, and we are talking

4   about over a million poles, is that right?

5             MR. SPOOR:  Yes.

6             MR. McNULTY:  Is it on the table, and would it be --

7   in consideration of the storms of the last few years, would it

8   be advisable that instead of kind of developing this over an

9   eight or ten-year period, would it be advisable to expedite a

10   pole database?

11             MR. SPOOR:  Well, again, I think as we look at

12   ultimately what are some of the solutions or options that we

13   have to explore, I believe that we will take a look at

14   everything.  That may be one of them, as well.  I don't think

15   we have made a decision yet.  Like I said, we are really right

16   now -- we have just recently got the KEMA report in terms of

17   how the system performed.  We are obviously quickly moving

18   toward the next phase, which is understanding what we need to

19   do moving forward.

20             MR. McNULTY:  I would like to speak for a moment

21   about the third-party poles.  And I think the KEMA report said

22   that FPL doesn't have a method today of tracking actions of

23   third parties once the third party has informed FPL that one of

24   their poles requires replacement, bracing, or treatment.  I

25   think that was a general statement at some point, a key

FLORIDA PUBLIC SERVICE COMMISSION

160

1   finding.  Is that something that needs to be addressed as well

2   in this process?  I mean, does FPL need to start looking at

3   third-party arrangements with the third-party providers, and

4   whether or not they do a follow-through of their pole

5   population that is affecting electric service?

6             MR. SPOOR:  Again, I believe that would be one of

7   those areas, again, that are certainly worthy of further

8   exploration in terms of what we can do with that moving

9   forward.

10             MR. McNULTY:  I think you just a little while ago

11   mentioned a 20 percent increase in the tree-trimming budget for

12   the coming year, and that that follows upon previous increases.

13   Do you have an idea how that will best be spent in terms of is

14   it doing more of the same, or are you going to fundamentally

15   change the type of tree trimming that you are doing?

16             And by that I mean, for instance, if today you are

17   doing tunneling whereby overhanging branches are allowed to

18   remain, is there something different that is in your sights

19   today for becoming more -- having a more robust system?

20             MR. SPOOR:  Yes.  That particular one I can't respond

21   to in terms of are we changing our vegetation trimming

22   techniques, if that is what the question is.

23             MR. McNULTY:  Yes.

24             MR. SPOOR:  I would certainly have to get back with

25   you on that one and have to defer that one to our vegetation

FLORIDA PUBLIC SERVICE COMMISSION

161

1   management group that are the arborists and kind of the experts

2   in that field.

3             MR. McNULTY:  Well, just in your general sense of it,

4   is there -- you looked at, and I think it was mentioned in the

5   KEMA report that trees are a very big factor and that

6   vegetation is a very big factor.  Do the utilities need to be

7   more aggressive in Florida in tree trimming, I mean, in the

8   sense of looking at those options?  I mean, I know you are

9   looking at them now, but there has to be some sort of

10   consensus, I'm sure, built within the company.  But is that

11   something that needs to be looked at not just in terms of the

12   cycle, but in terms of whatever that standard is for line

13   clearances, you know, given today's standard versus where we

14   need to be?

15             MR. SPOOR:  Well, again, I think that is one of those

16   areas that, you know, we would probably consider almost a

17   shared responsibility in that, you know, in terms of what we

18   spend or what trees we trim, how many miles we may clear.

19   Certainly those instances where, you know, communities may have

20   challenges in terms of where trees are planted, what types and

21   species of trees are planted in relationship to proximity of

22   our facilities, you know, I believe that whole area certainly

23   needs a little bit more analysis to determine.  I don't think

24   it is just about spending more money on vegetation.  I

25   certainly believe it is certainly one of kind of a shared

FLORIDA PUBLIC SERVICE COMMISSION

162

1   responsibility to understand what we can do to work with our

2   communities to better understand that.

3             MR. TRAPP:  Could I interject here just a second,

4   Bill, and ask do I understand that Florida Power and Light's

5   current tree-trimming policy is confined only to road

6   right-of-way easement?

7             MR. SPOOR:  When you say road --

8             MR. TRAPP:  Road right-of-way easement areas are the

9   only areas that you feel responsible for?

10             MR. SPOOR:  No, I believe part of our vegetation

11   program is trimming trees that are in close proximity to our

12   facilities, which is not just in road right-of-way.

13             MR. TRAPP:  What is your policy with respect to

14   responding to community or individual customer concerns about

15   trees on their property that may affect their service drop?

16             MR. SPOOR:  I believe that policy right now is

17   certainly reviewed by an arborist that actually goes out to the

18   site to evaluate the criticality of that and whether a crew has

19   to be dispatched right then or if it is incorporated into some

20   type of cycle we may be trimming on.  I believe that is how

21   those are addressed.

22             MR. TRAPP:  How many of the extended outages, the

23   longer outages that occurred during the last two years

24   hurricanes were associated with individual laterals versus --

25   excuse me, individual service drops as opposed to laterals or

FLORIDA PUBLIC SERVICE COMMISSION

163

1   primaries or long lines?  I mean, do you have a lot of

2   customers that are left over without power because they had

3   vegetation problems on their property?

4             MR. SPOOR:  I don't have that data to be able to know

5   if that's true or not.

6             MR. TRAPP:  Do you have an aggressive educational

7   program that you send out as bill-stuffers, for instance, to

8   your consumers saying how important it is to keep vegetation

9   away from their facilities?

10             MR. SPOOR:  Absolutely.  In fact, again, I referenced

11   it as kind of our right tree/right place campaign that we have.

12   We aggressively market to all of our customers in terms of

13   making sure that they are not planting trees, or more

14   specifically certain tree species in close proximity to our

15   lines that ultimately may cause some issues as the trees begin

16   to mature and grow.

17             MR. TRAPP:  And if you spent like another million

18   dollars on that program, would it significantly affect the 15

19   percent of the bill that's distribution now?

20             MR. SPOOR:  That I don't know.

21             MR. TRAPP:  It would come out of the existing

22   revenues, wouldn't it?

23             MR. SPOOR:  I'm not sure how we would pay for those

24   campaigns.

25             MR. TRAPP:  It would affect stockholders right now,

FLORIDA PUBLIC SERVICE COMMISSION

164

1   unless you came in for a rate case, is what I'm getting at.  Is

2   that not true?

3             MR. SPOOR:  Again, I'm more of a technical person.

4   In terms of how we would pay for those campaigns, I'm not quite

5   sure how we do that.

6             MR. TRAPP:  Thank you.

7             MR. SPOOR:  You're welcome.

8             MS. HELTON:  Mr. Breman, did you have some questions?

9             MR. BREMAN:  One or two.  I've read some of the other

10   companies' responses.  Progress, they decided in 2001 they are

11   going to get rid of all of their transmission -- wooden

12   transmission poles, especially their H-frame wood transmission

13   poles.  Last year after some of the storms, I took the liberty,

14   or was told to, drive down and explore some areas in the

15   Treasure Coast area of FPL.  And there is a lot of H-frame

16   construction on the transmission over there still, and some of

17   it was pretty patched together.  My words, not technical.  It

18   probably meets code and all of that.

19             I also took the liberty of looking through FPL's 1993

20   report post-Andrew, and it said FPL was reconsidering its use

21   of wooden H-frame pole construction.  So it seems to me that

22   adding two and two together suggests that FPL should be not

23   only mitigating away about not putting any new H-frames in, but

24   also replacing the old ones.  So where are we on that?

25             MR. SPOOR:  That particular question, if I can, I

FLORIDA PUBLIC SERVICE COMMISSION

165

1   will probably defer to Mike Warr, who is in our transmission

2   group.

3             MR. WARR:  With regards to wood H-frames on our

4   transmission system, we no longer do that.  It's not part of

5   our standard.  Our standards now are, for the lower voltage,

6   typically made up of round spun concrete pole with polymer post

7   insulators.  I recall the last sparwood H-frame line that we

8   installed was somewhere in the '80s, early '80s.

9             With regard to maintenance, whether we do

10   maintenance, relocations, new projects, we try and bring them

11   up to our current standards, which are round spun concrete

12   poles with polymer post insulators.

13             MR. BREMAN:  Also, probably a transmission-related

14   question, but it might also fit distribution.  Earlier today we

15   heard some comments about wind giving a good shake to the

16   infrastructure.  Also, in the KEMA report, if you read through,

17   one of the paragraphs talks about finding loose bolts, nuts,

18   some of them missing, probably due to the shaking and the

19   vibration that occurs when winds impact the facilities.  On

20   distribution it would be more related to the cross-arm

21   structures, whether they are bolted or whatever.

22             In the post-storm sweeps, how thorough are the

23   sweeps?  Do you all check for loose nuts and bolts like that?

24   Do you climb the poles that are in the hurricane wind areas?

25             MR. SPOOR:  For distribution, our post-sweep

FLORIDA PUBLIC SERVICE COMMISSION

166

1   assessments do not include climbing the poles.  It is certainly

2   more --

3             MR. BREMAN:  Well, you could use a bucket.

4             MR. SPOOR:  I'm sorry?

5             MR. BREMAN:  You could use a bucket.

6             MR. SPOOR:  We could use a bucket.  But really the

7   post-sweeps that we do are more about visually inspecting any

8   impacted areas items that certainly were caused by the

9   hurricane.  In terms of whether we climb each distribution pole

10   or use a bucket to check, you know, all of the hardware, it is

11   more of a visual inspection just because mainly of the scope of

12   the work that we have to do, and certainly things that -- and

13   we believe we do a pretty good job of visually inspecting those

14   types of damage that may still be out there as a result of the

15   hurricane.

16             MS. KUMMER:  Jim, if I could jump in just as a

17   follow-up.  What do you look for?  You do a visual inspection

18   for what?

19             MR. SPOOR:  Certainly poles that may be severely

20   leaning still, as an example, from the hurricanes.  Certainly

21   if there is dangered timber in that a tree was on the brink of

22   falling but has not fallen.  Those are probably two of the more

23   obvious ones that we would do as part of our post-sweep

24   assessment in the impacted areas.

25             MR. TRAPP:  On that transmission nuts and bolts

FLORIDA PUBLIC SERVICE COMMISSION

167

1   issue, am I given to understand that the nuts and bolts were

2   tightened to specification, but maybe the specification needs

3   to be revisited?

4             MR. WARR:  For that particular line section, they

5   were installed to industry standard and to the same manner that

6   other 500 kV lines were built.  But for that particular line

7   and than particular line design it wasn't sufficient in order

8   to keep them tight.  As a result of that, you know, FPL is

9   going out now and making sure that we tighten all of that, all

10   the bolts on every structure that is out there.  Additionally,

11   we are trying to look for commonalities with that particular

12   line section to see if they exist with other 500 kV lines that

13   we have on the system.

14             MR. TRAPP:  So in terms of your transmission

15   structures you are going to mechanically tighten as opposed to

16   hand tighten the 500 kV section that was affected, but you are

17   also going out there to check the looseness of any other bolts

18   that are --

19             MR. WARR:  I'm sorry, say that again, please.

20             MR. TRAPP:  In terms of the one 500 kV section that

21   went down, and then you found problems with the specifications

22   for tightening the bolts, you have not only tightened those

23   bolts is what I am hearing you say, but you are going out to

24   all other transmission structures and testing whether or not

25   the current procedures for tightening still apply.  Is that

FLORIDA PUBLIC SERVICE COMMISSION

168

1   what I heard?

2             MR. WARR:  Well, it's two-fold.  One of the things

3   that we are looking at are the commonalities for that

4   particular line section and does it apply for the rest of the

5   500 kV systems.  But additionally, yes, sir, we have hired

6   contractors to go out to the our other 500 kV lines that were

7   not affected during Hurricane Wilma to do inspections on those

8   facilities, as well, too.

9             MR. TRAPP:  What is confusing me is your terminology

10   "the commonality".  What does that mean?  You are looking for

11   similar --

12             MR. WARR:  Something caused the bolts to come loose.

13   And what are those commonalities that caused those bolts to

14   come loose, and do they exist on other 500 kV systems that we

15   have out there?

16             MR. TRAPP:  Okay.

17             MS. HELTON:  Tom, did we have any questions from the

18   audience?

19             MR. BALLINGER:  That, and I've got a couple of my own

20   I'll do first.

21             Do you know either through your own experience or

22   through the KEMA report what the primary cause of damage to the

23   transmission system was?  Was it flying debris, was it snapped

24   insulators, a general feel.

25             MR. WARR:  The majority of the damage that occurred

FLORIDA PUBLIC SERVICE COMMISSION

169

1   on the transmission system, I think we had a total of 100

2   structures that were impacted because of Hurricane Wilma, 65 of

3   those were single wooden poles.  We had very little damage or

4   impact to wooden H-frames.  The commonality between those

5   single wooden poles, they were confined, I think, to either

6   three or four transmission line sections, and they all had

7   similar profiles.  Most were located in flat open terrain and

8   had some type of elevation berm in close proximity to it.

9             MR. SPOOR:  I believe it is worth pointing out,

10   though, that I believe the KEMA report concluded that the

11   damage to the transmission structures did meet the standard at

12   the time that those structures were built, correct?

13             MR. WARR:  (Indicating yes.)

14             MR. BALLINGER:  And what is your typical inspection

15   and maintenance on your transmission system?  If you want to do

16   it by voltage level, that's fine, or if it varies?

17             MR. WARR:  It varies.  We are continuously doing

18   inspections.  We have primarily three methods of inspections.

19   The ones that we gauge everything off of is climbing

20   inspections, which is putting somebody on the structures and

21   physically climbing and sounding and looking and testing.  And

22   it is from substation pull off to substation pull offs and all

23   points in between, and it is on some type of cycle, either a

24   three-year, four-year, or eight-year cycle.  And the cycle is

25   consistent or is determined by several factors:  The number of

FLORIDA PUBLIC SERVICE COMMISSION

170

1   components that are involved, the importance of the line

2   section to the system, the last time it was inspected.  There

3   is a whole variety of components that go into determining what

4   frequency of cycle it is on.

5             There are other inspections that we do.  We do ground

6   inspections.  Contingency patrols, if we are taking out one

7   section what is going on with the other sections.  We do

8   vegetation patrols twice a year.  And then we do special

9   patrols, or special assessments for problems or challenges that

10   we have known or are considering.

11             MR. BALLINGER:  Back to these single wooden

12   transmission lines.  I presume they were probably 69 kV, or

13   were they much higher voltages?

14             MR. WARR:  Most of them -- I think all of them were

15   69 kV, yes, sir.

16             MR. BALLINGER:  Okay.  And are they required to have

17   the same, I guess, safety standards as we have for the

18   distribution poles, or what wind speeds are they designed to?

19   Is it any different than distribution, being that they are a

20   single pole construction?

21             MR. WARR:  The structures that came down during

22   Wilma, and actually and Frances and Jeanne, were primarily

23   built -- they were originally built like in the 1960s, and then

24   I think a couple of line sections had been relocated in the

25   1980s.  So I'm not exactly sure what the code was at that time,

FLORIDA PUBLIC SERVICE COMMISSION

171

1   but, no, they would not meet the 60-mile per hour exemption for

2   distribution.  But they would not be to the existing mile per

3   hour that is under the existing code.

4             MR. BALLINGER:  So somewhere in between?

5             MR. WARR:  Possibly, yes, sir.

6             MR. BALLINGER:  During Wilma, Frances, and Jeanne,

7   did you have any equipment supply problems?  Transformers,

8   conductors, insulators, did that ever cause a delay in

9   restoration that you can recall?

10             MR. WARR:  In terms of material and delivery?

11             MR. TRAPP:  Yes.

12             MR. WARR:  No, sir.

13             MR. BALLINGER:  Or labor problems?  Did you have too

14   little labor or too much labor?

15             MR. WARR:  No, sir.  Actually for all Charley,

16   Frances, Jeanne, Katrina, and Wilma, we did it with in-house

17   personnel and on-site contractors for transmission and

18   substation.

19             MR. BALLINGER:  So this is getting to that mutual aid

20   agreement, I guess, that seemed to work fairly well for you all

21   as far as -- I mean, does mutual aid also work for equipment as

22   well as labor?

23             MR. WARR:  Yes, sir.  And we never exhausted our

24   supply of materials.

25             MR. BALLINGER:  Internal with FPL?

FLORIDA PUBLIC SERVICE COMMISSION

172

1             MR. WARR:  Yes, sir, that's correct.

2             MR. SPOOR:  For transmission and distribution we,

3   again, did not have any material issues.

4             MR. BALLINGER:  Okay.  We heard a lot with Wilma of

5   significant damage to substations in this event, much more so

6   than any other storms, which is kind of an isolated thing.  Was

7   that ever a critical path in restoration of getting a

8   substation up, or was there still problems on the distribution

9   side that you had to worry about?

10             MR. WARR:  No, sir.

11             MR. BALLINGER:  So it wasn't a critical path?

12             MR. WARR:  That's correct, sir.

13             MR. BALLINGER:  And what was the primary damage to

14   your substations?  Was it flying debris, was it trees, was it

15   just wind damage to the actual structures?

16             MR. WARR:  I think Mike talked about it earlier, with

17   Wilma we only had eight substations, which is about 1.5 percent

18   of our entire system, that was considered inoperable.  The

19   majority of those were even restored upon arrival to the

20   substation, so most of those it was getting somebody there.  A

21   lot of our substations are built, you know, with redundancy, so

22   there is more than one transformer at a substation.  So as long

23   as one of them is there, you can still pick up service.

24             MR. BALLINGER:  I will jump to the third-party

25   attachments a little bit.  It's a little out of my field, but

FLORIDA PUBLIC SERVICE COMMISSION

173

1   it raised an interesting question.  What is done about contract

2   enforcement?  We have heard a lot about other suppliers, if you

3   will, attaching on your poles, not notifying you, adding

4   additional things where it is changing loading and the utility

5   is not aware of it.  What happens when you do find out about

6   something like this?  Explain to me the contract enforcement,

7   how you go about that.

8             MR. SPOOR:  In terms of if we find somebody attaching

9   to our facilities out in the field?

10             MR. BALLINGER:  Yes.

11             MR. SPOOR:  And, I'm sorry, if --

12             MR. BALLINGER:  If you find out that somebody has

13   attached without your knowledge or they have added on

14   additional equipment and increased the loading, how do you do

15   it with your current enforcement, I guess, with your contracts?

16             MR. SPOOR:  I don't know all the details of that.  I

17   do know we do engage periodically with assessments in the field

18   to determine, if you will, the attachments that we have on our

19   facilities, or for truing up in terms of what we do

20   specifically to address if there is a violation, I don't know

21   that right now.

22             MR. BALLINGER:  Okay.  I have one question from the

23   audience.  Did the KEMA report give you any specific

24   recommendations regarding the number or type of pole

25   inspections that FPL should do in the future?  I haven't read

FLORIDA PUBLIC SERVICE COMMISSION

174

1   the report, I will be honest with you, but did they have any

2   recommendations of what to do in the future either as --

3             MR. SPOOR:  Well, we really are right now still

4   engaged with KEMA to determine what indeed are the

5   recommendations.  Again, the first part of their task was to

6   assess how the system performed specifically to Wilma and did

7   it perform as it should have.  Now that that has been complete,

8   again, we are engaged with them in terms of not only

9   recommendations from lessons learned from Wilma, but certainly

10   moving forward are there things, again, that we can do to

11   harden our system.

12             MR. BALLINGER:  Okay.  So the going forward is going

13   forward, it is in progress?

14             MR. SPOOR:  Absolutely.

15             MR. BALLINGER:  Okay.  Did KEMA attempt to separate

16   any percentage of poles and their failure modes, either rotten

17   base, or tree damage, or debris?  Did they try to do anything

18   like that on the forensic side?

19             MR. SPOOR:  Well, I think on the forensics data they

20   did certainly do, I believe, an exhaustive analysis in terms of

21   certainly trying to get to causes of poles falling.  And I

22   believe that they concluded that the primary cause in terms of

23   why most of the distribution poles fell was because of wind

24   only.

25             MR. BALLINGER:  Okay.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

175

1             MR. BREMAN:  Excuse me, I have one clarifying

2   question.  I was curious about the presentation on collocation

3   issues going undetected.  I was wondering if you could support

4   the 20 percent range that was somewhat discussed this morning

5   by the one of the presenters?

6             MR. SPOOR:  I'm sorry, the first part of that?

7             MR. BREMAN:  The collocations going undetected.

8   Numbers like 20 percent were being talked about.  Do you have a

9   feel for what FPL's numbers are?

10             MR. SPOOR:  I don't.  Today I don't have that

11   information in terms of what that would be specific for FPL.

12             MR. BREMAN:  If it is near 20 percent, is that a

13   significant contributor to failure mode on the poles?

14             MR. SPOOR:  Again, I guess I would have to see how

15   that represents, or how that relates to FPL before I could say

16   whether 20 percent is a significant rate in terms of failure of

17   poles or not.  I can tell in normal performance, you know, I

18   think the KEMA report even highlighted that our pole

19   performance, if you will, is good.  And I don't believe they

20   identified that as a high cause in terms of pole failures that

21   occurred during Wilma.

22             MR. BREMAN:  Thank you.

23             MR. TRAPP:  I'm going to ask Mike Staten to throw up

24   a chart that I think will help with this next set of questions.

25   We can start with that one, Mike.

FLORIDA PUBLIC SERVICE COMMISSION

176

1             We have talked about it some this morning, I think

2   several speakers have touched on it, but I'm given to

3   understand that this is from the National Electric Safety Code,

4   and it classifies Florida as a light wind loading area.

5             MR. SPOOR:  I actually think the -- if I can

6   interrupt, I believe, and not to be well-versed on the National

7   Electric Safety Code, but I believe in terms of heavy, medium,

8   and light, that is in terms of ice loading.

9             MR. TRAPP:  To ice loading?  Good.  We will go to the

10   next slide, then.  This shows what I believe to be the high

11   wind speed criteria that's in the American National Safety

12   Code, and I'm given to understand that Florida does not use

13   this for distribution poles, that we classify our poles that

14   are below 60 feet in height as only basically having to

15   withstand 60 mile-per-hour winds.

16             My question, and I apologize, I haven't been able to

17   look at your presubmitted scatter diagrams where we were trying

18   to attempt to correlate where damage occurred during these

19   hurricanes and try to identify possible zones, and I think you

20   have touched on that, and I want to get this straight.  KEMA is

21   working with Florida Power and Light to identify trouble areas,

22   trouble hot spots I think it has been called today, zones, what

23   have you.

24             My question to you is will that recommendation be

25   along the lines of how close to conforming with these high wind

FLORIDA PUBLIC SERVICE COMMISSION

177

1   speeds should we get to in Florida, and how much will it cost?

2             MR. SPOOR:  Well, again, I think certainly we have

3   not, you know, done that analysis.  That's certainly one avenue

4   that we would at least try to understand in terms of if you

5   were to do this, not only what it would cost, but also what it

6   would gain you.  I think we recognize certainly that whatever

7   we do, we truly want to make sure that it benefits the

8   customers and certainly the residents of Florida.

9             And, again, I think, you know, we recognize, and that

10   is why we really endorse this concept of kind of having a tool

11   kit, if you will, for hardening.  Because it won't, I don't

12   necessarily believe, just be designing or increasing the

13   standard that you build to.  I believe if you do that and you

14   don't address things aggressively, or more aggressively in

15   terms of vegetation management or some of the other things that

16   could bring down those big poles just as easily as they may

17   bring down a smaller pole, I think those are all factors, when

18   you are doing this analysis, that you have to consider.

19             MR. TRAPP:  And I'm glad that you said that, because

20   I agree with you 100 percent.  Don't you have it look at these

21   lines of wind speed and ask yourself what does wind do?  It

22   directly affects the poles, it blows debris, and it fells trees

23   and branches.  Don't you have to correlate with this graph

24   vegetation densities in Florida, population growth and

25   development that produces the debris?

FLORIDA PUBLIC SERVICE COMMISSION

178

1             MR. SPOOR:  Yes, sir.

2             MR. TRAPP:  And don't you also have to correlate with

3   this type of concept flood zones?  Can we see a map also of

4   where the flood zones are so that we can cross-check

5   undergrounding versus overhead.  And when did you say that

6   study was going to be due?

7             MR. SPOOR:  We haven't mapped out a time frame

8   entirely, but I can tell you we are aggressively working

9   towards that next phase.  Again, this KEMA report in terms of

10   performance for Wilma is less than two weeks old, and so we are

11   certainly aggressively moving toward that second phase.  Again,

12   I think all of the IOUs recognize things that we need to do or

13   should at least explore.  You know, we are working aggressively

14   to do that in short order.

15             MR. TRAPP:  And when do you think you will know when?

16   I mean, when do you plan to make the decision when to analyze

17   the study?

18             MR. SPOOR:  Certainly over the next several weeks I

19   think we will be mapping out, kind of, that timeline to say,

20   you know, the tasks that we need or we believe need to be

21   explored and potentially the time it may take to explore those

22   tasks.

23             MR. TRAPP:  I think at the end of this workshop the

24   chair intends to announce that you have one week to submit

25   written comments based on what we have heard today.  What kind

FLORIDA PUBLIC SERVICE COMMISSION

179

1   of -- how far along toward that task will you be within a week?

2             MR. SPOOR:  We will certainly be as far as we can,

3   certainly.

4             MR. TRAPP:  You have been most helpful.  Thank you

5   very much.

6             MR. SPOOR:  You're welcome.

7             MR. McNULTY:  Mr. Spoor, I have just one additional

8   area of inquiry.  I want to ask you a little bit about wood

9   pole inspections.  I know that wood pole inspections were the

10   subject of a staff management audit, and I know that the

11   company provided comments on the audit.  And subsequently Wilma

12   occurred, and I think maybe Katrina may have post-dated that

13   period of the audit.  What I am curious about is I have noted

14   that the USDA rural utility service makes the

15   suggestion/recommendation for Florida that says that pole

16   inspections, wood pole inspections should be on the order of

17   eight to ten years.  And the types of inspections that they are

18   considering adequate in those cases are sound and bore

19   inspections that may include excavation, in fact, if certain

20   types of poles or types of wood are used.

21             I guess it is a two-pronged question.  One is is

22   eight to ten years, is that somewhat of a standard or should be

23   a standard in Florida for wood pole inspections in comportment

24   with what the USDA or US has suggested, and is FPL considering

25   a cycle, a wood pole inspection cycle that would comport with

FLORIDA PUBLIC SERVICE COMMISSION

180

1   that?

2             MR. SPOOR:  I think to answer the first part of your

3   question, I would probably have to defer until I actually see

4   the study to give an educated response in terms of whether I

5   think an eight to ten-year pole cycle is adequate.  I have not

6   seen that study that you reference, so --

7             MR. McNULTY:  It was a bulletin, a 1996 bulletin.

8             MR. SPOOR:  Okay.  I would have to certainly look at

9   that to be able to provide probably an educated response to

10   whether we agree or disagree with that study.

11             MR. McNULTY:  As is practiced in the industry, is a

12   ten-year cycle a common cycle for the types of wood pole

13   inspections that would be sound and bore type inspections?

14             MR. SPOOR:  Well, again, I think actually to the

15   second part of your question, which is what pole inspections

16   or, for that matter, any type of inspections that we may be

17   doing on a going-forward basis may look like.  And, again, I

18   think that is certainly an area in working with KEMA, who we

19   really are looking to leverage their expertise in the industry

20   in terms of what's adequate, that certainly would be part of

21   something that we would consider.

22             MR. McNULTY:  Thank you.

23             MS. HELTON:  Thank you, Mr. Spoor.  I'm sure you are

24   probably ready to sit down.

25             MR. SPOOR:  That's okay, thanks.  Good questions.

FLORIDA PUBLIC SERVICE COMMISSION

181

1             MS. HELTON:  Next we will hear from Progress Energy,

2   David McDonald and Gary Furman.

3             MR. McDONALD:  Good afternoon.  I'm David McDonald

4   and I'm the Director of Distribution Asset Management for

5   Progress Energy.  We appreciate the opportunity to be here and

6   be a part of this workshop.  We feel like that both the IOUs,

7   the staff, and the constituents of this state understand the

8   importance of these discussions.

9             So with that, I would like to say that we have filed

10   a response to the questions that were submitted to us by Staff.

11   We presented them earlier, and I'm sure that you have had an

12   opportunity to reflect upon those and look forward to the

13   discussion coming up.

14             I want to speak about what we have learned over the

15   past two years at Progress Energy.  We're going to be speaking

16   about the 2004 and '05 hurricanes, the impact to our service

17   territory.  Also we are going to be mentioning exactly what

18   type of damage that we happened to see and our response to that

19   impact.  And then we are going to offer up our opinions on the

20   outage mitigation opportunities that exist from the lessons

21   that we have learned.

22             One of the things I want to drive home about the 2004

23   and '05 storm season is there is really two issues of analysis

24   that we performed.  One, how did we respond?  What was our

25   response to the restoration efforts?  And we did an exhaustive

FLORIDA PUBLIC SERVICE COMMISSION

182

1   analysis of that.  Again, like FPL, and like Michael stated

2   earlier, we are very aggressive about our lessons learned.  We

3   had over 140 lessons learned that we identified to improve our

4   storm restoration response.  Those 140 lessons learned were

5   raised up to the highest level as far as the auditing of those

6   to ensure that we were very thorough in our response to those.

7             But then the second aspect of our analysis is how did

8   our system respond?  And from that, that is what the focus of

9   our attention today will be is the response of our system to

10   the 2004 and '05.  As you can imagine, for 2005 the impact to

11   us was minimal.  We were very fortunate in that, that we had

12   the fringes of what FPL happened to see.  We also had the

13   fringes of what Gulf happened to see from a Dennis perspective.

14   But from that there were still opportunities for us to learn.

15   Our discussions today are going to focus on the 2004 storm

16   season; more specifically, Charley, Frances, and Jeanne.

17             When you look at our service territory, we basically

18   cover the west coast north of Bradenton, and the central part

19   of the state of Florida.  We cover up west of Tallahassee, over

20   to Deland, which is northeast of the Orlando area, and then

21   down to the Lake Wales/Sebring area.

22             Now, the first hurricane that we encountered last

23   year was Charley.  You heard a lot of discussion about Charley.

24   That came through our service territory with 145-mile-an-hour

25   winds.  It came up through the southern portion and exited out

FLORIDA PUBLIC SERVICE COMMISSION

183

1   through Deland.  In that it came through the heart of our

2   central service territory.

3             Following that was Frances.  Frances was a very long

4   storm.  Again, coming in at the central part of our service

5   territory, moving throughout our system impacting every aspect

6   of our system.

7             And then the final one, Jeanne.  Jeanne was 110 miles

8   an hour.  As it moved through our service territory, we had

9   tropical force winds in the Pinellas County area, hurricane

10   force winds through the central part of the state.  As you can

11   see from that, that trajectory, I believe it is Frostproof,

12   somewhere in the Frostproof area had the unfortunate

13   circumstance of all three storms coming right over the top of

14   them.

15             When you consider the path of those storms, one of

16   the things that needs to be emphasized is that most of our

17   damage was wind related, it was not storm surge related.  These

18   were wind events for us at Progress Energy, these three events.

19             I want to speak to you for a few moments about our

20   outage experience.  Three areas that I'm going to bring to your

21   attention have to do with substations, transmission miles, and

22   finally peak customers out.  When you consider our substations

23   out, Frances had the greatest impact.  One of the things that

24   we have identified through our analysis of our substations is

25   that the majority, the majority, and I mean great majority of

FLORIDA PUBLIC SERVICE COMMISSION

184

1   the substations that were out were caused by

2   transmission-related events.  Damage within the footprint of

3   our substations was minimal for those three events.

4             Transmission miles out.  Those are the miles that we

5   had out.  And then finally peak customers out.  You see a

6   pattern for these three bar graphs, that pattern being

7   basically that Frances was the biggest impact for us.  And,

8   again, drawing your attention, Frances was over our service

9   territory for a very, very long time.

10             Sometimes when we see these graphs we focus on, the

11   previous graph about wind speed, we focus on just the

12   horizontal wind speed of hurricanes.  As we all know, there are

13   is a lot of wind phenomenon related to hurricanes.  There is

14   downbursts, there is tornadic activity, there is the horizontal

15   wind loading.  And I have seen instances, or there were

16   purported instances of a vertical -- I'm sorry, a horizontal

17   wind pattern associated with the front of Frances.  So when we

18   focus on wind phenomenon it goes way beyond just horizontal

19   wind loading and the wind speed that was reported.

20             The next item I want to speak to you about is our

21   damage experience.  When you consider it from a facilities

22   perspective, and you consider our transmission structures, you

23   see that Charley, a Class 4 hurricane, had the greatest impact

24   on us.  But then through the other storms that greatly

25   diminished.

FLORIDA PUBLIC SERVICE COMMISSION

185

1             Distribution transformers.  One of the things I want

2   to point out, distribution transformers at Progress Energy, we

3   have over 400,000 distribution transformers.  What you are

4   seeing reflected there is less than 1-1/2 percent of our

5   transformers we had to replace for those three storms.

6             Distribution poles replaced.  We have over 1.1

7   million poles at Progress Energy.  You are seeing 7/10ths of a

8   percent of our poles that failed as a result of three

9   hurricanes.

10             Yes, Jim.

11             MR. BREMAN:  Regarding the transformer failures for

12   distribution facilities, and I guess I failed to ask this

13   question of Mike Spoor when he was up there, because I'm pretty

14   sure FPL had transformer replacements for distribution, too.

15   I'm kind of curious, what is the mode of failure of the

16   transformers?

17             MR. McDONALD:  Well, there are several modes.  One

18   mode, as you can imagine, there is still existing open-wire

19   secondary on our facilities.  When you start having wind and

20   vegetation that interact with that open-wire secondary, there

21   is a good chance you are going to have shorting opportunities

22   that may occur.  So electrical failures internally.

23             You also can have failures of the transformer

24   actually being on a pole that may have come down.  Again, I

25   mentioned to you about our pole instances, or pole failures

FLORIDA PUBLIC SERVICE COMMISSION

186

1   were less than 7/10ths of a percent, so that is one of our

2   least significant contributors to pole failures.

3             So when you look at our transformer failures, the

4   third item that I would want to stress is the connection to

5   those transformers, whether it be service or secondary, trees

6   coming across those service or secondary, and the physical

7   movement of pulling that off the pole.  So when you consider

8   those three factors, they contributed mostly to our failures

9   that we saw at Progress Energy.

10             MR. BREMAN:  I guess the follow-up of that is is it

11   really time consuming to replace these transformers?  I know

12   you said it is not a large quantity compared to the existing

13   system on a total basis.  But all the people that are there,

14   you know, you have got 10,000 people scrambling around trying

15   to bolt the system back together and put it back up.  I'm just

16   wondering how much time is really required to reset a

17   transformer on a pole and then set the pole.

18             MR. McDONALD:  Well, what I would respond to that is

19   anytime we have a failure of any equipment it is going to be

20   time consuming, and dependent upon where that equipment happens

21   to be.  If it happens to be in a rear easement that we don't

22   have access to it by vehicles, that prolongs our restoration

23   efforts.  So, yes, there is time involved in replacing those

24   roughly 3,800 transformers.  But that time involvement, when

25   you look at the entire fleet of transformers we have, and you

FLORIDA PUBLIC SERVICE COMMISSION

187

1   think about it from a significance perspective, is it

2   impactful?  Absolutely.  Does it take time?  Absolutely.  But

3   when you look at in the grand scheme of things and you think

4   about it from a risk/benefit analysis, and, again, from an

5   anecdotal risk/benefit analysis, does the risk for that entire

6   fleet of 400,000 transformers warrant the standards that you

7   have that resulted in roughly 3,800 transformers.

8             MR. BREMAN:  Not having to replace the transformers

9   won't reduce the restoration costs?  I mean, I'm just thinking

10   about are there options.  Is this a way of identifying a hot

11   spot zone where prospectively we can improve our hurricane

12   hardening.

13             MR. McDONALD:  There's a couple of things that could

14   be considered, and that's part of this workshop, of what are

15   those things we should be consider.  When you think of the

16   physical connection, the electrical connection and the physical

17   connection, are there things that can be done?  We mentioned

18   the Homac and their breakaway.  Is there something else that

19   can be done at the connection at the transformer?  These are

20   questions that have to be resolved that are not answered at

21   this juncture.

22             So, yes, to answer your question, are those things

23   that we need to weigh going forward?  I think as IOUs that we

24   have to consider those types of issues and determine whether it

25   is the right investment.  And by right investment, I need to

FLORIDA PUBLIC SERVICE COMMISSION

188

1   stress, right investment is from a totality perspective.  From

2   the customers' perspective, from the company's perspective,

3   being the labor that it takes to restore that.  So, yes, it is

4   a total response that we have to consider.

5             MR. BREMAN:  I'm sorry.

6             MR. McDONALD:  No, no, I just wanted to make sure I'm

7   answering your questions.

8             Now, when you consider the restoration experience and

9   the resources and the restoration days and the cost in

10   millions, again, you will see that Charley was very impactful

11   for us.  You see that our restoration time frame for Charley,

12   which was our greatest, was nine days.  Five days for Jeanne.

13   If you reflect back, we had over 722,000 customers out for

14   Jeanne.  Cost in millions.  You see the reduction in the cost.

15             So when you consider the three storms and you

16   consider these slides in comparison, what you have to also make

17   a component of your thinking is that Charley, a Class 4

18   hurricane, is a hurricane that required us to rebuild to some

19   extent.  As you moved into the others it was more of a repair

20   and restore.

21             Damage assessment.  Some of the conclusions that we

22   have come to, again, by our assessment of the 2004 season.

23   Transmission.  Higher voltage performed better than lower

24   voltage.  By that we are talking about the 230, the 115 versus

25   the 69.  Concrete and steel performed better than wood for our

FLORIDA PUBLIC SERVICE COMMISSION

189

1   transmission structures.

2             Substations.  One of the things I mentioned earlier,

3   no significant damage within the footprint of the substation.

4   And the outages for those substations due primarily to the

5   transmission lines that connected them.

6             For distribution, the preponderance of our failures

7   were tree-related.  That damage was very prevalent throughout

8   our service territory that was impacted by these storms.  The

9   last bullet, code standards.  Not a significant issue from our

10   assessment.  And the 7/10ths of the pole failures.  When you

11   look at the wind-loading standards that we are required to

12   build to, in our assessment of the 2004 season, that was not a

13   significant contributor to our pole failures.  It was the wind

14   related to the vegetation that caused our damage.

15             Going into a little bit more detail.  Transmission,

16   Hurricane Charley.  You see the hurricane force winds depicted

17   by the red, tropical storm force winds depicted by the orange.

18   You see it was a very tight and compact storm.  Those locations

19   indicated there are the actual pole failures.  And you see

20   within the hurricane force winds is where we had the majority

21   of our transmission pole structure failures.

22             Substations --

23             MR. TRAPP:  Can you make an observation with regard

24   to the density of that curve in the center part of the state as

25   opposed to the coastal parts of the state?  Is there anything

FLORIDA PUBLIC SERVICE COMMISSION

190

1   to be drawn from that?

2             MR. McDONALD:  It's our service territory.

3             MR. TRAPP:  Okay.  So your service territory is just

4   in the center, you are not mapping the Power and Light

5   facilities?

6             MR. McDONALD:  No.

7             MR. TRAPP:  Do the Power and Light facilities show

8   the same pattern through the path of the storm?

9             MR. McDONALD:  I don't want to speak for Florida

10   Power and Light.  It would be just an assumption on my part.

11             MR. TRAPP:  I would like for you all to speak for the

12   state.  I mean, we asked you all to speak for the state.  What

13   I would like to know, and I would like perhaps for you all to

14   get your heads together on this and tell us whether or not

15   there is a pattern of damage that just simply follows the path

16   of the storm, or whether or not -- I mean, these are

17   transmission facilities.  As I understand it, they are subject

18   to the higher wind speed criteria and the national safety code.

19             MR. McDONALD:  That's correct.

20             MR. TRAPP:  I would be interested to know whether or

21   not because the center part of the state is built with regard

22   to the standard, it has to adhere to lower wind speed patterns,

23   whether or not you are picking up less damage on the coast

24   because they were built to higher wind speed levels, or whether

25   or not we are seeing some kind of pattern that might indicate

FLORIDA PUBLIC SERVICE COMMISSION

191

1   that one of the zones we have to be interested in is a more

2   equal wind speed application throughout the state.

3             MR. McDONALD:  I think as you see the subsequent

4   slides you will come to the conclusion that this is purely

5   following the path of the storm.  That's what we have found in

6   our analysis is that the damage is following the path of the

7   storm.  There is no designated hot pocket if you will.

8             MR. TRAPP:  I would like verification, joint

9   verification between Florida Power and Light and Progress on

10   this issue.  Because you all are peninsular Florida.  And it

11   seems to me that being the two largest companies in the state,

12   at least you all can get your heads together and answer this

13   question with respect to a statewide perspective.  Thank you.

14             MR. McDONALD:  Thank you.  On the next one, Frances,

15   again, you see the damage that is following the path of the

16   storm.  And then the subsequent one, Jeanne, fits the same

17   pattern.

18             MS. KUMMER:  Excuse me.

19             MR. McDONALD:  Yes, ma'am.

20             MS. KUMMER:  Looking at that, it looks like you have

21   got a significant amount of damage outside of the path of the

22   storm that you don't see on the other two slides.  What was

23   that?  Mine had a lot of --

24             MR. FURMAN:  If you flip back to Frances, or looking

25   at Jeanne, what you will see is -- and I think the professors

FLORIDA PUBLIC SERVICE COMMISSION

192

1   that talked, or the doctors that talked about hurricanes will

2   verify that probably your strongest wind in a lot of your wind

3   events, like tornadoes and so forth, to my understanding occur

4   in the top right quadrant of the hurricane.  And you will see

5   here in Jeanne, you see some of the damage up in that area

6   there.  So that is kind of the correlation that can be made

7   there.  And that is within -- I think the gold area is within

8   the path of the hurricane force winds, as well.

9             MR. BREMAN:  Excuse me.  Is that essentially 69 kV,

10   is it just a lower design standard?

11             MR. FURMAN:  Yes.  The majority of what in damage was

12   a single wood pole, which is 69 kV.  And a larger -- at that

13   voltage you will find a larger percentage of that in closer

14   proximity to vegetation, like along road right-of-ways and so

15   forth.  So you did see additional damage to the lower voltage

16   systems we believe for that reason, additional

17   vegetation-related failures at the lower voltages similar to

18   what you would find in distribution.

19             MR. BREMAN:  And just to beat a dead horse, the 69 kV

20   is built kind of shorter than the 115 and 230?

21             MR. FURMAN:  Yes, typically it is going to be

22   shorter.  And, you know, as you go down in voltage, you get

23   closer to your substations and so forth.  So the routing of

24   those lines follow closer the type of routings that you are --

25   or locations that you would find distribution in, as well.

FLORIDA PUBLIC SERVICE COMMISSION

193

1             MR. BREMAN:  So this isn't just showing wood, this is

2   showing concrete and everything?

3             MR. FURMAN:  That is showing all the pole failures.

4             MR. BREMAN:  Thank you.

5             MR. McDONALD:  Let's speak about distribution now for

6   Hurricane Charley.  I want to draw your attention to the map or

7   the graph on the left-hand side.  If you notice, there are

8   three different colors of severity, the greatest severity being

9   red.  Those are the amount of customers on a particular large

10   circuit, which we call feeders, the percentage of those

11   customers that were interrupted.  You see on the left-hand side

12   that there is a greater percentage of customers that have been

13   interrupted from a red perspective, if you will.  There is a

14   greater number of red than yellows on the left-hand side versus

15   the right-hand side.

16             Part of what this graph is depicting is what we

17   mentioned earlier, a major component or a major contributor to

18   our outages happens to be related to vegetation management and

19   the impact of wind on the vegetation.  The second aspect that I

20   wanted to bring out is rear lot line distribution.  We are

21   finding that the location of our poles is as predominant a

22   contributor as to what class the pole is built at from a safety

23   factor.  To be more specific, rear lot line distribution, we

24   have our poles placed between homes, as you can imagine, on the

25   property corners.  And within those rear lot line

FLORIDA PUBLIC SERVICE COMMISSION

194

1   distributions, again, you can probably imagine the type of

2   facilities that are there.  Besides just the vegetation that

3   happens to exist, you have fences of all types, whether they be

4   wood fences, whether they would be vinyl, galvanized.  You have

5   aluminum sheds.  All within that compacted area that is all

6   within the rear lot line distribution.  We have found that a

7   great or a large percentage of our outages were related to that

8   type of debris being blown into our facilities.

9             When you contrast that to the graph on the right-hand

10   side, the graph on the right-hand side has to deal with our

11   underground distribution.  You'll see that it performed better

12   in Charley than our overhead.  You'll see that there were fewer

13   customers out from a red, yellow, green perspective.  So during

14   Charley we did have good performance from our underground

15   system, and it's -- go ahead, Jim.

16             MR. BREMAN:  I apologize for keeping interrupting,

17   but just to confirm, when you have segregated out the overhead

18   and the outages, you have identified the point of failure so

19   that we know that the cause of the outage is due to a failure

20   of a piece of equipment that is either overhead or underground,

21   it's not a mixed bag like we heard some discussion earlier

22   today.

23             MR. McDONALD:  No, it is indeed a mixed bag.  What

24   you are seeing up there depicted is that on the left-hand side

25   over 50 percent of the customers served from those feeders are

FLORIDA PUBLIC SERVICE COMMISSION

195

1   overhead.  What you are seeing on the right-hand side is over

2   50 percent of those customers are underground, served

3   underground from those feeders.  Again, one thing I would

4   emphasize at this juncture, understanding the exact device that

5   failed during a storm of this magnitude and having a recorded

6   history of that is a very difficult thing to do.

7             One of the things that I want to bring out at this

8   juncture is that we at Progress Energy do appreciate the

9   performance of the underground system.  We did have good

10   performance from the underground system.  But you have to

11   understand that there are costs associated with that

12   underground system which we will talk about in greater detail

13   in just a few moments.

14             On the next page, again, similar diagrams for

15   Frances.  You see that we also had better performance from our

16   underground system as far as the number of customers impacted

17   off those facilities, those underground feeders.  And then

18   finally, with Jeanne, again, the same story.  So, again, from

19   this perspective I want to emphasize underground performed very

20   well for us.  Overhead was impacted by vegetation and impacted

21   by location.  Three key lessons that we have learned.

22             MR. TRAPP:  I'm still seeing, however, from these

23   charts that you are getting significant customer outages pretty

24   much in the same areas, whether it be overhead or underground.

25   Now, do you attribute that to underground being fed by

FLORIDA PUBLIC SERVICE COMMISSION

196

1   overhead?

2             MR. McDONALD:  It is the density, our customer

3   density.  If you look at that, there is a gap in our service

4   territory between that streak in the middle and the streak on

5   the left-hand side.  So you look at our population centers.

6   Those are two population centers.  The hurricane paths impacted

7   our population centers.

8             MR. TRAPP:  How big are the circles, I guess, because

9   I see some red where I don't see some red in the underground.

10             MR. McDONALD:  The circle is not depicting any type

11   of population.  It's not rated towards the number of customers

12   served.  It purely means we had a protected device of an

13   underground nature that interrupted at that location.  And if

14   you think about that in greater detail, there's a lot of

15   overlap that occurs in this map.

16             MR. TRAPP:  So I don't see -- weightings in this is

17   what I'm not seeing or --

18             MR. McDONALD:  Weightings related to the number of

19   customers on that device, no, you would not see that.  Not

20   based upon the circle size.

21             MS. KUMMER:  I think I heard you say that a lot of

22   the overhead damage was due to rear lot line construction.  Do

23   you build rear lot line construction any more?

24             MR. McDONALD:  No.  Rear lot line construction was

25   really predicated upon the previous easements that we had and

FLORIDA PUBLIC SERVICE COMMISSION

197

1   the construction standards not imposed by us, but imposed on

2   us.  So when you had the platting of easements in some of our

3   older service territory, the easement was in the rear.

4             MS. KUMMER:  So that is just primarily in the older

5   neighborhoods?

6             MR. McDONALD:  That's correct.  When you consider the

7   potential mitigation approach, and I think everyone has seen a

8   diagram like this or something very similar, starting at the

9   generation, moving to the substation via the transmission and

10   then to the distribution, what we have seen in our history and

11   our assessment of 2004 is the backbone, the feeders, if you

12   will, are something that we want to focus on and get back on

13   very quickly.  When you look at the customer, when it comes to

14   the customer and the service drop to the customer, that is a

15   focus area that we need to consider in our plans going forward.

16             From an overall diagram perspective, there are three

17   areas that we are going to touch on.  One, distribution,

18   mitigating the damage caused by the location, and also

19   considering the vegetation management.  Transmission, looking

20   at targeted actions to harden those facilities.

21             More specifically, potential mitigation options.  The

22   first one, evaluate a migration away from wood poles to steel

23   and concrete for transmission.  The second arena we would

24   consider, further review of targeted underground conversion,

25   and we'll talk about that in greater detail in just a moment.

FLORIDA PUBLIC SERVICE COMMISSION

198

1   And the final, evaluate ways to facilitate vegetation

2   management.

3             The first one, evaluate migration away from wood

4   transmission poles.  Referring back to what I discussed

5   earlier, we have found that our wood -- I'm sorry, our concrete

6   and steel in transmission performed better than our wood.

7   Roughly 80 percent of our facilities, our transmission

8   facilities, are wood poles.  So from a migration perspective or

9   a hardening perspective, we need to investigate that aspect of

10   it.

11             The next one I would like to talk about is further

12   review and feasibility of targeted underground.  We mentioned

13   targeted underground because we have all discussed the cost

14   related to undergrounding in its entirety.  And that cost that

15   we discussed unfortunately sometimes centers around purely the

16   dollar cost.  But I think when we consider undergrounding we

17   have to consider the total cost, what is the cost on the

18   customer.  When you look at a conversion of facilities from

19   overhead to underground, what is the change from a customer's

20   perspective.  That footprint that they had on their property

21   from a pole, how does that differ now.  Do they have a bigger

22   footprint from something that is above ground?  Questions that

23   have to be considered.

24             I can't stress enough from the Progress Energy

25   perspective, we understand how underground performed, we

FLORIDA PUBLIC SERVICE COMMISSION

199

1   appreciate how underground performed, but like everything else,

2   we need to evaluate all aspects of undergrounding.

3             Yes, Jim.

4             MR. BREMAN:  The term total cost is a buzz word among

5   economists that means something.  Could you please be careful

6   about what you mean by that.  What do you mean when you say

7   total cost?

8             MR. McDONALD:  Are you asking me?

9             MR. BREMAN:  Yes, sir.

10             MR. McDONALD:  Total cost is the entire cost

11   associated with undergrounding.  Not only the financial cost to

12   undergrounding the utility facilities, the financial cost to

13   the customer.  The financial cost of the facilities, where they

14   are located now, the easement rights that have to be gained,

15   those are just a portion of some of the costs that have to be

16   considered.

17             Now, the benefits also have to be considered and

18   should be considered first.  What are those benefits and how do

19   those benefits weigh against the cost?  So when you speak of

20   total cost, it is not just financial.  There is financial,

21   there is cultural, there is a lot of different aspects of cost.

22             MR. BREMAN:  And you are just proposing this for

23   conversions?  I'm wondering why that is not applicable to new

24   construction, as well.

25             MR. McDONALD:  When it comes to new construction, as

FLORIDA PUBLIC SERVICE COMMISSION

200

1   you can imagine, you are normally building within a greenfield,

2   so there is a lot of consideration that is being placed by the

3   developers and built into that particular project, if you will,

4   that these conversions would not have and would have to

5   overcome.

6             When you think about a developer that is developing

7   several hundred acres, what are the easements that they

8   provide, what are the areas that they provide for the equipment

9   above ground.  These are normally built into those projects.

10   So as a customer would actually take ownership of that land,

11   they would understand what they have from an overall ownership

12   perspective.

13             When you consider undergrounding, one of the things

14   that you need to consider is the reliability of our

15   underground.  And I mentioned during the hurricanes and during

16   our normal events the reliability of underground historically

17   does pretty well.  But when it comes to restoring those

18   facilities, normally there is a cost associated with that and a

19   time frame associated with that.  Those are some of the things

20   that need to be considered as we consider undergrounding

21   facilities.

22             One of the things I want to draw out at this point,

23   when we mentioned targeted, targeted is a key word.  And the

24   point being is based upon storm surge, there may be areas that

25   you don't want to convert to underground or at least you should

FLORIDA PUBLIC SERVICE COMMISSION

201

1   consider it.  The subsequent slide that I will show you will

2   illustrate this point.

3             This is a slide provided -- the information provided

4   by Pinellas County.  You see that it depicts the five

5   categories of storm and you see the storm surge associated with

6   that.  When you see this is Pinellas County, Category 5, you

7   see that a good portion of Pinellas County under a Category 5

8   storm is under water.  You really need to question is that

9   where we want our facilities to be underground from a society

10   perspective.  So those are some of the things that we need to

11   consider.

12             MR. McNULTY:  Mr. McDonald, if I could interrupt for

13   just a moment.  You talked about targeting underground

14   conversions.  What are the ideas that Progress has for

15   targeting those underground conversions without socializing any

16   costs across the entire body of ratepayers and targeting, you

17   know, costs to the cost causer?  How does the utility go about

18   encouraging those kind of conversions?

19             MR. McDONALD:  I heard two questions in there.  One

20   question I would ask how do we encourage conversions.  We have

21   a constant communication process by which we make known to the

22   municipalities and to homeowner associations the capabilities

23   they have to convert, what mechanisms exist that would

24   facilitate that process.

25             As an example, we have a tariff that within the

FLORIDA PUBLIC SERVICE COMMISSION

202

1   confines of that tariff it shows the mechanisms by which they

2   can recoup that cost.  So we communicate those mechanisms and

3   those capabilities, again, to the municipalities and to

4   homeowner associations, et cetera.

5             The other aspect of the question I heard was the

6   targeted aspect.  When it comes to targeting facilities, you

7   need to consider -- and I think it goes back to Mr. Trapp's

8   question -- what are those areas that you would think not only

9   from a hurricane perspective, or from a 51-week perspective,

10   and by that I'm saying the one-week hurricane and the 51 weeks

11   of normal performance, are there areas that you need to

12   consider from an undergrounding perspective that would improve

13   the overall performance of the system to be able to withstand

14   the hurricane and be able to provide a service long-term.

15             So when you think about targeting, one of the areas

16   that you may consider is rear easement.  Is that something that

17   you underground?  Should you underground the rear easement, or

18   should you move it out front?  Again, questions that need to be

19   evaluated if you are going for a long-term answer.

20             Yes, sir.

21             MR. TRAPP:  When do you think you will have your

22   recommendations finalized?

23             MR. McDONALD:  When you say recommendations, the

24   particular areas or --

25             MR. TRAPP:  Well, first of all, let me steal Mary

FLORIDA PUBLIC SERVICE COMMISSION

203

1   Anne's thunder and compliment you for being responsive by

2   including scatter diagrams, and analysis, and that type of

3   stuff that engineers like to get our teeth onto.  We do

4   appreciate that.

5             But we have heard both from Florida Power and Light

6   now, and I think from you, that we are going to study the

7   problem.  I thought you were getting real close to telling us

8   what you thought you should do, but I haven't heard it yet, so

9   I'm asking.  When will you have an opinion on what parts of

10   Pinellas County should be underground and should not?  When

11   will I hear that recommendation from the company?

12             MR. McDONALD:  Well, I think it would be unfair to

13   you to say that we have this particular date.  I will tell you

14   that the process is underway.  We have engineers that are

15   taking into consideration what we have encountered and the best

16   response to that.  Now, I heard earlier about a one-week

17   submittal --

18             MR. TRAPP:  Is that a one-week turnaround or --

19             MR. McDONALD:  Well, that's what I heard about here.

20             MR. TRAPP:  -- is that a one-year, or a ten-year

21   turnaround?  When will the company bring to us specific

22   short-term and long-term recommendations, or do you want to

23   hear them from us?

24             MR. McDONALD:  Well, I think that very soon we could

25   bring you recommendations.

FLORIDA PUBLIC SERVICE COMMISSION

204

1             MR. TRAPP:  One week?

2             MR. McDONALD:  I think very soon we could bring you

3   recommendations.

4             MR. TRAPP:  One week.

5             MR. McDONALD:  But you have to understand, in my

6   opinion, there's a lot that goes along with these one-sentence,

7   one-number recommendations that need to be considered by all of

8   us.  And to have this one-sentence explanation with one number,

9   I think without the adequate discussion, the adequate

10   understanding, the impact of that for all of us within the

11   state, I think that we need to weigh that very judiciously.

12             So, could we respond?  I think we could respond

13   quickly, yes.  But I would apply a caveat to that that we all

14   need to understand what that means from not only our

15   perspective, but yours.

16             MR. TRAPP:  And understand what staff is asking for,

17   too.  We are asking for the one line simple solutions to the

18   simple problems, not to the -- you know, you can always come up

19   with a simple solution to a complex problem that is always

20   wrong.  That is not what we are seeking here.  We are looking

21   for simple solutions to simple problems.  What's the

22   short-term.

23             But in terms of the long-term more complicated, more

24   convoluted, and the things that will take more time, I need a

25   path.  Can you recommend a path of study, a course of action?

FLORIDA PUBLIC SERVICE COMMISSION

205

1   So I want two things.  I want the short-term in a week and I

2   would like a path within a week, as well, if you understand

3   what I'm trying to communicate.

4             MR. McDONALD:  I understand what you are trying to

5   communicate, and I would hope that that would be something

6   jointly we are pursuing.  Because, quite candidly, I think

7   from -- and I will speak for my brethren, and maybe I

8   shouldn't, but I think from all of us this is a path we have to

9   embark on together, because this is not an easy answer.

10             And you said easy answers to easy problems.  In my

11   opinion, this is not an easy problem arena.  This is one that

12   requires some detailed understanding.  Now, is it so complex

13   that we are frozen into immobility?  Absolutely not.  But it is

14   one that requires consideration; and within that consideration,

15   a plan moving forward.  So can we meet your timetables?  I

16   think we can meet your timetables of submittals.  Do I think it

17   is the ultimate end all answer, absolutely not.

18             MS. KUMMER:  I think just to underscore what Bob has

19   said is that I have heard a lot of what, well, we're thinking

20   about it, we're going to look at it, we don't really know yet.

21   And, quite honestly, those aren't acceptable answers.  We need

22   to have a plan in place to be moving forward.  And our

23   Commission expects us to come back to them with recommendations

24   the end of February.  So we're going to need some help from you

25   all, or as Bob said, you can either help us plan it, or you can

FLORIDA PUBLIC SERVICE COMMISSION

206

1   depend on what we are going to come up with.  So it is -- we

2   don't have six months, eight months, a year to do this.  We

3   need to get moving on it.  And I think that's the point that

4   Bob is trying to make.

5             MR. McDONALD:  And I think he raises an excellent

6   point.  It may not be evident in the presentation that I'm

7   giving to you, I hope it would be.  But our intent is to come

8   here as an enabler of this process and to let you know that we

9   have looked at this from a broad perspective.  We do have

10   considerations of what we need to do going forward.

11             However, for us to do that in isolation without

12   consideration from you all's perspective, your Staff's

13   perspective, and our brethren, for lack of a better term,

14   without that, I think that would be irresponsible on our part.

15   So the intent would be how do we bring these parties together

16   to present here is what we're thinking, here is what we're

17   thinking, here is what we all should be thinking.  That is the

18   intent of our presentation here today.  So I would hope that

19   you would believe me.  I understand what you are asking for,

20   what all of you are asking for, and it is our intent to enable

21   you with that, but we are going to have to do it together.

22             So, again, depicting here a Category 5 storm surge

23   and the impact on Pinellas County.  Going to the next slide is

24   what we consider from a vegetation perspective.  When it comes

25   to our vegetation management, I'm going to sum it up in three

FLORIDA PUBLIC SERVICE COMMISSION

207

1   different bullet points.  We need to be able to have the

2   capability of trimming within our legal boundaries, from ground

3   to sky.  Is that strong?  That's something that needs to be

4   considered, and you will see subsequent pictures of that

5   concern that we have.  I think it was mentioned earlier about

6   the type of trimming:  The B trimming, the C trimming, the

7   tunnel trimming.  When it comes to vegetation management and

8   being able to lessen its impact from a hurricane perspective,

9   you have to look and ensure that you have the utmost clearance.

10             We have to look outside and ensure we have the rights

11   to trim those trees that come in contact with our facilities.

12   If you remember to the KEMA study, or the KEMA presentation

13   that was made today, it had a tree well outside of the easement

14   and its impact.

15             And then the final one is we need to have the

16   capability of doing something for those people that plant trees

17   directly in contact or in conflict with our facilities that

18   presently we do not have the right to be able to deal with.

19             MR. McNULTY:  Mr. McDonald, I'm trying to understand

20   a comment that you made.  You said we need the ability to be

21   able to trim our trees within our legal boundaries.  What

22   prevents you today from trimming in your legal boundaries if

23   they are your legal boundaries?

24             MR. McDONALD:  There are various municipal

25   limitations that we have that really restricts our ability to

FLORIDA PUBLIC SERVICE COMMISSION

208

1   trim within, whether it be the road right-of-way, and that is

2   where a large percentage of our feeders are located.  So when

3   you consider our main circuits in road right-of-way, and you

4   have municipal ordinances that limit that.  That is something

5   that needs to be considered, and how do we deal with that.

6             MR. McNULTY:  So are we talking about expanding the

7   legal authority for the utilities to trim, is that what we are

8   talking about?  I'm still a little bit hazy on the point.

9             MR. McDONALD:  Having the legal capability, or having

10   the capability to trim those facilities, trim it out completely

11   is what we are discussing, versus tunnel trimming or C

12   trimming, if you will.

13             MS. KUMMER:  Would, for example, perhaps legislation

14   giving you the right to trim that would override local

15   ordinances.  I'm not saying that is a good idea, necessarily,

16   but that would be an example of something that would perhaps

17   assist.

18             MR. McDONALD:  To your earlier point, as we came to

19   this meeting, the intent was we have a concern with vegetation

20   management.  One of the issues we have is within right-of-ways.

21   Having the capability of trimming the facilities such that it

22   minimizes the impact of vegetation on our facilities.  Right

23   now, local ordinances impede our abilities to get a true

24   ground-to-sky clearance from what we presently can do.

25             MR. McNULTY:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

209

1             MR. McDONALD:  In this next slide you see one of the

2   issues we're talking about.  If you look on the left-hand side

3   of that, you see that tree that is outside of our legal bounds

4   of trimming.  But under hurricane force winds, there is a good

5   chance that that tree is going to be within our facilities.

6             MR. TRAPP:  But it's growing under the line.

7             MR. McDONALD:  There are two of them.  If you look at

8   the one on the left, the taller one, the pine tree, the taller

9   one, that's the first one, and to your attention, the second

10   one is growing up into it.  Neither one of those trees do we

11   have the right to trim and remove.  But both of those, under

12   hurricane force winds, could definitely impact our facilities.

13             On the next slide, it is hard to see the facilities,

14   but you see the general V cut that is done.  And what you would

15   see here is that outside of our legal rights, the trees are

16   towering above our facilities.  Again, an issue when it comes

17   to vegetation management.

18             And the final one, we encounter this frequently.  We

19   have over 18,000 miles of overhead circuit.  Within one of our

20   jurisdictions it was brought to our attention that they just

21   planted 30 palm trees, and this was the municipal itself, just

22   planted approximately 30 palm trees right beneath our

23   facilities.  That is something we deal with, that's something

24   we communicate with them, that's something we try to resolve

25   with them.  But that is part of the challenge that you have

FLORIDA PUBLIC SERVICE COMMISSION

210

1   related to vegetation management.

2             We'll go ahead and move through these.  You'll see,

3   see, again -- finally, concluding thoughts.  Again, I have

4   stressed it here.  It is imperative that we weigh not only what

5   we encountered in 2004, we mentioned 2005 wasn't a major impact

6   to us, but it was to those across this country learning from

7   FPL, learning from Entergy, CLECO, those other companies.  That

8   is something a smart company does, and we are a smart company,

9   and we are pursuing understanding the lessons from those folks.

10             One of the things I want to impart to us all, we want

11   to do what is right, we want to do what is better, but we

12   should make sure we understand what that means.  It is

13   mentioned many times here, and it's a well-worn phrase, but I

14   think it is worth repeating:  There is no silver bullet.  These

15   are complex issues, they require complex solutions, but I'm

16   confident that we are capable of that.  Not only us, but the

17   staff assisting in that and guiding in that.

18             And, finally, Progress Energy Florida will continue

19   to evaluate alternatives in order to respond to this challenge

20   that we have going forward.  The intent of our efforts at

21   Progress Energy of Florida is to ensure that we understand that

22   we are a key component of the quality of life of our customers

23   and the constituents of this state.  And as such, we have a

24   responsibility to restore when a hurricane impacts us and make

25   sure that's the most efficient restoration effort, and to

FLORIDA PUBLIC SERVICE COMMISSION

211

1   invoke any and all cost beneficial, and I hate to use that

2   word, but I will use it, cost beneficial activities that will

3   ensure that our service territory is more resistant to

4   hurricane force winds.  Those conclude my comments.

5             MR. TRAPP:  I have two quick ones, if I might.

6             MS. HELTON:  I think Mr. Trapp isn't willing to let

7   you off the hook yet.

8             MR. TRAPP:  I just have two quick ones, to go back to

9   the earlier speakers and some points that were made this

10   morning.  First of all, what are you doing to work with and

11   communicate with your local communities?

12             MR. McDONALD:  We consistently, starting before the

13   storm season, during the storm season, during a storm, and

14   after a storm we are well linked with our community.  We

15   communicate to them on a couple of issues.  We communicate on

16   tree placement and the tree program.  We communicate to them on

17   our restoration efforts.  We build bridges based upon the

18   priorities that those communities have, and how do we best

19   respond to those priorities.  So our response to our community

20   is pervasive and it's ongoing.  It's a consistent process that

21   we pursue at Progress Energy.

22             MR. TRAPP:  And, number two, what are you doing with

23   your state universities?

24             MR. McDONALD:  State universities.  When it comes to

25   our universities, most of our efforts, as far as state

FLORIDA PUBLIC SERVICE COMMISSION

212

1   universities, has been very limited.  What we have been dealing

2   most of our efforts with have been more consortiums.  As an

3   example, one of the consortiums that we are involved with is

4   looking at the life-cycle cost of a pole.  And that is being

5   headed up by Davis Consulting, and it is involving over 18

6   utilities from throughout the United States and Canada.  And

7   the intent is to understand when should a pole be maintained,

8   how should a pole be maintained, what is the optimum life-cycle

9   of that from a strength perspective, and what activities should

10   you be involved in.  So we are more involved in our industry

11   consortiums than we have been historically with the --

12             MR. TRAPP:  Are you doing any work on wind speed and

13   the effect of wind speed on utility structures with the

14   consortiums?

15             MR. McDONALD:  I can only speak from distribution and

16   say that is very limited.  We haven't been dealing with them

17   recently on that particular initiative.  I'm not sure if

18   transmission has been.

19             MR. TRAPP:  I would encourage you to speak to the

20   professors that are here today and see what they might have to

21   offer in terms of data that might be useful to the company.

22             MR. McDONALD:  And that is a question that you asked

23   Mr. Spoor, and now you are asking me, and I think it is a key

24   question.  And the point being is we have to spread out our

25   knowledge base, our intelligence gathering mechanisms from what

FLORIDA PUBLIC SERVICE COMMISSION

213

1   we have had in the past, and that is a key one that we need to

2   pursue moving forward.

3             MR. TRAPP:  That's all I have.  Thank you.

4             MR. BREMAN:  Mr. McDonald, you just brought up one

5   question.  When is that Davis study going to be done, the one

6   that does the pole study, life-cycle cost thing?

7             MR. McDONALD:  To the best of my recollection, the

8   second quarter of this year is when the first phase of it is

9   complete.

10             MS. HELTON:  Mr. Ballinger?

11             MR. BALLINGER:  Yes, we had a few from the audience

12   come up.

13             You mentioned that in 2004 the prevalent cause of

14   damage was tree damage, trees interrupting lines.  Do you know

15   if your budgeted tree-trimming expenses increased or decreased

16   in 2005, subsequent to that event?

17             MR. McDONALD:  Well, a point of clarification, and

18   let me go back.  The prevalent cause of our interruptions was

19   debris-laden wind.  Whether that debris was vegetation, whether

20   it was aluminum sheds, it could be anything in that spectrum.

21   So that is a point of clarification that I wanted to add.  Now,

22   for those related to vegetation, and your question being more

23   specifically -- refresh my memory -- '04 to '05, is that what

24   you said?

25             MR. BALLINGER:  Yes.

FLORIDA PUBLIC SERVICE COMMISSION

214

1             MR. McDONALD:  Yes.  Our tree trimming budget

2   increased roughly 30 percent.

3             MR. BALLINGER:  And do you know if your company is

4   evaluating waterproofing underground equipment?

5             MR. McDONALD:  At this juncture -- when you consider

6   waterproofing equipment, underground equipment, most

7   underground equipment is sealed, except for the terminations.

8   And that is something that needs to be considered is those

9   points of termination, how do we seal those effectively.

10   Because that is where the intrusion, and that is where the

11   corrosion is imparted.  That is something that presently we are

12   working with our standards group to identify through the

13   industry what is available and how do we apply that.

14             MR. BALLINGER:  And one final question.  You

15   mentioned that Progress is looking into replacing a lot of its

16   transmission wooden poles with steel or concrete, since they

17   perform much better over time, obviously.  Do you anticipate

18   this coming out of current rates?  Are you doing this now with

19   your current rates and revenues?

20             MR. FURMAN:  In 1995, I guess, Progress Energy

21   stopped using wood poles for new construction.  And in 2001,

22   early in 2001 stopped using wood poles altogether.  So as we

23   replace wood poles at this time, we go back with either steel

24   or concrete poles.

25             MR. BALLINGER:  So your replacement program is one of

FLORIDA PUBLIC SERVICE COMMISSION

215

1   when it is in need, when it's rotten, when it's destroyed, or

2   whatever.

3             MR. FURMAN:  New construction.

4             MR. BALLINGER:  New construction.  Okay.

5             MR. FURMAN:  New construction and replacement,

6   maintenance replacement.

7             MR. BALLINGER:  Thank you.

8             MS. HELTON:  Thank you, Mr. McDonald, for including

9   some specific information in your presentation today.

10             MR. McDONALD:  Thank you.

11             MS. HELTON:  At this time let's take a break until

12   4:00 o'clock.

13             (Recess.)

14             MS. HELTON:  Please take your seats so we can get

15   started again.  Thank you.

16             We are ready to get started again.  At this point we

17   need to take things a little bit out of order.  Alan Shaffer,

18   who is here with Lakeland Electric, one of the municipal

19   utilities in the state, has a plane that he needs to catch.  So

20   we are going to take him in between all of the IOUs.

21             MR. SHAFFER:  And I do want to thank you for

22   accommodating that.  I wasn't quite sure what the schedule was

23   going to be, and then it got to the point where we couldn't

24   change it.  I do appreciate the opportunity to come and speak.

25   And while I'm certainly representing Lakeland Electric, beyond

FLORIDA PUBLIC SERVICE COMMISSION

216

1   that I was asked to represent FMEA, which is a conglomerate of

2   all the municipal utilities in the state, and so I am actually

3   speaking for them this afternoon on their behalf.  But I do

4   thank you for the opportunity.

5             And I certainly think that this is -- we have the

6   same goals coming through this.  And as we have done our

7   studies, looked at the information coming out of the storms of

8   2004, and 2005, we have the same type of customers that demand

9   reliable service, and so we are dealing with the same issues,

10   even though the jurisdiction may be a little bit different.

11             Just a couple of words on FMEA and our member

12   utilities.  We have 33 municipal electric utilities, but they

13   add up to be a significant portion of the state, about 15

14   percent of the total of Florida's electric customers.  That is

15   not insignificant.  About 11,000 miles of above-ground

16   distribution, 7,600 miles underground, 1,700 miles of

17   above-ground transmission, and 70 miles underground.

18   Approximately 300 substations.  And every one of these storms

19   that has impacted Florida has impacted in one way or another

20   one of our member utilities.

21             This map represents where we are, scattered

22   throughout the state.  And just goes to, I guess, verify how

23   anything that hits Florida basically impacts one of our members

24   in one way or another.

25             Narrowing the focus briefly in the next slide,

FLORIDA PUBLIC SERVICE COMMISSION

217

1   please, we had the unique situation in Lakeland and Polk County

2   to have seen the eyes of three storms come through the county.

3   I don't think it has never happened before, and hopefully it

4   never happens again, but it certainly changed our perspective

5   of what the storms can do.  We, in Lakeland, are thankful,

6   really, that they came in the order that they did.  Because

7   Charley impacted us the least significantly and taught us some

8   things about your emergency operations plan we didn't know, and

9   that we were able to make some adjustment.  As Frances came

10   through, and then Jeanne, it was most impactful to us.

11             But while we had our share of the impact of the 2004

12   storms, my comments today are basically a conglomeration of a

13   questionnaire that we sent out to our member utilities and

14   responded by about 12 member utilities that represent probably

15   80 or 90 percent of all the municipal utilities in the state as

16   far as the customer base.

17             The nature of storm damage that we felt in our system

18   is not like what you have already heard today.  The

19   transmission system in our particular cases was not that

20   significantly impacted, certainly not compared to the

21   distribution system which we will discuss in a little bit.  In

22   specific, some of these notes I will be making throughout the

23   way were responses from specific utilities that may have had

24   some significant things to say.  Kissimmee had 74 poles down

25   after Charley, which was a larger percentage than any of ours,

FLORIDA PUBLIC SERVICE COMMISSION

218

1   and recognizing the fact of the size of each of the utilities

2   that was a fairly large number of poles for them, and

3   significant for them.  Fortunately, not too many of us had the

4   kind of problem that Keys Energy had with sailboat masts

5   getting into quite a few of their transmission lines as they

6   tended to wander around.

7             The nature of storm damage on the distribution

8   systems, however, were just as reported to you by, that you

9   have already heard by the other utilities, and certainly in a

10   much greater extent, much more severely affected.  Vero Beach

11   lost 100 percent of their customers from Hurricane Jeanne.  In

12   Lakeland we lost 80 percent in Jeanne ourselves, which, as I

13   already mentioned, the most severely impacted by that storm.

14   And others, of course, throughout the state had varying amounts

15   lower, and through the different storms had to deal with

16   different significance of outages.

17             We had minor damage to pole -- minor to significant

18   damage to pole and wire failures, of course, naturally,

19   dependent on where the storms landed throughout our state.  But

20   we found by far the responses that we received the majority of

21   that distribution damage, just like as has already been shared,

22   came from trees or tree limb failures of surrounding vegetation

23   by and large.  I know in Lakeland we experienced that,

24   especially in the easements, between property lines in our rear

25   lot easements where growth had just taken over, and where you

FLORIDA PUBLIC SERVICE COMMISSION

219

1   have got trees in close proximity that, once again, you

2   couldn't get to to remove the tree.  But we could do some

3   trimming in the neighborhood.  You have seen already several

4   pictures of how they can fail and cause damage in those kinds

5   of events.  One bullet I did not put up here, of course, that

6   is impactful to us that we found out was wind load damage, of

7   course, we did have that significantly.

8             Others mentioned by other members were some lightning

9   damage to facilities of burning down wire, some pole failures

10   attributed to successive storms, just the softening of the

11   earth.  You know, had they been spread out, we weren't quite so

12   waterlogged, maybe the wind damage might not have been quite so

13   severe in some cases and caused further damage to distribution

14   facilities.  And we had some reporting, of course, vehicles

15   striking poles.

16             Underground systems, however, by and large faired

17   fairly well, other than flooding, as has already been

18   mentioned, also, that you would expect, and we did also

19   experience in coastal and low-lying areas, and also as trees

20   failed, uprooting some of those underground facilities.  They

21   are not always immune from failures.

22             Substations, as was reported by most utilities, we

23   had very little trouble with.  Very little debris issues,

24   nothing of any huge significance.  Some of the specifics

25   reported were Keys Energy lost a transformer, a load tap

FLORIDA PUBLIC SERVICE COMMISSION

220

1   changing transformer that was flooded and a 138 kV breaker

2   bushing flashover from salt contamination.  Of course, they

3   suffer from severe salt contamination issues there.

4             Jacksonville Electric Authority had three substation

5   transformers that failed after the fact that they attributed to

6   the damage incurred by many reclosings into faults during the

7   storm events themselves, but didn't actually fail until a week

8   or so after some of the storms had passed through.  And Vero

9   Beach had significant substation switch gear damage from water

10   intrusion that was very significant according to their size of

11   utility.  But overall the substations held up very well.

12             For many of us, we finally got to experience the

13   value of mutual aid agreements.  We participate in both the

14   Florida Municipal Electric Association and the American Public

15   Power Association mutual aid agreements that were in effect and

16   utilized.  They are administered and coordinated through the

17   FMEA Executive Director, Barry Moline, who is here today, and

18   the mutual aid coordinators, to which the requests come from

19   the utilities needing aid as well as you also respond, as the

20   utility, identifying what crews, what help you have available

21   to send, and they coordinate those activities.  We also work

22   closely with electric cooperatives and invest-owned utilities,

23   and, in fact, also supplied Florida Power and Light with some

24   out-of-state crews that were municipal crews.

25             Lakeland received aid from not only Florida

FLORIDA PUBLIC SERVICE COMMISSION

221

1   utilities, but municipals as far away as Texas, Kansas, Ohio,

2   Wisconsin, and New England.  And, of course, as you saw the

3   tracks of these storms that came up, many of the closer states

4   could not commit, because it was headed their direction.  But

5   we were very grateful for the assistance that we received from

6   the outside sources.  We actually tripled our work force to

7   restore after Jeanne, we had some 300 line clearance personnel

8   brought in, and an additional 200 line workers brought in to

9   help us recover from that.

10             Just an example of the mutual aid agreement we have,

11   and this is a pretty simple document that basically outlines

12   how aid is to be requested, and that it is administered solely

13   at the discretion of the aiding party.  And it defines how

14   invoicing and how the rate guidelines are going to be used for

15   returning the payment.

16             It is not only important to make the repairs to

17   restore customers, but for a larger goal, good is to do more --

18   is also to do the repairs according to the utility's standards

19   and that is on the next slide, please.  And I think this is an

20   issue all utilities deal with when they bring in external

21   crews.  You know, I think it's a specific question asked of us

22   also.  We attempted to utilize our personnel to guide visiting

23   personnel to make sure our standards were upheld so we didn't

24   have to go back and do a bunch of post-storm rework of things

25   that were done.  As I mentioned, it's important to get the

FLORIDA PUBLIC SERVICE COMMISSION

222

1   customers back in service, but we would rather do it right the

2   first time.  And so we quickly find out that the best use of

3   our personnel, especially when we got into bringing in that

4   many additional external crews, is to use them to guide our

5   personnel and to have them using the proper construction

6   standards.

7             Some reported performing post-restoration inspections

8   to check reconstruction and make additional corrections

9   after-the-fact.  You know, depending on how badly they were

10   impacted, some of them went back and reviewed more than one

11   time, rode circuits out to make follow-up reviews of how -- to

12   try and catch things that weren't caught before.  I think we,

13   as all utilities, also saw many residual effects the following

14   weeks and months after storms as things continued to fall.  I

15   know we certainly experienced that.  But you try and catch as

16   many of those things ahead of time as possible.  All utilities

17   supplied most of their own standard material for their repairs

18   and, once again, that helped keep it within our standards.

19             Concerning vegetation management and discussing our

20   routine distribution maintenance practices, most members

21   reported having a three-year trim cycle throughout their

22   distribution systems.  Keys Energy is limited to a six-month

23   growth trim by local ordinance, so they were under a little

24   different constraint there.  Tallahassee has an 18-month cycle.

25   And some like Gainesville and ourselves include service drops.

FLORIDA PUBLIC SERVICE COMMISSION

223

1   Not everyone reported also trimming for service drops on their

2   routine distribution maintenance.

3             Of course we do, in addition to the directional

4   pruning, we use herbicides and growth retardant, trim a four or

5   six-foot clearance, varying a little bit by utility there.

6   Danger trees are certainly removed where possible.  And I will

7   agree, too, as statements have already been made that we have

8   had a little bit more latitude in doing that as a result of the

9   last couple of years with people not being quite so interested

10   in saving that old historic tree that is sitting there beside

11   our facilities, and allowing us to sometimes go further as we

12   ask permission to trim even outside of our easements, if we see

13   danger trees, and they let us do that.

14             Outage data is used by many to target locations.  And

15   there was one mentioned by one of our members that there ought

16   to be some discussion, possibly with joint tree-trimming with

17   telcos, that would be beneficial.  We spent some time talking

18   about certainly joint use today and some of the

19   responsibilities there are.

20             Routine management on transmission systems has most

21   municipals maintaining an annual inspection trim cycle.

22   Jacksonville Beach and Gainesville inspect semiannually, and

23   most are trimmed to 10 to 15-foot clearances was mentioned

24   today, too, and that is primarily the 69 kV transmission and

25   above.

FLORIDA PUBLIC SERVICE COMMISSION

224

1             Post-storm inspections.  Most utilities were

2   inspecting the vegetation, of course, as part of the system

3   restoration inspection of outage areas.  We found this to be,

4   you know, certainly something we had to do.  Given that trees

5   were the majority of what our issues were, the causes for the

6   distribution outage, we had to make sure we were considering

7   them as we went along.  Some dependence on severity of storm

8   event being that, you know, if it was just very localized

9   areas, they certainly didn't go back and do too much in the way

10   of follow-up inspections.  So it just depends on how severe the

11   storm was, how severe the particular utility that was hit by

12   the storm had some bearing on their post-storm inspection

13   routines, too.

14             Keys Energy and Jacksonville Beach inspect all

15   transmission and main circuits, as well as some others did,

16   too, but they highlighted that.  All municipals conduct pole

17   inspections.  Most are a five to eight-year cycle.  Some

18   mentioned that they included conductors and connections to the

19   extent possible.  They weren't really specific with the short

20   time we had to turn around exactly how all of that was

21   accomplished, but visual inspections as much as possible.  It

22   wasn't mentioned if they did infrared inspections, or whatever,

23   but as much as possible, without inspecting the poles, they

24   were also inspecting what they could visually with the

25   hardware.  Tallahassee conducts pole-by-pole inspections of

FLORIDA PUBLIC SERVICE COMMISSION

225

1   circuits with the highest number of interruptions, so they used

2   some data, once again, to help drive them in their inspection

3   routine.

4             Undergrounding.  Florida's municipals have discussed

5   undergrounding with their communities for years, for many

6   years.  Citizens appreciate learning the pros and cons of that.

7   And, of course, it is a little bit of a challenge sometimes to

8   get them to understand some of the cost differences, but we

9   certainly think it's our part as utilities to educate them in

10   that way and try and just be as up front with them as we can.

11             Undergrounding does not solve all the hurricane

12   outage problems.  We have already mentioned some of the issues

13   about uprooting that lead to that, flooding, those issues, and

14   even in the normal situation, underground may be immune from a

15   lot of the problems, but when it does have outages, they need

16   to understand it takes longer to find where those outages, and

17   repair where those outages are.

18             We have certainly found out as everybody has

19   experienced that many citizens when we start discussing who is

20   going to pay for this and the relative cost of undergrounding,

21   especially existing electric facilities, that many are very

22   reluctant to pay for the cost of that conversion, even with

23   cost sharing.

24             Some utilities are considering converting overhead

25   lines to underground.  And to name a few that have mentioned

FLORIDA PUBLIC SERVICE COMMISSION

226

1   that specifically, Winter Park, who is really a brand new

2   municipal electric utility as of last year is beginning a

3   selective conversion in certain locations to underground.  Vero

4   Beach is converting aging lines when justified, and

5   Jacksonville Beach has said they are in the process of

6   converting all overhead within three blocks from the ocean.

7             Others of us are taking the opportunities, as we

8   continue on, to discuss that with our customers.  We felt like

9   there is probably a whole lot of initial push on the issue of

10   undergrounding and will continue to be.  But it is that

11   discussion that we have already had several discussions today

12   about that that cost, and the true cost, and the total cost

13   that we need to come up with, so we can represent that fairly

14   to the customers and to ourselves as to who is ultimately going

15   to be paying the price for that.

16             Design changes.  Now, some of the design changes that

17   will further harden our systems include additional movement to

18   spun concrete or steel poles and higher wind loading ratings

19   where that hasn't already occurred.  Many of our municipal

20   utilities have already started doing that.  Some selectively in

21   transmission and main line distribution areas, others have

22   targeted even other facilities for that.  Kissimmee says not

23   only some main line, but also distribution with three-phase

24   banks or three-phase risers.  So selectively targeting certain

25   areas that are harder to replace if those facilities fail and

FLORIDA PUBLIC SERVICE COMMISSION

227

1   they take longer to restore customers.

2             Over-insulating substation tie lines to reduce salt

3   intrusion.  Of course, that is an issue with outages near the

4   coast, largely.  Winter Park is installing additional switches,

5   three-phase gang-operated switches to speed sectionalizing, and

6   initiating the underground program that I already mentioned

7   earlier.  Some relocating of rear lot easements to the street

8   right-of-ways.  That is very difficult to do, as has already

9   been discussed somewhat today, also.  But where that can be

10   practically done and economically done and justified for

11   various reasons, that is being looked at by some of our member

12   utilities.

13             Key West had some very specific things that they have

14   done in their design practice.  They have increased their

15   wind-loading design to 165 mile per hour plus, using more

16   concrete poles, and eight-hour battery backup for traffic

17   lights.  Traffic lights, of course, are certainly a safety

18   consideration in restoring power and the aftereffects of a

19   storm.  And using more stainless steel hardware at some

20   locations just to make sure for the life of the facility that

21   they have better service.

22             Additional design changes.  Several have shortened

23   their pole and line clearance inspection cycles.  We mentioned

24   the cycles that were there, but some of them have readdressed

25   that that weren't within those time frames, and have added more

FLORIDA PUBLIC SERVICE COMMISSION

228

1   line clearance crews.  Several have become more aggressive with

2   removing and topping danger trees, as I mentioned before.

3   Customers are more willing to agree with clearance activities,

4   and we already discussed that a little bit.

5             The majority experienced few repair material

6   shortages, but some storm stock inventory levels have been

7   adjusted based on the experiences.  We really did not have

8   significant issues with running out of materials.  And

9   everybody generally has storm stock.  But some of us, where we

10   found areas, especially in certain key splice sizes for wire

11   that we had a lot of trouble with, we have changed some of our

12   storm stock inventories to adjust for that.

13             And, of course, we have got vendor alliances that are

14   occurring.  We have vendors that are stocking materials for us

15   that are part of that in some locations.  Several reported

16   emergency operation plan changes with lessons learned,

17   including helping us respond after the fact.  Revised personnel

18   assignments, train substation or meter personnel to assist the

19   T&D personnel.  Just to make sure, if they haven't already done

20   that, that they had more personnel to help respond, to do

21   assessment, and to do simple activities.  Using retired

22   personnel for the same purposes.  Those that had that kind of

23   knowledge that were still in the area and willing to come back

24   to work, find ways of putting them back to work under these

25   emergency situations.

FLORIDA PUBLIC SERVICE COMMISSION

229

1             And making an earlier determination of mutual aid and

2   contract crew needs and securing logistical needs.  I know

3   Lakeland kind of had a wake-up call with that ourselves.  As I

4   mentioned, the storms got succeedingly worse from Charley to

5   Frances to Jeanne in 2004, and we learned some things in

6   Charley that as we started looking, we called it -- we handled

7   Charley internally.  Frances we called a few external crews in,

8   but we started to recognize real quickly how quickly they

9   disappear.  How they get themselves obligated, if you don't

10   make those phone calls early.  And then addition needs, of

11   course.  The logistics of the hotel rooms, the feeding, the

12   ice, just all those kind of supplies to make sure that you had

13   the right facilities there to take care of them.

14             We learned a lot of lessons.  We, too, are trying to

15   put those lessons in place.  And we certainly welcome the

16   lessons learned from other utilities as we get to hear more

17   about what they have had to say, what they go through, welcome

18   the actions of the PSC that's coming forth through these

19   processes.  And we certainly -- our ears are open, also, to

20   help our utilities serve our customers better in the future as

21   a result of what we have learned through these storms.

22             MR. TRAPP:  I just have a couple.  First, just from a

23   rhetorical standpoint, let me speak as a Tallahassee resident,

24   and ask you since you are here representing Tallahassee today,

25   you're not going to cut down my live oak, are you?

FLORIDA PUBLIC SERVICE COMMISSION

230

1             MR. SHAFFER:  Where is that live oak?

2             MR. TRAPP:  I mean, it's right on the road

3   right-of-way, and it beautifully arches over all the lines, and

4   we haven't had any problem with it.  Now, you can take all the

5   water oaks and the sweet gums you want, but please leave my

6   live oak alone.

7             MR. SHAFFER:  Well, live oaks did fare better.  They

8   are stronger than some of the other varieties, but I can't

9   speak for Tallahassee in that regard.

10             MR. TRAPP:  I bring that up, because this morning we

11   had a suggestion from a local mayor that there needs to be more

12   cooperation at the local community level between local

13   officials and the utilities in the decisions that are made with

14   respect to vegetation control and undergrounding and things of

15   that nature.

16             I imagine since you represent the municipalities

17   which are pretty well embedded in the local community, that

18   some of the variances we see with respect to tree trimming,

19   like Tallahassee's 18-month cycle, have to do with certain give

20   and take and feedback.

21             MR. SHAFFER:  Certainly.  It is kind of interesting,

22   even between city departments we have found ourselves at odds

23   with trees.  Parks and rec, our parks and rec department has --

24   we have adopted standards with them about what trees were

25   acceptable to be planted underneath the power lines and what

FLORIDA PUBLIC SERVICE COMMISSION

231

1   weren't, and they promptly ignored those in some locations.  We

2   have had to go back and have some further discussions with

3   them.

4             And then we have got community development and others

5   that certainly are trying to develop, they are now talking

6   about canopy roads, and all of that.  Now, that is in new

7   developments that are underground anyway, because all of our

8   new developments are -- presently all of them, almost without

9   exception, are going in underground because we participate with

10   the developers in that.  And we put them in without any

11   additional cost as long as they put in the conduit

12   infrastructure.

13             But that's a balancing act.  Trees are an issue.  And

14   I, myself, love to see them there, but they do cause problems

15   under storms conditions like this.  So we have got to make

16   reasonable approaches.  What is appropriate.

17             MR. TRAPP:  I notice, again, that you have some

18   varying policies around the state in your member

19   municipalities, and I pose this to you from an investor-owned

20   utility side where they cover large geographic areas of the

21   state.  Does it make any sense, where rational variance is

22   required, that to the extent that it is cost-effective that it

23   be permitted?  But should we also be exploring alternative

24   pricing, ratemaking, funding mechanisms such as -- like

25   franchise fees, for instance, vary around the state.  And I

FLORIDA PUBLIC SERVICE COMMISSION

232

1   think the Commission rules call that they be collected directly

2   from the community which caused them to be incurred based on

3   the rates that are different in different parts of the state.

4             Would it make any sense for us to look at different

5   ratemaking schemes, if we declare a zonal hardening area, that

6   maybe the cost to support that zonal hardening should be

7   supported in that particular area as opposed to being spread

8   over the entire rate base?

9             MR. SHAFFER:  It seems to me like that would be

10   the -- most of our ratepayers or our owners would probably see

11   that as being the right approach to take.  You know, not

12   penalizing the ones that didn't have so much of the issue or

13   the concern or the troubled areas, and more applying that more

14   locally to the troubled areas as a source of funds to handle

15   those.

16             MR. TRAPP:  Let me turn now to the universities and

17   ask you do you get any assistance from the data that is

18   produced by our university research teams?

19             MR. SHAFFER:  I'm not aware.  I know Lakeland has

20   not -- other than passively reading some of that information

21   and having some interest in it, some of it I wasn't aware of

22   until I started seeing some of the presentations today, and as

23   they appeared earlier at the website.  We are not in a position

24   really to have the staff, I think, to dig into some of that

25   type of data analysis that maybe some of the larger utilities

FLORIDA PUBLIC SERVICE COMMISSION

233

1   would, but we certainly have a lot of interest in the final

2   results that they are coming out with and the end effect of

3   that information.

4             MR. TRAPP:  Thank you.

5             MS. HELTON:  Mr. Ballinger.

6             MR. BALLINGER:  We've got one from the audience.  I

7   know you have got a plane to catch.  What kind of cost sharing

8   arrangements do you or your members offer to your customers?

9   And I presume this would be more for retrofits than it is --

10   because you said that new construction is primarily 100 percent

11   underground.  So I guess on retrofits or whatever, what kind of

12   cost-sharing arrangements do you work out with some of your

13   customers?

14             MR. SHAFFER:  Nobody reported actually to having done

15   that yet.  So Lakeland, and I can only speak definitely for

16   them, several years ago we did have an undergrounding program.

17   We were actually allocating a million dollars a year.  And even

18   with the city -- even with the utility funding some areas

19   downtown, kind of in an older section, historic section that we

20   started to underground, we still had people that didn't want

21   those boxes in the front of their yards.  They wanted the line

22   still in the back, and they didn't have a problem with that.

23             The conversations that we have personally had when we

24   started talking ballpark ranges of 2 to 3 to $4,000 per lot for

25   conversion costs, tended to stifle that conversation real

FLORIDA PUBLIC SERVICE COMMISSION

234

1   quickly.  We did not intend to continue on with that project at

2   this point, especially with the present situation Lakeland

3   finds itself in budgetarily, that we could not continue to do

4   that.  We cut off the million dollar funding several years ago,

5   that annual funding.

6             So it would be our plan to present to our Commission,

7   anyway, for acceptance, if you were going to proceed with that,

8   that it be 100 percent funded by those that were actually going

9   to undergo the conversion, the residents that were actually

10   going to undergo the conversion.  I can't speak, because I did

11   not have any responses that I saw, from the other member

12   utilities of the same thing, how they were cost sharing and

13   their experience was.

14             MS. HELTON:  Mr. Shaffer, thank you very much for

15   coming today.  Thank you also for gathering information from

16   your sister municipal utilities.  It was very helpful.

17             MR. SHAFFER:  Thank you very much.

18             MS. HELTON:  Next we are going to hear from Paul

19   Davis with Tampa Electric.

20             MR. DAVIS:  Good afternoon.  Again, my name is Paul

21   Davis.  I am Director of the Energy Control Center at Tampa

22   Electric Company.  My presentation is somewhat brief.  I'm

23   going try to cover a summary of our 2004 and '05 storms, our

24   restoration process that we go through, our vegetation

25   management program, and the pole inspection, since that was an

FLORIDA PUBLIC SERVICE COMMISSION

235

1   area that staff zeroed in on on the questions, and mitigation

2   options.

3             Before we move to the next slide, actually you can go

4   ahead -- before we move to the next slide, I want to talk a

5   little bit about an overview of Tampa Electric Company.  We

6   have about 650,000 customers, around 10,500 miles of

7   distribution wire, about 1,200 miles of transmission lines, and

8   about 240,000 distribution poles, about 23,000 transmission

9   poles, of which 75 percent are wood and the balance are either

10   concrete or steel.

11             One interesting note about our distribution system is

12   that approximately 75 percent of it is overhead and

13   approximately 25 percent is underground.  As far as

14   installation goes, it is just the opposite way around, about 25

15   percent is being installed overhead and about 75 percent is

16   being installed underground.

17             A quick overview of our system also.  We design our

18   entire system to NESC Grade B, always have done that, and we

19   also adopted a concrete pole standard for relocation and new

20   construction in the early 1990s.

21             You have seen this slide before.  This is the

22   hurricane paths.  It's kind of well-worn.  Charley affected our

23   Polk County service area.  It took out around 95 percent of the

24   customers in that county that are in our service area.  We had

25   some damage in southeastern Hillsborough County in the Mulberry

FLORIDA PUBLIC SERVICE COMMISSION

236

1   area.  With Frances it was a long slow storm, we had

2   significant damage.  We had about -- in excess of 200,000

3   customers out, about 40 percent of our system.  With Ivan, we

4   had some residual outer band type issues, but nothing too

5   significant as far as storm.

6             It is interesting to note, though, that while Ivan

7   struck the panhandle the following week, it was very hot in

8   Florida.  There were natural gas issues and some difficulties

9   serving the load.  With Jeanne, which came shortly after, it

10   again affected our entire service area.  It was a little

11   stronger than Frances and, again, we had around 40 percent of

12   our customers out.

13             As we move on, this is just a quick graph of the

14   number of customers that we had out.  I kind of covered a

15   little bit of this.  Ninety percent restoration we reached in

16   three days for Charley, in three days for Frances, and five

17   days for Jeanne.  It's interesting to note that with Jeanne we

18   really had a problem, and really the entire state had an issue

19   where Ivan had just struck the panhandle, a lot of the

20   resources were tied up in Ivan.  And Jeanne, if you recall,

21   Jeanne was going to just skirt the east coast, and it kept

22   getting pushed over farther and farther.  And so it became a

23   real issue for all the IOUs and municipals.

24             What is also interesting to note is that, just to put

25   things in perspective as far as the number of personnel, we

FLORIDA PUBLIC SERVICE COMMISSION

237

1   have about 200 line personnel, 50 contractors, around 150

2   linemen and troublemen.  So you can see the -- and about 150

3   line clearance contractors that normally work for us.  So you

4   can see that we have to ramp up a great deal and rely on the

5   mutual assistance process to do that.

6             And another thing that is important to realize is

7   that when you begin to get a situation where you have got to

8   put into play such a large number of resources -- pardon me one

9   second, let me get a drink of water -- you get into a situation

10   where you really exhaust your normal work management system,

11   and gathering data in a situation like this is very difficult

12   after a storm, because you have to abandon your normal

13   computerized process to restore power.  And when you do that,

14   you are going through a paper system, at least for us we are

15   going through a paper system where we are doing damage

16   assessments, handing that very same paper to the foreign crews

17   that arrive and saying go and find all the problems in addition

18   to all the problems that are on the maps.

19             So as you begin to try to isolate where was that pole

20   that failed, where was that splice that failed, it becomes very

21   difficult to try to pinpoint that down without manually trying

22   to go through and review your entire system.  I just wanted to

23   bring that up very quickly.

24             Highlighting the system damage.  We did have

25   significant restoration and outages as I have alluded to, but

FLORIDA PUBLIC SERVICE COMMISSION

238

1   all in all, as also I failed to mention, we did submit

2   responses to the direct questions.  So I could kind of try to

3   hit the highlights in this presentation, but overall, we had a

4   very low failure rate as the other utilities have alluded to.

5   We also experienced minor substation damages.  In Charley we

6   had three substations which comprised 1.3 percent of our

7   system.  In Frances we had two.  One was partially submerged.

8   When Frances exited the Gulf, it began to get a little more

9   strength as it was headed up towards the panhandle, and the

10   southwest storm surge began to effect some of our distribution

11   subs, and we had a partially submerged sub.  And in Jeanne we

12   lost one transmission auto transformer and some transmission

13   breakers.  But all in all our substations fared fairly well.

14   And I want to highlight that in 2005, again, we were affected

15   in a minor way from the outer bands of Dennis and Katrina and

16   Wilma.

17             Very quickly, some of the highlights on mutual

18   assistance.  It has been talked about.  We rely on it greatly.

19   As you can see from the numbers, we rely on getting a lot of

20   folks down here.  And the agreements and the relationships that

21   we built with folks in the southeast, and then the new

22   relationships we have had to build with even those farther has

23   helped us.

24             The post-storm sweep.  In some of the questions there

25   were questions about a post-storm sweep.  We viewed the

FLORIDA PUBLIC SERVICE COMMISSION

239

1   post-storm sweep as the direct question was was there a

2   post-restoration sweep.  We did not have the type of damage

3   across our system that we felt like we had to go and do a

4   post-restoration sweep.  We did do a post-storm sweep in that

5   we dedicated our field engineers out there to go pole-by-pole

6   and down to every service to determine where the damage was and

7   they marked those up on the maps.

8             There was also some questions about standards.  As a

9   result of our experience in 2004, we also beefed up our

10   inventory and substantially raised the number of associated

11   storm equipment that we needed to have in place.  All of those

12   materials were approved ahead of time to meet the NESC

13   standards, so there were no as-available type issues with the

14   restoration process.  And we had done that in -- I mentioned

15   that we beefed it up in 2005, but even with our 2004 response

16   we were able to get adequate supplies and inventory in place to

17   where inventory was never an issue for us.

18             Another issue I wanted to highlight real quick that

19   was in the questions was about temporary repairs.  As far as

20   temporary repairs go, a part of our restoration process is that

21   we assign a Tampa Electric person for every two or three crews.

22   And as that Tampa Electric typically lineman is riding around

23   with those crews, he is looking to make sure that they are

24   making permanent repairs and not temporary repairs.  If

25   temporary repairs are made, then it is documented in our work

FLORIDA PUBLIC SERVICE COMMISSION

240

1   management system so that our own crews can follow up later.

2   But all in all very, very few temporary repairs were made, and

3   all the material that the linemen, the foreign crews were using

4   were coming out of our storage facility.

5             One of the processes and changes that we made through

6   our lessons learned was that with Charley, and it was a fairly

7   strong storm, we adopted a reclosing scheme to where we

8   disabled our normal reclosing scheme that we used day-to-day

9   for storms, and we disabled that so that as the storms begin to

10   move through the system, if something took a line out, it

11   became de-energized.  So, as more and more problems occurred,

12   as trees fell over the wires weren't burning together and

13   burning in the clear and causing more damage.  We found that

14   that worked very well for Charley.  It was a Cat 2 by the time

15   it came through Polk County.  Even though we lost the majority

16   of our customers, we found that we were able to quickly assess

17   where the problems were, get the issues cleared up, and to have

18   a fairly quick restoration time.

19             With Frances, since it worked well with Charley, we

20   approached the same type of reclosing scheme for Frances.

21   Frances was a Cat 1 storm as it came through Hillsborough

22   County and parts of Polk County, and we found that it didn't

23   work as well.  Because we had such widespread outages, we found

24   that there were a lot of circuits that had very minimal damage,

25   and it slowed the restoration process a little bit in trying to

FLORIDA PUBLIC SERVICE COMMISSION

241

1   determine and find where all the problems were.  Those are

2   lessons learned.

3             When we came to Jeanne, we reinstituted the reclosing

4   scheme, and even though Jeanne was a slightly stronger storm,

5   we just had a slightly few more customers out.  And my belief

6   is that if we had disabled that reclosing scheme, we would have

7   had more customers out and a tougher time.

8             I want to go ahead and move to the text one.  I want

9   to talk a little bit about vegetation management and pole

10   inspection, our annual program.  First of all, with vegetation

11   management, our transmission program, we annually inspect our

12   entire transmission system.  That complies with the balloted

13   NERC standard that is being proposed.  On our distribution

14   system, it's a reliability-based program where we take the

15   circuit performance on a circuit-by-circuit basis, and we run

16   that through a formula that is comprised of SAIDI, MAIFI,

17   tree-related outages, and the time since it has last been

18   trimmed, and that allows us to focus in on the worst performing

19   circuits and get those cleared up so that we have a better

20   overall SAIDI day-to-day.

21             On our annual pole inspection program we have a

22   ten-year pole inspection program, and there's two programs;

23   there is a transmission program and a distribution program.

24   The ten-year distribution program is a full excavation around

25   the pole, sound and boring test, and then any sort of

FLORIDA PUBLIC SERVICE COMMISSION

242

1   remediation that has to happen with the pole.  In some cases we

2   determine that those need to be replaced, and they are

3   replaced.  In others we can brace those, and then when we brace

4   them they are braced to a standard that is -- or at least to a

5   strength that is higher than the original pole installation.

6             And our ten-year program is comprised -- if you have

7   questions about that program, T.J. can probably speak to more

8   of the details, but it includes climbing and aerial and a

9   number of other types of inspections for our transmission

10   system.

11             Our storm response.  As far as our annual -- our

12   storm response is part of our vegetation and pole inspection.

13   Our storm response for pole inspection is not as comprehensive

14   as our ten-year program.  We are looking for structural

15   problems with the pole.  We are looking at all the hardware on

16   the pole.  Broken cross arms, broken braces, blown pieces of

17   equipment like lightning arrestors and things like that.  We

18   are looking at what may be causing the outage and what may

19   potentially cause an outage later, and we are identifying those

20   issues.

21             The storm response crews, especially with the line

22   clearance storm response, those folks are looking to cut the

23   vegetation in the clear.  And our typical annual program, we

24   usually get about ten feet of clearness on our distribution

25   system.  These folks that are down here on storm response don't

FLORIDA PUBLIC SERVICE COMMISSION

243

1   have the mulching equipment, they don't have a means to dispose

2   of the vegetation.  Those folks are cutting enough to get the

3   wire back up, and if there are issues where the circuit has got

4   issues, we are taking that input from those foreign crews and

5   addressing that in our annual program.  But their main focus is

6   to trim enough to get the wires back up.

7             Potential mitigation options.  We have kind of

8   covered some of these that we have already put into play, the

9   inventory, the system enhancements, the maintenance practices.

10   One of the things that we realized this past year, in our 2004

11   and '05 performance of our annual reliability, and also we

12   realized from our storm was that we needed to increase our

13   maintenance practices.  We increased our vegetation management

14   program by 5.5 million.  We are nearly doubling our substation

15   preventative maintenance program.  We are taking a number of

16   steps to increase maintenance that I think is going to both

17   help us in our day-to-day reliability and also help us with

18   these storm issues.

19             You know, I don't want to belabor some of the same

20   points, but vegetation management is an issue.  We need to find

21   a way to work cooperatively with the municipalities that we

22   serve, with the counties that we serve to get the adequate

23   clearance.  We do things in somewhat of a permissive fashion in

24   our annual program.  We go door-to-door, we hang door hangers,

25   we ask people to call us if they have issues, and then we work

FLORIDA PUBLIC SERVICE COMMISSION

244

1   with customers to the best of your ability to allow us to get

2   the trimming that we need.  And more legislation to make that a

3   little stronger can certainly help.

4             And then some of the same options that have been

5   brought up, undergrounding standards.  I'll answer one of the

6   questions that I know Bob is going to ask already about

7   universities.  One of the studies that we participated with the

8   University of South Florida was undergrounding, doing a

9   retrofit undergrounding of our Davis Island, which is just

10   south of downtown.  We participated with USF and with the local

11   community to come up with a cost estimate to do that.  So we do

12   participate with both the local community and universities

13   where we can.

14             And that pretty much concludes what I had on the

15   formal part of the presentation.

16             MR. TRAPP:  You got two of them, but I've got a

17   surprise one for you.  Were you here when David McDonald made

18   his presentation.

19             MR. DAVIS:  Yes, sir.

20             MR. TRAPP:  Do you remember the chart he put up about

21   Pinellas County and the projected title effects.  Have you done

22   anything similar to the Tampa Bay area.

23             MR. DAVIS:  I have looked at the FEMA maps.  And from

24   what I recall, the same issues apply in the Tampa Bay area,

25   especially with the way the Tampa Bay area is configured.  If a

FLORIDA PUBLIC SERVICE COMMISSION

245

1   hurricane like Charley was headed or were to come right up the

2   mouth of Tampa Bay, it pushes the water up into Tampa Bay.  And

3   Davis Island, for instance, would be one of the areas that

4   would be completely submerged.  A lot of the inner bay area, if

5   you are familiar with Tampa south of Kennedy, that area would

6   be submerged, especially for lower level hurricanes.  All along

7   the Rocky Point town and country area of Tampa would be

8   submerged, along the eastern Apollo Beach area.  It would

9   inundate quite a bit of Hillsborough County.

10             MR. TRAPP:  How many areas within Tampa's service

11   area might not be affected by floods and might be candidates

12   for underground zones?

13             MR. DAVIS:  Well, I think that is best answered by

14   pulling up that storm surge, the slosh model that wet

15   forecasters have put up, and we can certainly supply that so

16   that you can see the percentage of the system.

17             MR. TRAPP:  Is that model generally applicable for

18   the state as a whole?

19             MR. DAVIS:  I'm not a meteorologist, but I have seen

20   certain key urban areas modeled, like Pinellas County, like

21   Hillsborough County.

22             MR. TRAPP:  The reason I asked is I missed my

23   opportunity to specifically ask Florida Power and Light this

24   question, and maybe I can invite them to give me some input

25   with respect to the result of that model on what areas would be

FLORIDA PUBLIC SERVICE COMMISSION

246

1   affected by tidal surges, by category of storm as Progress has

2   so adequately provided.

3             Thank you.

4             MR. DAVIS:  Sure.

5             MS. HELTON:  Mr. Ballinger.

6             MR. BALLINGER:  We have got one.  Actually it's two

7   questions.  Did you say balloted NERC standards?

8             MR. DAVIS:  Yes.

9             MR. BALLINGER:  And I presume balloted means the NERC

10   standards go through a voting process of its members, that is

11   what you meant by that?

12             MR. DAVIS:  That's correct.

13             MR. BALLINGER:  And when you do your pole

14   inspections, how do you keep track of the status of each pole

15   inspection over the ten-year period?  Is there some kind of a

16   tracking thing, and is that available?

17             MR. DAVIS:  There is a data base of information that

18   we keep track of when the poles are inspected.  We typically

19   contract that out to a contractor who specializes in that, but

20   we keep a database of all the poles, what was found.  And then

21   the poles that have to be remediated especially by Tampa

22   Electric crews, as in pole replacements, those enter our work

23   management system, we categorize those into two areas, poles

24   that immediately need to be replaced and those that have a

25   six-month to a year time frame.

FLORIDA PUBLIC SERVICE COMMISSION

247

1             MR. BREMAN:  Just to do a little follow-up on the

2   pole location information.  Do you have -- in your asset

3   management database you have pole specific information on 100

4   percent of your poles?

5             MR. DAVIS:  Yes.

6             MR. BREMAN:  And all that data is tracked.  Does that

7   information also include your collocation issues?

8             MR. DAVIS:  No.  No, it does not.  The collocation

9   issues, periodically we conduct pole audits.  As was mentioned

10   by previous speakers, the main purpose up until now has been to

11   identify situations where there have been unauthorized

12   attachments and collect the revenues for those, so we do have

13   pole audit data from previous years.  We typically do that

14   every three to five years.  Did that answer your question about

15   whether or not we have the data?

16             MR. BREMAN:  Yes.  I was curious about it.  I was

17   just wondering how close you were to the 20 percent of people

18   attaching to your poles and you don't know about it.

19             MR. DAVIS:  I'm not sure about that data.  I'm not

20   sure if Regan has an answer to that.

21             MR. HAINES:  The 20 percent number is something I

22   really can't validate.  We would have to go back and look at

23   data and probably have to go through a new pole audit to

24   specifically look at what percentage are unauthorized, or go

25   back to the last one, which is about three years ago, to see

FLORIDA PUBLIC SERVICE COMMISSION

248

1   what that number was.

2             MR. BREMAN:  Do you take these people to court or

3   what?

4             MR. HAINES:  No.  Usually we go ahead and work out

5   the issues with the joint users.

6             MR. BREMAN:  Thank you.

7             MR. McNULTY:  I have a question that has to do with

8   the inspection program, the ten-year inspection program that,

9   as you mentioned, is pretty complete, and you have a database

10   behind that.  So I guess what I'm wondering is is there some

11   things that the company has found about specific subpopulations

12   of poles that would lead them to indicate that either in the

13   past they have decided to replace a certain type of pole of a

14   certain vintage, or a certain type, say a creosote pole,

15   anything along those lines, that you have learned from this

16   database that said, you know, it is cost-effective, the smart

17   thing to do to replace a certain type of pole?

18             MR. DAVIS:  Well, you just reminded me of an answer

19   that I answered incorrectly about every pole.  Let me qualify

20   that.  It just occurred to me that we generally are targeting

21   CCA poles that are greater than 20 years old, because CCA poles

22   have a very long life expectancy.  So we are looking at the

23   installation date of the pole.  And if it is less than 20

24   years, we are not inspecting those because we have found that

25   there is really no reason to inspect those.  So we are looking

FLORIDA PUBLIC SERVICE COMMISSION

249

1   at CCA poles that are older than 20 years old.  We are looking

2   at creosote poles and the various poles that we target, the

3   other types of poles, wood poles that we have on our system.

4   And what we have found from that is that the types of failure

5   rates, and I don't have the numbers here with me offhand, but

6   the types of failure rates do justify us to continue with a

7   ten-year cycle.  We have found that that seems to be the best

8   frequency, based on what we are finding as far as failures due

9   to rot and decay of the pole.

10             MR. McNULTY:  Okay.  And is there a specific type of

11   pole that you found that just didn't pass muster and needs to

12   be replaced, or a certain year, a certain vintage, anything

13   along those lines of a decision made from that review of that

14   data?

15             MR. DAVIS:  Not that I am aware of.

16             MR. McNULTY:  And when you say you have a ten-year

17   inspection cycle, that's a ten-year inspection cycle of just

18   those poles that are older than 20 years old?

19             MR. DAVIS:  Right.  And those new poles that have

20   entered into the time frame where they are older than 20 years

21   old.

22             MR. McNULTY:  Thank you.

23             MS. HELTON:  Thank you, Mr. Davis.

24             MR. DAVIS:  You're welcome.

25             MS. HELTON:  We are ready to move on now to Christie

FLORIDA PUBLIC SERVICE COMMISSION

250

1   Miree with Gulf Power.

2             MS. MIREE:  Good afternoon.  My name is Christie

3   Miree.  I am the Power Delivery Services Manager at Gulf Power

4   Company, and I would just like to start by saying that we

5   really appreciate the opportunity to come here today and to

6   participate in this worthwhile workshop.  And we look forward

7   to the continuing sharing of information between all of the

8   parties and hope to improve our processes going forward.

9             I'll give you a little bit of background about Gulf

10   Power.  Our size, we serve about 400,000 customers, and our

11   service area ranges from the Alabama state line on the west

12   over to the Apalachicola River on the east.  So we serve

13   basically the panhandle of Florida, and most of our customers

14   are in coastal areas that are subject to storm surge and salt

15   water intrusion.

16             We are part of the Southern Company.  Even though we

17   are a Florida utility, we do have the benefit of learning from

18   the experience of the other Southern Company utilities, and we

19   do have the benefit of their assistance when we are impacted by

20   a storm.  We are a relatively small company, so having other

21   companies to draw upon for resources when we are impacted so

22   heavily has been be a great benefit to us.

23             As part of the Southern Company, we also have a

24   communication division, the Southern Link, which has provided

25   us communications at a time when those are often hard to come

FLORIDA PUBLIC SERVICE COMMISSION

251

1   by.  So the wireless affiliation has been a benefit that we

2   have seen, as well.

3             As part of the service area, being in the Florida

4   panhandle, one of the benefits is that we do have access, which

5   is a little bit easier than some of the south Florida

6   utilities, where we are accessible from the north and the west

7   as well as the east.  And this aids not only in the evacuation

8   of our customers, but also in moving crews and materials and

9   other resources in to assist us.

10             A little bit about what we experienced in the '04 and

11   the '05 season.  Our system, as I mentioned, serves about

12   400,000 customers.  We have about 1,600 miles of transmission

13   lines, 7,200 miles of distribution lines, and about 20 percent

14   of our distribution system is underground.  We have about 126

15   substations, and within our distribution system we have about

16   250,000 distribution poles.

17             Some of the damage that we saw during Hurricane Ivan,

18   and primarily our area was impacted by Hurricanes Ivan and

19   Dennis.  We did experience some other storms.  We experienced

20   tropical storm force winds from Hurricane Katrina, we also had

21   several other minor tropical storms, Arlene and Cindy to name a

22   couple, but I'm primarily going to focus on Ivan and Dennis.

23   Ivan was part of the '04 season, Dennis was part of '05.  Ivan

24   was a much larger storm and much more widespread.  Dennis was a

25   very strong storm, but it was very compact, and so the amount

FLORIDA PUBLIC SERVICE COMMISSION

252

1   of damage was much more localized.

2             During Hurricane Ivan, we had about 1.6 percent of

3   our distribution poles were damaged.  During Dennis it was less

4   than one-half of a percent, about .3 percent.  And, as I

5   mentioned, Dennis was just a much more compact storm.  It was

6   very strong in the area of impact, but just a much smaller

7   width.

8             I have a few slides that may demonstrate a little bit

9   of the damage that we saw to kind of give you an impact.

10   Several of the other speakers have mentioned that they

11   primarily saw a wind impact from their storms.  We experienced

12   both impact from the winds, hurricane force winds, and the

13   storm surge.  And the storm surge impact was very substantial

14   to our underground system along the coast.  So I have just a

15   few slides to show a little bit of the storm surge impact on

16   the underground system.

17             Most of what we saw, the damage was caused by wind,

18   but primarily the debris and the trees that were toppled from

19   the wind, so a lot of the damage was from the debris that was

20   encompassed within the wind.  When we talk about the

21   underground and the damage to the underground system, as you

22   will see in some of our slides, the storm surge is part of it,

23   but there is also a great deal of the damage that can occur to

24   the underground system after the storm when we begin the debris

25   removal process.

FLORIDA PUBLIC SERVICE COMMISSION

253

1             As you are all aware, after the impact there is so

2   much debris on the side of the roads.  Homeowners are trying to

3   restore their lives back to normal.  And those large debris

4   piles of vegetation and just construction debris often cover up

5   our underground system.  So as the removers come through to

6   take that away, they may accidentally take our pad-mounted

7   transformers and other switch gear along with it.

8             In this area, you can see the area that's circled is

9   a cable-crossing pole and a regulator station.  The water at

10   the bottom of the picture is actually on the sound side, so

11   this is in the protected waters, and the line of our coastline

12   changed by probably 50 feet here.  You may also notice in the

13   background along the road we do have several of our

14   distribution poles that are still standing.  And at the very

15   top, under the word Navarre, you may notice a little path

16   between the condominiums there.  In one way that path allows

17   the storm surge to come through and provide additional damage

18   to the system, but in another way the condominiums somewhat

19   protected the poles that are still standing.  So it is hard to

20   say exactly which methodology provided the greatest amount of

21   protection in this particular situation since both of our

22   systems did sustain damage.

23             And also, you may note, at the top of that picture

24   there is a construction trailer.  That is one of the things we

25   would classify as debris that is floating around, or being

FLORIDA PUBLIC SERVICE COMMISSION

254

1   blown around in the midst of the storm that can cause a great

2   deal of damage to both an overhead and underground system.

3             This is an area where we try to use buildings and

4   other natural structures to product our underground equipment

5   as best we can.  But as you can see here, even though the

6   pad-mounted equipment was protected by a building, it still

7   suffered substantial damage.  We also have beach construction

8   where we use a lot of stainless steel equipment in the beach.

9   But even with the stainless steel construction, there is

10   substantial damage to that equipment.

11             This is a pad-mounted switch gear that serves a

12   condominium on the beach in Pensacola.  And this particular

13   condominium was expanding, was building two additional towers,

14   so they had very large cranes on top of the condos at the time

15   the storm came through.  I believe this was Dennis.  And one of

16   the cranes came down as part of the storm and landed on top of

17   our switch gear.  So this was tremendous damage that I don't

18   think there is any amount of hardening that would have

19   protected the equipment from a large crane falling on top of

20   it.

21             This is another one of our underground switch gear

22   cabinets located out on the beach.  This was completely covered

23   with sand.  So our first challenge was to find the equipment,

24   and once you find it, determine if it is still intact.  And if

25   it is intact, we have to pump the sand out of it, also pump the

FLORIDA PUBLIC SERVICE COMMISSION

255

1   salt water out of it and make any additional repairs.  As you

2   can imagine, when the beach roads are completely covered with

3   sand and you have bulldozers trying to clear the roads as

4   quickly as possible, there can be a great deal of damage to the

5   underground equipment that is buried underneath all of that

6   sand.

7             This is on Pensacola Beach.  And one of the things

8   that works somewhat to our advantage in this area is that we do

9   have a very sandy soil.  We are not on a coral base, or a rock

10   base.  And so in this case you can see there is a tremendous

11   amount of the debris in the road, but many of the poles,

12   because of the sandy soil conditions, would lean rather than

13   snap.  And this would allow us to be able to repair those

14   facilities much quicker than had they been underground or had

15   been located in a different type of soil condition.

16             This also demonstrates another important aspect of

17   the Gulf Power service area in that primarily all of our system

18   is located on road right-of-way, and very little rear lot

19   system.  This, in one hand, can cause us challenges when we

20   talk about vegetation management in only being allowed to trim

21   what is on the road right-of-way, but on the other hand it does

22   provide us a great ease of access and the ability to quickly

23   get to those facilities with bucket trucks and repair that in a

24   timely fashion.  And, as I mentioned, on the beach we do also

25   have stainless steel construction and beach construction in

FLORIDA PUBLIC SERVICE COMMISSION

256

1   this area.

2             One of the others problems that we encounter in this

3   situation is traffic control.  You know, as soon as the storm

4   has passed, many of the customers are trying to return to their

5   homes or trying to survey the damage in the area, and so

6   traffic control becomes an issue for us, especially when you

7   are dealing with facilities that are on road right-of-way.

8             As I mentioned earlier, the underground facilities

9   can often be covered by the debris that is along the roads and

10   streets in our communities.  Here, this is an overhead system

11   that we are still able to reach by bucket truck, but we could

12   have tremendous trouble restoring service here, had this been

13   underground and we were trying to get to it.

14             I just wanted to demonstrate with this one.  This

15   house was heavily impacted by the storm surge.  And if you

16   notice the roof line and the trees in the background, there is

17   very little wind damage, but the amount of surge damage to this

18   home and to the equipment and facilities near this was just

19   tremendous.  Most of the debris that you see in the front yard

20   actually washed through the house from the water side and came

21   into the front yard.

22             This is a photo out on Pensacola Beach, and that is

23   what is left of the road and our underground facilities that

24   were out there.  You can see at the top left corner of the

25   picture the remains of the road bed.  This was during Hurricane

FLORIDA PUBLIC SERVICE COMMISSION

257

1   Ivan.  And repairs had begun at the time Dennis hit and,

2   unfortunately, what had been repaired was again left in this

3   condition after Dennis, and it still looks like that today.

4             We have a person there to give you a scale of what

5   the impact is to the road and the infrastructure in that area.

6   Here is an example of some pad-mounted equipment that although

7   survived the storm, there is a significant amount of erosion

8   that occurred that has to be repaired following the storm.

9             Also, I have just a couple of maps to illustrate the

10   severity of the storm and some of the storm surge that we saw

11   in our service area.  This was Hurricane Ivan, and it's a

12   little difficult to see with the cover on the monitor, but we

13   had substantial winds.  And you can tell from the path that

14   once it makes impact, they died off significantly, but still

15   caused a great deal of damage in our area.

16             We were trying to illustrate here some of the areas

17   that are susceptible to storm surge and flooding in our service

18   area, which is predominately our entire service area.

19             What we did prior to this hurricane season.  Each

20   year following a hurricane season, hopefully we don't always

21   have a storm to do a post-critique on, but we do reevaluate our

22   storm plan each and every year, most especially in a year where

23   we have had to react in some way.  But not only do we try to

24   learn from the storms that impact our area, we also attempt to

25   learn from storms that impact other areas.  When we provide

FLORIDA PUBLIC SERVICE COMMISSION

258

1   assistance to other South Florida utilities, or Mississippi or

2   Louisiana utilities, we try to take away lessons learned and

3   provide a critique process for those storms, as well.

4             And as I mentioned, as being a part of Southern

5   Company, we do have the benefit of learning from what our

6   sister companies experience.  And this year, most notably it

7   was Hurricane Katrina and the dramatic impact on the

8   Mississippi and Alabama coast.  So we also were able to take

9   away some very powerful lessons learned from those critique

10   processes.

11             Before the season starts, we go through a rigorous

12   process of updating all the information on the employees in the

13   system, so that as we begin our storm assignments, we know we

14   have got accurate updated information and that we can contact

15   all of our employees in the event of a storm.

16             The storm assignments are communicated early in the

17   spring.  At that time we generate new maps and make sure that

18   those are dispatched ahead of time and ready to go in the event

19   we need those.

20             We also begin preparing storm kits for each

21   substation, gathering material that would be part of those

22   storm kits.  We ensure that we have adequate material for the

23   system, and we often compare our previous usage from storms.

24   Ivan in the past, what type of material usage we had during

25   Ivan so we know kind of how to gauge what we are about to face,

FLORIDA PUBLIC SERVICE COMMISSION

259

1   based on the size and the scale of the storm that is impending.

2             We also begin negotiating and confirming contracts

3   with vendors, tree and overhead line contractors, logistics

4   vendors.  We learned a great deal about logistics as a result

5   of Ivan.  There was a tremendous impact to the city's

6   infrastructure.  Not only the roads and bridges, but the hotels

7   and the condominiums that were in the area.  And so from that

8   we were forced to do a lot of non-traditional things in the

9   aftermath of Ivan with regards to how we house and care for the

10   people that provide us assistance.  So going into this year, we

11   were able to take a lot of those lessons learned, have those

12   contracts in place ahead of time.  We learned a lot about where

13   to stage some of those vendors in advance of the storm.

14             As you probably recall seeing some very graphic

15   photos of the I-10 bridge which was in the bay following Ivan,

16   that cut off our pathway to the east and made it very difficult

17   for us to bring crews from the east.  You may also remember

18   that most of those crews were in south Florida working

19   Hurricane Charley at that time.  So most everybody we were

20   going to be bringing in was coming from the east, and that

21   presented some tremendous challenges for us.  So a lot of

22   lessons learned about where we need to stage, and if we had

23   those types of issues again how we would respond.

24             We always try to plan for the worst case, especially

25   after Ivan when we felt we had experienced the worst case,

FLORIDA PUBLIC SERVICE COMMISSION

260

1   because it is much easier for us to scale back after the fact,

2   but we go into it assuming the worst.

3             What we did.  As the storm was approaching, as I

4   mentioned, we worked with our vendors to ensure we have

5   adequate amounts of material.  Many of vendors now we provide

6   with our internal communications, our radios, Southern Link

7   radios, because that has proven to be a very reliable

8   communication tool for us.  So ensuring that our vendors have

9   those radios as well has helped tremendously.

10             I mentioned the food, the lodging, the staging of

11   materials, and lodging vendors.  Because of the tremendous

12   damage to our infrastructure, we have used a lot of tents and

13   nonconventional housing.  And there is a lot of equipment that

14   goes with erecting a tent city, so staging of that equipment

15   before the storm.  Also, immediately before the storm we begin

16   communicating a great deal with our customers and our local and

17   state officials.  We want to make sure that our customers

18   understand what they are facing and encourage people to

19   evacuate as much as possible, but also what the duration of the

20   outages may potentially be, given the level of the storm.

21             We also begin talking within the Southeastern

22   Electric Exchange on mutual assistance agreements and acquiring

23   resources from as many diverse areas as possible.  It was very,

24   very interesting for us, and we were very proud that following

25   Hurricane Ivan we experienced our highest customer satisfaction

FLORIDA PUBLIC SERVICE COMMISSION

261

1   ratings ever, and we are very proud of that fact, and it made

2   us feel like in spite of some tremendous challenges that we had

3   done some things right throughout that restoration.  And so we

4   have tried to capitalize on what we did right and learn from

5   what we could do better and continue to refine and improve our

6   processes from year to year.

7             Post-storm.  One of the things -- to talk a little

8   bit about our restoration process, we have a very decentralized

9   restoration process.  We utilize a lot of the same people in

10   key storm roles from year to year so that there is some

11   stability.  They know their role, they know what's expected,

12   and they are not waiting to hear from the corporate office once

13   the storm impacts to know what to do.  They begin restoration

14   immediately.  And to the extent they have resources and

15   materials there, which we do stage in advance, they are able to

16   start restoration many times before the storm may have passed

17   through one part of our area.  For instance, a storm that would

18   make landfall in the Pensacola area, the Panama City to the far

19   east may be able to proceed with restoration while we are still

20   being heavily impacted.  And so they do proceed in that area

21   and start restoring service and going about the method of just

22   getting the lights back on as quickly as possible.

23             A little bit about the post-storm sweeps.  The sweeps

24   that we do after a storm, we do sweeps to determine damage

25   assessment, which is the initial post-storm sweep.  The

FLORIDA PUBLIC SERVICE COMMISSION

262

1   post-restoration sweep that Paul mentioned, those are done more

2   on an as-needed basis based on the input from our field

3   employees who are in charge of the restoration effort.  We make

4   a determination if those types of sweeps are needed, but they

5   have a much different focus from our routine pole maintenance

6   inspections.  These are looking more at damage to the

7   facilities that were caused by the storm versus overall

8   maintenance of the pole and the pole hardware.

9             Go ahead and click to the link.  Some of the things

10   that we are looking at when we go through the post-storm

11   sweeps, we are looking at the number of poles that are down, if

12   there's conductors that are still down or low hanging, if there

13   is damage to any of the equipment or the lights on the pole, if

14   there is damage to the guy wires.  This isn't a below ground

15   sound and boring testing, it is not that type of sweep.

16             What about the future?  We have talked an awful lot

17   about underground today, and we have heard people mention the

18   need to listen to our customers and communicate with them about

19   options that are available for undergrounding.  And we have

20   done that in the past.  We have a series of books that are

21   available to our customers that we use on a regular basis to

22   communicate with them about options for going underground.

23   There is a tremendous amount of activity in our service area

24   right now where certain areas have elected to convert their

25   systems from overhead to underground, and we are working with

FLORIDA PUBLIC SERVICE COMMISSION

263

1   each and every one of those customers to come with up with what

2   the best options are for them.

3             We do have a department that focused strictly on

4   underground conversions.  And as I said, they are very busy.

5   And there are a lot of pros and cons to underground.  It is not

6   the silver bullet that we would all love for it to be, as you

7   can see from the photos that I showed earlier.  And in many

8   cases the underground facilities that are exposed to storm

9   surge are very vulnerable and can experience a tremendous

10   amount of devastation.  And when that occurs, the outages are

11   going to be much longer and much more expensive do repair.

12   However, we do have that as an option for customers that wish

13   to pursue that.

14             One of the other things that we are looking at in the

15   future is a lot of discussion about vegetation management.

16   Most of our vegetation outages that occurred throughout the

17   storm were from trees that were off road right-of-way.  We do

18   have outages that are also from trees within the right-of-way,

19   but an enormous number of outages are from those that are

20   outside of our control or that would not be trimmed within our

21   normal vegetation trimming process.  And we can work and do

22   work with the public to try to educate them more about what

23   types of vegetation are most favorable to plant in and around

24   our facilities.

25             Our specifications, which has also been discussed a

FLORIDA PUBLIC SERVICE COMMISSION

264

1   great deal today, that is an evolving process.  We are

2   continuously looking at new materials and new ways of doing

3   things, and trying to balance what is the most appropriate

4   decision long-term.  Not strictly storm mitigation or storm

5   restoration, but what is going to provide a cost-effective

6   alternative and a reliable piece of equipment that is going to

7   work on our system long-term, and also try to prevent storm

8   damage as much as possible.  So that is a continual process.

9   We want to make sure that in evaluating new equipment we don't

10   solve one problem and then create two or three additional

11   problems down the road.  So we evaluate those new technologies

12   very carefully, but we look at that continuously.

13             We are getting increased data from our mapping

14   system.  And as we have moved into a GIS mapping system, it has

15   much more capabilities than what we have had in the past.  We

16   have recently converted to that system in the past year, and so

17   we are trying to begin populating that system with increased

18   data that we have not had available to us in the past.

19             Another area that we see in the future are increased

20   areas to improve our damage assessment.  Up until now the focus

21   has always been to go and restore service as quickly as

22   possible, and there has not been the focus on gathering of data

23   of what caused an outage or was it an outage on the underground

24   or the overhead, or where the cause lies.  It has just strictly

25   been try to restore the service safely as quickly as possible

FLORIDA PUBLIC SERVICE COMMISSION

265

1   to the most number of people.  So the kind of data that I know

2   you would like to see today with scatter diagrams is just not

3   available for us yet.  As we have moved into our new systems

4   and we look at new technology and new tools that could be

5   available to us in the future, we would like to move towards

6   gathering more data, to the extent that that data gathering

7   does not hamper the restoration effort.

8             Our focus so far has been on improving -- not so much

9   hardening our system, but improving our restoration process,

10   because that is the piece of this that we feel like we have the

11   greatest amount of control over.  We have total control over

12   how we respond to a system.  We may not have control over

13   mother nature, or what other things are in the community that

14   can impact our system.  And we can harden our system to some

15   degree, but to the extent that the community is not storm

16   hardened, there still is going to be an impact  And we can

17   build a system that will withstand higher wind levels, however,

18   it may not withstand debris that is being blown at those higher

19   wind levels.  So we try to balance the amount of resources that

20   we want to pour into storm hardening, when we know that that is

21   not going to totally protect our system to build it to a higher

22   level.

23             Also, what is in the future.  I have touched a little

24   bit more on vegetation management, what our current practices

25   are with regards to vegetation management, our pole

FLORIDA PUBLIC SERVICE COMMISSION

266

1   inspections, and speak briefly about the NESC, which has been

2   discussed today, and our specifications.  Currently our

3   vegetation work is performed by contractors.  At the time that

4   they clear, they prune based on the current NESC requirements,

5   and the way we gauge our vegetation management program is based

6   on reducing vegetation-related SAIDI, our customer satisfaction

7   ratings.  As there are justified PSC complaints related to tree

8   trimming, we evaluate those, and also public safety and our

9   focus on preventing accidents.

10             For us, we have a reliability-based vegetation

11   management program versus a cycle-based program, much like Paul

12   described at TECO.  We evaluate the reliability of individual

13   feeders.  Our vegetation management team will do an assessment

14   of those feeders each year, and will also incorporate any

15   feedback they have received from customers and our field

16   engineering team to put together a work plan for the following

17   year.

18             Our program has a mix of maintenance pruning and

19   targeted spot pruning.  As I mentioned, those work plans are

20   developed based on our forestry services team along with our

21   reliability data and customer information.  And 100 percent of

22   our transmission system is inspected each year and the

23   hazardous situations that are noticed are corrected.

24             Our distribution pole inspection.  We have

25   approximately 250,000 wooden distribution poles.  We are on a

FLORIDA PUBLIC SERVICE COMMISSION

267

1   ten-year pole inspection cycle.  And we just completed our

2   first ten-year inspection style and have started on the second

3   ten-year cycle in 2003.  All of our poles are inspected using

4   one of the following methods; either visual, sound and bore, or

5   partial or total excavation.  And I would note that on the

6   first ten-year cycle we were inspecting only non-CCA poles at

7   that time.  The second cycle will inspect all poles based on

8   age, location, and previous treatment.

9             Transmission inspection cycle for all transmission

10   poles is 12 years.  We do perform aerial patrols at least four

11   times a year, and every structure on the transmission system is

12   inspected every six years using at least one of the following

13   inspection types that are listed:  Ground, routine aerial

14   patrol, some comprehensive aerial patrols.  I won't go through

15   all of those, but at least every six years one of those is

16   performed.

17             We have also talked about the National Electric

18   Safety Code today, and if we were to increase the code

19   requirements what impact that might have.  I just wanted to

20   make the point that the safety code, the purpose of the safety

21   code is not necessarily to act as a building code for the

22   electrical system, and that it is also not intended to be a

23   design specification for the building code.  So although we may

24   be able to increase the design standards that we build to, that

25   still may not provide the protection that I think we are

FLORIDA PUBLIC SERVICE COMMISSION

268

1   seeking for our system, and that there are other things that

2   are blowing around or washing around in the area that could

3   impact that that a higher design standard may not necessarily

4   protect us from.

5             In closing, I would just like to say that we do learn

6   from every single storm.  And I think that our decentralized

7   restoration process has been a real advantage for us as has our

8   construction that is primarily on road right-of-way and not

9   rear lot lines.  And these things, along with some other

10   factors, have enabled us to respond quickly and effectively in

11   the two major storms that we have seen as part of the last two

12   storm seasons.  We will continue to look for ways to improve as

13   we have in the past, and continue to look at post-storm

14   critiques, both of ours and others and within the industry and

15   try to learn as best we can from those, and incorporate new

16   methodologies, new work practices, and consideration of design

17   changes as we move forward.  This has been a great opportunity

18   for us to share ideas.  We look forward to the continuation of

19   this process and what we can learn from this going forward.

20             Thank you.

21             MR. TRAPP:  I have two.  First, are you Sharon

22   Allbritton's cousin?

23             MS. MIREE:  Yes.

24             MR. TRAPP:  Sharon says hi.  Universities.  Are you

25   using any university data?

FLORIDA PUBLIC SERVICE COMMISSION

269

1             MS. MIREE:  I missed your question.  No, at this time

2   we have not done any collaborative effort with the

3   universities.  Until the past two storm seasons, we have been

4   able to effectively restore service throughout the storms that

5   we have seen, so at this time we have not been doing anything.

6             MR. TRAPP:  Do you have plans in the future?  I mean,

7   do you see a usefulness for the data?

8             MS. MIREE:  We have not looked at that yet, but we

9   are certainly open to that.

10             MR. TRAPP:  Thanks.

11             MR. BALLINGER:  We have one from the audience.  When

12   you track the information you get from your pole inspections,

13   how is that kept in the database, or is that part of your

14   mapping system, too, that you are going to incorporate?

15             MS. MIREE:  It is not part of our mapping system at

16   this time.  That is one of the things that we would like to

17   capture going forward and build a much more comprehensive pole

18   database as part of our mapping system.  But right now that is

19   a very labor intensive manual process.

20             MR. BALLINGER:  Thank you.

21             MR. BREMAN:  You brought out that the NESC is not a

22   design standard.  Do you work with a standards committee that

23   sets design standards for the electric utility industry?

24             MS. MIREE:  We work with -- we have members across

25   Gulf Power and the other Southern Companies that participate in

FLORIDA PUBLIC SERVICE COMMISSION

270

1   many industry committees, if I understood your question

2   correctly, that look at many different things.  Within Gulf, we

3   utilize our own standards and we often build to meet or exceed

4   the NESC requirements.  But as I mentioned, there's different

5   locations within our system that may require the flexibility to

6   provide more than what would you get in a standard design, for

7   instance, on the beach where I mentioned sandy soils and/or

8   beach construction.

9             MR. BREMAN:  So the NESC acts as a minimum standard,

10   and then you build up from there?

11             MS. MIREE:  Yes.

12             MR. BREMAN:  Is there any organized structure to the

13   electric utility industry that seeks to modify the minimum

14   building standards?

15             MS. MIREE:  Not that I am aware of.

16             MR. BREMAN:  Thank you.

17             MR. BALLINGER:  I have one more.  You showed a lot of

18   pictures of damage along the coastline to your underground

19   stuff.  Do these same customers, are they still requesting

20   underground service, even after the destruction?

21             MS. MIREE:  Yes, they are.  Primarily, our

22   underground requests have stemmed around aesthetics and not

23   really protection, storm protection.  And so there is still a

24   lot of activity in that area right now.  And we try to be as

25   forthcoming as we can about the pros and cons of underground,

FLORIDA PUBLIC SERVICE COMMISSION

271

1   especially in a storm surge prone area, and it is ultimately

2   the customer's decision.

3             Thank you.

4             MS. HELTON:  Thank you very much, Ms. Miree.  It has

5   been very informative.  For those of you who have been studying

6   the agenda and see that we have two speakers left and are

7   looking at the clock and wondering how are we going to do it,

8   we are going to finish today.  However, I have been assured by

9   the two remaining speakers that they don't have very long at

10   all, so you can plan your evenings accordingly.

11             Next we will hear from Mark Cutshaw with Florida

12   Public Utilities.

13             MR. CUTSHAW:  Good afternoon.  I do assure you that

14   this won't take long because I anticipated being at this point

15   of the agenda, and I'm sure everybody is wanting to get out, so

16   we will move rather quickly.

17             I am Mark Cutshaw.  I am the General Manager for

18   Florida Public Utilities in our Northeast Florida Division.

19   What I wanted to do quickly is kind of go over a little bit

20   about our company.  Most people are not aware of Florida Public

21   Utilities Company, but we are a small investor-owned electric

22   utility in Florida.  We are that fifth company that most people

23   overlook.  We only have 27,500 customers.  We have two service

24   territories; one is located on Amelia Island north of

25   Jacksonville right at the Florida/Georgia border.  We have

FLORIDA PUBLIC SERVICE COMMISSION

272

1   another service territory in the Florida panhandle centered in

2   Marianna, Florida, which is between Panama City and Dothan,

3   Alabama.

4             So we have two different areas.  And, unfortunately,

5   if a storm hits Florida it probably will affect one or the

6   other of our service territories.  So during the 2004/2005 time

7   period, we did get impacted several times.  As you can imagine,

8   having only 27,000 customers, we are rather small.  We have a

9   limited staff level and limited resources.

10             Even though we were impacted by seven different

11   storms in our service territories, the only major impact was

12   associated with the tornados caused by Hurricane Ivan.  Even

13   though we weren't close to the center of the hurricane, we did

14   have several significant tornados move through our service

15   territory and did a large amount of damage to those areas.

16             Seven storms hit both areas.  We had 74 poles broken.

17   So you can see from that, compared to some of the other stories

18   that you have been hearing, that our damage was minimal.  Out

19   of the 74 poles, 60 of them were associated with the tornados,

20   so we were very, very lucky during the storm seasons that we

21   were not impacted.  Three and a quarter miles of distribution

22   line.  Again, the major cause of that were the tornados during

23   Hurricane Ivan.

24             As we mentioned, we had minimal damage.  We were

25   lucky and we realize that it could have been much worse, given

FLORIDA PUBLIC SERVICE COMMISSION

273

1   the situations of some of the other companies that were

2   directed impacted by the hurricanes.  We did have successful

3   times during this system restoration activity.  We had no

4   problems with our inventory.  We were able to make all the

5   repairs with the inventory on hand.

6             We did have additional manpower from outside the

7   company through mutual assistance agreements and contractors.

8   They were there, they were ready to go to work when the storms

9   occurred, and we were able to make the things happen.

10             On average, most of our customers experienced about a

11   two-day restoration period.  A lot of them had service the same

12   day after the storm passed.  The longest outage was associated

13   with the tornados.  We did have some customers that were out

14   five days.  That was the longest impacted customer we had.

15             We did a little research in preparing for this

16   workshop and looked at some of the questions that were posed to

17   us, and we estimated that about -- I think it's about 30

18   percent of our system doesn't meet our current standards.  They

19   were constructed many, many years ago, but they are out there.

20   And to replace that 30 percent we estimated about $41 million.

21   Our current rate base is about 37.8.  If you look at the damage

22   from the 2004/2005 hurricanes, does it really justify that

23   expenditure?  Probably not, based on our experience.

24             However, if we look at what other companies have

25   experienced, the things that need to be done, yes, we need to

FLORIDA PUBLIC SERVICE COMMISSION

274

1   become a little more proactive and start working towards being

2   able to have those areas replaced, do more hardening on our

3   system.  So we do have a significant step to get to where we

4   would like to be, and we are going to participate.

5             We are the small little brother in this IOU

6   organization.  We do depend on the other companies a lot for

7   assisting us, coaching us, and as you can see by the next

8   slide, we have not done a lot of comprehensive research.  Those

9   people that are familiar with Florida Public Utilities

10   understands our situation.  But we are going to work with the

11   other utilities.  We are involved in different organizations.

12   We are ready to do what we need to do as we move forward.

13             In conclusion, we were lucky during the 2004/2005

14   time period.  We were impacted by several storms, but we feel

15   like based on the preparations that we made, the manpower, the

16   inventory that we had available, our maintenance programs that

17   proved to be quite effective during the impact of the storms,

18   we felt like we were successful.  But we know, just like

19   everybody else, that we can do better and we will be prepared

20   in the future.  Thank you.

21             MR. TRAPP:  Just one.  You said that your estimate

22   was based on an assumption of 30 percent of the existing

23   facilities not meeting current standards, that's because of the

24   grandfathering nature of the code?

25             MR. CUTSHAW:  That's correct.

FLORIDA PUBLIC SERVICE COMMISSION

275

1             MR. TRAPP:  What is your average design criteria,

2   Class C?

3             MR. CUTSHAW:  We build according to what we consider

4   Class C standards.  I know there have been some changes.  We

5   have not updated our standards in the last few years, so we

6   think what we are doing now meets the current standards for

7   Class C.

8             MR. TRAPP:  And if you were to -- based on the same

9   assumptions, if you were to look forward on a replacement basis

10   only, not a retrofit, but just as things needed to be retired,

11   do you have a feel for how that would affect the cost estimate?

12             MR. CUTTING:  I guess we, in talking, looked to do

13   this over a 10 to 15-year time period.

14             MR. TRAPP:  So this assumption is based on a

15   ten-year?

16             MR. CUTSHAW:  That is doing it now.  That is total

17   cost right now in today's dollars, but we would move forward

18   and do it over a 10 to 15-year time period.  And that does

19   include distribution and transmission.

20             MS. HELTON:  Thank you, Mr. Cutshaw.

21             And our last speaker is Michelle Hershel with the

22   Florida Co-op Association.

23             MS. HERSHEL:  Thank you.  I will be much quicker than

24   Mark.

25             I'm Michelle Hershel.  I'm with the Florida Electric

FLORIDA PUBLIC SERVICE COMMISSION

276

1   Cooperative Association, and really I have nothing to add.  I

2   just wanted to tell you all that there are 16 electric

3   distribution co-ops in the state, and they receive their power

4   from two generation and transmission electric cooperatives.

5   All of our co-ops have detailed hurricane plans.  And like the

6   other utilities, we continuously critique our performance and

7   improve our plans, including the plans of our association and

8   our national association to assist with mutual aid.

9             Like the other utilities, we have made significant

10   improvements to our design standards over the years both to

11   minimize damages to our facilities and to expedite the

12   restoration process.  Thank you.

13             You don't have a question, Bob.  (Laughter.)

14             MR. TRAPP:  I have to question for everybody,

15   Michelle.

16             You are representing the rural electric cooperatives,

17   I imagine you have some experiences to share with respect to

18   tree trimming and that type of thing.  You are mostly serving

19   customers in rural areas, which I imagine are highly foliaged.

20   Are there any particular --

21             MS. HERSHEL:  I can get you some specifics.

22             MR. TRAPP:  We'll ask for a late-filed later.  Thank

23   you.

24             MS. HELTON:  Thank you, Ms. Hershel.  I would also

25   like to thank all of the presenters who have come and traveled

FLORIDA PUBLIC SERVICE COMMISSION

277

1   today to Tallahassee.  Everyone who has sat through the

2   audience.  I can't believe we still have this many people in

3   the audience at 5:40 in the afternoon.  I would like to thank

4   all of the staff who have worked so hard in putting this

5   workshop together.  I think it has been very productive, and

6   very informative, and I hope that you all have found it to be

7   so, as well.

8             As Bob and Connie have already mentioned today, we do

9   envision having post-workshop comments being filed.  However,

10   if they are going to be of any use to us in our immediate

11   actions, we need those by no later than next Monday, January

12   30th.  You could provide them to our Clerk's Office, and they

13   will get them to the appropriate staff.

14             As I think either Connie or Bob, or maybe both of

15   them have mentioned, our next immediate action of the staff is

16   to bring to the Commission a recommendation at the

17   February 27th Internal Affairs.  And as they have also

18   mentioned, we hope to give them some recommendations of actions

19   that the Commission can take both on a short-term and a

20   long-term basis.  And you can help us, and you can give us some

21   ideas, or we can be telling the Commissioners without your

22   input.  But we are asking for your input.

23             And, Commissioners, we hope that we have provided for

24   you some meaningful information and some information that will

25   be useful for us to make short-term and long-term goals.

FLORIDA PUBLIC SERVICE COMMISSION

278

1             With that, the workshop is adjourned.

2             (The workshop concluded at 5:41 p.m.)

3

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

279

1

2   STATE OF FLORIDA    )

3                       :              CERTIFICATE OF REPORTER

4   COUNTY OF LEON      )

5

I, JANE FAUROT, RPR, Chief, Office of Hearing

6   Reporter Services, FPSC Division of Commission Clerk and

Administrative Services, do hereby certify that the foregoing

7   proceeding was heard at the time and place herein stated.

8             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

9   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

10   proceedings.

11             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

12   or employee of any of the parties' attorney or counsel

connected with the action, nor am I financially interested in

13   the action.

14             DATED THIS 25th day of January, 2005.

15

16             ___________________________________________

JANE FAUROT, RPR

17                   Official FPSC Hearings Reporter

FPSC Division of Commission Clerk and

18                       Administrative Services

(850) 413-6732

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION