STORM PREPAREDNESS IMPLEMENTATION PLAN

KEYS ENERGY SERVICES - KEY WEST

JUNE 1, 2006

A.	INTRODUCTION:

This report provides responses to specific questions related to ongoing efforts 	of Keys Energy Services (KEYS) to prepare for severe weather events such as 	hurricanes.  Section "A" includes basic information about KEYS and the 2005 	Hurricane Season.

1.	Contact person for clarifications or additional information

Dale Finigan

Director of Engineering/Control Center

1001 James Street

Key West, Florida 33040

Phone (305) 295-1042

Fax (305) 295-1044

Dale.Finigan@KeysEnergy.com

2.	Keys Energy Service

-Municipal Electrical Company

-154 Employees

-27,000 customers

-Service territory - Key West & the Lower Florida Keys

-Entire service area is classified as coastal

3.	Electrical Statistics/System Configuration

-142 MW system load

-83 MW on-island local generation

-8 substations with 35 feeders

-257 miles distribution @ 13.8kV

-60 miles of transmission @ 69 & 138kV

-1 radial line - interconnection to Florida Keys Electric Coop (FKEC)

4.	Historical Information on 2005 hurricane impact to KEYS

Hurricane Dennis - 7/9/05

-Transmission Damage			-minor (10 hr outage)

-Distribution Damage			-moderate

-Outside Support			-60 crew

-95% Customer Restoration Time	-2.4 days

Hurricane Katrina- 8/26/05

-Transmission Damage			-minor (4 hr outage)

-Distribution Damage			-moderate

-Outside Support			-40 crew

-95% Customer Restoration Time	-2.5 days

Hurricane Rita - 9/20/05

-Transmission Damage			-minor (2 hr outage)

-Distribution Damage			-moderate

-Outside Support			-80 crews

-95% Customer Restoration Time	-2 days

Hurricane Wilma - 10/24/05

-Transmission Damage			-minor (18 hr outage)

-Distribution Damage			-moderate

-Outside Support			-120 crews

-95% Customer Restoration Time	-4 days

-Other Comments			-major flooding

B.	Three-Year Vegetation Management Cycle

KEYS currently has a two year cycle that has been in effect for several years.  		We are able to attain this cycle with two of KEYS' in-house crews and three 			Asplundh crews.  KEYS tries to, where possible, maintain clearance of:

1.  -15 feet minimum on transmission lines

2.  -10 feet minimum on all open conductors greater than 600 volts.

3.    -5 feet minimum clearance on all open conductors less than 600 volts.

4.    -3 feet minimum clearance on all covered conductors less than 600 volts.

5.    -3 feet minimum clearance on all communications.

C.	Transmission & Distribution Geographic Information System

KEYS uses an automated GIS System.  The GIS is based on Intergraph's "FRAME" software.  This electric utility application allows KEYS to track all T&D electrical attributes for KEYS' facilities (i. e. pole, transformer, protective devises, capacitors, conductors, anchors, street lights etc).  This data is very carefully maintained for accuracy.  The system is on KEYS' intranet for various departments to utilize.  In addition, all outages are reviewed, evaluated and corrective action is taken as needed.  KEYS also review outage data to identify devices (i. e. fuses, breakers, feeders) that have experienced multiple outages over a defined period of time.  This allows KEYS to identify potential problem areas before the problem becomes more severe.

D.	Wooden Transmission vs. Concrete Transmission Statues

KEYS has no wood transmission poles in our system.  All KEYS' transmission poles are 	concrete (either round or square) or steel.

E.	Post-Storm Data Gathering, Data Restoration and Forensic

After every hurricane, all of KEYS' departments conduct individual sections 				"Debriefing Meeting" to obtain input on recovery efforts.  In addition, KEYS' 				departments also conduct a company wide meeting to analyze the cause and effect 			of the outages and evaluate any change/improvements that can be made.  A more 			detailed summary report is available upon request.  This comprehensive report 			contains:

-Comparison tables of all 2005 storms

-Detail summary reports

-Survey on "Lines Energized Impacts"

-Debriefing meetings/summaries

In addition, KEYS' staff has participated in "Storm Evaluation Sessions" conducted by 		Florida Municipal Power Association (FMPA).  These meeting have enabled KEYS to 			interact with others to obtain "lessons leaned" from these storm restoration efforts.

F.	Audit of Joint Use Pole Attachment

When KEYS receives a request to attach to KEYS' poles, KEYS will perform a stress 			analysis for ones that only involve transmission facilities.  KEYS does not perform a 			detailed stress review for attachment request to KEYS' distribution poles.  If the 			request includes "heavy copper communication" (not fiber) or involves an "angle 			(turn) structure" KEYS will review request in more detail.  Furthermore, KEYS has 			not experienced any significant failures do to pole loading caused by "foreign 				utilities".

G.	Six Year Transmission Inspection Program

KEYS does perform aerial inspections of the top part of KEYS' facilities (electrical 			section) every two years.  The foundation and anchors are inspected every

three - four years.

H.	Collection of Outage Data Differentiating between the Reliability	Performance of Overhead and Underground Systems

KEYS' outage data is recorded by system dispatchers in trouble logs and entered into 		an Excel's spreadsheet.  This database includes the outage duration, number of 			customers affected and outage cause.  Standard reliability indices are then 				calculated for the entire system.  At the end of each month FMPA collects reliability 			indices from all member utilities and publishes a report comparing reliability 				performance.  Each year KEYS' outage records are also sorted by feeder number, 			and standard reliability indices are calculated again for each feeder.  This data is 			then used to identify problematic outage causes and geographic areas affected.  			Appropriate investigation is made through data collection and analysis and 				appropriate corrective action is taken.  KEYS is modifying its reports by separating 			into two categories (overhead and underground distribution).

I.	Coordination with Local Governments

KEYS coordinate all of KEYS' tree removals with the City, County and customers 			before any trees are removed.  Any tree that is removed is either an evasive tree or 			a tree that may cause trouble with KEYS' distribution lines.  Also, the protected trees 		that are in or near our lines, KEYS call for the City to assist in getting proper 				clearances without hurting the tree and to maintain a two year cut back.  KEYS also 			works with the Nature Conservancy removing all evasive trees non indigenous to the 		keys.

b.	With regards to storm preparedness/recover, KEYS are active participants in the 				local Emergency Operations Center (EOC) for both the City and County.  If either 			EOC is activated, a KEYS' representative is stationed at the EOC throughout the 				entire storm/recovery period.  This person provides a direct contact between the 				EOC, other response agencies and KEYS.

c.	KEYS will contact local government facilities agencies about facilities that are 				critical 	and have a need for backup-generation.  KEYS incorporated this into their 			"Priority Restoration Policy".

J.	Collaborations Research through Public Utility Research Center (PURC)

Keys Energy Services (KEYS) participates in PURC activities retailed to storm 				hardening through its membership in the Florida Municipal Power Association 				(FMPA).