E.3.0  Forecast of the City’s Electrical

Demand and Consumption

The City’s forecasts for peak demand and energy requirements are developed utilizing a methodology first employed by the City in 1980, and are updated and revised every year.  The remainder of this section provides details of the methodology used to develop the City’s base case load forecast, and presents the base case load forecast as well as high and low load growth sensitivity cases.

E.3.1  Load Forecast Methodology

The methodology used to develop the load forecast consists of approximately 10 multi-variable linear regression models that are based on detailed examination of the system’s historical growth, usage patterns, and population statistics.  Several key regression formulas utilize econometric variables.

Table E.3-1 presents the econometric-based linear regression forecasting models that are used in the development of the load forecast.  The City uses regression models with the capability of separately predicting commercial customers and consumption by rate sub-class: general service non-demand (GSND), general service demand (GSD), and general service large demand (GSLD).  Along with the residential class, these represent the major classes of the City’s electric customers.  The City also uses two additional regression models to separately predict summer and winter peak demand.  The key explanatory variables used in each of the models are indicated by an “X” on Table E.3-1.

Table E.3-2 documents the City’s internal and external sources for historical and forecast economic, weather, and demographic data.  In conjunction, Tables E.3-1 and E.3-2 summarize the details of the models used to generate the City’s customer, consumption, and seasonal peak load forecasts.  Among the explanatory variables listed is a component included in the models that reflects the acquisition of certain Talquin customers over the study period, consistent with the territorial agreement negotiated between the City and Talquin and approved by the FPSC.

Using the 5 year average of the actual temperature extremes at the times of seasonal peak demands, routinely updating the forecast model coefficients, and incorporating other model refinements have improved the accuracy of the forecast so that it is more consistent with the historical trend of growth in seasonal peak demand and energy consumption.

| Table E.3-1 Key Explanatory Variables |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model Name | Leon County Population | Residential Customers | Total Customers | Cooling Degree-Days (CDDs) | Heating Degree-Days (HDDs) | Tallahassee per Capita Taxable Sales | Price of Electricity | State of Florida Population | Minimum Winter Peak Day Temperature | Maximum Summer Peak Day Temperature | Appliance Saturation | R Squared(1) |
| Residential Customers | X |  |  |  |  |  |  |  |  |  |  | 0.989 |
| Residential Consumption |  | X |  | X | X | X | X |  |  |  | X | 0.921 |
| Florida State University Consumption |  |  |  | X |  |  | X | X |  |  |  | 0.930 |
| State Capitol Consumption |  |  |  | X |  |  | X | X |  |  |  | 0.892 |
| Florida A&M University Consumption |  |  |  | X |  |  |  | X |  |  |  | 0.926 |
| Street Lighting Consumption | X |  |  |  |  |  |  |  |  |  |  | 0.961 |
| GSND Customers |  | X |  |  |  |  |  |  |  |  |  | 0.958 |
| GSD Customers |  | X |  |  |  |  |  |  |  |  |  | 0.927 |
| GSND Consumption | X |  |  | X | X | X | X |  |  |  |  | 0.961 |
| GSD Consumption | X |  |  | X | X |  |  |  |  |  |  | 0.960 |
| GSLD Consumption | X |  |  | X | X |  |  |  |  |  |  | 0.974 |
| Summer Peak Demand |  |  | X |  |  |  |  |  |  | X | X | 0.982 |
| Winter Peak Demand |  |  |  |  |  |  |  |  | X |  | X | 0.965 |
| (1)R Squared, also referred to as the coefficient of determination, is a commonly used measure of goodness of fit of a linear model. If the observations fall on the model regression line, R Squared is 1. If there is no linear relationship between the dependent and independent variables, R Squared is 0. A reasonably good R Squared value may be anywhere between 0.6 to 1.0. |  |  |  |  |  |  |  |  |  |  |  |  |

| Table E.3-2 Sources of Forecast Model Input Information |  |  |
| --- | --- | --- |
| Energy Model Input Data |  | Source |
| 1. | Leon County Population | City Planning Office |
| 2. | Talquin Customers Transferred | City Power Engineering |
| 3. | CDDs | National Oceanic & Atmospheric Administration (NOAA) Reports |
| 4. | HDDs | NOAA Reports |
| 5. | Air Conditioning Saturation Rate | Residential Utility Customer Trends |
| 6. | Heating Saturation Rate | City Utility Research |
| 7. | Real Tallahassee Taxable Sales | Department of Revenue |
| 8. | Florida Population | Governor’s Office of Budget and Planning |
| 9. | State Capitol Incremental | Department of Management Services |
| 10. | FSU Incremental Additions | FSU Planning Department |
| 11. | FAMU Incremental Additions | FAMU Planning Department |
| 12. | GSLD Incremental Additions | City Utility Services |
| 13. | Other Commercial Customers | City Utility Services |
| 14. | Tallahassee Memorial Curtailable | City System Planning/Utilities Accounting |
| 15. | FSU 4th Meter Additions | City System Planning/Utilities Accounting |
| 16. | State Capitol Center 2 Special Accounts | Utilities Accounting |
| 17. | Customer Definitions | City Utility Services |
| 18. | System Peak Historical Data | City System Planning |
| 19. | Historical Customer Projections by Class | City System Planning and Customer Accounting |
| 20. | Historical Customer Class Energy | City System Planning and Customer Accounting |
| 21. | Gross Domestic Product (GDP) Forecast | Governor’s Planning and Budgeting Office |
| 22. | Consumer Price Index (CPI) Forecast | Governor’s Planning and Budgeting Office |
| 23. | Florida Taxable Sales | Governor’s Planning and Budgeting Office |
| 24. | Interruptible, Traffic Light Sales, and Security Light Additions | City System Planning and Customer Accounting |
| 25. | Historical Residential Real Price of Electricity | City Utility Services |
| 26. | Historical Commercial Real Price of Electricity | City Utility Services |

Important input assumptions for the sales forecast include the incremental load modifications at Florida State University (FSU), Florida A&M University (FAMU), Tallahassee Memorial Hospital (TMH), and the State Capitol Center.  These four customers represent approximately 14 percent of the City’s annual energy sales.  Each entity submits its proposed incremental additions/reductions to the City, and these modifications are included as submitted in the load and energy forecast.

The customer models are used to predict the number of customers by customer class, which in turn serve as inputs into the customer class consumption models.  The customer class consumption models are aggregated to form a total base system sales forecast.  The effects of conservation and DSM programs, estimated reductions from interruptible and curtailable customers, and system losses are incorporated into the base forecasts of seasonal peak demand and sales to produce the forecasts of system seasonal net peak demand and NEL requirements.

E.3.2	Forecast System Demand and Energy Requirements –

Base Case

Table E.3-3 presents the City’s base case load forecast.  The City produced the forecasts with the assistance of R.W. Beck, Inc., for the years 2006 through 2025.

E.3.3	Forecast System Demand and Energy Requirements –

Sensitivity Cases

The City’s high and low load growth sensitivity cases were developed to address the uncertainty associated with forecast input variables by adjusting selected input variables in the load forecast models.  For the sensitivities to the base energy forecast that was developed, the key explanatory variables that were changed included Leon County population, Florida population, HDDs, and CDDs.  For the peak demand forecasts, the number of customers, maximum summer temperature, and minimum winter temperature were changed.  As with the base case forecast, the high and low load growth forecasts were developed for the years 2006 through 2025.  Table E.3-4 presents the City’s high and low load growth sensitivity cases.

| Table E.3-3 City of Tallahassee Load Forecast – Base Case |  |  |  |
| --- | --- | --- | --- |
| Calendar Year | Net Summer Peak Demand (MW) | Net Winter Peak Demand (MW) | Annual NEL (GWh) |
| 2006 | 609 | 546 | 2,895 |
| 2007 | 626 | 570 | 2,976 |
| 2008 | 637 | 584 | 3,056 |
| 2009 | 646 | 596 | 3,115 |
| 2010 | 656 | 608 | 3,170 |
| 2011 | 666 | 621 | 3,225 |
| 2012 | 676 | 633 | 3,280 |
| 2013 | 686 | 645 | 3,336 |
| 2014 | 696 | 658 | 3,394 |
| 2015 | 705 | 670 | 3,451 |
| 2016 | 714 | 681 | 3,506 |
| 2017 | 723 | 692 | 3,562 |
| 2018 | 732 | 703 | 3,618 |
| 2019 | 741 | 714 | 3,675 |
| 2020 | 750 | 726 | 3,732 |
| 2021 | 758 | 736 | 3,789 |
| 2022 | 767 | 747 | 3,847 |
| 2023 | 775 | 758 | 3,906 |
| 2024 | 784 | 768 | 3,965 |
| 2025 | 793 | 779 | 4,025 |

| Table E.3-4 City of Tallahassee Load Forecast – Sensitivity Cases |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Low Load and Energy Growth |  |  | High Load and Energy Growth |  |  |
|  | Net Summer Peak Demand (MW) | Net Winter Peak Demand (MW) | Annual NEL (GWh) | Net Summer Peak Demand (MW) | Net Winter Peak Demand (MW) | Annual NEL (GWh) |
| 2006 | 588 | 496 | 2,721 | 636 | 596 | 3,102 |
| 2007 | 605 | 519 | 2,800 | 654 | 620 | 3,185 |
| 2008 | 616 | 533 | 2,878 | 665 | 635 | 3,268 |
| 2009 | 625 | 545 | 2,935 | 674 | 647 | 3,330 |
| 2010 | 635 | 557 | 2,987 | 684 | 660 | 3,387 |
| 2011 | 644 | 569 | 3,040 | 695 | 672 | 3,445 |
| 2012 | 654 | 581 | 3,093 | 705 | 685 | 3,503 |
| 2013 | 664 | 593 | 3,147 | 715 | 697 | 3,561 |
| 2014 | 673 | 606 | 3,203 | 725 | 710 | 3,622 |
| 2015 | 683 | 618 | 3,258 | 735 | 723 | 3,682 |
| 2016 | 691 | 629 | 3,311 | 744 | 734 | 3,740 |
| 2017 | 700 | 640 | 3,364 | 753 | 746 | 3,798 |
| 2018 | 709 | 651 | 3,419 | 762 | 757 | 3,857 |
| 2019 | 718 | 661 | 3,474 | 771 | 768 | 3,916 |
| 2020 | 726 | 672 | 3,529 | 780 | 780 | 3,976 |
| 2021 | 735 | 683 | 3,584 | 789 | 791 | 4,036 |
| 2022 | 743 | 693 | 3,640 | 798 | 802 | 4,096 |
| 2023 | 752 | 704 | 3,696 | 807 | 813 | 4,157 |
| 2024 | 760 | 714 | 3,754 | 816 | 824 | 4,219 |
| 2025 | 769 | 725 | 3,812 | 824 | 835 | 4,282 |