E.4.0  The City’s Need for Capacity

Prudent utility practices require a utility to plan for sufficient capacity resources to meet its peak demand and to maintain an additional margin of capacity should unforeseen events result in higher system demand or lower than anticipated availability of capacity resources.  This section presents the development and analysis of the reliability criteria used by the City.

For capacity planning purposes, the City plans to maintain a 17 percent reserve margin for the summer and winter seasons.  The planning reserve margin covers uncertainties in extreme weather, forced outages for generators, and uncertainty in load projections.  The 17 percent reserve margin was determined to be appropriate through analysis performed as part of the City’s 2002 integrated resource plan.

E.4.1  Reliability Criteria

A number of methods are used in the electric utility industry to calculate a utility’s system reliability.  One method is the reserve margin and another is the Loss of Load Probability (LOLP), which apply deterministic and probabilistic methods, respectively, to calculate the reliability of a system.  The City uses a reserve margin for planning purposes.  These two methods are discussed below.

E.4.1.1  Reserve Margin

The most commonly used deterministic method is the reserve margin method, which is calculated as follows:

System Net Capacity - System Firm Peak Demand (After Interruptible Load)

System Firm Peak Demand (After Interruptible Load)

E.4.1.2  Loss of Load Probability

The second commonly used method of calculating the reliability of a utility system is the LOLP method.  This method is advantageous in that it can result in a measure of how much capacity (and reserves) is needed to meet a target level of reliability (typically, an LOLP criterion of no more than 1 day in 10 years is used).  FRCC utilizes a reserve margin criterion (Resource Adequacy Standard) for capacity planning purposes that results in resource levels that meet an LOLP criterion of no more than 1 day in 10 years.  The Resource Adequacy Standard calls for a reserve margin of 15 percent versus firm load.  Therefore, the City uses the reserve margin method as the planning criterion that produces the most conservative reliability level.

E.4.2  Need for Capacity

Tables E.4-1 and E.4-2 present the capacity additions required to maintain the City’s 17 percent reserve margin for the summer and winter seasons, respectively.  The capacity balances are based on the City’s base case forecast peak demands as presented in Section E.3.0, as well as the existing and committed capacity resources (including purchased power) and the schedule of unit retirements presented in Section E.2.0.  The planned combined cycle repowering of Hopkins Unit 2 in the summer of 2008 (discussed in more detail in Section E.2.0) is also reflected in the capacity balances.  An analysis of Table E.4-1 shows that the City is expected to encounter a capacity shortfall in the summer of 2011, at which time approximately 22 MW of additional capacity will be required.  The need for additional summer capacity increases to approximately 294 MW by 2025.  Table E.4-2 shows that the City is expected to have sufficient capacity in the winter until 2017, at which time approximately 79 MW of additional capacity will be required.  The need for additional winter capacity increases to approximately 206 MW by 2025.

The characteristics of the City’s electric system dictate that summer generating capability versus summer peak load drive the forecast need for capacity.  Therefore, the City’s capacity additions presented in this Application will be scheduled to address projected summer capacity shortfalls and are assumed to be operational by May 1 of the year in which they are installed.

| Table E.4-1 City of Tallahassee Summer Capacity Balance |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Generating Resources (MW) |  |  | Capacity Requirements (MW) |  |  | Excess/(Deficit) Capacity to Maintain 17 Percent Reserves |
|  | Owned(1) | Purchased Power | Total | Peak Demand(2) | 17 Percent Reserves | Total |  |
| 2006 | 746 | 11 | 757 | 609 | 104 | 713 | 45 |
| 2007 | 746 | 11 | 757 | 626 | 106 | 732 | 25 |
| 2008 | 814 | 11 | 825 | 637 | 108 | 745 | 80 |
| 2009 | 814 | 11 | 825 | 646 | 110 | 756 | 70 |
| 2010 | 814 | 11 | 825 | 656 | 112 | 768 | 58 |
| 2011 | 746 | 11 | 757 | 666 | 113 | 779 | (22) |
| 2012 | 746 | 11 | 757 | 676 | 115 | 791 | (34) |
| 2013 | 746 | 11 | 757 | 686 | 117 | 803 | (45) |
| 2014 | 746 | 11 | 757 | 696 | 118 | 814 | (57) |
| 2015 | 734 | 11 | 745 | 705 | 120 | 825 | (80) |
| 2016 | 658 | 11 | 669 | 714 | 121 | 835 | (166) |
| 2017 | 634 | 0 | 634 | 723 | 123 | 846 | (212) |
| 2018 | 634 | 0 | 634 | 732 | 124 | 856 | (222) |
| 2019 | 634 | 0 | 634 | 741 | 126 | 867 | (233) |
| 2020 | 634 | 0 | 634 | 750 | 128 | 878 | (244) |
| 2021 | 634 | 0 | 634 | 758 | 129 | 887 | (253) |
| 2022 | 634 | 0 | 634 | 767 | 130 | 897 | (263) |
| 2023 | 634 | 0 | 634 | 775 | 132 | 907 | (273) |
| 2024 | 634 | 0 | 634 | 784 | 133 | 917 | (283) |
| 2025 | 634 | 0 | 634 | 793 | 135 | 928 | (294) |
| (1)Owned capacity reflects all unit retirements presented in Section E.2.0, as well as the combined cycle repowering of Hopkins Unit 2 in May 2008. (2)Peak demand forecast includes expected reductions associated with the City’s existing conservation and DSM programs. |  |  |  |  |  |  |  |

| Table E.4-2 City of Tallahassee Winter Capacity Balance |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Generating Resources (MW) |  |  | Capacity Requirements (MW) |  |  | Excess/(Deficit) Capacity to Maintain 17 Percent Reserves |
|  | Owned(1) | Purchased Power | Total | Peak Demand(2) | 17 Percent Reserves | Total |  |
| 2006 | 797 | 11 | 808 | 546 | 93 | 639 | 170 |
| 2007 | 797 | 11 | 808 | 570 | 97 | 667 | 142 |
| 2008 | 797 | 11 | 808 | 584 | 99 | 683 | 125 |
| 2009 | 893 | 11 | 904 | 596 | 101 | 697 | 197 |
| 2010 | 893 | 11 | 904 | 608 | 103 | 711 | 173 |
| 2011 | 893 | 11 | 904 | 621 | 106 | 727 | 158 |
| 2012 | 823 | 11 | 834 | 633 | 108 | 741 | 94 |
| 2013 | 823 | 11 | 834 | 645 | 110 | 755 | 80 |
| 2014 | 823 | 11 | 834 | 658 | 112 | 770 | 65 |
| 2015 | 823 | 11 | 834 | 670 | 114 | 784 | 51 |
| 2016 | 809 | 11 | 820 | 681 | 116 | 797 | 24 |
| 2017 | 731 | 0 | 731 | 692 | 118 | 810 | (79) |
| 2018 | 705 | 0 | 705 | 703 | 120 | 823 | (118) |
| 2019 | 705 | 0 | 705 | 714 | 121 | 835 | (130) |
| 2020 | 705 | 0 | 705 | 726 | 123 | 849 | (144) |
| 2021 | 705 | 0 | 705 | 736 | 125 | 861 | (156) |
| 2022 | 705 | 0 | 705 | 747 | 127 | 874 | (169) |
| 2023 | 705 | 0 | 705 | 758 | 129 | 887 | (182) |
| 2024 | 705 | 0 | 705 | 768 | 131 | 899 | (194) |
| 2025 | 705 | 0 | 705 | 779 | 132 | 911 | (206) |
| (1)Owned capacity reflects all unit retirements presented in Section E.2.0, as well as the combined cycle repowering of Hopkins Unit 2 in May 2008. (2)Peak demand forecast includes expected reductions associated with the City’s existing conservation and DSM programs. |  |  |  |  |  |  |  |