E.5.0  The City’s Economic Analysis

A detailed economic analysis was performed to evaluate the cost-effectiveness of the City’s participation in TEC and to determine the least-cost capacity expansion plan to meet the City’s forecast capacity requirements during the planning horizon, as presented in Section E.4.0.  This section presents the assumptions and methodology used in the economic analysis, as well as the results of the base case analysis.

The economic analysis described herein compares the economics of the least-cost capacity expansion plan utilizing conventional supply-side alternatives, including the City’s share of capacity and energy from TEC, versus the economics of the least-cost expansion plan for the City’s system utilizing conventional supply-side alternatives, which does not include participation in TEC.  The capacity associated with the City’s share of TEC, as well as construction of any of the supply-side alternatives presented in Section A.6.0, is only sufficient to satisfy the City’s forecast capacity requirements for a portion of the expansion planning horizon.  To meet the forecast capacity requirements, multiple unit additions were selected from the City’s supply-side alternatives considered for individual participation that passed the supply-side screening described in Section A.6.7.  Analyses of the City’s joint participation in supply-side alternatives other than TEC are presented as sensitivity cases in Section E.6.0.

E.5.1  Expansion Planning and Production Costing Methodology

The supply-side evaluations of generating unit alternatives were performed using POWROPT, an optimal generation expansion model that Black & Veatch developed as an alternative to other optimization programs.  POWROPT has been benchmarked against other optimization programs and has proven to be an effective modeling program.  Both POWROPT and its detailed chronological production costing module, POWRPRO, have been used in numerous Need for Power Applications approved by the FPSC, including FMPA’s Treasure Coast Energy Center (TCEC) Unit 1 Need for Power Application approved in July 2005, and the Orlando Utilities Commission (OUC) Stanton B Need for Power Application approved in May 2006.

POWROPT operates on an hourly chronological basis and is used to determine a set of optimal capacity expansion plans to satisfy forecast capacity requirements, simulate the operation of each of these plans, and select the most desirable plan based on cumulative present worth revenue requirements.  POWROPT evaluates all combinations of generating unit alternatives and purchase power options, in conjunction with existing capacity resources, while maintaining user-defined reliability criteria.  All capacity expansion plans were analyzed over a 30 year period from 2006 through 2035.

After the optimal generation expansion plan was selected using POWROPT, Black & Veatch’s POWRPRO was used to obtain the annual production cost for the expansion plan.  POWRPRO is a computer-based chronological production costing model developed for use in power supply systems planning.  POWRPRO simulates the hour-by-hour operation of a power supply system over a specified planning period.  Required inputs are carried forward from those used in POWROPT and include the performance characteristics of generating units, fuel costs, and the system hourly load profile for each year.

POWRPRO summarizes each unit’s operating characteristics for every year of the planning horizon.  These characteristics include, among others, each unit’s annual generation, fuel consumption, fuel cost, average net operating heat rate, the number of hours the unit was on line, the capacity factor, variable operations and maintenance (O&M) costs, and the number of starts and associated costs.  Fixed O&M costs were included only for new unit additions, since fixed O&M costs for existing units are generally considered sunk costs that will not vary from one expansion plan to another.  Similarly, the annual capacity charges for the existing PEF purchase were not included, since they also represent sunk costs.  In addition, fixed costs for firm natural gas transportation capacity from the Florida Gas Transmission Company (FGT) for existing units are considered sunk costs and were not included.  The operating costs of each unit were aggregated to determine the annual operating costs for each year of the expansion plan.  Capital costs, fixed O&M costs, and incremental costs for natural gas transportation (for combined cycle capacity addition alternatives) were then added for each capacity addition selected, at which point the cumulative present worth cost (CPWC) of each expansion plan was calculated.

The CPWC calculation accounts for annual system costs (fuel and energy, fixed O&M for capacity additions, nonfuel variable O&M, startup, and levelized capital) for each year of the expansion planning period and discounts each back to 2006 at the present worth discount rate of 5.0 percent.  These annual present worth costs were then summed over the 2006 through 2035 period to calculate the total CPWC of the expansion plan being considered.  Such analysis allows for a comparison of CPWC between various capacity expansion plans, and the plan with the lowest CPWC is considered the least-cost capacity expansion plan.

E.5.2  Least-Cost Capacity Expansion Analysis

The economic analysis consisted of comparing the economics of the optimal capacity expansion plan, including the City’s participation in TEC, with the optimal capacity expansion plan not including participation in TEC.  As described previously in this section, Black & Veatch first used its optimum generation expansion program, POWROPT, to select unit additions from the City’s supply-side alternatives considered for individual participation, which was presented in Section A.6.0.  Once the least-cost expansion plan for each case was determined, POWRPRO was used to determine the annual total system costs and to develop a comparison of CPWCs associated with each expansion plan.

E.5.2.1  Peak Demand and Energy Growth

As presented in Section E.3.0, a forecast of peak demand and NEL was provided for the City’s system through 2025.  For evaluation purposes (as discussed in Section A.8.0), loads have been held constant beyond 2025.

E.5.2.2  Supply-Side Candidate Unit Additions

As described in Section E.4.0, the City’s forecast capacity requirements are dictated by projected capacity shortfalls in the summer season of each year of the planning period.  On a weather-normalized basis, the City’s summer peak typically occurs in August of a given calendar year; however, the City’s actual summer peak could occur as early as June.  To ensure that new capacity additions are available to meet forecast summer reserve margin requirements, all unit additions considered for the City’s individual ownership (as presented in Section A.6.0) are assumed to be installed by May 1.

Section A.6.0 presented capital and O&M costs for the units considered for individual ownership by the City.  As described in more detail in Section A.6.0, absent additional investment, the City’s existing Purdom and Hopkins generating stations do not have sufficient infrastructure or site space to accommodate the number of unit additions required to meet the City’s forecast capacity requirements.  Therefore, the capital costs for all individual ownership alternatives were developed on a greenfield basis, since the all-in costs of constructing additional generating units at either Purdom or Hopkins (after considering the costs required for the necessary site improvements) would likely be equivalent to construction at greenfield locations.

E.5.2.3  Fuel Prices and Natural Gas Transportation

As described in Section A.4.0 of this Application, projections of delivered fuel prices were developed by the TEC Fuels Committee.  The base case fuel price projections presented in Section A.4.0 have been used for the evaluations presented in this section.

For all capacity expansion plan evaluations, it was necessary to account for natural gas transportation capacity associated with the new combined cycle unit alternatives.  The City currently has a contract in place with FGT for firm natural gas transportation to fuel its existing natural gas fired units.  For the 1x1 7FA combined cycle option included in Section A.6.0, it was assumed that the City would purchase firm transportation in accordance with FGT’s tariff so that 6.0 percent of the daily natural gas transportation allocation would be adequate to operate the unit at full load for an hour, based on the performance at average ambient conditions.  This would require 37,323 MBtu of firm natural gas per day.  Using the Firm Transportation Service reservation charge of $0.769 per MBtu (pursuant to FGT’s April 2006, effective rates for incremental Firm Market Area Transportation), firm transportation costs of $2.92 per kW-month were added to the fixed O&M costs of the 1x1 7FA combined cycle alternative.  It has been assumed that the City will not purchase firm natural gas transportation capacity from FGT for simple cycle CTs but, instead, will utilize an interruptible service rate assumed to be $0.37 per MBtu, which was added to the annual commodity price forecasts for natural gas presented in Section A.4.0.  Any natural gas required for the City’s system in excess of the firm natural gas transportation for the existing and new units is priced at the interruptible service rate.

E.5.2.4  Emissions Cost Considerations

To reflect the economic effects of the Clean Air Interstate Rule (CAIR) and the Clean Air Mercury Rule (CAMR) (as described in Section A.5.0), the forecast prices of emissions allowances were incorporated into the fuel costs for each unit, including existing units that will be regulated under CAIR and CAMR, beginning with the first phases of CAIR and CAMR.  The allowance price forecasts presented in Section A.5.0 provide emissions costs on a dollar per ton (dollar per pound for mercury [Hg]) basis.  These costs were used to calculate a fuel cost adder for both existing units and candidate units based on the emissions rates of each individual unit.  As a result, each generating unit was modeled using different prices for fuel because of differences in emissions rates.  The forecast market value of the allowances allocated to the City’s existing units was not included in the economic analysis, since it represents the same credit for each capacity expansion plan.

Emissions rates for some of the City’s existing units may be modified through fuel switching or retrofits for emissions control to help meet the NOx and sulfur dioxide (SO2) reductions mandated by CAIR.  Since complete emissions control strategies, the resulting reductions in emissions rates, and the generating unit output and performance impacts from potential emissions control measures are not entirely known, no changes in emissions rates or unit output and performance were considered for the existing units in this analysis, with the exception of the repowered Hopkins Unit 2 combined cycle.  Table E.5-1 presents the emissions cost adders for the City’s existing units.  In years when units are no longer available to the City because of retirement, “N/A” is used to indicate that the adders are no longer applicable, since the resources are not included in the City’s dispatch model.  Table E.5-2 presents the emissions cost adders for the City’s candidate units, which were presented in Section A.6.0.  The City’s existing generating system does not include any Hg emitting units and, therefore, no adders for Hg emissions allowance costs are included for the City’s existing units.

E.5.2.5  Dispatch Assumptions

Nonfuel variable O&M and forecast emissions allowance costs were included in the unit dispatch modeling in POWROPT and POWRPRO, along with the fuel costs.  These costs were included in the dispatch modeling to ensure the most cost-effective dispatch of both the existing and new generating units.

E.5.2.6  Analysis of the City’s Participation in TEC

The evaluation of the City’s participation in TEC was performed by modeling a capacity expansion plan that included a seasonal purchase of 22 MW in the summer of 2011, and TEC as a committed resource beginning May 1, 2012. The seasonal purchase was modeled with an assumed energy cost of $160.09 per MWh and a capacity cost of $7.50 per kW-month in 2011 dollars.

POWROPT was used to determine the optimum set of capacity additions after the construction of TEC from the conventional technologies considered for individual ownership by the City, as presented in Section A.6.0.  Taking into account the seasonal purchase in 2011 and the capacity from TEC beginning May 1, 2012, additional capacity for the City’s system is projected to be required during the summer of 2016.  All of the generating alternatives, except the integrated gasification combined cycle (IGCC) option, were assumed to be available to meet capacity requirements in 2016.  Given its current developmental status, it has been assumed that the IGCC option would not be available before 2018.  This would allow for 3 years of successful commercial operation of the next generation of IGCC units, such as OUC’s Stanton B IGCC, which is scheduled to begin operation on June 1, 2010, followed by an assumed 2 year engineering, permitting, and licensing process and 3 year construction schedule.

| Table E.5-1 Combined SO2 and NOx, Emissions Cost Adders for the City’s Existing Units (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Hopkins 1 | Hopkins CT 1 | Hopkins CT 2 | Purdom 8 | Purdom 7 | Hopkins LM6000s | Hopkins 2 1x1 CC |
| 2009 | $0.24 | $0.37 | $0.37 | $0.03 | $0.25 | $0.02 | $0.01 |
| 2010 | $0.33 | $0.51 | $0.51 | $0.05 | $0.35 | $0.03 | $0.01 |
| 2011 | $0.35 | $0.54 | $0.54 | $0.05 | $0.36 | $0.03 | $0.01 |
| 2012 | $0.36 | $0.56 | $0.56 | $0.05 | N/A | $0.03 | $0.01 |
| 2013 | $0.37 | $0.57 | $0.57 | $0.05 | N/A | $0.04 | $0.01 |
| 2014 | $0.40 | $0.62 | $0.62 | $0.06 | N/A | $0.04 | $0.01 |
| 2015 | $0.64 | $0.99 | $0.99 | $0.09 | N/A | $0.06 | $0.02 |
| 2016 | $0.69 | N/A | $1.07 | $0.10 | N/A | $0.07 | $0.02 |
| 2017 | N/A | N/A | $0.92 | $0.09 | N/A | $0.06 | $0.02 |
| 2018 | N/A | N/A | N/A | $0.09 | N/A | $0.06 | $0.02 |
| 2019 | N/A | N/A | N/A | $0.12 | N/A | $0.08 | $0.03 |
| 2020 | N/A | N/A | N/A | $0.14 | N/A | $0.09 | $0.03 |
| 2021 | N/A | N/A | N/A | $0.14 | N/A | $0.09 | $0.03 |
| 2022 | N/A | N/A | N/A | $0.13 | N/A | $0.09 | $0.03 |
| 2023 | N/A | N/A | N/A | $0.17 | N/A | $0.11 | $0.04 |
| 2024 | N/A | N/A | N/A | $0.25 | N/A | $0.16 | $0.06 |
| 2025 | N/A | N/A | N/A | $0.27 | N/A | $0.18 | $0.06 |
| 2026 | N/A | N/A | N/A | $0.29 | N/A | $0.19 | $0.07 |
| 2027 | N/A | N/A | N/A | $0.32 | N/A | $0.21 | $0.08 |
| 2028 | N/A | N/A | N/A | $0.34 | N/A | $0.22 | $0.08 |
| 2029 | N/A | N/A | N/A | $0.37 | N/A | $0.24 | $0.09 |
| 2030 | N/A | N/A | N/A | $0.39 | N/A | $0.26 | $0.09 |
| 2031 | N/A | N/A | N/A | $0.42 | N/A | $0.28 | $0.10 |
| 2032 | N/A | N/A | N/A | $0.45 | N/A | $0.30 | $0.11 |
| 2033 | N/A | N/A | N/A | $0.48 | N/A | $0.32 | $0.11 |
| 2034 | N/A | N/A | N/A | $0.52 | N/A | $0.34 | $0.12 |
| 2035 | N/A | N/A | N/A | $0.55 | N/A | $0.36 | $0.13 |

| Table E.5-2 Combined SO2, NOx, and Hg Emissions Cost Adders for the City’s Candidate Units (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LM6000 CT | 7EA CT | 7FA CT | 1x1 7FA CC | TEC | CFB (100 percent coal) | 1x1 IGCC (100 percent coal) | LMS100 CT | LM6000 1x1 CC |
| 2009 | $0.01 | $0.01 | $0.01 | $0.01 | $0.08 | $0.10 | $0.07 | $0.01 | $0.01 |
| 2010 | $0.01 | $0.01 | $0.01 | $0.01 | $0.15 | $0.19 | $0.10 | $0.01 | $0.01 |
| 2011 | $0.01 | $0.01 | $0.01 | $0.01 | $0.16 | $0.20 | $0.11 | $0.01 | $0.01 |
| 2012 | $0.01 | $0.01 | $0.01 | $0.01 | $0.16 | $0.20 | $0.11 | $0.01 | $0.01 |
| 2013 | $0.01 | $0.01 | $0.01 | $0.01 | $0.17 | $0.21 | $0.11 | $0.01 | $0.01 |
| 2014 | $0.01 | $0.01 | $0.01 | $0.01 | $0.18 | $0.22 | $0.12 | $0.01 | $0.01 |
| 2015 | $0.02 | $0.02 | $0.02 | $0.02 | $0.28 | $0.36 | $0.20 | $0.02 | $0.02 |
| 2016 | $0.02 | $0.02 | $0.02 | $0.02 | $0.30 | $0.38 | $0.21 | $0.02 | $0.02 |
| 2017 | $0.02 | $0.02 | $0.02 | $0.02 | $0.27 | $0.34 | $0.18 | $0.02 | $0.02 |
| 2018 | $0.02 | $0.02 | $0.02 | $0.02 | $0.30 | $0.37 | $0.19 | $0.02 | $0.02 |
| 2019 | $0.03 | $0.03 | $0.03 | $0.03 | $0.36 | $0.46 | $0.25 | $0.03 | $0.03 |
| 2020 | $0.03 | $0.03 | $0.03 | $0.03 | $0.42 | $0.53 | $0.30 | $0.03 | $0.03 |
| 2021 | $0.03 | $0.03 | $0.03 | $0.03 | $0.42 | $0.52 | $0.28 | $0.03 | $0.03 |
| 2022 | $0.03 | $0.03 | $0.03 | $0.03 | $0.41 | $0.51 | $0.27 | $0.03 | $0.03 |
| 2023 | $0.04 | $0.04 | $0.04 | $0.04 | $0.54 | $0.67 | $0.35 | $0.04 | $0.04 |
| 2024 | $0.06 | $0.06 | $0.06 | $0.06 | $0.74 | $0.93 | $0.52 | $0.06 | $0.06 |
| 2025 | $0.06 | $0.06 | $0.06 | $0.06 | $0.84 | $1.05 | $0.57 | $0.06 | $0.06 |
| 2026 | $0.07 | $0.07 | $0.07 | $0.07 | $0.91 | $1.13 | $0.61 | $0.07 | $0.07 |
| 2027 | $0.08 | $0.08 | $0.08 | $0.08 | $0.98 | $1.22 | $0.66 | $0.08 | $0.08 |
| 2028 | $0.08 | $0.08 | $0.08 | $0.08 | $1.05 | $1.31 | $0.71 | $0.08 | $0.08 |
| 2029 | $0.09 | $0.09 | $0.09 | $0.09 | $1.13 | $1.41 | $0.76 | $0.09 | $0.09 |
| 2030 | $0.09 | $0.09 | $0.09 | $0.09 | $1.21 | $1.51 | $0.82 | $0.09 | $0.09 |
| 2031 | $0.10 | $0.10 | $0.10 | $0.10 | $1.29 | $1.62 | $0.88 | $0.10 | $0.10 |
| 2032 | $0.11 | $0.11 | $0.11 | $0.11 | $1.39 | $1.73 | $0.94 | $0.11 | $0.11 |
| 2033 | $0.11 | $0.11 | $0.11 | $0.11 | $1.49 | $1.86 | $1.01 | $0.11 | $0.11 |
| 2034 | $0.12 | $0.12 | $0.12 | $0.12 | $1.59 | $1.99 | $1.08 | $0.12 | $0.12 |
| 2035 | $0.13 | $0.13 | $0.13 | $0.13 | $1.71 | $2.13 | $1.15 | $0.13 | $0.13 |
| CFB = Circulating Fluidized Bed. |  |  |  |  |  |  |  |  |  |

E.5.2.6.1  TEC Capital Cost.  As described in Sections A.3.0 and A.8.0, the installed capital cost for TEC would be $1,752.4 million in 2012 dollars, inclusive of escalation and interest during construction.  It was assumed that the City would be responsible for a percentage of the capital costs equal to the City’s ownership share of 20.3 percent.  The City’s total share of TEC’s installed cost is $355.7 million in 2012 dollars, which includes the costs for engineering, procurement, and construction (EPC); allowance for funds used during construction (AFUDC); land; community contribution; initial coal inventory; and owner’s costs for TEC.  Table E.5-3 presents a summary of the City’s share of the capital costs for TEC.

| Table E.5-3 TEC Capital Cost – The City’s Share (All Costs in 2012 Dollars) |  |  |
| --- | --- | --- |
| Description | Entire Unit ($1,000s) | The City’s Share(1) ($1,000s) |
| EPC Cost | $1,420,892 | $288,441 |
| AFUDC | $135,413 | $27,489 |
| Owner’s Cost | $116,994 | $23,750 |
| Initial Coal Inventory | $39,010 | $7,919 |
| Community Contribution | $20,000 | $4,060 |
| Land Cost | $20,100 | $4,080 |
| Total | $1,752,409 | $355,739 |
| (1)Reflects the City’s 20.3 percent ownership share of TEC. |  |  |

E.5.2.6.2  Transmission Considerations.  As described in Section A.3.0, the City will be utilizing the transmission system of PEF for delivery from the Perry Substation to the City’s transmission system.  The City will be required to pay a transmission tariff to PEF.  The transmission tariff assumed for the City’s use of the PEF transmission system is $1,193.00 per MW-month.  It is assumed that the City will purchase firm transmission for 155.4 MW, which will ensure that enough firm transmission is available for the City to receive its full entitlement of capacity and energy from TEC in both the winter and summer seasons.  The annual transmission tariff that the City will pay to PEF is $2,224,578.  This cost is included as an additional cost to the City starting on May 1, 2012.

The line loss for the PEF transmission system is 2.10 percent.  This loss was considered when modeling the City’s participation in TEC, and the resulting net output and net plant heat rates for the City are summarized in Table E.5-4.

| Table E.5-4 The City’s Share of TEC (Ambient Average Conditions) Output and Performance Considering Transmission Losses |  |  |  |
| --- | --- | --- | --- |
| Without Transmission Losses |  | Including Transmission Losses(1) |  |
| Output (MW) | Net Plant Heat Rate (Btu/kWh) | Output (MW) | Net Plant Heat Rate (Btu/kWh) |
| 155.4 | 9,238 | 152.1 | 9,436 |
| 151.8 | 9,238 | 148.6 | 9,436 |
| 120.3 | 9,428 | 117.8 | 9,630 |
| 79.7 | 9,933 | 78.1 | 10,146 |
| 55.3 | 10,535 | 54.2 | 10,761 |
| (1)Assumes loss of 2.10 percent. |  |  |  |

E.5.2.6.3  Operations and Maintenance Costs.  Section A.3.0 presented the fixed and nonfuel variable O&M costs for TEC.  It was assumed that the City would be responsible for a share of the O&M costs for TEC equal to the City’s ownership share of 20.3 percent.  Total fixed O&M costs for TEC include an adder for ongoing capital expenditures of $2.97 per kW-year in 2012 dollars, which escalates 2.0 percent higher than the general inflation rate.  Excluding the adder for ongoing capital expenditures, the total annual cost for TEC’s fixed O&M is $17.7 million in 2005 dollars.  The City’s share of the fixed O&M cost for TEC is $3.60 million or about $23.63 per kW-year (net after considering transmission losses) in 2005 dollars.  Section A.3.0 presented the nonfuel variable O&M cost for TEC before transmission losses as $1.36 per MWh.  With transmission losses considered, the City’s net nonfuel variable O&M cost is $1.39 per MWh in 2005 dollars.

E.5.2.6.4  TEC Scheduled Maintenance and Forced Outages.  As presented in Section A.3.0, TEC is expected to have an average of 16 scheduled maintenance days per year.  Scheduled maintenance is assumed to begin on October 1st of every year after 2012.  The scheduled maintenance period is consistent for all of the economic evaluations presented in this Application.  TEC is assumed to have an equivalent forced outage rate of 5.23 percent.

E.5.2.6.5  Community Contribution.  For the purposes of this analysis, the TEC Participants are assumed to pay a community contribution of $2.5 million per year, in addition to an initial contribution of $20.0 million (included in the capital cost) previously described in this section.  Similar to the other fixed costs for TEC, it was assumed that the City would be responsible for a percentage of the annual community contribution proportionate to its ownership share of TEC.  The City’s share of the annual community contribution is approximately $507,500 in 2012 dollars.  The community contribution is included as an additional annual cost to the City, escalated at the general inflation rate of 2.5 percent per year after May 1, 2012.

E.5.2.7  Analysis of Alternative Expansion Plans to Participation in TEC

The base case capacity expansion plan presented in Subsection E.5.2.6 indicates a seasonal purchase during the summer of 2011, followed by participation in TEC in 2012. However, for this alternative expansion plan analysis, it was assumed that the City would neither purchase seasonal capacity nor participate in TEC.  Instead, Black & Veatch’s POWROPT was utilized to determine the least-cost capacity expansion plan for the City’s system, beginning with the initial forecast need for capacity in the summer of 2011.  To determine this plan, POWROPT selected generating unit alternatives from among the City’s individual ownership supply-side alternatives identified in Section A.6.0.  All supply-side alternatives were assumed to be available to meet the City’s need for capacity in the summer of 2011, except for the CFB and the IGCC options.  Considering the time likely required to permit, license, and construct a solid-fuel unit in Tallahassee (including the conducting of a referendum consistent with the City’s charter), it has been assumed that the CFB option would first be available in 2015 and, as previously described in Subsection E.5.2.6, the IGCC option was first assumed to be available in 2018.

E.5.3  Cumulative Present Worth Cost Analysis

The previous sections described the assumptions and methodology that were used in POWROPT to select least-cost capacity expansion plans for a scenario that included the City’s participation in TEC and another scenario in which it was assumed that TEC would not be constructed.  Once these least-cost capacity expansion plans were identified, POWRPRO was used to determine the total annual system costs and to develop a comparison of CPWCs associated with each expansion plan.

E.5.3.1  Analysis of the Capacity Expansion Plan with TEC

The least-cost capacity expansion plan, assuming that the City participates in TEC in May 2012, includes a seasonal purchase in the summer of 2011, followed by an LMS100 CT unit in 2016, and a second LMS100 CT unit in 2021.

E.5.3.2  Analysis of Alternative Capacity Expansion Plan

The least-cost capacity expansion plan without the City’s participation in TEC includes an LMS100 CT unit in 2011, followed by a CFB unit in 2016.

E.5.3.3  Comparison of Cumulative Present Worth Costs

As shown in Table E.5-5, the CPWC of the least-cost capacity expansion plan that includes the City’s participation in TEC is approximately $4,320.0 million.  Table E.5-6 indicates that the CPWC of the least-cost capacity expansion plan without TEC is $4,472.6 million.  A comparison of the CPWCs for the two plans demonstrates that the expansion plan that includes participation in TEC is the least-cost plan by $152.6 million over the planning period.