1

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3   In the Matter of:

4

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070297-EI

5   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

6   TAMPA ELECTRIC COMPANY.

--------------------------------------

7

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070298-EI

8   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

9   PROGRESS ENERGY FLORIDA, INC.

----------------------------------------

10

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070299-EI

11   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

12   GULF POWER COMPANY.

---------------------------------------

13

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070301-EI

14   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

15   FLORIDA POWER & LIGHT COMPANY.

________________________________________/

16

17

18

19

20             ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

21               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

22

23                              VOLUME 1

24                         Pages 1 through 124

25   PROCEEDINGS:        HEARING

FLORIDA PUBLIC SERVICE COMMISSION

2

1   BEFORE:             CHAIRMAN LISA POLAK EDGAR

COMMISSIONER MATTHEW M. CARTER, II

2                       COMMISSIONER KATRINA J. McMURRIAN

COMMISSIONER NANCY ARGENZIANO

3                       COMMISSIONER NATHAN A. SKOP

4   DATE:               Tuesday, October 2, 2007

5   TIME:               Commenced at 9:45 a.m.

6   PLACE:              Betty Easley Conference Center

Room 148

7                       4075 Esplanade Way

Tallahassee, Florida

8

REPORTED BY:        LINDA BOLES, RPR, CRR

9                       Official FPSC Reporter

(850) 413-6734

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

3

1   APPEARANCES:

2             JOHN T. BUTLER, ESQUIRE, 700 Universe Boulevard, Juno

3   Beach, FL, 33408-0420, and NATALIE F. SMITH, ESQUIRE, 215 South

4   Monroe Street, Tallahassee, Florida 32301, appearing on behalf

5   of Florida Power & Light Company.

6             JOHN T. BURNETT, ESQUIRE, Progress Energy Florida,

7   Inc., Post Office Box 14042, St. Petersburg, Florida

8   33733-4042, appearing on behalf of Progress Energy Florida,

9   Inc.

10             LEE L. WILLIS, ESQUIRE, and JAMES D. BEASLEY,

11   ESQUIRE, Ausley Law Firm, Post Office Box 391, Tallahassee,

12   Florida 32302, appearing on behalf of Tampa Electric Company.

13             JEFFREY STONE, ESQUIRE; RUSSELL A. BADDERS, ESQUIRE;

14   and STEVEN GRIFFIN, ESQUIRE, Beggs & Lane Law Firm, Post Office

15   Box 12950, Pensacola, FL 32591, and ERIC B. LANGLEY, ESQUIRE,

16   Balch & Bingham, LLP, 1710 Sixth Avenue North, Birmingham,

17   Alabama 35203, appearing on behalf of Gulf Power Company.

18             DULANEY L. O'ROARK III, GENERAL COUNSEL, Southeast

19   Region Verizon, 5055 North Point Parkway, Alpharetta, Georgia

20   30022, appearing on behalf of Verizon Florida LLC.

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

4

1   APPEARANCES (Continued):

2             TRACY HATCH, ESQUIRE, 101 North Monroe Street, Suite

3   700, Tallahassee, Florida  32301-1549, and JENNIFER S. KAY,

4   ESQUIRE, c/o Nancy H. Sims, Esquire, 150 South Monroe Street,

5   Suite 400, Tallahassee, Florida  32301, appearing on behalf of

6   AT&T.

7             SUSAN S. MASTERTON, ESQUIRE, 1313 Blair Stone Road,

8   Tallahassee, Florida 32301, appearing on behalf of Embarq

9   Florida, Inc.

10             BETH KEATING, ESQUIRE, Akerman, Senterfitt Law Firm,

11   106 East College Avenue, Suite 1200, Tallahassee, Florida

12   32301, and MARIA T. BROWNE, ESQUIRE, and JOHN D. SEIVER,

13   ESQUIRE, Davis, Wright, Tremaine LLP, 1919 Pennsylvania Avenue,

14   NW, Suite 200, Washington, DC  20006-3402, appearing on behalf

15   of Florida Cable Telecommunications Association, Inc.

16             ROBERT SCHEFFEL WRIGHT, ESQUIRE, and JOHN T. LAVIA,

17   III, ESQUIRE, Young van Assenderp, P.A., 225 South Adams

18   Street, Suite 200, Tallahassee, Florida 32301, appearing on

19   behalf of the City of Panama City Beach, the Town of Jupiter

20   Island, the Municipal Underground Utilities Consortium, the

21   Town of Palm Beach, and the Panama City Beach Community

22   Redevelopment Agency.

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

5

1   APPEARANCES (Continued):

2             KEINO YOUNG, ESQUIRE; LISA C. BENNETT, ESQUIRE;

3   KATHERINE E. FLEMING, ESQUIRE; H. F. RICK MANN, ESQUIRE; and

4   ADAM J. TEITZMAN, ESQUIRE, FPSC General Counsel's Office, 2540

5   Shumard Oak Boulevard, Tallahassee, Florida 32399-0850,

6   appearing on behalf of the Commission Staff.

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

6

1                              I N D E X

2                              WITNESSES

3

NAME:                                              PAGE NO.

4

5   JASON CUTLIFFE

6        Prefiled Direct Testimony Inserted               53

7   MICKEY GUNTER

8        Prefiled Direct Testimony Inserted               75

9   EDWARD J. BATTAGLIA

10        Direct Examination by Mr. Badders                83

Prefiled Direct Testimony Inserted               85

11        Cross Examination by Mr. Wright                 108

12

13

14

15

16

17

18   CERTIFICATE OF REPORTER                              124

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

7

1                              EXHIBITS

2   NUMBER:                                           ID.  ADMTD.

3   1    Comprehensive Exhibit List                   28    28

4   2    Staff's Composite Exhibits - 2 stipulated    28    28

5   3    Staff's Composite Exhibits - 3 stipulated    28    28

6   4    Staff's Composite Exhibits - 4 stipulated    28    28

7   5    Staff's Composite Exhibits - 5 stipulated    28    28

8   6    Staff's Composite Exhibits - 6 stipulated    28    28

9   7    Staff's Composite Exhibits - 7 stipulated    28    28

10   9    JC-1T                                        52    52

11   10   JC-2T                                        52    52

12   11   JC-3T                                        52    52

13   12   MG-1T                                        74    74

14   13   MG-2T                                        74    74

15   14   MG-3T                                        74    74

16   15   MG-4T                                        74    74

17   16   MG-5T                                        74    74

18   17   MG-6T                                        74    74

19   18   EJB-1                                        84

20   44   Slavin Depo Transcript, Pages 1-4,           15

61-70, Certificate of Oath, Errata

21        Sheet

22   45   Gulf's Responses to PCB Interrogatories     109

Nos. 41-47

23

46   FPL's Storm Secure Plan - January 2006      117

24

25

FLORIDA PUBLIC SERVICE COMMISSION

8

1                         P R O C E E D I N G S

2             CHAIRMAN EDGAR:  Good morning.  I call this hearing

3   to order.  We'll begin by asking our staff to read the notice.

4             MR. YOUNG:  Good morning.  Good morning.  By notice

5   issued September 11th, 2007, this time and --

6             CHAIRMAN EDGAR:  Okay.  Additional technical

7   difficulties.  Bear with us.  Okay.  Everybody sit tight for a

8   minute and we'll see if we can get the sound turned up.  And,

9   again, I'm having some technical difficulties here on the

10   bench, so just give us a moment.

11             (Pause.)

12             Okay.  They said it would be about five minutes to

13   work on the sound system.  So everybody at ease.  We will be on

14   break for a few minutes, but if you would just kind of stay

15   close.

16             (Pause.)

17             Okay.  We are going to go back on the record and we

18   are going to try to get started again.  My apologies for the

19   technical difficulties.  And thank you all for your patience.

20   And let's go back to -- I'd like to ask Mr. Young to please

21   read the notice.

22             MR. YOUNG:  Thank you.  By notice issued

23   September 11th, 2007, this time and place has been set for a

24   hearing in the following dockets:  Docket Number 070297-EI,

25   Docket Number 070298-EI, Docket Number 070299-EI, and Docket

FLORIDA PUBLIC SERVICE COMMISSION

9

1   Number 070301-EI for the review of the 2007 Electric

2   Infrastructure Storm Hardening Plans filed pursuant to Rule

3   25-6.0342, Florida Administrative Code, submitted by Tampa

4   Electric Company, Progress Energy Florida, Incorporated, Gulf

5   Power Company and Florida Power & Light Company.  The purpose

6   of the hearing is set out in the notice.

7             CHAIRMAN EDGAR:  Thank you, Mr. Young.  And now we'll

8   go ahead and take appearances.  And recognizing that we do have

9   a number, thank you, a number of parties and a number of

10   dockets, when you are giving us your appearance, if you would

11   please state who you are representing and which dockets you are

12   participating in and we will try to keep it all straight.  And

13   we'll begin to my left.

14             MR. BUTLER:  Thank you, Madam Commissioner.

15             John Butler and Natalie Smith of Florida Power &

16   Light Company appearing in Docket 070301.

17             MR. BURNETT:  Good morning, Commissioners.  John

18   Burnett for Progress Energy Florida appearing in 070298.

19             MR. WILLIS:  I'm Lee L. Willis appearing together

20   with James D. Beasley for Tampa Electric Company in Docket

21   Number 070297-EU (sic.)

22             CHAIRMAN EDGAR:  Thank you.

23             MR. BADDERS:  Good morning, Commissioners.  Russell

24   Badders on behalf of Gulf Power Company in Docket 070299.  Also

25   appearing with me is Jeffrey A. Stone, Steven R. Griffin and

FLORIDA PUBLIC SERVICE COMMISSION

10

1   Eric B. Langley.  All of their addresses are as shown in the

2   Prehearing Order.

3             CHAIRMAN EDGAR:  Thank you.

4             MR. O'ROARK:  Good morning, Commissioners.  I'm De

5   O'Roark appearing on behalf of Verizon Florida, LLC, in Docket

6   Numbers 070297, which is the Tampa Electric docket; 070298,

7   which is the Progress Energy docket; and 070301, which is the

8   FPL docket.

9             CHAIRMAN EDGAR:  Thank you.

10             MR. HATCH:  Tracy Hatch and Jennifer Kay appearing on

11   behalf of BellSouth Telecommunications, Inc., d/b/a AT&T

12   Florida, and also TCG South Florida.  AT&T -- we're in all four

13   dockets.

14             MS. MASTERTON:  Susan Masterton representing Embarq

15   Florida, Inc., in all four dockets.

16             MS. KEATING:  Good morning, Commissioners.  Beth

17   Keating appearing on behalf of the Florida Cable

18   Telecommunications Association in Dockets 070298 and 070299.

19   Also appearing today on behalf of the FCTA are Maria Browne and

20   John Seiver, and they're appearing in all four dockets.

21             CHAIRMAN EDGAR:  Thank you.

22             Mr. Wright.

23             MR. WRIGHT:  Thank you, Madam Chairman.  Good

24   morning.  My name is Robert Scheffel Wright and together with

25   my partner, John T. Lavia, III, we are appearing in Docket

FLORIDA PUBLIC SERVICE COMMISSION

11

1   070299, the Gulf Power docket, on behalf of the City of Panama

2   City Beach, the Panama City Beach Community Redevelopment

3   Agency and the Municipal Underground Utilities Consortium.

4   Additionally, in Docket 070301, the FPL Storm Hardening Plan

5   docket, we are appearing on behalf of the Municipal Underground

6   Utilities Consortium, the Town of Palm Beach and the Town of

7   Jupiter Island.  Thank you.

8             CHAIRMAN EDGAR:  Thank you.

9             And staff.

10             MR. YOUNG:  Keino Young, Katherine Fleming, Lisa

11   Bennett, H. F. Mann and Adam Teitzman, Commission staff.

12             CHAIRMAN EDGAR:  Thank you.  Staff, preliminary

13   matters.

14             MR. YOUNG:  There are several preliminary matters

15   which staff recommends be taken up after the public testimony

16   portion of the hearing when we begin with the technical

17   portion.

18             CHAIRMAN EDGAR:  Okay.  All right.  Then we will move

19   to the public testimony portion of this proceeding.  And I need

20   to ask if there are any members from the general public who

21   would like to address the Commission at this time on this

22   matter or in any of these dockets.  Okay.  Seeing none.

23             Mr. Young.

24             MR. YOUNG:  Thank you, Madam Chairman.

25             Madam Chairman, first, all the parties in all the

FLORIDA PUBLIC SERVICE COMMISSION

12

1   dockets have stipulated to an approval by the Commission of the

2   process to engage third-party attachers, which is attached to

3   Exhibit KS-1 to the prefiled testimony of AT&T Florida witness

4   Kirk Smith, with the sentence of Paragraph 7 therefore revised

5   to read, "The electrical utilities will file with the Director

6   of the Division of Economic Regulations by March 1st."  And

7   this is attached with that statement that was handed to the

8   Commissioners.

9             CHAIRMAN EDGAR:  Thank you.  Commissioners, are there

10   any questions regarding the proposed stipulation on the process

11   to engage third-party attachers?  Seeing none, then is there a

12   motion to approve the stipulation as revised?

13             COMMISSIONER CARTER:  So moved.

14             COMMISSIONER SKOP:  Second.

15             CHAIRMAN EDGAR:  There's a motion and a second.  All

16   in favor, say aye.

17             (Unanimous affirmative vote.)

18             Show it adopted.

19             MR. YOUNG:  Thank you, Madam Chairman.  With that,

20   with the Commissioners agreeing on the proposed stipulation,

21   AT&T has asked that Witness Kirk Smith be excused if the

22   Commissioners have any -- no questions, if you don't have any

23   questions.

24             CHAIRMAN EDGAR:  Commissioners, any questions for

25   Witness Smith when we get to that point in the proceeding?  If

FLORIDA PUBLIC SERVICE COMMISSION

13

1   there are none, we will excuse him.  I see none, and so Witness

2   Smith may be excused.

3             MS. FLEMING:  Good morning, Chairman.  I would like

4   to note that Verizon has filed a notice of withdrawal of the

5   testimony of Dr. Slavin and Mr. Walker in the FPL docket.

6             MR. O'ROARK:  Just for clarification, it's only a

7   portion of the Walker testimony.

8             MS. FLEMING:  That's correct.  Just Walker's

9   testimony as it pertains to the FPL docket.

10             CHAIRMAN EDGAR:  Okay.  So there is a notice filed by

11   Verizon to withdraw, this is to make sure I have it straight,

12   to withdraw the testimony that had been filed by Dr. Slavin and

13   a portion of Witness Walker's testimony.

14             MR. O'ROARK:  That is correct.

15             CHAIRMAN EDGAR:  Correct.  Okay.  So noted for the

16   record.

17             MS. FLEMING:  As far as for clarification, the

18   portion of Witness Walker's testimony that's been withdrawn

19   starts on Page 6, Line 1, and ends on Page 7, Line 18.

20             CHAIRMAN EDGAR:  Are there any additional questions

21   or comments on that?

22             MR. SEIVER:  May it please the Chair.

23             CHAIRMAN EDGAR:  Yes, sir.

24             MR. SEIVER:  On behalf of FCTA, we had originally

25   objected to the withdrawal of Dr. Slavin's testimony.  We have

FLORIDA PUBLIC SERVICE COMMISSION

14

1   reached an agreement with Florida Power & Light and Verizon to

2   withdraw our objection to the withdrawal of the testimony and

3   instead stipulate to the admission of portions of Mr., of Dr.

4   Slavin's deposition transcript into the record in place of

5   that.  And particularly the pages that have been agreed to are

6   Pages 1 through 4 of the deposition, as well as Pages

7   61 through 70, plus the Certificate of Oath and the Errata

8   Sheet.

9             CHAIRMAN EDGAR:  Okay.  So as has just been described

10   to us, FCTA is proposing to put forth -- can we do this as an

11   exhibit?

12             MS. FLEMING:  Yes, Chairman.

13             CHAIRMAN EDGAR:  Okay.

14             MS. FLEMING:  We can identify this as hearing Exhibit

15   Number 44.

16             CHAIRMAN EDGAR:  Okay.  So we will put forth portions

17   of the deposition testimony of Mr. Walker; correct?

18             MR. SEIVER:  No.  Dr. Slavin.

19             CHAIRMAN EDGAR:  Dr. Slavin.  Thank you.  Of Dr.

20   Slavin.  And I believe you said Pages 1 through 4, 61 through

21   70, the Certificate and the Errata Sheet.

22             MR. SEIVER:  That's correct.

23             CHAIRMAN EDGAR:  Okay.

24             MS. FLEMING:  And for clarity of the record, this

25   will only be, this hearing exhibit will be only identified in

FLORIDA PUBLIC SERVICE COMMISSION

15

1   the FPL docket, which is Docket Number 070301.

2             CHAIRMAN EDGAR:  Okay.  We will mark as Exhibit

3   Number 44 the portions of the deposition testimony that have

4   been described for Dr. Slavin offered by FCTA and for the FPL

5   docket.

6             (Exhibit Number 44 marked for identification.)

7             MS. FLEMING:  And we'd also like to note for the

8   record that FCTA has filed a notice of withdrawal of Witness

9   Harrelson's prefiled testimony in the Gulf docket, which is

10   070299.

11             CHAIRMAN EDGAR:  Any comments or questions?  None.

12   Okay.  So noted.

13             MS. FLEMING:  At this point, we can address the

14   proposed stipulations.  All the Commissioners, all the parties

15   and the court reporter have received a copy of the proposed

16   stipulations in this docket.  Staff would suggest going docket

17   by docket and providing a brief summary of the stipulations.

18             CHAIRMAN EDGAR:  Okay.  Before we move to the

19   stipulations, let me just mention one, I'm going to call it a

20   personal preliminary matter to share with the parties and

21   Commissioners for planning purposes.  We will be planning to

22   take a break at 12:00 to a little after 12:00 for lunch.  After

23   that we'll come back depending -- what do you say, Commissioner

24   Carter, about 1:00 or 1:30?  Okay.  We'll announce that at the

25   time.  Probably about 1:30.  I need to attend to some other

FLORIDA PUBLIC SERVICE COMMISSION

16

1   matters this afternoon, so Commissioner Carter will be

2   presiding over the portion of the proceeding while I am out

3   this afternoon.  And I will, of course, review the record for

4   the portion that I miss.  And with that, I think we can move to

5   stipulations.

6             MS. FLEMING:  In the TECO docket, Number 070297,

7   there are proposed stipulations on 1 through 6, 8 through 11.

8   Issues 1 through 6 are checklist type of requirements that TECO

9   has satisfied.  The parties have agreed that TECO has satisfied

10   the requirements of the Rule 25-6.0342 for compliance with the

11   National Electric Safety Code extreme wind loading standards,

12   mitigation of flooding and storm surge and front lot

13   construction.

14             On the proposed stipulations for Issues 8 through 11,

15   they're predicated on the Commission's approval of the process

16   to engage third-party attachers, which the Commission just

17   approved.  We would like to note for the record that AT&T and

18   TCG have not affirmatively stipulated to the issue, but take no

19   position on Issues 1, 8, 9 and 11, and AT&T, Embarq, TCG and

20   Verizon take no positions on 2, 3, 4, 5, 6 and 10.

21             CHAIRMAN EDGAR:  Commissioners, are there any

22   questions about the proposed stipulations relating to the Tampa

23   Electric Company docket?  Seeing none, is there a motion to

24   approve the stipulations for this docket?

25             COMMISSIONER CARTER:  So move.

FLORIDA PUBLIC SERVICE COMMISSION

17

1             COMMISSIONER SKOP:  Second.

2             CHAIRMAN EDGAR:  I have a motion and a second.  All

3   in favor, say aye.

4             (Unanimous affirmative vote.)

5             Opposed?  Show it adopted.  And we can move to the

6   next stipulation.

7             MS. FLEMING:  The next stipulations are in the Gulf

8   docket, in 070299.  We have stipulations on Issues 27, 31,

9   32 and 38.  The proposed stipulations on this issue, they're

10   that Gulf has satisfied the requirements of the rule with

11   compliance with the National Electric Safety Code, mitigation

12   of flooding and storm surge and front lot construction.

13             On proposed stipulation Issue 38, it's a recognition

14   that Gulf's plan contains written procedures for the

15   third-party attachers.

16             Staff would note for the record that AT&T has taken

17   no position on Issues 27 and 38, and AT&T has taken no -- AT&T

18   and Embarq have taken no position on 31, on 31 and 32.

19             CHAIRMAN EDGAR:  Commissioners, any questions about

20   the proposed stipulations for the Gulf Power Company docket?

21   Seeing none, is there a motion to adopt the stipulations?

22             COMMISSIONER ARGENZIANO:  So move.

23             COMMISSIONER CARTER:  Second.

24             CHAIRMAN EDGAR:  All in favor, say aye.

25             (Unanimous affirmative vote.)

FLORIDA PUBLIC SERVICE COMMISSION

18

1             Opposed?  Show it adopted.

2             MS. FLEMING:  In addition to the issues just

3   mentioned for Gulf, I was just informed that there is also a

4   proposed stipulation on Issue 33 for the Gulf docket, and I

5   would defer to Gulf Power to address that.

6             MR. BADDERS:  Yes.  Good morning.  Russell Badders on

7   behalf of Gulf Power.  I believe Issue 33 is a stipulated

8   issue.  It does not appear that any of the parties have taken

9   issue with Gulf's position.  I believe some of them have either

10   taken no position or they agree with us.

11             CHAIRMAN EDGAR:  Ms. Fleming.

12             MS. FLEMING:  Staff has no objections.  And if none

13   of the parties have any objections, staff would recommend that

14   the Commissioners approve the stipulation on Issue 33.

15             CHAIRMAN EDGAR:  Commissioners, any questions?

16   Seeing none, is there a motion to approve the stipulation as

17   described?

18             COMMISSIONER ARGENZIANO:  So moved.

19             COMMISSIONER CARTER:  Second.

20             CHAIRMAN EDGAR:  There's a motion and a second.  All

21   in favor, say aye.

22             (Unanimous affirmative vote.)

23             Show it adopted

24             MS. FLEMING:  The next docket is the FPL docket,

25   070301, and there are proposed stipulations on Issues 40 and

FLORIDA PUBLIC SERVICE COMMISSION

19

1   45.  The stipulation states that FPL's plans meet the

2   requirements of the rule for compliance with the National

3   Electric Safety Code and front lot construction.

4             Staff would note for the record that AT&T takes no

5   position on Issues 40 and 45, and AT&T, Embarq and Verizon take

6   no position on 45.

7             CHAIRMAN EDGAR:  Thank you.

8             Commissioners, any questions on the proposed

9   stipulations for Issue 40 and Issue 45 as described?  Seeing

10   none, is there a motion?

11             COMMISSIONER ARGENZIANO:  So move.

12             COMMISSIONER CARTER:  Second.

13             CHAIRMAN EDGAR:  All in favor of the motion to adopt

14   the proposed stipulations on Issue 40 and Issue 45 for the

15   Florida Power & Light docket, say aye.

16             (Unanimous affirmative vote.)

17             Show it adopted.

18             MR. BUTLER:  Madam Chairman, I believe that we have

19   an additional --

20             CHAIRMAN EDGAR:  Mr. Butler.

21             MR. BUTLER:  -- I'm sorry, an additional issue that I

22   think is stipulated for FPL, and I'd like to address it at this

23   point if it's the appropriate time.

24             CHAIRMAN EDGAR:  This is the appropriate time.  What

25   issue number would that be?

FLORIDA PUBLIC SERVICE COMMISSION

20

1             MR. BUTLER:  It would be Issue 51.  And 51 is the

2   issue regarding FPL's plan including written attachment

3   standards and procedures.  And we have agreed to this language

4   with the FCTA, and I don't believe that there's any other party

5   that would disagree with our taking this position.

6             Our position on, or the agreed position on

7   Issue 51 would say, "Yes.  FPL is not seeking approval of the

8   standards and procedures, but instead is stating that it has

9   attachment standards and procedures for third-party attachments

10   that meet or exceed the NESC."

11             CHAIRMAN EDGAR:  Any comments from any of the other

12   parties?  No?  Staff?

13             MS. FLEMING:  Staff has no objection.  Staff would

14   recommend that this stipulation be approved.

15             CHAIRMAN EDGAR:  Commissioners, we have a

16   recommendation from our staff to adopt the proposed stipulation

17   for Issue 51 on the docket regarding Florida Power & Light.

18   Any questions?  Is there a motion?

19             COMMISSIONER ARGENZIANO:  So move.

20             COMMISSIONER CARTER:  Second.

21             CHAIRMAN EDGAR:  There's a motion and a second.  Did

22   I hear -- no.  Okay.  All in favor of the motion, say aye.

23             (Unanimous affirmative vote.)

24             Show it adopted.

25             Mr. Butler.

FLORIDA PUBLIC SERVICE COMMISSION

21

1             MR. BUTLER:  I'm sorry.  If I may, Madam Chairman, in

2   connection with that issue, some of Mr. Harrelson's testimony

3   goes to this subject, and I will let Ms. Browne speak to it,

4   but I believe that there will be a companion motion for

5   withdrawal of a portion of his testimony that relates to that

6   subject.

7             CHAIRMAN EDGAR:  And we can take that up at the time

8   that, when Mr. Harrelson comes forward, as he will be

9   testifying in other dockets.  Does that work?

10             MR. BUTLER:  That's fine.  Or we can do it now.  We

11   have been covering withdrawal of other witnesses' testimony,

12   and either way is fine with me.

13             CHAIRMAN EDGAR:  I will look to our staff.

14             MS. FLEMING:  Just for clarification, does this

15   correction of Mr. Harrelson's testimony consist of withdrawing

16   Harrelson's testimony in the FPL docket?

17             MS. BROWNE:  We could withdraw a portion of the

18   testimony in the FPL docket.

19             MS. FLEMING:  Then if Mr. Harrelson will still be

20   appearing in the FPL docket and providing testimony, I would

21   suggest we take it up at the time that Mr. Harrelson takes the

22   stand.

23             CHAIRMAN EDGAR:  Okay.  All right.  Then we will hold

24   that matter for when we come to Witness Harrelson as we go

25   through the witness list.

FLORIDA PUBLIC SERVICE COMMISSION

22

1             MR. BURNETT:  Madam Chairman.

2             CHAIRMAN EDGAR:  Yes, sir.

3             MR. BURNETT:  John Burnett on behalf of Progress

4   Energy.

5             Based on the Commission's approval just now of the

6   process within the process and FCTA's stipulation that we

7   reached yesterday with them changing their position from "No"

8   to "No objection" on Progress Issues 20, 24, 25 and 26, I

9   believe that Progress Energy is now in the position to where we

10   have either "Yes," "No objection" or "No position" to all of

11   our Progress issues.  So we would -- we should be in the same

12   position as some of the other companies to have a stipulation

13   on all the Progress Issues 14 through 26 is either "No

14   objection", "No position" or "Agree."

15             CHAIRMAN EDGAR:  Ms. Fleming.

16             MS. FLEMING:  Just for clarification then, the

17   stipulation would be based on Progress's position in the

18   Prehearing Order?

19             MR. BURNETT:  That is correct, Ms. Fleming, with the

20   notation of Issue 25, that there was a submitted change of

21   Progress's position in FCTA's yesterday to, to change that

22   position.  But with that, we should be in a position to

23   stipulate all Progress issues.

24             MS. FLEMING:  If there are no objections from any

25   other parties, then staff would recommend that those proposed

FLORIDA PUBLIC SERVICE COMMISSION

23

1   stipulations be approved by the Commission.

2             CHAIRMAN EDGAR:  Yes, ma'am.

3             MS. KEATING:  Madam Chair, thank you.

4             I was just going to suggest, I don't believe that we

5   have officially changed our position in the record, and I was

6   going to offer that today, that in light of good discussions

7   with Progress as well as with Gulf, FCTA is changing its

8   position on Issues 20, 24, 25 and 26 in Docket 070298 to "No

9   objection."  And in 070299 we are changing our position on

10   Issues 33, 35, 37, 38 and 39 to "No objection."

11             CHAIRMAN EDGAR:  Thank you, Ms. Keating.

12             And, Commissioners, I do believe that you have that

13   in writing in front of you as well.  Thank you.

14             So, Ms. Fleming, we need to, a motion to adopt the

15   proposed stipulations as discussed and described?

16             MS. FLEMING:  Yes.  It is my understanding that on

17   Issues 14 through 26 the proposed stipulations will be

18   Progress's position as stated in the Prehearing Order, with the

19   exception of the position change at Issue 25 that was provided

20   to all Commissioners and the court reporter.

21             CHAIRMAN EDGAR:  Thank you.

22             Commissioner Carter, did you have a question?

23             COMMISSIONER CARTER:  I just wanted to be sure for

24   note purposes, for Progress it's Issues 14 through 26.  And

25   what was the other number?

FLORIDA PUBLIC SERVICE COMMISSION

24

1             CHAIRMAN EDGAR:  Issues 14 through 26 to be

2   reflected, and correct me if I get this wrong, 14 through 26 to

3   be reflected as described in the Prehearing Order; however,

4   Issue 25 to have a different position reflected for FCTA.  Is

5   that correct?

6             MS. KEATING:  That is correct.

7             CHAIRMAN EDGAR:  Commissioner Carter, does that --

8             COMMISSIONER CARTER:  Thank you, Madam Chair.

9             CHAIRMAN EDGAR:  You're very welcome.

10             Okay.  Then, Commissioners, if I could, a motion to

11   adopt the proposed stipulations as discussed and described by

12   Ms. Fleming.

13             COMMISSIONER CARTER:  So move.

14             COMMISSIONER ARGENZIANO:  Second.

15             CHAIRMAN EDGAR:  All in favor, say aye.

16             (Unanimous affirmative vote.)

17             Show it adopted.

18             MR. BURNETT:  Madam Chairman, if I may, John Burnett,

19   one more.  Progress Witness Mickey Gunter, I'm informed by

20   staff that staff has no questions for Mr. Gunter.  And based on

21   the stipulation just entered, no parties should have any

22   questions for Mr. Gunter.  So if the Commission had no

23   questions, his direct testimony could be entered into the

24   record and he could be dismissed if it was the Commission's

25   pleasure.

FLORIDA PUBLIC SERVICE COMMISSION

25

1             CHAIRMAN EDGAR:  Commissioners, as you've heard,

2   Progress is proposing that in light of the stipulations that

3   have been approved and related discussions, that Witness

4   Gunter, who is third on our list of witnesses, could be

5   stipulated and excused if there are no questions.

6   Commissioners, is there a desire to have Witness Gunter

7   available for questions or may he be stipulated and excused?

8             Okay.  I'm seeing no questions, no objections.  So we

9   will excuse Witness Gunter.  And, Ms. Fleming, should we go

10   ahead and, and enter testimony, or for the sake of order of the

11   record should we wait?  For sake of the order of the record --

12             MS. FLEMING:  I would suggest we wait and move in any

13   stipulated exhibits and testimony as we get to that witness.

14             CHAIRMAN EDGAR:  As we come to them.  That works for

15   me.  Does that work for you?  Okay.

16             MR. BURNETT:  Thank you.

17             CHAIRMAN EDGAR:  Thank you.

18             Other matters.

19             MR. BADDERS:  Yes, Commissioner.  Russell Badders on

20   behalf of Gulf Power.  I believe, given the stipulation that

21   we've reached with FCTA, that Witness Alan McDaniel's rebuttal

22   could go into the record without objection.

23             CHAIRMAN EDGAR:  Ms. Fleming.

24             MS. FLEMING:  Staff does not object.  If any of the

25   parties do not object and the Commissioners don't have

FLORIDA PUBLIC SERVICE COMMISSION

26

1   questions of that witness, we can go ahead and take up his

2   rebuttal testimony in turn as we would with the other

3   witnesses.

4             CHAIRMAN EDGAR:  And, again, we're going to try to

5   move through as far as entering the testimony, so will you

6   remind me when we come to that that we have discussed that

7   previously?

8             MR. BADDERS:  I will indeed.

9             CHAIRMAN EDGAR:  Okay.  Thank you.

10             MR. O'ROARK:  Madam Chairman.

11             CHAIRMAN EDGAR:  Yes, sir.

12             MR. O'ROARK:  Verizon has one additional matter.  I'm

13   pleased to report that Verizon and TECO have been able to

14   resolve their differences, so we would request that for the

15   TECO issues, for issues that have not been stipulated, that the

16   Verizon position now be changed to simply "No position."

17             Further, we would like to withdraw an additional

18   portion of Mr. Walker's testimony, the portion beginning at

19   Page 4, Line 3, and going through Page 5, Line 24.  That's the

20   portion that deals with the TECO plan.

21             Further, I've tried to canvass the parties, and it

22   appears that no one would have cross-examination for Mr. Walker

23   on the balance of his testimony.  We would therefore request

24   that the remainder of his direct testimony be stipulated and

25   that Mr. Walker be excused.

FLORIDA PUBLIC SERVICE COMMISSION

27

1             CHAIRMAN EDGAR:  Ms. Fleming.

2             MS. FLEMING:  I don't believe staff has any

3   objections to that, if none of the other parties do.

4             CHAIRMAN EDGAR:  Okay.  So let me again make sure

5   that I understand what you're proposing:  To withdraw a portion

6   of Witness Walker's testimony at Page 4 from Line 3 through

7   Page 5, Line 24; and then, in light of the agreements and

8   stipulations, to excuse him.  And I need you to repeat that

9   last part for me again.

10             MR. O'ROARK:  To stipulate his testimony that remains

11   and then to excuse him from the proceeding.

12             MS. FLEMING:  Madam Chairman, if I may.  The

13   testimony that he's referring to stipulating would be the

14   testimony relating to the Progress docket.  So in essence

15   Mr. Walker is withdrawing the testimony as it relates to the

16   TECO docket and he's withdrawing the testimony as it relates to

17   the FPL docket.  The only remaining testimony would be the

18   Progress docket, which would be stipulated.

19             CHAIRMAN EDGAR:  Okay.  Yes.

20             MR. BADDERS:  One preliminary.  Instead of moving

21   Mr. McDaniel's testimony into the record, we actually need to

22   withdraw that.  The testimony of Mickey Harrelson against Gulf

23   Power was withdrawn earlier as a result of the approval of the

24   stipulation.  This is rebuttal to that testimony, so it should

25   also be withdrawn.

FLORIDA PUBLIC SERVICE COMMISSION

28

1             CHAIRMAN EDGAR:  The testimony of Witness McDaniel.

2             MR. BADDERS:  Yes, just his rebuttal.

3             CHAIRMAN EDGAR:  Ms. Fleming.

4             MS. FLEMING:  Okay.  Staff would like to note as well

5   that we have a Comprehensive Exhibit List, and the hearing

6   Exhibit Number 1 is the Comprehensive Exhibit List itself.

7   Staff also has Exhibits 2 through 7 that have been identified

8   that are stipulated exhibits, and at the appropriate time staff

9   would ask that Exhibits 1 through 7 be identified and moved

10   into the record.

11             CHAIRMAN EDGAR:  Would this be the appropriate time?

12             MS. FLEMING:  I believe so, Madam Chairman.

13             CHAIRMAN EDGAR:  Okay.  Any questions or comments

14   about the proposed stipulated list and Exhibits 1 through 7?

15   Okay.  Seeing none, the list will be marked as Exhibit 1 and

16   the items as described marked 2 through 7, and Exhibits

17   1 through 7 will be entered into the record.

18             (Exhibits 1 through 7 marked for identification and

19   admitted into the record.)

20             MR. WILLIS:  Madam Chairman, for Tampa Electric

21   Company, we have agreement of all the parties, I believe, to

22   move the order of witnesses so that Regan Haines would testify

23   after Manuel Miranda.  This is in order to give us some

24   additional time to try to work out a, a settlement and

25   stipulation with FCTA.  We're -- I think we can represent that

FLORIDA PUBLIC SERVICE COMMISSION

29

1   we're close to that, but we need just a little bit more time

2   and this will enable us to do that.

3             CHAIRMAN EDGAR:  Okay.  So the request is to take

4   Witness Haines out of order after Witness Miranda, which means

5   that we would, after oral -- opening statements, excuse me,

6   after opening statements we would begin with Progress Witness

7   Cutliffe.  And that is amenable to Progress?

8             MR. BURNETT:  Yes, ma'am.

9             CHAIRMAN EDGAR:  Thank you.  Any objections?  Seeing

10   none, okay, we will proceed in that manner when we come to the

11   witnesses.

12             Are there other matters?

13             MR. HATCH:  Madam Chairman, one housekeeping detail.

14   With the adoption by the Commission of the third-party attacher

15   process, there was an exhibit to Mr. Smith's testimony.  It's

16   left hanging what to do with Mr. Smith's actual direct

17   testimony, which basically is just explanatory of the exhibit

18   that was attached.  We can either withdraw it or you can -- the

19   parties had already previously agreed to stipulate it in.  It's

20   your choice.

21             CHAIRMAN EDGAR:  Ms. Fleming.

22             MS. FLEMING:  I don't think staff has a preference.

23   If the parties don't object to stipulating, putting it into the

24   record, I would suggest that we just put in the stipulated

25   testimony as well as the prefiled exhibit when we take up

FLORIDA PUBLIC SERVICE COMMISSION

30

1   Witness Smith's name.

2             MR. HATCH:  That works for us.  Thank you.

3             CHAIRMAN EDGAR:  And you'll remind me of that as

4   well?

5             MR. HATCH:  Yes, ma'am.

6             CHAIRMAN EDGAR:  Thank you.  Okay.  Any other matters

7   at this time?

8             Okay.  Ms. Fleming, any other matters from staff?

9             MS. FLEMING:  I'm not aware of any.

10             CHAIRMAN EDGAR:  Okay.  Is there any need at all to

11   take a few minutes to get papers in order in light of the

12   stipulations and other matters that we have addressed or are

13   you ready to move?

14             MS. FLEMING:  We're ready to proceed.

15             CHAIRMAN EDGAR:  You're ready?  Okay.  Then as

16   described in the Prehearing Order, we have opening statements

17   for each of the parties to be limited to five minutes.  I

18   recognize that Mr. Wright is representing two parties.  My

19   understanding, Mr. Wright, is that you will be making two

20   statements that roughly combine to approximately five minutes.

21   Is that --

22             MR. WRIGHT:  Yes, ma'am.

23             CHAIRMAN EDGAR:  And he says "Yes, ma'am," for the

24   record.  Okay.  Thank you very much.

25             Okay.  Give me just a moment and then we will begin

FLORIDA PUBLIC SERVICE COMMISSION

31

1   with opening statements.

2             (Pause.)

3             Okay.  Who would like to, who would like to kick us

4   off for the opening statements?  Mr. Butler, is that you?

5             MR. BUTLER:  I would be happy to.  Although I

6   conferred with staff at that brief break, and I think they

7   intend to do it in docket number order.  Is that right?

8             MR. YOUNG:  Yes, Madam Chairman.  For the clear

9   demarcation of the record, following the docket number order,

10   we believe, is more appropriate.  So we'll begin with TECO's

11   docket.

12             CHAIRMAN EDGAR:  Okay.  Mr. Willis, are you ready?

13             MR. WILLIS:  I am ready.

14             CHAIRMAN EDGAR:  Okay.  We are -- you are recognized.

15             MR. WILLIS:  I'm Lee Willis representing Tampa

16   Electric Company in Docket Number 070297-EU.  And we're here to

17   present Tampa Electric's storm hardening, which is a very

18   simple plan really.

19             Tampa Electric plans to continue as it has done since

20   the 1970s to build to construction Grade B, and that would be

21   for new distribution facilities, for expansions, rebuilds,

22   relocations of existing facilities.  The company also plans to

23   engage in specifically targeted pilot projects and upgrades

24   which will harden its system.  Most of Tampa Electric's plan

25   has been stipulated, and we are in the process, as we mentioned

FLORIDA PUBLIC SERVICE COMMISSION

32

1   earlier, of working on additional stipulations.

2             But with respect to construction Grade B, the purpose

3   of this docket is to require Tampa Electric's infrastructure to

4   be hardened to provide additional resilience to severe weather

5   and to reduce outages and restoration times.  Construction

6   Grade B is particularly appropriate for Tampa Electric's

7   service area because it has an equivalent wind speed of

8   116 miles an hour, which fits the storm profiles that the

9   company has experienced in its service area over the past 150

10   years.  Construction Grade C standards, on the other hand, has

11   an equivalent wind speed of only 86 miles an hour.  There's no

12   doubt that stronger Class B poles provide a more hardened

13   system than Class C poles.  Class B poles are required where

14   the crossing of the lines goes over an interstate highway, a

15   navigable waterway or a railroad, and this is because the

16   stronger B poles are less likely to cause an outage that would

17   obstruct a critical infrastructure that supports

18   transportation.  The systematic change out of poles which do

19   not meet Grade B is a part of Tampa Electric's plan, and it

20   will enable the company to conform its system systemwide to

21   Class B in a shorter period of time.

22             With respect to attachment standards, your rule

23   requires that the company submit an attachment standard and

24   procedures as part of its Storm Hardening Plan.  Tampa Electric

25   has done that.  And this rule provides that each utility shall

FLORIDA PUBLIC SERVICE COMMISSION

33

1   maintain written safety, reliability, pole loading capacity and

2   engineering standards for attachment by others to the electric

3   utility transmission and distribution system.  Each of the

4   standards which we propose are definitely related to the

5   provision of safe, adequate and reliable service.

6             It's really important, Commissioners, for utilities,

7   electric utilities in particular, to maintain control of what's

8   being added to their poles to assure that these poles are not

9   overloaded.  Tampa Electric, as you will see in the testimony,

10   has experienced some 20 percent of its attachments that were

11   unnoticed and unauthorized.  We believe that these standards

12   will help us reduce that, that number and to eliminate the

13   overloadings on the company's system.

14             In summary, Commissioners, Tampa Electric complies

15   with your rule by providing a reasonable and measured approach

16   to storm hardening, and we urge that it be approved.

17             CHAIRMAN EDGAR:  Thank you, Mr. Willis.

18             And next will be Progress.

19             MR. BURNETT:  Thank you, Madam Chair.  John Burnett

20   on behalf of Progress Energy.

21             Commissioners, after the 2004 and 2005 unprecedented

22   hurricane season this Commission immediately took action.  This

23   Commission looked, I think, at what we saw in 2004 and 2005 and

24   said on a, on a systemic basis, on a statewide basis what can

25   this Commission do to enhance hurricane hardening and

FLORIDA PUBLIC SERVICE COMMISSION

34

1   reliability?  The Commission came out with the wood pole

2   inspection plan, the vegetation management plan, the ten-point

3   storm preparedness plan and a comprehensive March 1st

4   reliability report that all of the IOUs adhere to now.  All

5   those plans again focused on statewide implementations of sound

6   practices and innovative practices that has helped Florida

7   become a more hardened and hurricane-ready state.

8             Also the Commission focused down at the next level

9   and said, and said, what can we do to focus in on particular

10   IOUs?  And that's the genesis of this storm hardening rule.

11   And the storm hardening rule takes it to another layer and says

12   what within a particular service territory, a particular

13   experience with a particular IOU can the IOUs do to harden

14   within their particular service territories?  And within that

15   we have focused on our particular activity and engaged in a

16   series of workshops.  The, the Commission had a series of

17   workshops where we got together with all of the other IOUs, the

18   third-party attachers and with staff.  And through these series

19   of workshops we learned a lot about what others were doing,

20   what was important, what were lessons learned, and we took that

21   and put that all together and it was a valuable process.

22             Also, we -- apart from learning, we also reached

23   important stipulations to that process with our third-party

24   attachers of how to communicate better, the process within the

25   process that the Commission just approved.  It is, it is now a

FLORIDA PUBLIC SERVICE COMMISSION

35

1   uniform process that we communicate with our third-party

2   attachers.  We came to important stipulations in Progress on

3   overlashing and pole identification that's going to help our

4   hurricane restoration efforts be that more fluid.

5             So in summary, what we're here for today is we're

6   focusing on the specific utility plans.  What has Progress

7   Energy done on that next level down in addition to all the

8   other initiatives the Commission has enacted?  And Progress's

9   Storm Hardening Plan absolutely helps enhance reliability and

10   will help to reduce restoration costs and outage times in a

11   prudent and cost-effective manner.

12             As you've seen here today with this myriad of

13   stipulations that went on, all the Intervenors in Progress's

14   docket have either taken no objection, have agreed to or have

15   not objected to Progress's plan.  So we're here today to answer

16   any questions that the Commission or staff may have, and we

17   look forward to entertaining those questions at the appropriate

18   time.  Thank you.

19             CHAIRMAN EDGAR:  Thank you.

20             And that brings us to Gulf.

21             MR. BADDERS:  Good morning.

22             CHAIRMAN EDGAR:  Good morning.

23             MR. BADDERS:  I'm Russell Badders and I'm appearing

24   on behalf of Gulf Power Company.

25             The Commission has before it Gulf Power's first Storm

FLORIDA PUBLIC SERVICE COMMISSION

36

1   Hardening Plan filed pursuant to the Commission's storm

2   hardening rules.  Gulf received praise from its customers and

3   governmental entities alike for its storm restoration efforts

4   after Hurricanes Ivan and Dennis in 2004 and in 2005.

5   Notwithstanding, Gulf did not sit back and continue business as

6   usual.  The company further refined its storm restoration plan

7   and actively participated here at the Commission in storm

8   hardening discussions.

9             Gulf Power recognized, as did this Commission, that a

10   further look at preventing storm damage was prudent.  Gulf's

11   Storm Hardening Plan is the result of that closer look at storm

12   hardening.  Hurricanes Ivan and Dennis both provided Gulf with

13   recent, first-hand experience with impacts of wind and storm

14   surge on an electric utility system.  These experiences form

15   the basis of Gulf's Storm Hardening Plan.

16             Briefly, what is Gulf's plan?  The foundation of

17   Gulf's plan is Gulf's ten-point plan already approved by the

18   Commission.  In addition to that, Gulf is adopting Grade B

19   construction standards for all new distribution, construction

20   and major distribution rebuilds.  Further, Gulf's plan is to

21   conduct pilot projects to determine the effectiveness of

22   extreme wind load standards.  Gulf will also continue to look

23   at potential damage mitigation techniques related to

24   underground facilities.

25             After Hurricanes Ivan and Dennis caused severe damage

FLORIDA PUBLIC SERVICE COMMISSION

37

1   to Gulf's coastal underground utilities in 2004 and 2005, Gulf

2   implemented several design changes in underground construction

3   to test their effectiveness for mitigation of storm damage.  It

4   is important to note that both the Commission and the parties

5   have acknowledged that this is an evolving process and that

6   this Storm Hardening Plan is just a first step.  This plan will

7   also be refined over time as more and better information

8   becomes available.

9             Gulf is committed to pursuing cost-effective storm

10   hardening measures.  The plan before you -- while the

11   activities in Gulf's Storm Hardening Plan can reasonably be

12   expected to enhance reliability and to reduce restoration costs

13   and outage times in a cost-effective manner, Gulf will continue

14   to look at the activities in its plan and at new activities as

15   they develop so Gulf can better understand and implement storm

16   hardening.  Thank you.

17             CHAIRMAN EDGAR:  Thank you.

18             And now Mr. Butler.

19             MR. BUTLER:  Thank you, Madam Chairman.  Good

20   morning, Commissioners.

21             Following the 2005 storm season two things became

22   very clear to FPL.  First, our customers and public officials

23   representing them were unhappy with the number and especially

24   the length of the power outages following hurricanes.  This

25   concern reached a peak, excuse me, following Hurricane Wilma in

FLORIDA PUBLIC SERVICE COMMISSION

38

1   October 2005 when FPL needed 18 days to fully return service to

2   all of our customers.  These outages were not lengthy because

3   of any limitations on FPL's restoration efforts.  Rather, they

4   were lengthy because the damage to FPL's electric distribution

5   system was substantial.  One significant complicating factor in

6   FPL's restoration efforts was the number of broken poles.

7   Replacing broken poles is time-consuming and expensive, but

8   restoration work on the affected facilities cannot progress

9   until the broken poles are replaced.

10             Second, FPL's newly developed Storm Forensics Team

11   found that one factor unexpectedly caused over half of the

12   broken poles in Hurricane Wilma:  Wind-only damage.  These

13   poles failed not because anything fell on them or because they

14   were deteriorated, but simply because the wind forces on the

15   poles exceeded their design strength.  This was true even

16   though the great majority of FPL's distribution poles were

17   designed for the NESC's highest normal standard of

18   construction, Grade B, and KEMA concluded that FPL's system

19   performed as designed.

20             Over the past year and a half the Commission and the

21   IOUs have collaborated effectively to develop several programs

22   to address the public concern over hurricane-related outages.

23   Consistent with the Commission's ten-point storm initiatives,

24   FPL now has a program in place to increase tree trimming, which

25   should help reduce the downed wires and broken poles caused by

FLORIDA PUBLIC SERVICE COMMISSION

39

1   vegetation.  Pursuant to the Commission's pole inspection

2   order, we have an aggressive pole inspection program, and that

3   should help identify and repair or replace poles that are

4   deteriorated or have an accumulation of too many facilities

5   attached to them.  And the Commission has approved FPL's GAF

6   tariff, which helps local governments pay for underground

7   conversion when they believe this is the best way to protect

8   their communities against hurricane-related outages.

9             However, none of those programs addresses the more

10   than 50 percent of all pole failures in Hurricane Wilma that

11   were wind only.  FPL cannot consider its response to the

12   lessons of the 2004/2005 storm seasons to be complete without

13   addressing wind-only pole breakage.

14             FPL's Electric Infrastructure Storm Hardening Plan

15   that's before you today is our response to wind-only pole

16   breakage.  Basically it starts with the premise that even

17   building to the NESC's highest normal construction standard has

18   proven inadequate to protect FPL's distribution system against

19   wind-only pole breakage.

20             Based on the 2005 forensics data, the KEMA report and

21   analysis of industry pole breakage experience by Davies

22   Consulting we propose to move FPL's distribution system toward

23   the NESC's extreme wind loading or EWL standard.  The EWL

24   standard has served extremely well for years as the basis for

25   designing FPL's transmission system but previously it has not

FLORIDA PUBLIC SERVICE COMMISSION

40

1   been applied to FPL's distribution system.  FPL plans to focus

2   our EWL hardening initially on the distribution circuits

3   serving facilities that are the most critical to have operating

4   during and after a hurricane such as 911 centers and acute care

5   hospitals.  We have worked with the EOCs in each county to

6   identify and prioritize these critical infrastructure

7   facilities.  Our plan also recognizes the importance of having

8   key commercial establishments available after a hurricane such

9   as grocery stores, gasoline stations and restaurants.  We

10   intend to apply a highly targeted cost-effective technique

11   called incremental hardening to the circuits serving these

12   commercial establishments.

13             Finally, our plan calls for all new facilities and

14   major rework of existing facilities to be built to EWL

15   standards consistent with our ultimate goal of EWL hardening

16   all of the distribution system.

17             Because of the size and complexity of FPL's

18   distribution system, fully implementing FPL's hardening plan

19   will take many years.  There will be many opportunities along

20   the way for FPL, the Commission and interested parties,

21   including third-party attachers, to revisit our approach.  We

22   welcome this continued review and we are prepared to adjust

23   both the direction and the deployment of our plan where

24   appropriate.

25             We cannot agree, however, with the position that we

FLORIDA PUBLIC SERVICE COMMISSION

41

1   should not even begin to implement EWL hardening until more

2   data has been collected.  We feel that the lessons of the

3   2004/2005 storm seasons are clear enough to compel action now.

4   Waiting for more data will simply mean lost opportunities to

5   start protecting customers against the disruptions that became

6   all too familiar in 2004 and 2005.  Thank you.

7             CHAIRMAN EDGAR:  Thank you.  And we'll proceed down

8   the list as, as it is in the Prehearing Order, unless there is

9   a compelling reason to do it in a different order.  And so that

10   would bring us next to recognizing FCTA.

11             MS. BROWNE:  Thank you, Madam Chair, Commissioners.

12             My name is Maria Browne and I represent the Florida

13   Telecommunications Cable Television Association, FCTA.

14             The FCTA intervened in this proceeding because its

15   member operators have hundreds of thousands of attachments.

16             (Technical difficulty with audio system.)

17             CHAIRMAN EDGAR:  Did we -- oh, are we back?  Okay.  I

18   apologize.

19             MS. BROWNE:  That's okay.

20             CHAIRMAN EDGAR:  Then we'll keep going.

21             MS. BROWNE:  I'll start over.  The FCTA has

22   intervened in this proceeding because its member operators have

23   hundreds of thousands of attachments on poles covered by the

24   four utility Storm Hardening Plans.  FCTA's members rely on

25   these pole attachments for the delivery of their video, voice

FLORIDA PUBLIC SERVICE COMMISSION

42

1   and Internet services to over 5 million residents throughout

2   the State of Florida.  It is therefore equally important to

3   FCTA's members, as it is to the electric utilities, to ensure

4   that the Florida utility pole infrastructure is safe, reliable

5   and able to withstand storms and extreme weather.  Indeed, the

6   shared goal of pole owners and attachers is to prevent Florida

7   residents from losing power, cable, telephone and Internet

8   services in storms such as those experienced in the 2005

9   season, and when that does not happen, to ensure that service

10   is restored as quickly as possible.

11             The controlling rule mandates that utility poles be

12   storm hardened in a prudent, practical and cost-effective

13   manner, and requires consideration of not only the benefits

14   that may be produced by building to different grades of

15   construction, but also the potential costs to the utility

16   ratepayers and to third-party attachers.  After months of

17   workshops, exchanging information and further development of

18   the plans we have a better, if not clearer, sense of what the

19   costs of building to extreme wind will be.  Unfortunately,

20   given the untested nature of applying extreme wind to poles

21   less than 60 feet tall, it is not yet evident that building to

22   extreme wind will guarantee that significantly fewer poles will

23   come down in storms.  That is why FCTA supports the limited

24   pilot project approach that has been advocated by three of the

25   four utilities in their plans.

FLORIDA PUBLIC SERVICE COMMISSION

43

1             FCTA also supports applying extreme wind to the

2   interstate highway crossings, which all four utilities have

3   also done.  It is prudent, practical and cost-effective to test

4   extreme wind on critical infrastructure and to collect forensic

5   data about the effectiveness of these construction techniques.

6   It is not prudent, however, to decide based on the results of

7   one storm to deploy extreme wind throughout an entire utility

8   footprint, regardless of topography.  And to clarify, FCTA is

9   not asking this Commission to delay applying extreme wind to

10   pilot projects or critical infrastructure or to the interstate

11   highway crossings.

12             The controlling rule also requires pole owners to

13   collaborate with, seek impact from and attempt in good faith to

14   address the concerns raised by third-party attachers.  FCTA has

15   worked closely with Mickey Harrelson, a utility infrastructure

16   consultant, in evaluating the details of each Storm Hardening

17   Plan, including the different grades of construction being

18   proposed, each utility's deployment strategy and its standards

19   and procedures for third-party attachments.  Mr. Harrelson has

20   evaluated the extent to which each plan meets or exceeds the

21   NESC and has attempted, with the information that has been

22   provided, to evaluate the costs and benefits of each planned

23   third-party attacher.

24             Among the concerns raised by Mr. Harrelson are the

25   significant potential cost increases to cable operators

FLORIDA PUBLIC SERVICE COMMISSION

44

1   associated with the new grades of construction in the form of

2   increased make-ready charges, transfer costs and increased

3   rental rates, as well as the substantial potential delays in

4   provisioning service in a highly competitive market resulting

5   from new attachment procedures.

6             We are, however, very excited about the improved

7   communication that will result from the approved process within

8   a process.  It is clear that each of the utilities has

9   attachment standards and procedures that meet or exceed the

10   NESC, and it is FCTA's belief that such a finding is all that

11   is required by this Commission.  The specific manner in which

12   each utility assures that its attachment standards and

13   procedures meet or exceed the NESC cannot be dictated

14   unilaterally by the utility.  Instead, the specific standards

15   and procedures must be negotiated in good faith under the

16   auspices of the Federal Communications Commission.  Indeed, the

17   rates, terms and conditions of pole attachment agreements have

18   been litigated before the FCC, the federal courts of appeal and

19   the United States Supreme Court.  These issues need not be

20   revisited in the context of the Storm Hardening Plans.  In

21   fact, they cannot be because the jurisdiction over the rates,

22   terms and conditions of access to utility poles in the State of

23   Florida is under the exclusive jurisdiction of the Federal

24   Communications Commission.

25             While the FCTA has raised issues in response to all

FLORIDA PUBLIC SERVICE COMMISSION

45

1   four plans as previously reported today, it is pleased that it

2   was able to reach an amicable resolution with Progress Energy

3   Florida, Gulf Power and on certain issues with FPL.  It is

4   continuing to discuss issues with Tampa Electric Company and

5   it's hopeful that it will also be able to resolve matters

6   there.  Thank you.

7             CHAIRMAN EDGAR:  Thank you.  Mr. Hatch.

8             MR. HATCH:  AT&T waives its opening.

9             CHAIRMAN EDGAR:  Thank you.  Ms. Masterton.

10             MS. MASTERTON:  Thank you, Commissioner.  Embarq also

11   waives its opening statement.

12             CHAIRMAN EDGAR:  Okay.  Mr. O'Roark.

13             MR. O'ROARK:  Verizon also waives its opening

14   statement.

15             CHAIRMAN EDGAR:  Thank you.  Mr. Wright.

16             MR. WRIGHT:  Thank you, Madam Chairman.  Because it's

17   presented in this order in the Prehearing Order, I will give

18   the MUUC's opening statement in the FPL docket first, followed

19   by the Panama City Beach opening statement in the Gulf Power

20   docket.

21             Commissioners, your rules, specifically Rule

22   25-6.0342(1), declare that the rules applicable to this

23   proceeding are intended to require the cost-effective

24   strengthening of critical electric infrastructure to increase

25   the ability of transmission and distribution facilities to

FLORIDA PUBLIC SERVICE COMMISSION

46

1   withstand extreme weather conditions and reduce restoration

2   costs and outage times to end use customers associated with

3   extreme weather conditions.

4             Your same rule, (2) goes on to require Storm

5   Hardening Plans to be filed by the investor-owned utilities and

6   to declare the Commission's standard of review of those plans

7   as follows.  In a proceeding to approve a utility's plan, the

8   Commission shall consider whether the utility's plan meets the

9   desired objectives of enhancing reliability and reducing

10   restoration costs and outage times in a prudent, practical and

11   cost-effective manner to the affected parties.

12             FPL's plan addresses the requisite items listed in

13   the Commission's rules, and we would agree that FPL's plan is

14   practical as far as it goes.  In particular, FPL's plan

15   deserves credit for moving to the extreme wind loading criteria

16   for new distribution and for major reconstruction, relocation

17   and refurbishment work.  However, the MUUC believes that

18   additional efforts, especially with regard to encouraging and

19   implementing underground facilities, would be cost-effective

20   and therefore prudent because we believe FPL's plan does not

21   provide adequate analysis of the cost and benefits of

22   undergrounding as a hardening technology as compared to

23   alternate construction modes.  We believe that FPL's plan

24   cannot be said to be demonstrably prudent and cost-effective

25   and accordingly should not be approved to that degree.

FLORIDA PUBLIC SERVICE COMMISSION

47

1             That concludes my opening statement with regard to

2   070301.  I'd like to proceed to my opening statement, our

3   opening statement in the Gulf Power docket.

4             In Docket 070299, Commissioners, I represent the City

5   of Panama City Beach and the Panama City Beach Community

6   Redevelopment Agency.  The Municipal Underground Utilities

7   Consortium has also joined in that docket to support the City

8   of Panama City Beach, which is a member of that consortium.  I

9   previously read to you the declarations of policy and intent

10   and standard of review from your rules, and I don't intend to

11   repeat those now, but they're equally applicable to Gulf's

12   plan.

13             Panama City Beach and its Community Redevelopment

14   Agency are asking the Commission in this docket that you not

15   approve Gulf's Storm Hardening Plan because it is inadequate

16   with respect to its consideration of undergrounding as a storm

17   hardening measure.  Despite Gulf's claims that it considered

18   undergrounding as a storm hardening measure and its further

19   claims that it considers cost-effectiveness and reliability in

20   evaluating potential storm hardening measures, Gulf did not

21   make an adequate evaluation of the costs and benefits of

22   undergrounding either with respect to the dollar cost and

23   benefits or with respect to the reliability benefits available

24   from undergrounding in developing its plan.  Perhaps most

25   egregiously Gulf dismisses undergrounding in this docket with

FLORIDA PUBLIC SERVICE COMMISSION

48

1   its assertion that it lacks, quote, definitive proof, unquote,

2   of the benefits of undergrounding, and that it will in the

3   future after future storms hit its service area and impact its

4   customers collect data that can be used to evaluate

5   undergrounding, while at the same time ignoring data that has

6   been readily available to Gulf.  Gulf's own data show, provided

7   in discovery show that Panama City Beach with a much higher

8   percentage, roughly double, of underground facilities than

9   Pensacola faired much, much better than Pensacola in comparable

10   storm conditions in Hurricane Dennis in 2005.  At a bare

11   minimum, these data indicate that further and deeper evaluation

12   of undergrounding is warranted.  I apologize that I forget the

13   name of the famous person who made this quote, but it reminds

14   me of the famous quote, "Those who do not learn from history

15   are doomed to repeat its mistakes."  Gulf should be looking at

16   its own data and now.

17             Our witnesses, Peter Rant and R. L. Willoughby, have

18   specific field experience that indicates that there is at least

19   sufficient definitive proof, including the Federal Emergency

20   Management Agency providing grants to support undergrounding on

21   barrier islands served by a coastal utility in North Carolina,

22   to warrant deeper and more thorough investigation.  And FPL's

23   specific real-world experience also indicates that there is

24   sufficient proof for this largest IOU in Florida to make

25   undergrounding one of the focal efforts of its Storm Secure

FLORIDA PUBLIC SERVICE COMMISSION

49

1   Plan.  We are not saying that undergrounding is a panacea or

2   that all of Gulf's or any other utility's existing overhead

3   facilities should be converted to underground in a blanket

4   fashion starting immediately on a wholesale basis.  What we are

5   saying is that any utility's Storm Hardening Plan should be

6   based on a solid, thorough evaluation of the costs and

7   benefits, both dollars and real reliability impacts of all

8   available alternatives.  Utility Storm Hardening Plans should

9   be implemented to provide and informed by accurate value, cost

10   and price signals for all available storm hardening techniques,

11   including undergrounding.

12             The evidence shows that Gulf's plan must be found

13   lacking in this regard and, accordingly, the Commission should

14   disapprove Gulf's plan as it relates to undergrounding, and to

15   direct Gulf to return to the Commission soon, we would suggest

16   next June or July, with a more adequate plan.  Thank you.

17             CHAIRMAN EDGAR:  Thank you, Mr. Wright.

18             That concludes the opening statements.  And we will

19   move here in a moment to administering the oath to the

20   witnesses.  But before we do that, staff, are there any general

21   comments?

22             MR. YOUNG:  Yes, Madam Chairman.  Staff would note

23   for the record, as indicated in the Prehearing Order, that the

24   four dockets were previously consolidated for purposes of the

25   hearing, and some parties have only intervened in a specific

FLORIDA PUBLIC SERVICE COMMISSION

50

1   utility docket.  To that end, staff and the parties have agreed

2   on the following process.  Each witness's testimony summary

3   should make clear the storm hardening docket, the Storm

4   Hardening Plan to which his or her testimony pertains.

5   Intervenor witnesses who have prefiled testimony in multiple

6   dockets shall summarize their testimony separately for each

7   such docket and will then be cross-examined with respect to

8   that docket before proceeding to testify in other dockets, and

9   that process will follow for each docket they have intervened

10   in.  Only those parties that have intervened in a specific

11   Storm Hardening Plan docket may cross-examine the witness

12   pertaining to the testimony in that docket.  Cross-examining

13   parties shall clearly specify on the record which Storm

14   Hardening Plan the cross-examination is directed.

15             CHAIRMAN EDGAR:  And as always, and to once again

16   state the obvious, we have numerous dockets, we have numerous

17   parties, we have numerous witnesses.  I ask for your

18   cooperation as we move through it.  And as I always do, would

19   ask that we make every effort to limit friendly cross.  And

20   with that, I will ask the witnesses to stand with me as a group

21   and we'll go ahead and swear you in.

22             (Witnesses collectively sworn.)

23             Okay.  We will move to witness testimony.  But before

24   we do, let's just take about five minutes to switch out and

25   move to the next stage of the proceeding.  My intention will be

FLORIDA PUBLIC SERVICE COMMISSION

51

1   to go for about an hour or so and then we will take a lunch

2   break.  So we are on a short recess for approximately five

3   minutes, and then we will begin with the first witness.

4             (Recess taken.)

5             We will go back on the record.  And when we had gone

6   on break we were just about to begin with the witness

7   testimony.  We previously agreed to take up Witness Haines a

8   little later in the proceeding, and so that brings us to

9   Witness Cutliffe.

10             Mr. Burnett.

11             MR. BURNETT:  Yes, ma'am.  Thank you, Madam Chairman.

12   I didn't know if there was a potential to have Mr. Cutliffe

13   excused, Ms. Fleming.

14             MR. YOUNG:  Staff has no questions.

15             CHAIRMAN EDGAR:  I was actually waiting for you to

16   ask.

17             MR. BURNETT:  Oh, I'm very sorry.

18             CHAIRMAN EDGAR:  No.  That's okay.

19             MR. BURNETT:  But my understanding is staff has no

20   questions.  So if it please the Commission, Mr. Cutliffe could

21   be excused.

22             CHAIRMAN EDGAR:  Okay.  Commissioners, are there any

23   questions for Witness Cutliffe?  Seeing none.  And staff has

24   concurred with the request, so let's go ahead and take up -- do

25   we need to take up the exhibits and prefiled testimony?

FLORIDA PUBLIC SERVICE COMMISSION

52

1             MS. FLEMING:  That's correct, Madam Chairman.

2             MR. BURNETT:  Yes, ma'am.  And at this point we would

3   move in the direct prefiled testimony of Jason Cutliffe and his

4   exhibits JC-1T through JC-3T into evidence.

5             CHAIRMAN EDGAR:  Okay.  The prefiled testimony of

6   Witness Cutliffe will be entered into the record as though

7   read.  And Exhibits 9, 10 and 11, seeing no objection, will be

8   entered into the record.

9             (Exhibits 9, 10 and 11 marked for identification and

10   admitted into the record.)

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

74

1             MR. BURNETT:  Thank you, Madam Chairman.  And also

2   the direct prefiled testimony of Mickey Gunter and his prefiled

3   exhibits as well, we would move those into the record as though

4   read.

5             CHAIRMAN EDGAR:  Okay.  And staff concurs?

6             MS. FLEMING:  Yes.  Madam Chairman, we would like to

7   note for the record that Exhibits 9 through 17 are being moved

8   into only Docket 070298.

9             CHAIRMAN EDGAR:  Okay.  Exhibits 9 through 17, so

10   noted, are being entered into the record for the docket

11   regarding the Progress plan.  And we will go ahead and enter

12   12, 13, 14, 15, 16 and 17 into the record.

13             (Exhibits 12 through 17 marked for identification and

14   admitted into the record.)

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

82

1             MR. BURNETT:  And, Madam Chair, if I may, based on

2   the stipulations today, Progress has no cross-examination for

3   any of the rebuttal witnesses, I mean, for any of the

4   intervenor witnesses, nor do we have any rebuttal.  So if it

5   please the Commission, we would ask to be excused from the

6   proceeding.

7             CHAIRMAN EDGAR:  You don't want to stay for the

8   party?

9             MR. BURNETT:  I would love to, Madam Chair, but --

10             (Laughter.)

11             CHAIRMAN EDGAR:  Recognizing that Progress's case in

12   chief has basically been made with the stipulations and the

13   testimony and exhibits that have been entered, you may be

14   excused from the rest of the proceeding.

15             MR. BURNETT:  Thank you.

16             CHAIRMAN EDGAR:  Thank you.  Okay.  So that takes

17   care of Witness Cutliffe, Witness Gunter, and brings us to

18   Witness Battaglia.

19             MR. BADDERS:  I believe we're ready to proceed,

20   Commissioner.

21             CHAIRMAN EDGAR:  We're ready.

22             MR. BADDERS:  Thank you.

23                         EDWARD J. BATTAGLIA

24   was called as a witness on behalf of Gulf Power Company and,

25   having been duly sworn, testified as follows:

FLORIDA PUBLIC SERVICE COMMISSION

83

1                         DIRECT EXAMINATION

2   BY MR. BADDERS:

3        Q    Mr. Battaglia, were you present earlier this morning

4   when the witnesses were sworn?

5        A    Yes, I was.

6        Q    And you took the oath?

7        A    Yes.

8        Q    Please state your name and your business address for

9   the record.

10        A    My name is Edward J. Battaglia.  My business address

11   is 1 Energy Place, Pensacola, Florida 32520.

12        Q    By whom are you employed and in what capacity?

13        A    Gulf Power Company as Technical Services Manager.

14        Q    Have you prefiled direct testimony consisting of 20

15   pages?

16        A    Yes.

17        Q    Do you have any changes to that testimony?

18        A    No.

19        Q    If I were to ask you the same questions today, would

20   your answers be the same?

21        A    Yes.

22        Q    Do you also have one exhibit attached to your

23   testimony?

24        A    Yes.

25        Q    And it has ten schedules?

FLORIDA PUBLIC SERVICE COMMISSION

84

1        A    No.

2        Q    How many schedules is attached --

3        A    Oh, excuse me.  Ten schedules.

4        Q    Ten schedules.  I would like to -- do you have any

5   changes to that exhibit?

6        A    No.

7             MR. BADDERS:  I would like to identify Exhibit EJB-1.

8             CHAIRMAN EDGAR:  Which is marked as Exhibit 18 in the

9   comprehensive exhibit list.

10             MR. BADDERS:  Thank you.

11             (Exhibit 18 marked for identification.)

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

105

1   BY MR. BADDERS:

2        Q    Mr. Battaglia, please provide the summary of your

3   testimony.

4        A    Gulf based the development of its Storm Hardening

5   Plan on its many years of storm restoration experience, the

6   lessons learned from Hurricanes Ivan and Dennis, along with

7   feedback from state and county emergency operation personnel.

8   The foundation of Gulf's plan is the ten-part initiatives and

9   wood pole inspection plan already approved by this Commission.

10             Gulf's operational, maintenance and storm restoration

11   experience strongly support that these initiatives hold the

12   most potential for accomplishing the objectives of reduced

13   customer outages and reduced restoration time during both storm

14   situations and on a day-to-day reliability basis.

15             Based on the potential benefits and costs these

16   initiatives will provide the most value to our customers in

17   regard to storm hardening and being cost-effective in meeting

18   the real requirements.

19             Building on the ten-part initiatives and the wood

20   pole inspection program, Gulf formulated a plan to meet the

21   requirements of the new rules which address extreme wind

22   loading.  While there is no empirical forensic data showing the

23   exact storm impacts of Hurricanes Ivan and Dennis, field

24   observations by Gulf personnel involved in the restoration

25   effort after these hurricanes and past storms were used as an

FLORIDA PUBLIC SERVICE COMMISSION

106

1   input for determining how to storm harden Gulf's system, along

2   with its experience with day-to-day operation and maintenance

3   of its electric system.

4             Gulf's storm field experience strongly indicates that

5   pole failures on its distribution system are not the result of

6   the wind itself during a hurricane, but rather the wind-carried

7   debris and off right-of-way trees.  Based on this information,

8   Gulf improved its existing design specifications, developed new

9   specifications and updated storm preparations and restoration

10   practices which reflect these lessons learned from past

11   hurricanes.  And over the next three years Gulf will be

12   undertaking targeted pilot projects to upgrade its critical

13   infrastructure and interstate crossings to extreme wind loading

14   standards.

15             In addition, Gulf listened and learned from the

16   Florida Public Service Commission workshops and reviewed

17   National Oceanic and Atmospheric Administration data for

18   Northwest Florida's hurricane history.  Based on this, Gulf

19   amended its plan.  For new construction, major expansions,

20   rebuilds and relocations of distribution facilities Gulf is

21   adopting the NESC standard for Grade B construction.

22             In the development of Gulf's Storm Hardening Plan,

23   transitioning to underground was considered as a storm

24   hardening option.  Although underground distribution appears to

25   be an attractive method of avoiding wind damage during a storm

FLORIDA PUBLIC SERVICE COMMISSION

107

1   event, underground construction has limitations that cause

2   additional issues on a day-to-day operational basis and during

3   storm restoration.  Finding and repairing damage to underground

4   facilities after a storm event and on a day-to-day basis takes

5   longer, resulting in longer outages.

6             Finally, underground is susceptible to storm surges

7   and to damage during cleanup after storms.  Gulf has recent

8   first-hand experience with the damage storm surge does to

9   underground facilities on barrier and coastal areas.  Based on

10   Gulf's experience with underground construction on both a

11   day-to-day operational basis and during storm restoration,

12   underground construction was not adopted as a storm hardening

13   activity in the plan.  However, Gulf has not ruled out

14   underground as a storm hardening option in the future.  Gulf is

15   conducting several distribution pilot projects in potential

16   storm surge areas to test the effectiveness of mitigation

17   techniques and has joined the other IOUs through PURC in

18   further studying underground as a possible storm hardening

19   option.

20             In conclusion, this is Gulf's first Storm Hardening

21   Plan pursuant to Florida Public Service Commission rule.  As

22   data continues to be gathered and research progresses, Gulf

23   will continue to evaluate and refine its approach to storm

24   hardening in a way that balances storm hardening with the need

25   to maintain reasonable cost to all of its customers and still

FLORIDA PUBLIC SERVICE COMMISSION

108

1   achieve the expected results of reduced outages and restoration

2   times.  This concludes my summary.

3             MR. BADDERS:  For clarity of the record,

4   Mr. Battaglia's testimony is offered in Docket 070299, the Gulf

5   Power docket.

6             CHAIRMAN EDGAR:  Thank you.

7             MR. BADDERS:  And we tender Mr. Battaglia for cross.

8             CHAIRMAN EDGAR:  Are there questions from AT&T?  No

9   questions.  Embarq?  No questions.  FCTA.

10             MR. SEIVER:  No questions.

11             CHAIRMAN EDGAR:  No questions.

12             Mr. Wright.

13             MR. WRIGHT:  Thank you, Madam Chairman.  Good

14   morning.

15                          CROSS EXAMINATION

16   BY MR. WRIGHT:

17        Q    Good morning, Mr. Battaglia.  As I understand it, you

18   are sponsoring and testifying with regard to most of Gulf's

19   Storm Hardening Plan; is that correct?

20        A    That is correct.

21        Q    Mr. McDaniel is sponsoring those parts that relate to

22   the third-party attacher issues; is that correct?

23        A    That is correct.

24        Q    Thank you.  And I believe you claim at Pages 19 and

25   20 and perhaps elsewhere in your testimony that Gulf's plan is

FLORIDA PUBLIC SERVICE COMMISSION

109

1   cost-effective.  Is that also correct?

2        A    That is correct.

3             MR. WRIGHT:  Thank you.  I'm going to distribute an

4   exhibit which consists of Gulf's responses to Panama City

5   Beach's interrogatories 41 through 47, Madam Chairman.

6             CHAIRMAN EDGAR:  So we will mark this as Exhibit

7   Number 45.

8             (Exhibit 45 marked for identification.)

9             MR. WRIGHT:  Madam Chairman, thank you for marking

10   this as Exhibit 45 for identification.

11   BY MR. WRIGHT:

12        Q    Mr. Battaglia, I'd like to ask you first to turn sort

13   of towards the back of this and look at Gulf's responses to

14   Interrogatories 46 and 47.  I believe that the attachments to

15   each of Gulf's responses 46 and 47 is exactly the same

16   document, but could, as a preliminary matter could you confirm

17   that they're the same document?

18        A    They are the same.

19        Q    Thank you.  I would like to understand what this

20   document shows us.  From your testimony it, it seems to show

21   the benefits, potential benefits of going to extreme wind

22   loading standards, but I'm not 100 percent clear that that's

23   what it is.  Is that accurate?

24        A    The calculation methodology that you're looking at,

25   that methodology is basically to try to give an estimated

FLORIDA PUBLIC SERVICE COMMISSION

110

1   benefits associated with, can be used for, in conjunction with

2   Grade B and with extreme wind loading as far as trying to

3   identify possible benefits.

4        Q    So I think the bottom line number is based on total

5   benefits for a major storm the expected value is about

6   $1.1 million; is that accurate?

7        A    Based on these calculation sheets, it can range up to

8   that.  And, again, in looking at this particular methodology,

9   it needs to be understood that this is based on extreme, as far

10   as extreme conditions, data that we basically use from

11   Hurricane Ivan since at this point that was Gulf's worst storm

12   that it experienced.  So, again, it was trying to tag off of

13   that as far as using it to, to try to get some sense of

14   possible benefits which can range up to that maximum shown.

15   But also with the understanding that it's dependent upon

16   obviously the frequencies of storms as far as, and intensity of

17   storms as far as how often you may actually see these possible

18   benefits.

19        Q    Just so the record is clear, is the $1.1 million the

20   maximum benefit as a comparison of extreme wind loading to

21   Grade C or Grade B to Grade C or what's the -- what is it that

22   would provide the $1.1 million a year in benefits is the

23   question I'm trying to ask?

24        A    In conjunction with question number 6, it is with

25   extreme wind loading criteria.

FLORIDA PUBLIC SERVICE COMMISSION

111

1        Q    Thank you.  I believe you testified in your direct

2   testimony, I think at Page 13 and also in your summary you

3   mentioned that it is Gulf's experience that the vast majority

4   of damage sustained by your distribution system is due to

5   flying debris; is that correct?

6        A    That is correct.

7        Q    Thank you.  Will you agree that undergrounding,

8   undergrounded facilities are, with very rare exceptions, not

9   subject to damage from wind-blown debris?

10        A    Up to a point.  And, again, underground facilities,

11   part of what goes on with underground facilities is typically

12   having pad-mounted switch gears, perhaps aboveground,

13   transformers aboveground, all of which could possibly be

14   damaged by wind-blown debris, which includes trees coming down

15   perhaps on an underground.  So there is some possible damage

16   due to wind-blown debris even with underground.

17        Q    Yes.  And I understand that.  That's why I qualified

18   my question by saying "with rare exceptions."

19             Will you agree that the type of damage that you just

20   described from wind-blown debris impacting underground

21   appurtenances is relatively rare?

22        A    Again, based on my experience as far as saying

23   relatively rare, you have to qualify that in the sense that,

24   relatively rare in the sense that in some areas your percentage

25   of underground versus overhead may be very small.  So, again,

FLORIDA PUBLIC SERVICE COMMISSION

112

1   the odds of wind-blown debris affecting a very small piece of

2   it wherever it may be located may be rare.  But if you have an

3   area that is a high percentage underground, that may not be the

4   case.

5        Q    Have you ever seen a road sign removed from its

6   foundation by the wind take a transformer or a switch cabinet

7   out of service?

8        A    I have not seen a road sign, no.

9        Q    Have you, have you seen a tree, where a tree has

10   fallen on a transformer cabinet?

11        A    Yes, I have.

12        Q    How many times?

13        A    In my experience as far as from hurricane, excuse me,

14   as far as the area that I worked on, there were several small

15   areas in which it was impacted.

16        Q    Can you say how many cabinets you've actually seen

17   had a tree fall on them?

18        A    Personally I would say, you know, less than a half a

19   dozen.

20        Q    Thank you.  Will you agree that with regard to

21   potential damage from wind-blown debris, undergrounding will

22   sustain less damage and, therefore, will incur less storm

23   restoration costs as a result of being impacted by wind-blown

24   debris?

25             MR. BADDERS:  I'm going to object to the form of the

FLORIDA PUBLIC SERVICE COMMISSION

113

1   question.

2             CHAIRMAN EDGAR:  For what reason?

3             MR. BADDERS:  I think there were two questions there

4   with two assumptions.

5             CHAIRMAN EDGAR:  Can you rephrase?

6             MR. WRIGHT:  Surely.

7   BY MR. WRIGHT:

8        Q    Will you agree that the storm restoration costs

9   associated with underground facilities being impacted by

10   wind-blown debris are generally less than the storm restoration

11   costs associated with overhead facilities being impacted by

12   wind-blown debris?

13        A    Gulf has not done any kind of studies that, that

14   basically based on those assumptions that I'm hearing that,

15   that show that that's the case.

16        Q    Well, I understand that, and I intend to inquire

17   about studies that Gulf has and has not done.  But let me ask

18   you based, the same question based on your personal experience

19   with restoration work in the field for more than 17 named

20   storms.

21        A    Repeat the question, please.

22        Q    Will you, based on your experience with more than 17

23   named storms, will you agree that the storm restoration costs

24   associated with underground facilities being impacted by

25   wind-blown debris are less than the storm restoration costs

FLORIDA PUBLIC SERVICE COMMISSION

114

1   associated with overhead facilities being impacted by

2   wind-blown debris?

3        A    And, again, based on what I am understanding from the

4   question, Gulf has not had the data or have I been able to try

5   to determine those differences between the two as far as the

6   costs impacting one or the other to a greater degree.

7        Q    Mr. Battaglia, I asked you the question very

8   specifically on the basis of your personal experience.  If you

9   are not able to answer it, you can say I don't know.  But

10   you've answered in terms of --

11             CHAIRMAN EDGAR:  Mr. Wright.

12             MR. BADDERS:  I'm going to have to object.

13             MR. WRIGHT:  Oh, Madam Chairman, I'm trying to get

14   the witness to answer the question on the basis of his

15   experience.  He continues to revert to the basic answer that

16   Gulf has not done any studies and has not given me an answer to

17   the question I asked him based on his personal experience.  I

18   would like him to answer that question.  If he doesn't know, he

19   can say he doesn't know.

20             CHAIRMAN EDGAR:  Mr. Badders.

21             MR. BADDERS:  I believe the witness answered the

22   question.  I think he answered the same question twice.  And I

23   believe what he said was what he had reviewed did not indicate

24   one way or the other.

25             CHAIRMAN EDGAR:  All right.  Let's try it this way.

FLORIDA PUBLIC SERVICE COMMISSION

115

1   To the witness, please try to answer the question, if you can,

2   as the question is posed to you.  And, Mr. Wright, let's try it

3   one more time and then let's move on.

4             MR. WRIGHT:  Yes, ma'am.

5   BY MR. WRIGHT:

6        Q    Mr. Battaglia, I'm asking you based on your

7   experience in the field with more than 17 named storms is it

8   your experience that storm restoration costs associated with

9   underground facilities, that would be their aboveground

10   appurtenances, being impacted by wind-blown debris are less

11   than the corresponding storm restoration costs associated with

12   overhead facilities being impacted by wind-blown debris?

13        A    I do not know.

14        Q    Thank you.  And just to clarify the record, I think,

15   I think your previous answer indicated that Gulf has not done

16   any analyses of the relative costs and benefits of underground

17   facilities versus overhead with regard to wind-blown debris

18   impacts; is that correct?

19             MR. BADDERS:  I'm going to object.

20             CHAIRMAN EDGAR:  Mr. Badders.

21             MR. BADDERS:  I believe the record stands for itself.

22   I mean, what the witness answered in response to that is in the

23   record.  And we've now heard the question three times.

24             CHAIRMAN EDGAR:  We have heard the question three

25   times.  I agree with that.

FLORIDA PUBLIC SERVICE COMMISSION

116

1             Mr. Wright, just, if you would, try to stick to

2   asking the questions and not rephrasing the answers.  Let's try

3   that.

4             MR. WRIGHT:  I was really just trying to get clear as

5   to what Gulf has and has not done, Madam Chairman.

6             CHAIRMAN EDGAR:  Do you have further questions for

7   this witness?

8             MR. WRIGHT:  Oh, yes, ma'am.

9             CHAIRMAN EDGAR:  Okay.

10   BY MR. WRIGHT:

11        Q    All right.  Mr. Battaglia, I'd like to ask you now to

12   look at Gulf's responses to interrogatories numbers 42, 43, 44,

13   and 45.

14             MR. WRIGHT:  Madam Chairman, I would note that the

15   last page of what has been marked as Exhibit 45 is the

16   certificate from Ms. Susan Ritenour, the secretary and

17   treasurer and regulatory manager of Gulf Power who avers that

18   the answers to these interrogatories are true and correct.  May

19   I simply ask the witness?

20   BY MR. WRIGHT:

21        Q    Mr. Battaglia, were you involved in preparing the

22   answers to these interrogatories?

23        A    Yes.

24        Q    And to your knowledge the answers to each of these

25   interrogatories is true and correct; is that accurate?

FLORIDA PUBLIC SERVICE COMMISSION

117

1        A    Yes.

2        Q    Thank you.  Other than the material that's presented

3   in response, I think, to interrogatories 44, 46 and 47, are you

4   aware of any other benefit cost or cost-effectiveness analyses

5   performed by or for Gulf relative to the costs and benefits of

6   undergrounding as a storm hardening measure?

7        A    No.

8        Q    Thank you.  Mr. Battaglia, you've been in the utility

9   business in Florida for a pretty long time; is that true?

10        A    Yes, sir.

11        Q    Are you familiar with Florida Power & Light Company's

12   Storm Secure Plan?

13        A    To a certain degree.

14        Q    Thank you.

15             MR. WRIGHT:  Madam Chairman, I would like to

16   distribute as an exhibit, which I would ask be marked as 46, a

17   copy of FPL's Storm Secure Plan or initiative filed with the

18   Commission on January 30th, 2006.

19             CHAIRMAN EDGAR:  Yes, sir.

20             MR. WRIGHT:  Thank you.

21             CHAIRMAN EDGAR:  Okay.  And as Mr. Wright has

22   requested, we will mark this as Exhibit 46, FPL's Storm Secure

23   Plan, January 30, 2006.

24             (Exhibit 46 marked for identification.)

25             MR. WRIGHT:  Thank you, Madam Chairman.

FLORIDA PUBLIC SERVICE COMMISSION

118

1   BY MR. WRIGHT:

2        Q    Mr. Battaglia, have you in your experience with this

3   issue reviewed this document?

4        A    Yes, to a certain degree.

5        Q    Thank you.  I want to simply read the witness one

6   sentence from the first page of the text of the document and

7   ask him whether he agrees with it or not.  And that sentence is

8   the first sentence following the heading "Background," which

9   reads, "Two extraordinary hurricane seasons have made it clear

10   that significant changes are required in the way that Florida

11   utilities design, construct and operate their electrical

12   systems."

13             Mr. Battaglia, do you agree with that statement or

14   disagree or unable to answer?

15        A    I agree.

16        Q    And are you familiar that FPL's Storm Secure Plan

17   includes as a significant component of that plan certain

18   undergrounding initiatives?

19        A    Yes.

20        Q    And would I understand correctly that your testimony

21   addressing Gulf's consideration of undergrounding as a storm

22   hardening option is given largely at Page 9 and I think

23   continuing over on to Page 10 of your direct testimony?

24        A    Correct.

25        Q    Thank you.  At Page 6 of Gulf's Amended Storm

FLORIDA PUBLIC SERVICE COMMISSION

119

1   Hardening Plan Gulf makes the statement effectively that Gulf's

2   position does not favor one over the other, meaning overhead or

3   underground, as long as Gulf is able to recover associated

4   costs.  Is that an accurate characterization of Gulf's plan?

5        A    And, again, repeat for me which page you were on.

6        Q    My notes indicate that it was on Page 6.

7             I'm sorry.  Perhaps that's your testimony, Page 6.

8        A    No.  You are correct.  It's on Page 6.  I saw it, and

9   that's correct.

10             MR. WRIGHT:  All right.  Thank you.  I apologize for

11   the confusion, Madam Chairman.

12   BY MR. WRIGHT:

13        Q    With regard to Gulf's recovery of associated costs,

14   would it also be Gulf's position that Gulf's Storm Hardening

15   Plan and all of Gulf's policies should send accurate value or

16   price signals to Gulf's customers?

17        A    Please repeat that question again.  I'm not sure I

18   understand it.

19        Q    Would it be Gulf's position that Gulf's Storm

20   Hardening Plan and all of Gulf's policies should, to the

21   maximum extent feasible, send accurate value or price signals

22   to Gulf's customers?

23        A    As far as providing value and what Gulf tries to do

24   in its Storm Hardening Plan, yes.  As far as cost signals, I'm

25   not sure I understand what you're referring to there.

FLORIDA PUBLIC SERVICE COMMISSION

120

1        Q    Okay.  I'll try to explain.  Will you agree that to

2   the extent that undergrounding provides benefits, measurable

3   dollar benefits to Gulf and its general body of customers,

4   those benefits should be recognized in calculating who pays how

5   much of the cost of any underground projects?

6        A    And, again, it sounds like you're making the

7   assumption that there are benefits associated with underground

8   in conjunction with storm hardening, and, again, you know, Gulf

9   has nothing to indicate that at this time.  But based on your

10   question as worded in conjunction with the other part, I would

11   have to agree.

12        Q    Thank you.  Are you familiar with Commission Rule

13   25-6.115 which relates to contributions in aid of construction

14   for undergrounding?

15        A    To a certain degree, yes.

16        Q    Are you familiar with the provision of that rule that

17   requires each utility to include in its CIAC calculations the

18   estimated differences between the storm restoration costs

19   including other operational costs, or I think it's the other

20   way around, operational costs including storm restoration costs

21   associated with overhead and underground facilities?

22        A    And, again, please repeat the question.

23        Q    Are you familiar with the provision of Rule

24   25-6.115 that requires utilities to include in their CIAC

25   computations the estimated difference in operational costs,

FLORIDA PUBLIC SERVICE COMMISSION

121

1   including storm restoration costs, associated with overhead and

2   underground facilities?

3        A    To a certain degree, yes.

4        Q    My question -- that was a predicate question, Madam

5   Chairman.

6             And the question is has Gulf done the analysis, any

7   specific cost-benefit analyses or cost-effectiveness analyses

8   to value those factors articulated in the Commission's rule?

9        A    Gulf has currently underway processes to capture

10   those costs.  But up to this point Gulf does not have the

11   needed information associated with storm restoration to

12   basically make those quantitative analyses as far as the

13   differences in the operational costs between the underground

14   and the overhead system.

15        Q    So just so the record is clear, is the specific

16   answer to my specific question, no, but you're in the process

17   of conducting studies?

18        A    Gulf is in the process of collecting the needed data

19   associated with those.  As far as conducting a study at this

20   time, the answer is no.

21        Q    Thank you.  Excuse me.  At Page 10 of your direct

22   testimony you testify that Gulf is conducting several

23   distribution pilot projects in potential storm surge areas.  Do

24   you recall that testimony?

25        A    And, again, please repeat.  It's in Page 10 of the

FLORIDA PUBLIC SERVICE COMMISSION

122

1   direct?

2        Q    Page 10, beginning at Line 8.

3        A    Yes, I see that.

4        Q    Thank you.  Now your testimony states that for a

5   further description of those pilot projects one should look at

6   Section 6.0 of the plan, which I think is on Page 24.  Is that

7   accurate?

8        A    Are you going to Page 24 of my direct testimony

9   versus Appendix 6 in the plan?

10        Q    I'm sorry.  Section 6 of the plan, which I think is

11   on Page 24 of your amended Storm Hardening Plan.

12        A    And your question is?

13        Q    I just want to make sure we're in the same place.

14        A    Yes, we are.

15        Q    Okay.  Thank you.

16             My first question is where were these pilot projects

17   implemented?

18        A    And again I apologize, but clarify as far as pilot

19   projects.  Again, on Page 24 what I'm looking at is the table

20   that shows the extreme wind loading projects.

21        Q    Oh, excuse me.  If you would look at Section 6.1,

22   which is the final paragraph on Page 24 at least of the plan

23   that I have, that is what I understood Page 10 of your direct

24   testimony to be referring to.  If my understanding is

25   incorrect, please set me straight.

FLORIDA PUBLIC SERVICE COMMISSION

123

1             CHAIRMAN EDGAR:  Well, and on that, if I may

2   interject, it is 12:00.  I had commented at the beginning of

3   the proceeding that we would be breaking for lunch around

4   12:00, and this seems like perhaps as good a time as any within

5   this couple of minute time period.  So if there is no

6   objection, I would like to propose that we stop at this point.

7   We will take a lunch break; come back at 1:30.  And when we

8   come back, we will continue questioning with this witness.

9   And, Mr. Wright, you will have the opportunity to continue, and

10   then, of course, see if there are any questions from staff and

11   then move to redirect.  And as I mentioned earlier, I do have

12   another matter I need to attend to.  So Commissioner Carter

13   will be presiding when you come back at 1:30, and I will see

14   you all later.  And with that, we are on break.

15             (Lunch recess taken.)

16             (Transcript continues in sequence with Volume 2.)

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

124

1   STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2   COUNTY OF LEON      )

3

4             I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing proceeding was

5   heard at the time and place herein stated.

6             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

7   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

8   proceedings.

9             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

10   or employee of any of the parties' attorneys or counsel

connected with the action, nor am I financially interested in

11   the action.

12              DATED THIS ______ day of October, 2007.

13

14                  ________________________________

LINDA BOLES, RPR, CRR

15                  FPSC Official Commission Reporter

(850) 413-6734

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION