125

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

In the Matter of:

3

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE     DOCKET NO. 070297-EI

4   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

5   TAMPA ELECTRIC COMPANY.

6   ---------------------------------------

7   REVIEW OF 2007 ELECTRIC INFRASTRUCTURE     DOCKET NO. 070298-EI

STORM HARDENING PLAN FILED PURSUANT TO

8   RULE 25-6.0342, F.A.C., SUBMITTED BY

PROGRESS ENERGY FLORIDA, INC.

9   ----------------------------------------

10   REVIEW OF 2007 ELECTRIC INFRASTRUCTURE     DOCKET NO. 070299-EI

STORM HARDENING PLAN FILED PURSUANT TO

11   RULE 25-6.0342, F.A.C., SUBMITTED BY

GULF POWER COMPANY.

12

---------------------------------------

13

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE     DOCKET NO. 070301-EI

14   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

15   FLORIDA POWER & LIGHT COMPANY.

________________________________________/

16

17

18

ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

19                 A CONVENIENCE COPY ONLY AND ARE NOT

THE OFFICIAL TRANSCRIPT OF THE HEARING,

20            THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

21

22                              VOLUME 2

23                        Pages 125 through 306

24

25   PROCEEDINGS:        HEARING

FLORIDA PUBLIC SERVICE COMMISSION

126

1

2

3   BEFORE:             CHAIRMAN LISA POLAK EDGAR

COMMISSIONER MATTHEW M. CARTER, II

4                       COMMISSIONER KATRINA J. McMURRIAN

COMMISSIONER NANCY ARGENZIANO

5                       COMMISSIONER NATHAN A. SKOP

6   DATE:               Tuesday, October 2, 2007

7   TIME:               Commenced at 9:30 a.m.

Concluded at 4:50 p.m.

8

9   PLACE:              Betty Easley Conference Center

Room 148

10                       4075 Esplanade Way

Tallahassee, Florida

11

12

REPORTED BY:        JANE FAUROT, RPR

13                       Official FPSC Reporter

(850) 413-6732

14

15   APPEARANCES:        (As heretofore noted.)

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

127

1                              I N D E X

2                              WITNESSES

3

NAME:                                               PAGE NO.

4

EDWARD J. BATTAGLIA

5

Continued Cross Examination by Mr. Wright        129

6        Cross Examination by Mr. Bennett                 148

7   ALLEN G. McDANIEL

8        Direct Examination by Mr. Langley                152

Prefiled Direct Testimony Inserted               155

9        Cross Examination by Mr. Wright                  163

10   MANUEL B. MIRANDA

11        Direct Examination by Mr. Butler                 166

Prefiled Direct Testimony Inserted               169

12        Cross Examination by Mr. Seiver                  193

Cross Examination by Mr. Wright                  206

13        Redirect Examination by Mr. Butler               221

14   REGAN B. HAINES

15        Direct Examination by Mr. Willis                 225

Prefiled Direct Testimony Inserted               227

16        Cross Examination by Ms. Browne                  254

17   SANFORD WALKER

18        Prefiled Direct Testimony Inserted               264

19   KIRK SMITH

20        Prefiled Direct Testimony Inserted               271

21   MICHAEL T. HARRELSON

22        Direct Testimony by Mr. Seiver                   279

Prefiled Direct Testimony (withdrawn)

23        Cross Examination by Mr. Willis (stricken)       285

24

CERTIFICATE OF REPORTER                               306

25

FLORIDA PUBLIC SERVICE COMMISSION

128

1                              EXHIBITS

2   NUMBER:                                      ID.    ADMTD.

3   18                                                    151

4   19                                                    165

5   45 through 48                                         152

6   8                                                     262

7   20 through 22                                         223

8   46                                                    224

9   49        (Late-filed) National Hurricane

Center Tropical Cyclone Report              209

10

50        TECO's responses to FCTA's First   259      262

11             Set of Interrogatories Nos. 1-30

12   27        KS-1, Process to Engage            270      270

Third-Party Attachers

13

51        TECO's responses to FCTA's First   296

14             Request for PODs No. 7

15   44                                                    305

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

129

1                         P R O C E E D I N G S

2             (Transcript follows in sequence from Volume 1.)

3             COMMISSIONER CARTER:  We will go back on the record.

4   In our last episode of don't throw the baby out with the bath

5   water, I think we had -- oh, that was the wrong script.

6   (Laughter.)

7             Mr. Wright, you're recognized.

8             MR. WRIGHT:  Thank you, Mr. Chairman.

9                         EDWARD J. BATTAGLIA

10   continues his testimony under oath from Volume 1:

11                     CONTINUED CROSS EXAMINATION

12   BY MR. WRIGHT:

13        Q    Good afternoon, Mr. Battaglia.  The pending question

14   that --

15             COMMISSIONER CARTER:  Let's take five.

16             (Off the record; technical difficulties.)

17             COMMISSIONER CARTER:  We are back on the record.

18             You're recognized, Mr. Wright.

19             MR. WRIGHT:  Thank you again, Mr. Chairman.

20   BY MR. WRIGHT:

21        Q    Good afternoon, again, Mr. Battaglia.

22             The pending question that I was trying to ask you

23   when we broke for lunch is where, geographically or physically,

24   is Gulf conducting the distribution pilot projects relative to

25   undergrounding in storm surge areas as reflected or referred to

FLORIDA PUBLIC SERVICE COMMISSION

130

1   at Page 10 of your testimony?

2        A    For Gulf's underground conversions new installations,

3   as I stated probably in other parts of my testimony, they are

4   customer driven at this point in time.  So as far as where any

5   particular conversion may occur, or new underground

6   installation involved with new business and so on, it's

7   difficult to say as far as where those particular types of new

8   construction will occur and conversion of existing.

9             What I was referring to in my testimony was in

10   Appendix 6 of the storm hardening plan, I was referring to our

11   new specifications to apply storm hardening to our underground

12   jobs that did occur, based on, again, being customer driven.

13   And so when you look in Gulf's storm hardening plan, and you

14   look in Appendix 6, that's where you'll see the specifications

15   for ball type flush-mounted switchgear, heavy-duty concrete

16   lids encasing the undergrounding feeder conduits in concrete,

17   utilizing methods such as locating the pad mounts, and if we do

18   use above-ground switchgear in areas that would reduce the

19   opportunities for them being impacted by storm surge by taking

20   into account whatever protection is offered by the natural lay

21   of the land or in buildings.

22        Q    I apologize if I am just dense, but your testimony

23   states clearly that Gulf is conducting several distribution

24   pilot projects, and the question I was trying to ask, Mr.

25   Battaglia, is where geographically those projects as referred

FLORIDA PUBLIC SERVICE COMMISSION

131

1   to in this testimony are being conducted?  Can you answer that

2   question, Mr. Battaglia?

3        A    Based on ones that have occurred up to this point?

4             MR. WRIGHT:  Mr. Chairman, the question I'm trying to

5   ask him is what he is referring to in his testimony.

6             COMMISSIONER CARTER:  Do you know of any that have

7   been done in any geographical location within the confines of

8   your service area?

9             THE WITNESS:  Yes, sir.  Pensacola City Beach is a

10   good example of a large project that has occurred in recent

11   history.  We have had several in the Destin area, Main Street

12   Destin that I recall in particular, and some in the Panama City

13   Beach area that I believe it was several projects.  Going

14   forward, as far as, again, those type of projects, since they

15   are customer driven and we do have some that are on the drawing

16   board, but until they are accepted by the customer it is

17   difficult to say whether or not those are going to occur or

18   not.

19             COMMISSIONER CARTER:  Mr. Wright.

20   BY MR. WRIGHT:

21        Q    Mr. Battaglia, could I ask you to look at Appendix

22   7 of Gulf's storm hardening plan.  It's the legal-sized

23   spreadsheet.

24        A    Yes, I'm there.

25        Q    I'd like to ask you to look, if you would, at Row P

FLORIDA PUBLIC SERVICE COMMISSION

132

1   there which appears to relate to mitigating flood and storm

2   damage to underground and supporting overheard facilities

3   piloted project incremental costs.  And my question is does the

4   71,680 expended in '05 and the 446,000 expended in

5   '06 correspond to the projects you just mentioned?

6        A    Yes, sir.  Basically what is shown there as far as

7   cost represents that incremental difference of those items that

8   are referred to in Appendix 6 for storm hardening measures that

9   were associated with projects that were done as far as those

10   years and in looking at it going forward.

11        Q    Thank you.

12             MR. WRIGHT:  Mr. Chairman, if Mr. Battaglia would

13   like to take a water break, that's fine with me.

14             THE WITNESS:  I think I'm fine now.

15             COMMISSIONER CARTER:  How much more time do you think

16   you will need with Mr. Battaglia?

17             MR. WRIGHT:  Probably on the order of half an hour,

18   Mr. Chairman.  I was just trying to be respective of his voice.

19             COMMISSIONER CARTER:  I think he's ready.

20             THE WITNESS:  I appreciate that, but I'm ready.

21   BY MR. WRIGHT:

22        Q    Mr. Battaglia, referring to Page 24 of Gulf's amended

23   storm hardening plan, the statement is made there, "Gulf

24   recognized and piloted underground system storm hardening

25   design changes in response to lessons learned from Ivan in

FLORIDA PUBLIC SERVICE COMMISSION

133

1   2004."

2             Would I be correct to understand that what you just

3   described using flush-mounted cabinetry and stainless steel

4   gear are the principal lessons learned from Ivan in 2004?

5        A    Yes, to a certain degree.  For example, on the

6   stainless steel transformers, that's not entirely correct in

7   the sense that Gulf has recognized the need to use those types

8   of installations prior to Ivan, and it has been part of our

9   specifications for many years in beach type areas.  As far as

10   the specifications, moving forward with the vault type

11   installations, items such as, again, locating the pads where it

12   mitigates damage and all, that's correct.  That's part of it.

13        Q    Thank you.  Were there any other lessons learned from

14   Ivan that would be applicable here than those you have already

15   discussed?

16        A    I think there are many lessons that we learned from

17   Ivan that are reflected in our storm hardening plan, both on

18   the overhead side and on the underground side, and also with

19   how we perform our restoration after a storm as far as helping

20   us to fine tune everything from logistics to communications,

21   staging of materials and so on.  As far as directly as far as

22   back to, say, overhead, you know, again looking at every

23   opportunity to storm harden our system, one of the items that

24   we came up with as far as we recognized based on feedback

25   direct experience, field experience by restoration crews was

FLORIDA PUBLIC SERVICE COMMISSION

134

1   doing some things that were very basic such as in our

2   construction practices adding another spool rack, an insulator

3   in which we connect our service wire to at the transformer and

4   then as the service runs to the house, if the service is

5   impacted by flying debris or what have you, that it goes ahead

6   and puts that strain at those spool racks and not let it be

7   transferred up to the transformer and damage transformer

8   bushings and basically escalating the damage.

9             And, again, there is many of those that are part of

10   the storm hardening plan, part of what we have adopted in our

11   specs in trying to -- as far as lessons learned and continuous

12   improvement.

13        Q    Thank you.

14             With regard to the lessons you learned relative to

15   undergrounding, did Gulf use those lessons to define or

16   establish its underground storm hardening specifications for

17   underground facilities as those are set forth in Appendix 6 of

18   Gulf's plan?

19        A    Yes, that was part of formulating those particular

20   specifications as far as improvements and going forward.

21        Q    Thank you.  If you can, can you relate -- can you

22   state what level of confidence you have that those underground

23   storm hardening specifications set forth in Appendix 6 will be

24   effective?

25        A    Again, based on as far as the degree of effectiveness

FLORIDA PUBLIC SERVICE COMMISSION

135

1   of those particular items, based on what we have observed

2   directly in the field, we feel that many of them hold high

3   potential.  But at the same time, as far as a trial of fire so

4   to speak, that remains to be seen.  But we feel that such

5   things as covering the conduit with concrete, putting those

6   heavy-duty vaults in as far as flush-mounted switchgear based

7   on what we know at this point hold high potential.

8        Q    Can you in the same context say how confident you are

9   that your guidelines for placing underground switch cabinets

10   and transformer cabinets on the landward side of roads or

11   sheltered by other buildings would be effective?

12        A    And, again, we feel that in moving forward, based on

13   what we have seen, we feel that they do have a high potential

14   to be effective, but at the same time realizing that they may

15   be up to a certain point with certain types of storms and

16   certain associated storm surges, so to what degree, to what

17   level of category storm that they may be effective, that is

18   still an unknown for Gulf.

19        Q    Thank you.  I have a couple of questions for you that

20   relate to Gulf's reliability and storm hardening initiatives

21   report dated March 1st, 2007.  Do you have a copy of that

22   document with you?

23        A    I should in short order.  Yes, sir.

24        Q    Thank you.  I would like to ask you to look at Page

25   40 of that document, Mr. Battaglia.

FLORIDA PUBLIC SERVICE COMMISSION

136

1             MR. WRIGHT:  Mr. Chairman, these are brief questions,

2   and I don't intend to mark this as an exhibit.  It's

3   voluminous.

4        A    Yes, sir.

5        Q    At Page 40, Gulf is discussing the activity and costs

6   incurred with regard to gathering data relative to underground

7   and overhead.  Is that an accurate characterization?

8        A    Yes, sir.

9        Q    And the document says Gulf will collect data on

10   outages as they occur with respect to underground and overhead

11   facilities, correct?

12        A    Yes.

13        Q    A couple of questions beyond that.  Will the data

14   collected identify the customers' status as an overhead surge

15   or underground surge customer?

16        A    Yes, I believe it will, based on our trouble call

17   management system under which this data would be collected.

18        Q    Will it also identify for any given outage where the

19   outage occurred?  And if I can clarify my question, if there is

20   a distribution route that is part overhead and part

21   underground, will your data collection program as set forth in

22   this document identify whether outages occurred on the overhead

23   piece of the system or the underground piece of the system?

24        A    Yes, it will.

25        Q    I would like to ask you to look briefly at the last

FLORIDA PUBLIC SERVICE COMMISSION

137

1   short paragraph in that Section 10.1, the last sentence of

2   which reads, "The costs for this are minimal as it utilizes

3   existing systems and processes."  I'm just trying to understand

4   what that means.  What does it mean when it says costs are

5   minimal?

6        A    In that particular case, the cost that it's referring

7   to is what we had to do in order to make it a part of our

8   existing data collection process as far as our trouble call

9   management system.  That we were able to program it to add the

10   appropriate drop down boxes so that our operators could key in

11   the correct information based on the reports by the crews and

12   capture that for us.

13        Q    So it was a software modification that will now

14   enable you to enter data, is that accurate?

15        A    That's correct.  Back during the -- when this was

16   done as far as back during the first part of the year, we had

17   set in place the needed modifications so we could test it and

18   be sure that it would do what we expected it to do.

19             MR. WRIGHT:  Thank you.

20             Mr. Chairman, Mr. Battaglia, during the break I

21   handed out, in the interest of time, two documents.  One is

22   Gulf's response to Panama City Beach's Interrogatory Number 16,

23   which I asked to be marked as Exhibit 47, and the other was

24   Gulf's responses to Panama City Beach's Interrogatories 39 and

25   40, which I asked to be marked as Number 48.  And I have a

FLORIDA PUBLIC SERVICE COMMISSION

138

1   couple of questions for the witness about Exhibit 47.

2   BY MR. WRIGHT:

3        Q    First, Mr. Battaglia, are you familiar with these

4   interrogatory answers?

5        A    Please excuse me for a second.  I thought you said

6   Interrogatory 47?

7        Q    No, I'm sorry.  It's Interrogatory Number 16, which

8   has been marked as Exhibit 47.

9        A    I apologize.  Yes, I have got it.  And, yes, I'm

10   familiar with it.

11        Q    All right.  And looking at the very last page of that

12   exhibit, which is Page 7 of 7 of Gulf's response, will you

13   agree that in 2004 and 2005 Gulf spent just slightly more than

14   $200 million in storm restoration costs?

15        A    Based on what's there, correct.

16        Q    Can you tell us how much of that was spent for

17   restoring overhead facilities and how much was spent -- I

18   should say overhead distribution facilities -- and how much was

19   spent for restoring underground distribution facilities?

20        A    Based on the information that's there, I cannot tell

21   you that as far as, or recall as far as having that type of

22   breakdown of that existing information.

23        Q    Do you know whether that information is available?

24        A    That I do not know.

25        Q    So would it be fair to say that you did not consider

FLORIDA PUBLIC SERVICE COMMISSION

139

1   any such information in your work on Gulf's storm hardening

2   plan?

3        A    Please repeat the question.

4        Q    Would it be fair to say, then, based on your previous

5   response, that you did not consider any such information in

6   connection with your work on Gulf's storm hardening plan?

7        A    Based on the previous answer, that leads to an

8   assumption as far as me saying yes, but that is not entirely

9   correct.  And, again, what I would refer to is that as far as

10   hard numbers to differentiate between the two after a storm

11   restoration process, that we do not have.  But at the same

12   time, from my experience and personally being involved in

13   multiple storm restoration efforts, I do know and have seen and

14   observed as far as what it takes to put that overhead system

15   back together and the associated problems with it, and to put

16   that underground system back together and the problems

17   associated with it.

18             And even though I do not have the dollars that I can

19   state what that is, I have observed as far as how long those

20   crews take in doing that process.  I do have an idea as far as

21   the value of the materials associated with those repair

22   processes that leads me to the conclusion that based on those

23   observations, those field observations, that on those

24   one-for-one bases that underground is more costly in performing

25   those type of activities after a major storm.

FLORIDA PUBLIC SERVICE COMMISSION

140

1        Q    I would like to ask you to look, if you would, at

2   what has been marked as Exhibit 48?

3        A    Which is interrogatory --

4        Q    It's Gulf's answers to Panama City Beach's

5   Interrogatories 39 and 40.  It's the second document I handed

6   out during the break.

7        A    I've got it.

8        Q    Okay.  Just to confirm, the answers to these

9   interrogatories are true and correct to the best of your

10   knowledge, is that correct?

11        A    Yes, sir.

12        Q    Thank you.

13             Are you familiar with a term continuing property

14   record?

15        A    No, sir, I'm not an accountant.

16        Q    Are you familiar with any Gulf records that identify

17   the cost of distribution facilities as they are installed in

18   the field?

19        A    Assuming that -- based on as far as new installations

20   for underground and overhead, or are you referring to

21   restoration efforts?

22        Q    I would actually appreciate your answering both of

23   those questions if you can.

24        A    As far as new installations, to a certain degree,

25   based on the current work order process for estimating those

FLORIDA PUBLIC SERVICE COMMISSION

141

1   type of jobs, I have some degree of feel for that.  As far as

2   the restoration process as what I stated before, again other

3   than my field type observations I don't have a direct, or have

4   the data involved with those direct costs.

5        Q    In the restoration process, is there some sort of

6   document like a work order document that would be created that

7   would identify facilities that were installed in connection

8   with the restoration effort?

9        A    In that particular case, as far as high level, there

10   are what I would call a work order to collect the charges

11   associated with doing all of the restoration work, which I have

12   to assume that's what the figures shown in the other response,

13   how that was generated.

14        Q    Well, let me ask you kind of a real world kind of

15   question.  Suppose you've got a crew out there doing storm

16   restoration work, and on a given day they replaced ten poles

17   and 750 feet of conductor.  Is that an okay example to work

18   with so far?

19        A    Yes, sir.

20        Q    Will there be a work order document that would

21   identify that installation of those poles and that conductor?

22        A    Based on my field experience up to this point as far

23   as a work order that would give you that type of granular cost

24   information for restoring a piece of a feeder and a piece of

25   the underground, not that I'm aware of.

FLORIDA PUBLIC SERVICE COMMISSION

142

1        Q    In that answer you referred to -- I think you stated

2   you're not aware of that kind of document that would provide

3   data at that granular level.  Is there some document within

4   Gulf's accounting or inventory system that would identify

5   poles, conductor -- poles and conductor installed during storm

6   restoration?

7        A    And, again, I'm not an accountant, and as far as the

8   process that occurs during storm restoration, I cannot say I

9   have a high degree of familiarity with that other than knowing

10   that at least up to this point we do have high level work

11   orders in which to collect those charges.  And I would have to

12   assume that in order to break it out as far as the appropriate

13   purc's (phonetic) and poles and wire that that is part of the

14   process that accounting performs.

15        Q    In your work on Gulf's storm hardening plan, did you

16   attempt to research any such information?

17        A    Based on at least what I was aware of up to this

18   point, no, I did not attempt to research that type of

19   information because of what I have been aware of to this point,

20   it didn't exist.

21             MR. WRIGHT:  Thank you.  Mr. Chairman, I think I have

22   just a few more questions.

23             COMMISSIONER CARTER:  You're on a roll, go ahead.

24             MR. WRIGHT:  I'm working on it, yes, sir.

25   BY MR. WRIGHT:

FLORIDA PUBLIC SERVICE COMMISSION

143

1        Q    Mr. Battaglia, I would like you to look at Page 14 of

2   Gulf's amended storm hardening plan.  And my question, question

3   or two are going to relate to the geographic information

4   system, or GIS information, the discussion of which begins at

5   Page 13.  So if you want to look at that, that is fine.  I will

6   get to the point and here it is.

7             The document states that Gulf expects to complete the

8   initial mapping of its transmission system into its GIS within

9   the next six years.  Is that an accurate characterization of

10   Gulf's plan with regard to that item?

11        A    For the transmission system, again, based on what we

12   have in the plan there, yes, that's correct.

13        Q    Do you believe that this is an adequate pace to

14   accomplish the mapping of Gulf's transmission system

15   information into its GIS?

16        A    Based on my knowledge as far as on the transmission

17   side, again, I'm on the distribution side, and I have to assume

18   that those that provided that information felt that it was the

19   correct pace.

20        Q    Looking at the paragraph regarding the distribution

21   GIS, there is no -- I did not see anyway, any corresponding

22   information as to when Gulf expects to complete that mapping.

23   Can you tell us when Gulf expects to complete the mapping of

24   the distribution system into its distribution GIS?

25        A    The mapping of Gulf Power Company's distribution

FLORIDA PUBLIC SERVICE COMMISSION

144

1   system into GIS is complete.  And, again, it's evolving every

2   day as far as new facilities are being built, adjustments made

3   to feeders.  Obviously it's in a constant state of evolution.

4   But as far as getting the initial base in there, it's complete.

5        Q    Mr. Battaglia, I'm looking at a copy of the

6   Commission's electric infrastructure storm hardening rule,

7   which I read in Section 25-6.0342, Sub 4, to require a detailed

8   description of the utility's deployment strategy, including the

9   communities and areas within the utility's service area where

10   the improvements are to be made.  Are you familiar with that

11   provision of the Commission's rule?

12        A    Yes, sir.

13        Q    In that connection, I was looking for where Gulf

14   attempted to comply with that provision, and it appears to me

15   that that would be with regard to a Schedule 10 of your Exhibit

16   EJB-1, and also the plan at Pages 26 and 27.  And my first

17   question is am I correct that that is the information provided

18   by Gulf in its endeavor to comply with that provision of the

19   rule?

20        A    In our storm hardening plan, again, were you

21   referring to Pages 26 and 27?  That's correct.

22        Q    Yes, sir, Sections 9-1 and 9-2, and then Schedule

23   10 of your exhibit.

24        A    Schedule 10 in my direct testimony does show part of

25   it as far as the extreme wind loading.

FLORIDA PUBLIC SERVICE COMMISSION

145

1        Q    I did not see there a detailed subscription of the

2   communities affected.  Can you show me what I missed or is this

3   what there is?

4        A    If you go to Gulf's storm hardening plan and refer --

5        Q    Excuse me, were you looking at the amended storm

6   hardening plan?

7        A    That is correct, the amended storm hardening plan.

8        Q    Okay.

9        A    And in addition to what you've already stated as far

10   as the write-ups in the previous pages, if you look at Appendix

11   1, the service area map that's shown there indicates the

12   projects that Gulf will be doing under the extreme wind

13   loading, which is, again, part of the plan.

14        Q    I'm looking at the map, and I note that it has got

15   the extreme wind loading standard contours on it.  Do the

16   stars -- the stars indicate where the projects are, is that

17   accurate?

18        A    That is correct.

19        Q    Thank you.

20             You don't have any experience as a city manager or

21   assistant city manager, do you?

22        A    No, sir.

23        Q    As a city planner, urban planner?

24        A    No, sir.

25        Q    Municipal or county emergency services administrator?

FLORIDA PUBLIC SERVICE COMMISSION

146

1        A    No, sir.

2        Q    Do you have any testimony to offer as to how such

3   city or county personnel could use this to understand exactly

4   what was doing on here as set forth in your plan?

5        A    In looking at what we have set forth in our plan

6   here, it does provide, in Gulf's opinion, the needed detail for

7   the cities and municipalities to get initial grasp as far as

8   what projects are occurring and where.  And then in addition to

9   that, Gulf has very good relationships established throughout

10   all of our communities, and the necessary Gulf Power folks in

11   place to help explain and elaborate upon the details of the

12   projects, depending upon the interest expressed by each city or

13   each emergency operation center.

14             And especially in the case of the emergency

15   operations centers, Gulf has obviously because of the mutual

16   need there in communications and so on, Gulf has long

17   established good communications with those departments, those

18   individuals, to be able to explain any facet of our storm

19   hardening plan and to be proactive in -- as opportunities are

20   seen as far as with particular projects to discuss that with

21   them.

22        Q    Thank you.  I just have a couple more questions.

23             Do you have a working knowledge of what the term

24   optimal means?

25        A    Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

147

1        Q    Would you agree -- this is an abstract kind of

2   question.  Would you agree that if the incremental benefits of

3   making an incremental expenditure on a given program or

4   measure, if the incremental benefits are greater than the

5   incremental costs, that making that additional expenditure

6   would be tending toward optimizing the program?

7        A    Yes, to a certain degree.  But, in looking at those

8   type of situations, you have to look at more than just the

9   surface numbers and understand what the numbers mean, versus at

10   times taking them just for face value as far as how they are

11   developed and in what respect do they apply to a particular

12   situation.

13        Q    And referring back to Appendix 7 of the storm

14   hardening plan, do I conclude correctly that Gulf is not able

15   to estimate the benefits from the undergrounding activities

16   indicated at Row P or Row O, the letter O, at this time?

17        A    At this particular time, that's correct.

18             MR. WRIGHT:  Thank you.

19             Thank you, Mr. Chairman; that's all the questions I

20   have for Mr. Battaglia.

21             COMMISSIONER CARTER:  Commissioners, my plans are, if

22   it is appropriate, is to see if there are other parties that

23   have questions, and then maybe go to staff and then to

24   Commissioners.  But if you have questions at this point in

25   time, obviously at any time any Commissioner can ask any

FLORIDA PUBLIC SERVICE COMMISSION

148

1   question that you would like.  Would that be appropriate?

2             Any other question from any party on this witness

3   before I recognize staff?  Staff, you're recognized.

4             MS. BENNETT:  Thank you, Chairman Carter.

5                          CROSS EXAMINATION

6   BY MS. BENNETT:

7        Q    Mr. Battaglia, my name is Lisa Bennett.  We have

8   spoken earlier in your deposition.  I just have a few

9   questions.

10             Prior to the submission of its storm hardening plan

11   in this docket, it is true that Gulf submitted a ten-part

12   initiative, is that correct?

13        A    That is correct.

14        Q    And was this ten-part initiative approved by the

15   Commission in Order PSC 060781 and PSC 060947?

16        A    That is correct.

17        Q    And would you agree that the Gulf ten-part initiative

18   is mostly annual system-wide activities?

19        A    Yes.

20        Q    Did Gulf's proposed hardening plan, the one that's

21   the subject of this docket, include the ten-part initiative

22   previously approved by the Commission?

23        A    Yes, it did.

24        Q    Would you agree that the proposed hardening plan in

25   this docket is a three-year look ahead?

FLORIDA PUBLIC SERVICE COMMISSION

149

1        A    Yes, I would.

2        Q    And is it subject to change as more information is

3   gathered and costs are refined?

4        A    Yes.

5        Q    Would you agree that Gulf's previously approved

6   ten-part initiative and the Gulf proposed hardening plan are

7   complementary to each other?

8        A    Yes, I would.

9        Q    Would you agree that Gulf is responsible for pursuing

10   the most cost-effective storm hardening projects?

11        A    Yes, I would.

12        Q    And would you agree that the Public Service

13   Commission expects each utility to prudently manage its

14   resources?

15        A    Yes.

16        Q    And would you agree with me that the Commission's

17   overarching objective to Rule 25-6.032 of the Florida

18   Administrative Code is to promote a corporate culture that

19   reduces storm restoration costs and storm-caused outages to

20   affected parties?

21        A    Yes, I would.

22             MS. BENNETT:  I have no further questions.

23             COMMISSIONER CARTER:  You have no further questions?

24             MS. BENNETT:  No more questions.

25             COMMISSIONER CARTER:  Commissioners, any questions?

FLORIDA PUBLIC SERVICE COMMISSION

150

1             Mr. Badders, you're recognized for redirect.

2             MR. BADDERS:  No redirect.  Thank you.

3             COMMISSIONER CARTER:  Okay.

4             Ms. Fleming, let's get ourselves in the proper

5   posture here.

6             MR. BADDERS:  At this time I would like to move

7   Mr. Battaglia's exhibit into the record.

8             COMMISSIONER CARTER:  That would be exhibit -- on our

9   list it would be Exhibit 18, is that correct?

10             MR. BADDERS:  That is correct.

11             MS. FLEMING:  That is correct.

12             COMMISSIONER CARTER:  Yes, ma'am, you are recognized.

13             COMMISSIONER ARGENZIANO:  I need to make a comment,

14   because I'm not sure of what the last line of questioning was

15   from staff, and I just need to ask.  It seems that we are on

16   the defensive, and I'm not sure what the line of questioning

17   was intending.  I mean, you don't work for Gulf Power, but I

18   don't understand why that line of questioning came up the way

19   it did.

20             MS. BENNETT:  We're just filling out the record for

21   the recommendation later.

22             COMMISSIONER ARGENZIANO:  Thank you.

23             COMMISSIONER CARTER:  And Commissioner Skop.

24             COMMISSIONER SKOP:  Thank you, Mr. Chair.

25             Equally, I have the same concern, and I am just going

FLORIDA PUBLIC SERVICE COMMISSION

151

1   to bring it out and say it directly to the witness.  But there

2   are situations where counsel on cross-examination have

3   propounded questions, I believe Mr. Wright was seeking to

4   devote testimony on cross-examination from the witness, and the

5   witness was -- ultimately I think the answer was I don't know.

6   But, again, instead of being evasive, if the witnesses would

7   just answer the questions that might also help round out the

8   record for the benefit of the Commission, also.

9             Thank you.

10             COMMISSIONER CARTER:  Thank you, Commissioners.

11             Any other comments from any other Commissioner before

12   we proceed further?  I think we are in the process of admitting

13   Exhibit 18 for Mr. Battaglia and his testimony.  That would

14   just be Exhibit 18, is that correct, Ms. Fleming?

15             MS. FLEMING:  Yes, that's correct, Exhibit Number 18.

16             COMMISSIONER CARTER:  Any objection?  Hearing none,

17   show it done.

18             (Exhibit 18 admitted into the record.)

19             MR. WRIGHT:  And, Mr. Chairman, I would move the

20   admission of Exhibits 45, 46, 47, and 48.

21             COMMISSIONER CARTER:  What have been previously

22   marked Exhibits Number 45, 46, 47, and 48.  Any objection?

23             MR. BADDERS:  No objection.

24             COMMISSIONER CARTER:  Show it done.

25             (Exhibits 45 through 48 admitted into the record.)

FLORIDA PUBLIC SERVICE COMMISSION

152

1             COMMISSIONER CARTER:  Ms. Fleming, procedurally where

2   are we now with this witness?

3             MS. FLEMING:  If we are concluded with Mr.

4   Battaglia's direct testimony, I suggest that we can move on to

5   the next witness, Mr. McDaniel.

6             COMMISSIONER CARTER:  Okay.  Call your next witness.

7             MR. BADDERS:  Thank you.  We call Allen McDaniel to

8   the stand.

9                          ALLEN G. McDANIEL

10   was called as a witness on behalf of Gulf Power Company, and

11   having been duly sworn, testified as follows:

12                         DIRECT EXAMINATION

13   BY MR. LANGLEY:

14        Q    This is Eric Langley for Gulf Power.

15             Mr. McDaniel, were you in here earlier when the

16   witnesses were sworn in?

17        A    Affirmed, I was.

18        Q    Please state your full name and business address.

19        A    My name is Allen G. McDaniel.  My business address is

20   One Energy Place, Pensacola, Florida 32520.

21        Q    And by whom are you employed and in what capacity?

22        A    I am employed by Gulf Power Company as the Project

23   Services Manager of Power Delivery.

24        Q    Are you the Allen McDaniel that prefiled direct

25   testimony in the Gulf Power docket consisting of eight pages?

FLORIDA PUBLIC SERVICE COMMISSION

153

1        A    Yes, sir.

2        Q    Do you have any changes or corrections to that

3   testimony?

4        A    No.

5        Q    If I were to ask you the same questions today, would

6   your answers be the same?

7        A    Yes, they would.

8        Q    Do you have any exhibits attached to your direct

9   testimony that you will be referring to?

10        A    No, I do not.

11        Q    Mr. McDaniel, what is the purpose of your direct

12   testimony?

13        A    The purpose of my testimony is to explain and address

14   Sections 11.0 and 12.0 of Gulf's storm hardening plan as

15   amended on August 14th, 2007.  I will discuss how each section

16   addresses and supports the requirements set forth in the Rules

17   25-6.0341 and 25-6.0342, and explain how Gulf's third-party

18   attachment standards and procedures assure, as far as

19   reasonably practical, that third-party attachments do not

20   impair electric safety, reliability, or pole loading capacity

21   on our system.

22             MR. LANGLEY:  And to clarify, Mr. McDaniel's

23   testimony is in Docket 070299-EI.

24             And at this time we tender Mr. McDaniel for

25   cross-examination.

FLORIDA PUBLIC SERVICE COMMISSION

154

1             COMMISSIONER CARTER:  Any questions?  Mr. Wright.

2             MR. WRIGHT:  Thank you, Mr. Chairman.  I have a very

3   few questions for --

4             COMMISSIONER CARTER:  One second.  Any questions by

5   any other parties, or just Mr. Wright is the only one with

6   questions?

7             MR. SEIVER:  FCTA has no questions, Mr. Chairman.

8             MR. LANGLEY:  And, Mr. Chairman, I suppose I should

9   move for the entry of Mr. McDaniel's direct testimony into the

10   record.

11             COMMISSIONER CARTER:  As though read.  Done.

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

163

1             COMMISSIONER CARTER:  Mr. Wright, you're recognized.

2             MR. WRIGHT:  Thank you, Mr. Chairman.

3                          CROSS EXAMINATION

4   BY MR. WRIGHT:

5        Q    Good afternoon, Mr. McDaniel.

6        A    Good afternoon.

7        Q    As I said, I have very few questions for you.  Your

8   testimony indicates that you have direct field experience in

9   storm restoration with 12 named storms, is that accurate?

10        A    Yes, sir.

11        Q    How much of your field experience was with overhead

12   restoration activities and how much was with underground

13   restoration activities?

14        A    I would say all of it.

15        Q    Can you give us a percentage breakdown?

16        A    Well, what I meant by the answer was I dealt with

17   both overhead and underground each and every time during those

18   storms.  Obviously 80 percent or so of our system is overhead

19   and the rest is underground, and I would say that the

20   experience was proportional to the amount of each.

21        Q    Thank you.  Have you observed poles that you

22   believed, based on your own observation, failed because of

23   additional loading from telecommunications or cable television

24   facilities, i.e., the facilities of third-party attachers being

25   attached to Gulf's facilities?

FLORIDA PUBLIC SERVICE COMMISSION

164

1        A    No, I have not.

2        Q    Have you observed instances where electric

3   telecommunications and cable television facilities were tangled

4   up after a storm hit overhead facilities?

5        A    Could you clarify that?  When you say tangle up, did

6   you say with electric utilities?

7        Q    I tried to say where all three, or electric and

8   telecommunication, electric and cable, or electric and

9   telecommunications and cable altogether were tangled up from

10   overhead facilities?

11        A    I have seen where they were down.  I wouldn't say

12   tangled up as much as they tend to stay attached to the pole

13   but go down.

14        Q    So they fall down with the poles?

15        A    Yes.

16             MR. WRIGHT:  Thank you.  That's all I have.

17             COMMISSIONER CARTER:  Once again, before asking staff

18   or Commissioners, any other parties -- any other parties have

19   any questions for this witness?

20             Commissioners?  Staff?

21             MS. BENNETT:  No questions.

22             COMMISSIONER CARTER:  Okay.

23             MR. LANGLEY:  No redirect.

24             COMMISSIONER CARTER:  No direct.  Smart man.  Okay.

25   Then you would be moving in Exhibit 19, is that correct?

FLORIDA PUBLIC SERVICE COMMISSION

165

1   Ms. Fleming, is that right?

2             MS. FLEMING:  That's correct, it's Exhibit 19 only in

3   the Gulf Docket, 070299.

4             COMMISSIONER CARTER:  Any objections?  Hearing none,

5   show it done.

6             (Exhibit 19 admitted into the record.)

7             COMMISSIONER CARTER:  Any other questions for this

8   witness?  You may be excused.

9             MR. LANGLEY:  Mr. Chairman, as a housekeeping matter,

10   I don't believe we asked that Mr. Battaglia be excused.  May he

11   be excused?

12             COMMISSIONER CARTER:  Commissioners, early on I took

13   a note here about -- oh, that would be Mr. McDaniel's withdrawn

14   as to rebuttal.

15             MS. FLEMING:  Commissioner, I believe Mr. Battaglia

16   will be coming back up later for his rebuttal testimony.  It

17   was only Mr. McDaniel that had the rebuttal testimony withdrawn

18   in the Gulf docket.

19             MR. LANGLEY:  That's right.  I meant excused from --

20   with respect to Mr. Battaglia, excused from his direct

21   testimony and cross-examination.  He will be presenting

22   rebuttal.  Mr. McDaniel will not.

23             COMMISSIONER CARTER:  Okay, then.

24             MS. FLEMING:  I think that is a given since Mr.

25   McDaniel is already on the stand.

FLORIDA PUBLIC SERVICE COMMISSION

166

1             MR. LANGLEY:  Fair enough.

2             COMMISSIONER CARTER:  All righty, then.

3             MR. BUTLER:  Mr. Chairman, I believe that FPL's

4   Witness Manuel B. Miranda is the next witness, is that correct?

5             COMMISSIONER CARTER:  That's what my list says, Mr.

6   Butler.

7             MR. BUTLER:  Then I will call Mr. Miranda to the

8   stand.

9                          MANUEL B. MIRANDA

10   was called as a witness on behalf of Florida Power and Light

11   Company, and having been duly sworn, testified as follows:

12                         DIRECT EXAMINATION

13   BY MR. BUTLER:

14        Q    Mr. Miranda, will you please state your name and

15   business address for the record?

16        A    Sure.  My name is Manuel B. Miranda.  I go by the

17   nickname of Manny.  My address is 9250 West Flagler Street,

18   Miami, Florida 33174.

19        Q    Mr. Miranda, have you previously been sworn?

20        A    Yes, I have.

21        Q    Do you have before you a document consisting of 21

22   pages and three attached exhibits entitled Direct Testimony of

23   Manuel B. Miranda in Docket Number 070301-EI, dated August 24,

24   2007?

25        A    Yes, I do.

FLORIDA PUBLIC SERVICE COMMISSION

167

1        Q    Was this document prepared under your direction,

2   supervision, and control?

3        A    Yes, it was.

4        Q    Do you have any changes or corrections to your

5   prefiled testimony or exhibits?

6        A    Yes, I do.

7        Q    Would you please state those.

8        A    On my direct testimony, Page 17, Line 13, the number

9   nine should be seven.  And on Exhibit MBM-3, the first bullet

10   that says ten utilities should be seven utilities for a total

11   of ten data points.

12        Q    Thank you, Mr. Miranda.

13             MR. BUTLER:  Staff, I would like to inquire at this

14   point.  You had prepared, based on information I had provided

15   you, a list of revisions -- I'm sorry, it only applies to

16   rebuttal testimony.  Nevermind.  Nothing here that we need to

17   do with Mr. Miranda's direct testimony.

18   BY MR. BUTLER:

19        Q    Mr. Miranda, with the changes that you just made, do

20   you adopt this prefiled testimony as your direct testimony in

21   this proceeding?

22        A    Yes, I do.

23             MR. BUTLER:  I would ask that Mr. Miranda's prefiled

24   testimony be inserted into the record as though read.

25             COMMISSIONER CARTER:  The prefiled testimony will be

FLORIDA PUBLIC SERVICE COMMISSION

168

1   accepted into the record as though read.

2             MR. BUTLER:  And I note that Mr. Miranda's Exhibits

3   MBM-1, 2, and 3 are prenumbered 20, 21, and 22 respectively.

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

190

1   BY MR. BUTLER:

2        Q    Mr. Miranda, would you please summary your testimony.

3        A    Yes; thank you.

4             Good afternoon, Commissioners.  Seven storms impacted

5   FPL and its customers during the 2004 and 2005 hurricane

6   seasons resulting in significant customer outages that required

7   extraordinary efforts to rebuild and restore FPL's system.

8   This, along with forecasts of increased hurricane activity, led

9   FPL to conclude that without significant changes similar

10   disruptions from future storms would occur.  While several

11   hardening initiatives have already been implemented, for

12   example, the pole inspection program and the ten storm

13   preparedness initiatives, which includes vegetation management,

14   there remains one major initiative, strengthening the overhead

15   system to better withstand strong hurricane winds.

16             Two key conclusions from our recent storm experience

17   formed the basis for FPL's plan.  One, for Hurricane Wilma,

18   wind was the predominant root cause of distribution pole

19   breakage; and, two, FPL's transmission structures which are

20   already built to the NESC extreme wind loading criteria

21   performed well over all.  Based on this experience, FPL

22   proposes a three-prong approach to harden the overhead

23   distribution system so that it can better withstand strong

24   winds.

25             First, apply extreme wind loading criteria to

FLORIDA PUBLIC SERVICE COMMISSION

191

1   facilities that serve critical infrastructure of customers.

2   For example, our hospitals and 911 centers.  Two, apply

3   incremental hardening to existing infrastructure that serves

4   critical community needs, such as gas stations and grocery

5   stores.  Three, employ revised design guidelines to apply

6   extreme wind to overhead construction, major plan work,

7   relocation projects, and daily work activities.  For 2007, FPL

8   plans to utilize extreme wind to harden 34 critical

9   infrastructure feeders and associated laterals to serve 28

10   acute care facilities, 43 highway crossings, and the first pole

11   out of a substation for 78 feeders.  Additionally, FPL will

12   complete incremental hardening on feeders serving 34 community

13   projects.  In total, this will result in hardening

14   approximately 145 overhead circuit miles, including replacing

15   2,100 existing poles and installing 700 intermediate poles.

16             FPL's overall three-pronged approach will continue in

17   2008 and 2009.  Detailed plans have not been finalized, but it

18   is FPL's intent to complete extreme wind hardening for all

19   hospitals and 911 centers by the end of 2009.  FPL will

20   annually provide detailed updates to its plan for these out

21   years.

22             Cost range estimates for FPL's hardening efforts are

23   48.5 to $61.5 million in 2007, 75 to 125 million in 2008, and

24   100 to 150 million in 2009.  Our analysis indicates that the

25   restoration cost savings per mile of hardened feeder are

FLORIDA PUBLIC SERVICE COMMISSION

192

1   estimated to range from 45 percent to 70 percent of the costs

2   to harden the feeder assuming a storm frequency of every three

3   to five years respectively.  More frequent storms could cause

4   the restoration cost savings to exceed the hardening costs.

5   For instance, if a storm of Hurricane Wilma's intensity

6   occurred once every three years, the restoration cost savings

7   would then become about equal to the hardening costs.

8             Once the system is hardened, FPL's plan, along with

9   the other initiatives recently implemented, will result in

10   fewer customer outages and a reduction in overall distribution

11   restoration time.  This is a significant benefit for our

12   customers beyond the anticipated savings of restoration costs.

13   While there are uncertainties that limit FPL's ability to

14   quantify precisely the results and benefits associated with the

15   hardening activities, our recent storm experience dictates that

16   the action should be taken.  Our plan is prudent, practical,

17   and cost-effective.  It focuses initially on critical

18   infrastructure facilities and community projects, facilities

19   that provide critical and essential needs to our communities

20   and our customers.

21             Since FPL's system is diverse and geographically

22   large, hardening will take many years to complete.  The initial

23   plan is a first step based on our current systems, our

24   processes, our technologies, and our equipment.  The

25   comprehensive plan to harden our system which includes the full

FLORIDA PUBLIC SERVICE COMMISSION

193

1   implementation of the pole inspection program and the ten storm

2   preparedness initiatives will result in a more resilient system

3   which means fewer customer outages and a reduction in overall

4   distribution time.

5             The Commission should approve FPL's plan in this

6   proceeding so that we can begin to provide our customers the

7   added protection against future hurricanes that they have told

8   us and the Commission which is so important to them.

9             Thank you.

10             MR. BUTLER:  Thank you, Mr. Miranda.  I tender Mr.

11   Miranda for cross-examination.

12             COMMISSIONER CARTER:  Let's see who all has questions

13   of this witness.

14             MR. SEIVER:  FCTA has some questions, Your Honor.

15             COMMISSIONER CARTER:  Why don't we let you go first.

16   You're recognized.

17             MR. SEIVER:  Thank you, Mr. Chairman.

18             John Seiver for the Florida Cable Telecommunications

19   Association.

20                          CROSS EXAMINATION

21   BY MR. SEIVER:

22        Q    Good afternoon, Mr. Miranda.

23        A    Good afternoon, Mr. Seiver.

24        Q    I believe in your testimony you had commented that

25   the cost-effectiveness of FPL's storm hardening plan depends on

FLORIDA PUBLIC SERVICE COMMISSION

194

1   the timing and severity of future storms, is that right?

2        A    We provide an estimate which shows storms

3   effectiveness every three years and every five years.

4        Q    And the strength and severity of those storms is

5   important to consider the cost-effectiveness?

6        A    For the purposes of our benefit we utilize an average

7   storm that we experienced in the 2004 and 2005 hurricane

8   season, so that was the basis by which we conducted our

9   analysis.

10        Q    And this analysis as far as the cost/benefit and

11   recovering the costs, which I believe you testified to, is over

12   a period of 30 years, is that right?

13        A    Yes.  The analysis is about the effects of the net

14   present value over a 30-year period.

15        Q    So in order to have -- you need more than one storm

16   every three years, you would need ten storms in 30 years in

17   order for the analysis to run out to the end, is that right?

18        A    And that would assume that we would be building

19   everything overnight, which as you know will be a gradual

20   implementation over this period, as well.

21        Q    But it wouldn't take you 30 years to build-out the

22   storm hardening plan?

23        A    No, that's correct.

24        Q    As far as the severity and strength of the storms,

25   that's not based on any meteorological analysis that you

FLORIDA PUBLIC SERVICE COMMISSION

195

1   yourself performed, is that right?

2        A    None that I have personally performed, it is just

3   based on what meteorologists and experts are saying about the

4   heightened hurricane activity period that we are.

5        Q    Is there anything that the meteorologists have said

6   about the hurricane activity in this record, or an exhibit, or

7   anywhere in anybody's testimony?

8        A    No.

9        Q    And you also had mentioned, I think, that we are

10   maybe in a period of increased hurricane activity, is that

11   right?

12        A    That is correct.

13        Q    Is that based again similarly on predictions of some

14   experts?

15        A    Statements that you hear from the National Hurricane

16   Center, it is statements based on our activities that we saw in

17   the '04 and '05 season, and even historically I would say on

18   average we have experienced a storm about once every five

19   years, so it should be consistent with those.

20        Q    If there is a storm once every five years the

21   restoration cost savings drop, don't they?

22        A    Correct.

23        Q    And, in fact, I think you testified that if it's

24   every five years would it be about 45 percent restoration cost

25   savings per mile?

FLORIDA PUBLIC SERVICE COMMISSION

196

1        A    Right.  And those costs are associated with FPL's

2   direct costs.  Of course, we did not measure the value that

3   there might be to the communities, to our customers, and, you

4   know, the economic impact by having services restored quicker

5   would have.

6        Q    And putting aside Hurricane Wilma for the moment, if

7   there is a storm at a frequency of once every three years, but

8   not of Wilma's strength, it would only be 70 percent

9   cost-recovery, putting aside the other benefits, is that right?

10        A    That's correct.

11        Q    And as far as Hurricane Wilma is concerned, that was

12   a fairly unique storm in your service territory, wasn't it?

13        A    It was the most recent storm that we have had, but it

14   was a Category 3 that impacted our territory.

15        Q    But it was unique from all the other Category 3s that

16   have impacted your territory, isn't it?

17        A    I wouldn't say it is unique.  I think it is, you

18   know, where it impacted our service territory and how it came

19   in through, but all hurricanes, you know, they are powerful

20   forces of nature, so you never quite know what they are going

21   to bring.

22        Q    Well, didn't you testify that Hurricane Wilma was

23   unique in that there were many more wind-only pole failures

24   than with any other storm?

25        A    What we said was that we had conducted the forensic

FLORIDA PUBLIC SERVICE COMMISSION

197

1   analysis during Wilma, and we had conducted forensics in the

2   2005 hurricane season, and Wilma, which was the one that was a

3   Category 3, wind only was the predominant root cause.

4        Q    And would it be fair to say that your storm hardening

5   plan that you have proposed here to build your facilities to

6   the extreme wind standards is really based on your experience

7   with Wilma alone, isn't it?

8        A    Well, Wilma clearly identified that wind only was the

9   predominant root cause.  And when you look at our other

10   initiatives that we have under our storm secure initiatives,

11   which is the increased vegetation trimming, which is the pole

12   inspection, we just could not ignore the wind-only component.

13   So, Wilma was the one where we identified the root cause, but

14   if you look at meteorological history, which is what we

15   anchored on for the proposal of extreme wind, you know, the

16   chances of having those types of winds in our service territory

17   in the future are very possible.

18        Q    But you are not being discriminate about applying the

19   extreme wind standard, you're doing it throughout your service

20   territory regardless of proximity of trees, or vegetation, or

21   open areas, is that right?

22        A    Well, we are deploying in a very targeted approach.

23   We are looking at the contours of the extreme wind map, and as

24   you know it has the different contours throughout our state,

25   and the southernmost part of our service territory where we

FLORIDA PUBLIC SERVICE COMMISSION

198

1   have the highest likelihood of having the strongest winds,

2   there we propose a 145-mile-an-hour zone, and as me move

3   throughout the state we will actually have three zones, one of

4   130 miles an hour and one at 105 miles per hour.  So, it is not

5   a one-size-fits-all throughout our service territory.  And then

6   we are also approaching it from a gradual implementation of

7   looking at our critical infrastructure, looking at incremental

8   hardening, and then looking at it also from the new

9   construction perspective.

10        Q    But within those wind contour zones that you are

11   referring to, which are from the NESC, am I right?

12        A    That's correct.

13        Q    In those wind contour zones, there is a great

14   difference in the service territory and the location of your

15   distribution and your feeder poles, isn't that right?

16        A    I'm sorry, could you clarify that?

17        Q    I'll try it again.  Within those wind contour zones,

18   your service territory as far as the feeders and the laterals

19   is not exactly the same as being in open areas, or in urban

20   others, or rural areas, it varies throughout that zone, is that

21   right?

22        A    You mean the geography of our service territory?

23        Q    Correct.

24        A    Yes.  I mean, we have very urban environments, we

25   have facilities with trees, we have facilities without trees,

FLORIDA PUBLIC SERVICE COMMISSION

199

1   it really varies across our service territory.

2        Q    Mr. Miranda, on Page 16 of your direct testimony,

3   there is some uncertainties that you referred to.  If you want

4   to look at Page 16, Line 8, do you see that?

5        A    Yes.

6        Q    In Line 10 you say that FPL's experience shows its

7   systems designed to withstand stronger winds have greater

8   overall resiliency to storms.  Do you see that?

9        A    Yes.

10        Q    Now, when you say stronger winds, you're not talking

11   about extreme winds, you are just talking about stronger

12   construction, is that right?

13        A    What we are referring to there is the different

14   levels of hurricanes, and having a Grade B construction that

15   can better withstand stronger winds.

16        Q    Well, you have a comparison of Grade B and Grade C

17   construction, but not of extreme wind and Grade B or extreme

18   wind and Grade C construction, is that right?

19        A    Correct.  It is combined (inaudible) and wind Grade B

20   versus Grade C.

21        Q    So, for example, in the exhibit that's at the end of

22   your testimony, the Davies?

23        A    Yes.

24        Q    Which am I to understand from your correction is not

25   for ten utilities, but for seven utilities?

FLORIDA PUBLIC SERVICE COMMISSION

200

1        A    That's correct.

2        Q    And, while you are turning to that, which is Exhibit

3   MBM-3, am I right that we don't know which seven utilities

4   those are that were subject to the Davies analysis?

5        A    Subsequent to the deposition we were asked by Staff

6   to go back and look to see if we can get a release of

7   confidentiality from some of these utilities.  Four of the

8   utilities released -- were willing to release their names,

9   three of them were not.

10        Q    And have you released those four names to us?

11        A    I can if you like.

12        Q    Would you, please?

13        A    Sure.  One was Dominion, one was BG&E, one was SCANA

14   (phonetic), and the other one was Cleco (phonetic).

15        Q    Are any of those utilities in Florida?

16        A    No, they are not.

17        Q    And I also wanted to ask you, did any of those

18   utilities build any of their systems to Grade B?

19        A    It was a comparison of Grade C construction.

20        Q    And there are utilities in Florida that have built to

21   Grade B, is that right?

22        A    I understand that TECO builds to Grade B.

23        Q    So we wouldn't be able to use this as a comparison --

24   I'm sorry, let me restate that.  In fact, I'll withdraw that.

25             If we go back to Page 16, on Line 10 and 11, where I

FLORIDA PUBLIC SERVICE COMMISSION

201

1   read to you about withstanding stronger winds, after the comma

2   on Line 11, it says there is little directly measured data on

3   the improved resilience.  Let me ask you is the Davies chart

4   that you have attached at the back the only data that we have

5   in the record?

6        A    Yes, that's the data that we utilized for the

7   purposes of at least comparing the Grade C to the Grade B, and

8   what I was referring to in there is that, you know, there is no

9   forensics analysis after a hurricane that has been conducted on

10   the facilities that have been built to extreme wind.

11        Q    So as we sit here today, we can't predict whether

12   facilities built to extreme wind will have improved resilience

13   over Grade B, for example?

14        A    Well, I mean, if you look at my exhibit which shows

15   Grade B versus Grade C, the implication is that those

16   facilities that are built to a higher standard, like Grade B,

17   had we built our FPL facilities to a Grade C during Wilma we

18   may have seen maybe instead of a 1-1/2 percent pole failure

19   rate, maybe a 2-1/2 or 3 percent pole failure rate.  And as far

20   as the forecast, as far as the benefits associated, what we

21   approached is, of course, we have a lot of direct experience

22   that we had following the '04 and '05 hurricane season to see

23   what the root causes were of the interruptions.  So as we apply

24   these countermeasures, they tackle the root cause.  We also

25   contracted with KEMA to assist us in developing our extreme

FLORIDA PUBLIC SERVICE COMMISSION

202

1   wind criteria and standards.  Our own experience with our

2   transmission facilities and, of course, finally the Davies

3   exhibit that you referred to.  So that was the foundation by

4   which we estimated what we thought the benefits would be.

5        Q    Are you aware of any other studies in the record or

6   elsewhere that would contradict the conclusion that Grade B

7   facilities have improved resilience to storms over Grade C?

8        A    That would contradict?  No, I do not.

9        Q    You don't remember our discussions of the KEMA

10   report?

11        A    I remember you stated that they contradicted, and I

12   provided a clarification on what I thought the impression was

13   of that section of the KEMA report.

14             MR. SEIVER:  Mr. Chairman, if I might for a moment, I

15   had discussed with Mr. Butler, counsel for FPL, there is

16   rebuttal testimony by Mr. Miranda that I also will ask him

17   about, and because his rebuttal testimony gets into that area

18   more, I would like to reserve my time for questioning him about

19   things like the KEMA report and some of the other rebuttal

20   issues until Mr. Miranda is up for rebuttal.  I don't want to

21   be mixing up the jurisdiction of the direct and the rebuttal.

22             So if the Chair is all right with that, I'm going to

23   move on to a different subject.  I didn't want to think that I

24   was just abandoning the KEMA report.

25             COMMISSIONER CARTER:  Mr. Butler, is that your

FLORIDA PUBLIC SERVICE COMMISSION

203

1   understanding?

2             MR. BUTLER:  If that's the way he would like to do

3   it, it is fine.  I think it does relate to the rebuttal

4   testimony, so certainly it is okay for him to ask the questions

5   then.

6             COMMISSIONER CARTER:  You may proceed.

7             MR. SEIVER:  Thank you.

8   BY MR. SEIVER:

9        Q    And, Mr. Miranda, when we were just talking about the

10   evidence about improved resilience, in that testimony on Page

11   16, the second item that you mentioned at Line 13 is that no

12   one can know for sure how frequently FPL's service territory

13   will be impacted by strong hurricanes?

14        A    (Indicating yes.)

15        Q    And that still is your testimony today, is that

16   right?

17        A    That's correct.  I mean, we cannot predict exactly

18   when the next hurricane will strike us, but like we always have

19   said, we have to be ready for the next one.

20        Q    But you are relying on these meteorological analyses

21   that aren't in the record you say of increased storm activity

22   and likelihood of future storms?

23        A    That's correct.

24        Q    And, Mr. Miranda, is it fair to say then that as far

25   as building to extreme wind, that we have to make two

FLORIDA PUBLIC SERVICE COMMISSION

204

1   assumptions, the first that extreme wind will be more resilient

2   than other forms of construction, and that, second, there will

3   be more frequent hurricanes than nonfrequent, is that fair?

4             MR. BUTLER:  I would object to the characterization

5   of more frequent hurricanes.  Compared to what?

6             COMMISSIONER CARTER:  Just ask the question a little

7   clearer.

8             MR. SEIVER:  Do you agree, then, that there are two

9   assumptions, that the extreme wind will be more resilient, the

10   extreme wind construction will be more resilient to the storms,

11   and that there will be more frequent storms during this 30-year

12   period, is that right?

13             MR. BUTLER:  Again, I'm going to object to the

14   question.  More frequent compared to what?  It is an ambiguous

15   question.

16             COMMISSIONER CARTER:  Can you answer this question

17   based upon your experience?

18             THE WITNESS:  I think the first part is our

19   assumptions being that based on our experience, you know, the

20   KEMA support, you know, the Davies study, and in our own

21   transmission experience, yes, that it will be based on those

22   experiences and the assumptions that we have put behind that.

23   And as far as the more frequency of storm, that is why we laid

24   out two scenarios, one every three years and one every five

25   years, not having the certainty, of course, of when those

FLORIDA PUBLIC SERVICE COMMISSION

205

1   storms will impact us.

2   BY MR. SEIVER:

3        Q    And that is when we were discussing that over the

4   30-year period if a storm was every three years, there would be

5   a 70 percent storm savings, if there was a storm every five

6   years, there would be a 45 percent savings, is that right?

7        A    Correct, to the distribution, to the restoration

8   efforts.

9        Q    For the restoration cost savings, not including any

10   other benefits.  Did you also consider in the extreme wind

11   construction process whether restoration times would be

12   extended because of either more poles being impacted or more

13   expensive and difficult poles to replace?

14        A    Well, I believe that we would have shorter

15   restoration time, less poles that get damaged, which will

16   result in faster restoration time overall.

17        Q    Did you look at for doing extreme wind of putting in

18   additional poles to shorten spans?

19        A    Yes.

20        Q    And did you look at the increased probability of

21   automobile accidents with the additional poles that are along

22   rights-of-way where cars travel?

23             MR. BUTLER:  I would object.

24             COMMISSIONER CARTER:  I don't think there is nothing

25   in the record to support that, so let's stay on task.

FLORIDA PUBLIC SERVICE COMMISSION

206

1   BY MR. SEIVER:

2        Q    Did you consider any other unintended consequences of

3   building to extreme wind, Mr. Miranda?

4        A    Unintended consequences.  Could you elaborate?

5        Q    Beyond storm hardening benefits?

6        A    No.  I think our main goal was to improve the

7   resiliency of our electric system and to make it stronger so it

8   can withstand these hurricane winds.

9             MR. SEIVER:  That's all I have at this time, Mr.

10   Chairman.

11             COMMISSIONER CARTER:  Before the next person,

12   Commissioners, any questions at this point in time?  Obviously

13   we will have more time at the end, but I want to see if based

14   upon this do you have any questions?  Otherwise we will go

15   ahead with the next person.  And also at any time,

16   Commissioners, if you have any questions whatsoever we will do

17   that.

18             I think next will be Mr. Wright, is that correct?

19   You are recognized, sir.

20             MR. WRIGHT:  Thank you, Mr. Chairman.

21                          CROSS EXAMINATION

22   BY MR. WRIGHT:

23        Q    Good afternoon, Mr. Miranda.

24        A    Good afternoon, Mr. Wright.

25        Q    Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

207

1             I want to start by clarifying something that I

2   thought was already clear.  You testified in response to some

3   questions by Mr. Seiver to the effect that Wilma was a Category

4   3 storm, correct?

5        A    That's correct.

6        Q    Have you reviewed the National Hurricane Center's

7   tropical cyclone report, the final report for Hurricane Wilma?

8        A    Have I?

9        Q    That's my question.

10        A    No, I have not.

11        Q    Are you aware that my clients filed that report in

12   various proceedings relating to undergrounding and storm

13   hardening before this Commission?

14        A    They may have, I just don't recall reading it in

15   detail, but I just go by what the categories of the hurricane

16   were in our records, which is a Category 3 storm.  I think

17   there are multiple opinions on that storm.

18        Q    Will you agree that the National Hurricane Center's

19   official report and official measurements are as good an

20   opinion as one could get on the strength of that storm?

21        A    I would say yes.

22             MR. WRIGHT:  Mr. Chairman, I think the right thing

23   for me to do here is to explain the proffer that I wish to

24   make.  I will be brief.  I will aver to you -- and this

25   document has been submitted to the Commission at least twice in

FLORIDA PUBLIC SERVICE COMMISSION

208

1   connection with the proceedings that have been going on for the

2   last year and a half -- that the National Hurricane Center's

3   final tropical cyclone report on Hurricane Wilma includes all

4   of the official wind speed measurements for all the recording

5   stations for which data exists on mainland Florida and the

6   Florida Keys.

7             COMMISSIONER CARTER:  Here's what we are going to do,

8   we are going to take about a three-minute break.  Let me get a

9   chance to talk with staff and we will be back on that before we

10   do any proffer or anything like that, okay?

11             MR. WRIGHT:  Certainly.  May I just kind of close the

12   loop briefly?

13             COMMISSIONER CARTER:  You may finish your statement.

14             MR. WRIGHT:  I would simply -- I had not expected

15   this testimony because it's contradicted by the National

16   Hurricane Center's tropical cyclone report on Hurricane Wilma.

17   I was not prepared with an exhibit for that reason.  It is an

18   official report of a recognized government agency.  I would

19   like leave to provide it as a late-filed exhibit to this

20   proceeding.

21             COMMISSIONER CARTER:  We will take three minutes.

22             MR. WRIGHT:  Thank you.

23             (Off the record.)

24             COMMISSIONER CARTER:  We are back on the record.

25             Mr. Wright, you're recognized.

FLORIDA PUBLIC SERVICE COMMISSION

209

1             MR. WRIGHT:  Thank you, Mr. Chairman.  To make it as

2   short as possible, I believe that FPL has no objection to my

3   request to introduce the National Hurricane Center's final

4   tropical cyclone report for Hurricane Wilma, and with that I

5   will move on to my few remaining questions.

6             COMMISSIONER CARTER:  You're going to file it as a

7   late-filed exhibit, you said?

8             MR. WRIGHT:  Yes, sir.

9             COMMISSIONER CARTER:  Mr. Butler.

10             MR. BUTLER:  Do you want to give it an exhibit

11   number?

12             COMMISSIONER CARTER:  That will be 49.

13             (Late-filed Exhibit 49 marked for identification.)

14             MR. BUTLER:  And I will observe we don't have any

15   objection to its admission, I certainly am not wanting that to

16   suggest that we necessarily agree with everything that's said

17   in it.  We haven't even seen what it is yet, but we feel

18   confident that any comments we may feel the need to make about

19   it we can do in briefing.

20             COMMISSIONER CARTER:  That sounds like a great idea.

21   So what we will do is we will just -- you'll reserve your right

22   to whatever objections that you may have at that point in time,

23   if any.

24             MR. BUTLER:  I don't intend to object to it, I'm just

25   saying that I don't want to take my not objecting to it to mean

FLORIDA PUBLIC SERVICE COMMISSION

210

1   that I'm agreeing substantively with what it says.

2             COMMISSIONER CARTER:  Okay.  That's fine.

3             Mr. Wright, you any proceed.

4             MR. WRIGHT:  Thank you, Mr. Chairman.  And I will

5   endeavor to have copies for everybody by tomorrow, assuming

6   that we are back here tomorrow.  And if not, I will have it to

7   the Clerk.

8             Thank you.

9   BY MR. WRIGHT:

10        Q    Mr. Miranda, will you agree that underground

11   facilities are less vulnerable to wind damage than overhead

12   facilities constructed to extreme wind loading standards?

13        A    Would you repeat that one more time?

14        Q    Certainly.  Will you agree that underground electric

15   distribution facilities are less vulnerable to wind damage than

16   are overhead facilities built to EWL criteria or standards?

17        A    Up to a certain wind speed, Mr. Wright.  In other

18   words, when it reaches catastrophic type winds, I'm not sure if

19   the underground system will have equal wind damage as the

20   overhead at a certain point, but up to that certain point, yes.

21        Q    And in that context, what do you mean by

22   catastrophic?

23        A    Like if you have got a Category 5 hurricane, a

24   Hurricane Andrew type storm.

25        Q    Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

211

1             Will you similarly agree that underground

2   distribution facilities are less vulnerable to damage from

3   wind-blown debris than overhead facilities built to extreme

4   wind loading criteria?

5        A    Yes, they would have less damage from a wind blown.

6        Q    Thank you.  I noticed you remarked several places in

7   your testimony about FPL's storm secure plan, but you did not

8   make it an exhibit to your testimony.

9             MR. WRIGHT:  Mr. Chairman, I would ask that what has

10   already been admitted as Exhibit 46, FPL's storm secure plan,

11   be received into the record of Docket 070301, as well.  I can't

12   imagine there would be an objection.

13             COMMISSIONER CARTER:  I believe it's already in

14   070301.  Staff?

15             MS. FLEMING:  Actually, it has only been entered in

16   Docket 070299 during the cross-examination of the Gulf witness,

17   but we could also identify it for Docket 070301.

18             COMMISSIONER CARTER:  Mr. Butler.

19             MR. BUTLER:  I have no objection to that.

20             COMMISSIONER CARTER:  Okay.  Well, then that will be

21   Exhibit 50.

22             MR. WRIGHT:  I think it can just remain Exhibit 46,

23   if that's okay with everybody.

24             COMMISSIONER CARTER:  Well, we are going to keep them

25   separated based upon each docket number.  Is that correct?

FLORIDA PUBLIC SERVICE COMMISSION

212

1             MS. FLEMING:  Exhibits have been identified

2   separately per docket number, but if it is a duplicative

3   exhibit we can just identify which docket that exhibit is

4   appearing in and only identify it once.

5             COMMISSIONER CARTER:  Okay.  So long as it's clear in

6   the record.

7             MS. FLEMING:  Yes, sir.

8             COMMISSIONER CARTER:  Show it done.

9             MR. WRIGHT:  Thank you, Mr. Chairman.

10             COMMISSIONER CARTER:  Any more curveballs?

11             MR. WRIGHT:  Mr. Chairman, I hope they are all just

12   fast fastballs right down the pike.

13             COMMISSIONER CARTER:  You're recognized.

14             MR. WRIGHT:  Thank you.

15   BY MR. WRIGHT:

16        Q    Mr. Miranda, in connection with Gulf's storm secure

17   plan -- FPL's storm secure plan, I apologize, FPL generally

18   supports undergrounding, is that a fair characterization?

19             MR. BUTLER:  Mr. Wright, if you want to ask him about

20   the storm secure plan and having made it an exhibit, can you

21   provide him a copy of it, or we can probably do so, but I would

22   rather have him have it in front of him if you are going to be

23   asking him questions about it.

24             MR. WRIGHT:  Mr. Chairman, in response to Mr.

25   Butler's question, I don't intend to ask him any real detailed

FLORIDA PUBLIC SERVICE COMMISSION

213

1   questions about it.  I'll be happy to give him a copy of it.

2   Why don't I do that.

3             COMMISSIONER CARTER:  Mr. Butler has one for him.

4   Let's just take a second here.  Now, you say you only had,

5   like, one question, right?

6             MR. WRIGHT:  I think what I said is that I don't have

7   any real detailed questions with regard to the storm secure

8   plan.

9             COMMISSIONER CARTER:  You're recognized, sir.

10             MR. WRIGHT:  Thank you.

11   BY MR. WRIGHT:

12        Q    Mr. Miranda, FPL performed an analysis of storm

13   restoration cost savings from undergrounding that became part

14   of -- that led to the inclusion of FPL's governmental

15   adjustment factor proposal in its storm secure plan, is that

16   correct?

17        A    That's correct.

18        Q    And are you familiar with --

19             MR. BUTLER:  I'm going to have to after the fact

20   object to the question.  I believe that it is stating a

21   foundation that is incorrect.  Could you repeat the question,

22   Schef?  It took me a moment to understand the question you were

23   asking.

24             MR. WRIGHT:  Certainly.

25   BY MR. WRIGHT:

FLORIDA PUBLIC SERVICE COMMISSION

214

1        Q    FPL performed an analysis of the storm -- well, is it

2   true that FPL performed an analysis of the estimated storm

3   restoration cost savings for underground facilities that formed

4   the basis for FPL's proposed governmental adjustment factor

5   credit that is part of FPL's storm secure plan?

6             COMMISSIONER CARTER:  That was quite convoluted,

7   wasn't it?  Could you break it down into bite-sized chunks, Mr.

8   Wright, or was that a bite-sized chunk?

9             MR. WRIGHT:  I shall try, Mr. Chairman.  Thank you.

10             MR. BUTLER:  Would it help for me to explain what my

11   confusion is about the question?

12             COMMISSIONER CARTER:  That would be very helpful, Mr.

13   Butler.  It would be appreciative at this point in time.

14             MR. BUTLER:  We did propose the governmental

15   adjustment factor as one of the elements of storm secure, the

16   plan that Mr. Wright was referring to.  But the economic

17   analysis he is talking about, we later filed a tariff and then

18   had a lengthy proceeding about the tariff, which is where the

19   economic analysis came up.  And I was stumbling on the fact

20   that the chronology didn't seem right in his question.  That

21   was really the reason for my objection and my seeking

22   clarification.

23   BY MR. WRIGHT:

24        Q    Just so I'm clear, did you all do the economic

25   analysis to which Mr. Butler refers before or after you filed

FLORIDA PUBLIC SERVICE COMMISSION

215

1   the storm secure plan?

2        A    It was after.

3        Q    Thank you.  That was my confusion.  I apologize.

4             Mr. Miranda, are you aware of the provision of Rule

5   25-6.115 that requires CIAC calculations to incorporate other

6   operational cost differences into the CIAC calculations?

7        A    Yes, I am.

8        Q    And would you agree that that information would be

9   appropriate to inform the development of the storm hardening

10   plan?

11        A    It's part of one of the CIAC requirements.

12        Q    Thank you.

13             Are you aware that my clients have been awaiting

14   FPL's estimates of the other operational costs for sometime?

15        A    I understand that.  Subsequent to the rule coming

16   out, we have been working diligently trying to establish the

17   costs, the operational costs of an overhead system versus an

18   underground system, and there are some components within an

19   overhead system and an underground system which are easy to

20   clarify.

21             For example, you might have cable locations as an

22   underground expense, a nice simple bucket that we can identify.

23   Where we have run into a stumbling block has been, as you know,

24   the majority of a distribution system -- there is a hybrid

25   system, an overhead and underground system, and our work order

FLORIDA PUBLIC SERVICE COMMISSION

216

1   system is not designed to break those costs out.  So we have

2   been working from the ground up to try to split those expenses

3   up into an overhead bucket and an underground bucket so that we

4   can determine the true operational costs between an overhead

5   system and an underground system.

6             One thing I will add, Mr. Wright, is that, as you

7   know, once we establish that numbers to which we are working to

8   provide you as quickly as we can, it will be retroactive, so

9   none of your clients hopefully will experience any economic

10   loss as a result of that factor not being in their hands today.

11        Q    Thank you very much.  Mr. Seiver asked you some

12   questions about the expected cost-effectiveness of FPL's storm

13   hardening plan, and I think that that relates to your testimony

14   at Page 18.  I'm not sure I caught the specific details of your

15   colloquy with Mr. Seiver, but there was some discussion about

16   your analysis being based on the expectation that there would

17   be ten storms in 30 years, is that about right?

18        A    We said a storm either every three years or a storm

19   every five years.

20        Q    Would you agree that this line of analysis cuts both

21   ways?

22        A    Could you clarify the question?

23        Q    Sure.  If storms are, in fact, more frequent than

24   every three years, the benefits of storm hardening will be

25   greater, correct?

FLORIDA PUBLIC SERVICE COMMISSION

217

1        A    And that is what we have stated.  If the frequency of

2   storms increases, we have even stated that if you continue to

3   have a Wilma type event every three years, you would recover

4   your costs -- it would be a break-even, and if it comes even

5   more frequent than that, like the '04 and '05 hurricane

6   seasons, it would be greater than that.

7        Q    I wanted to ask you the same question with regard to

8   the potential for higher strength or higher category storms.

9        A    We have, you know, designed our wind zones according

10   to the NESC map.  If the storm is of a higher strength, like it

11   is a Wilma, Cat 3, then they will obviously have more benefits.

12   But if it is catastrophic, if you have a Category 5, then the

13   benefits, of course, don't play as great for anybody because

14   that is not what we are designing our infrastructure towards.

15        Q    I have, I think, just one question for you about

16   FPL's deployment plans for 2008 and 2009, which is addressed in

17   your testimony at Page 13 and 14.  And my question is, I hope

18   simply, is the list of 2008 and 2009 CIF projects that has been

19   submitted as Exhibit MBM-2 to your direct testimony, is that

20   what we have in connection with FPL's plan regarding its

21   deployment plan for '08 and '09?

22        A    Well, what we have stated is that our intent is to

23   complete all the acute care facilities, the small hospitals,

24   and the 911 facilities by the end of 2009, and that is just a

25   listing of the circuits.  We have also provided the primary

FLORIDA PUBLIC SERVICE COMMISSION

218

1   diagram of where these facilities are located.

2        Q    Was that provided in discovery or within the plan

3   document itself?

4        A    I think it was an interrogatory document request.

5             MR. BUTLER:  It's actually in his rebuttal exhibits,

6   Schef.

7        Q    Thanks.

8             Mr. Miranda, has FPL conducted any benefit/cost

9   analysis of extreme wind loading built overhead facilities as

10   compared to underground facilities for different categories of

11   storms?

12        A    I'm not quite following your question.  Try it one

13   more time.

14        Q    Have you done any benefit/cost analysis of

15   undergrounding as compared to building facilities to extreme

16   wind loading criteria, just that question by itself?

17        A    I would say that if you look at the basis by which we

18   developed a GAF it was almost on an equal platform as we have

19   developed for the extreme winds.  So you can almost compare

20   those two cost/benefit analysis, one for the underground system

21   and the other one for the extreme wind.

22        Q    Okay.  And then the question I was trying to get to

23   is have you done any further analyses that compared overhead

24   facilities built to EWL standards to underground for different

25   categories of storm?

FLORIDA PUBLIC SERVICE COMMISSION

219

1        A    We did it for an average number of storms, for the

2   average type of storm that we experienced in 2004 and 2005, and

3   then we also for the underground looked at a storm every three

4   years and a storm at every five years.  So if you took those

5   two cost/benefit analyses you could make a comparison between

6   extreme wind and the underground system.

7        Q    Thank you.  I just have a couple of questions with

8   regard to your testimony at Pages 19 and 20 where you are

9   discussing FPL's plan as producing optimum results.  And as I

10   understand your testimony, you define optimum in this context

11   as being the best results for a given level of expenditure.  Is

12   that an accurate characterization?

13        A    Yes.

14        Q    Wouldn't you agree that the level of expenditure

15   itself has to be considered in determining whether optimum

16   results are achieved?

17        A    One more time.

18        Q    Well, your testimony posits holding the level of

19   expenditure constant, is that fair?

20        A    I think my testimony was along the lines of being

21   cost-effective, and that the approach that we are taking to

22   hardening our infrastructure really ramps up from the most

23   cost-effective once we have identified what needs to be

24   hardened from our tool kit all the way up to, in some cases,

25   undergrounding facilities.

FLORIDA PUBLIC SERVICE COMMISSION

220

1        Q    And my question goes to this:  Wouldn't you agree

2   that if you could spend some incremental money and get benefits

3   greater than incremental cost, that that also would be an

4   optimizing expenditure?

5        A    It could be viewed that way.

6        Q    Would you agree that it would be appropriate to view

7   it that way?

8        A    Again, the approach we took was we made the decision

9   that we wanted to harden our critical infrastructure, build to

10   the extreme wind, and then take the most cost-effective

11   approach to achieve that objective.

12             MR. WRIGHT:  Thank you.  That's all the questions I

13   have, Mr. Chair.

14             COMMISSIONER CARTER:  Thank you.

15             Commissioner McMurrian.

16             COMMISSIONER McMURRIAN:  Thank you.

17             Mr. Miranda, I have a question or two with respect to

18   the GAF tariff that was approved recently.  Have any

19   communities availed themselves of this offering at this time?

20             THE WITNESS:  We currently have a lot of active

21   requests.  We currently have the requests coming in different

22   facets, and I will answer you directly.  In those communities

23   that generally start with a ballpark request and then they will

24   just ask for generic, but then they move into what we call a

25   binding estimate request phase.  We currently have 18

FLORIDA PUBLIC SERVICE COMMISSION

221

1   communities that are in the binding estimate phase, of which

2   four of them are pretty active, and we have one community that

3   we have already given a GAF and it is now moving into the

4   second phase of their development, which is the Jupiter Island

5   project.  And we are getting ready to provide them their

6   estimate.  We did the pilot already, that has been completed,

7   and we are getting ready to do Phase A, which is part of a

8   five-phase project, and we are getting ready to provide them

9   their estimates in the next day or two.

10             COMMISSIONER McMURRIAN:  Thank you.  And I guess one

11   follow up to that.  In fact, you probably mentioned it there.

12   I think there was some window for the offering.  Can you remind

13   me when that wind closes?

14             THE WITNESS:  It's through October of 2008.

15             COMMISSIONER McMURRIAN:  Thank you.

16             Thank you, Chairman.

17             COMMISSIONER CARTER:  Thank you, Commissioner.

18             Before I ask staff, any other parties have any

19   questions of this witness on cross?

20             Staff, you're recognized.

21             MS. FLEMING:  We have no questions.

22             COMMISSIONER CARTER:  That was easy.

23             Mr. Butler.

24             MR. BUTLER:  I have a very brief redirect.

25                        REDIRECT EXAMINATION

FLORIDA PUBLIC SERVICE COMMISSION

222

1   BY MR. BUTLER:

2        Q    Mr. Miranda, you were asked about Hurricane Wilma.

3   Do you consider Hurricane Wilma to be a unique hurricane impact

4   on FPL's service territory?

5        A    I guess in all of our discussions we are always

6   talking about Wilma in that context, and I guess unique only in

7   the sense that we were able to get some really great forensic

8   data.  But hurricanes of Wilma, I fully expect will continue to

9   come into our territory for years to come, and there is nothing

10   unique about hurricanes hitting our service territory.  And so,

11   a Wilma type storm, in my view, is not unique.  We will

12   continue to experience hurricanes going forward in FPL's

13   territory.

14             MR. BUTLER:  Thank you.

15             That's all the redirect that I have.

16             COMMISSIONER CARTER:  Okay.  Let's get ourselves in

17   the proper posture here.  I think we've got exhibits

18   numbered --

19             MR. BUTLER:  I would move Exhibits 20, 21, and 22,

20   which are the prefiled exhibits with Mr. Miranda's testimony.

21             COMMISSIONER CARTER:  20, 21 and 22.  I'm showing --

22   I suppose these would be for rebuttal are the other ones?

23             MR. BUTLER:  Mr. Chairman, it is probably worth

24   noting on the record is that in Exhibit 1 of the staff exhibit

25   list, Mr. Miranda's Exhibits MBM-4, 5, and 6 actually appear

FLORIDA PUBLIC SERVICE COMMISSION

223

1   twice.  They appear as 23, 24, and 25, which would be direct

2   exam exhibits, and then they reappear as 41, 42, and 43.

3   Really those latter numbers, the 41, 42, and 43 are probably

4   appropriate because they are rebuttal exhibits, they are to his

5   rebuttal testimony, not to his direct testimony.

6             COMMISSIONER CARTER:  So they are probably

7   appropriate in the sequence where they fall, but what about 23,

8   24, and 25?

9             MS. FLEMING:  Staff would suggest that 23, 24, and 25

10   not be moved into the record as direct because they are, in

11   fact, rebuttal exhibits, and they are labeled accordingly as

12   41, 42, and 43 and we can move them in at the time that we take

13   up the rebuttal exhibits.

14             COMMISSIONER CARTER:  Okay.  Let's get ourselves

15   together here, then.  So we are dealing with Exhibits 20, 21,

16   and 22, is that correct?

17             MR. BUTLER:  That's correct.

18             COMMISSIONER CARTER:  Any objections?  Show it done.

19             (Exhibits 20, 21, and 22 admitted into the record.)

20             COMMISSIONER CARTER:  Ms. Fleming, where are we now

21   procedurally?

22             MR. WRIGHT:  Mr. Chairman.

23             COMMISSIONER CARTER:  Mr. Wright.

24             MR. WRIGHT:  I apologize.  Just to the extent

25   necessary, I do want to confirm that Exhibit 46 has been

FLORIDA PUBLIC SERVICE COMMISSION

224

1   recognized in Docket 070301.

2             COMMISSIONER CARTER:  Exhibit Number 46, yes, as in

3   070301, FPL's storm hardening plan.

4             (Exhibit 46 admitted into the record.)

5             MR. WRIGHT:  Thank you.

6             COMMISSIONER CARTER:  Is that where we are, staff?

7   That's what I have.

8             MS. FLEMING:  Yes, that is correct.

9             MR. WRIGHT:  And I just wanted to confirm that

10   subject to any conceivable objection which we don't expect,

11   Exhibit 49, which will be the National Hurricane Center's

12   tropical cyclone report on Wilma will be received as Exhibit

13   49.

14             COMMISSIONER CARTER:  Show it done.  No objections on

15   that from Mr. Butler, right?

16             MR. BUTLER:  No.

17             COMMISSIONER CARTER:  Okay.  Ms. Fleming.

18             MS. FLEMING:  I believe that brings us to TECO's

19   Witness Haines.

20             COMMISSIONER CARTER:  Give us a second here.

21             MR. BUTLER:  May Mr. Miranda be excused?

22             COMMISSIONER CARTER:  For now.

23             Mr. Willis.

24                           REGAN B. HAINES

25   was called as a witness on behalf of Tampa Electric Company,

FLORIDA PUBLIC SERVICE COMMISSION

225

1   and having been duly sworn, testified as follows:

2                         DIRECT EXAMINATION

3   BY MR. WILLIS:

4        Q    Mr. Haines, could you please state your name and

5   address for the record.

6        A    Yes.  My name is Regan B. Haines, and my business

7   address is 702 North Franklin Street, Tampa, Florida 33601.

8        Q    Have you previously been sworn?

9        A    Yes, I have.

10        Q    Mr. Haines, did you prepare and cause to be prefiled

11   the prepared direct testimony of Regan B. Haines in this

12   docket, which is Docket Number 070297-EI?

13        A    Yes, I did.

14        Q    Do you have any additions or corrections to that

15   testimony?

16        A    Yes, I do.

17             On Page 23 of my direct testimony, on the response

18   for the first question, I would like to add Section 8.2.2 to

19   the list of sections that we are seeking approval for.

20        Q    And that would be on Line 7?

21        A    That is correct.

22        Q    Did you prepare an exhibit titled "Exhibit of Regan

23   B. Haines," which was attached to your prepared direct

24   testimony?

25        A    Yes, I did.

FLORIDA PUBLIC SERVICE COMMISSION

226

1             MR. WILLIS:  Mr. Chairman, that exhibit has been

2   premarked as Exhibit Number 8.

3             COMMISSIONER CARTER:  Is that shown our list as 38?

4             MR. WILLIS:  No, it's shown as Exhibit 8.  I think

5   our rebuttal exhibit is 38.

6             COMMISSIONER CARTER:  Okay.  I'm taking a step back

7   now.  Oh, I'm reminded now that we agreed to take Mr. Haines

8   out of order.  You're out of order.  (Laughter.)

9             MR. WILLIS:  The order has arrived.  (Laughter.)

10   BY MR. WILLIS:

11        Q    Mr. Haines, if I were to ask you the questions

12   contained in your prepared direct testimony, would your answers

13   be the same if they were asked you here today with the

14   correction that you have already noted?

15        A    Yes, they would be.

16             MS. FLEMING:  I would ask that Mr. Haines' prepared

17   direct testimony be inserted into the record as though read.

18             COMMISSIONER CARTER:  His prefiled testimony will be

19   accepted into the record as though read.

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

252

1   BY MR. WILLIS:

2        Q    Would you please summarize your testimony, Mr.

3   Haines?

4        A    Yes, I would.

5             Good afternoon, Commissioners.  Tampa Electric's

6   2007-2009 storm hardening plan filed on May 7th of this year is

7   an essential part of Tampa Electric's multi-prong approach to

8   enhance the reliability of its transmission and distribution

9   systems and to reduce restoration costs following a major storm

10   event.

11             Tampa Electric's plan contemplates continuing to

12   design and construct its system based on the National

13   Electrical Safety Code's Grade B criteria for all new

14   construction, relocations, and rebuilds of distribution

15   facilities as the company has done since the 1970s.  Although

16   the National Electric Safety Code Grade C criteria is the

17   typical minimum guidelines used for most electrical systems in

18   the United States, building to Grade B criteria, which is

19   significantly stronger than Grade C, fits with the storm

20   profiles that have been experienced in Tampa Electric's service

21   area for the last 150 years.  In fact, the National Oceanic

22   Atmospheric Administration, NOAA, coastal service center

23   records over that time period show that the maximum sustained

24   wind experienced in Tampa Electric's service territory was 115

25   miles per hour both in 1949 and 1960.

FLORIDA PUBLIC SERVICE COMMISSION

253

1             Construction based on Grade B criteria has an

2   affected wind speed of 116 miles per hour while construction

3   based on Grade C has an effective wind speed of only 86 miles

4   per hour.  Moreover, the National Electrical Safety Code

5   extreme wind maps covering Tampa Electric's service territory

6   range from 100 miles per hour in the east to slightly over 120

7   miles per hour on our western edge.

8             In addition, Tampa Electric's plan proposes to

9   conduct several targeted pilot projects to evaluate the NESC

10   extreme wind criteria on circuits serving the Port of Tampa and

11   St. Joseph's Hospital, two critical facilities within the City

12   of Tampa.  The effect of these upgrades will be evaluated after

13   any occurrence of an extreme weather event in Tampa Electric's

14   service area to determine if more widespread application of the

15   NESC extreme wind criteria would be cost-effective.

16             Additionally, Tampa Electric will underground

17   interstate overhead distribution crossings, introduce

18   enhancements to its underground system, and convert the

19   remaining 4 kV distribution circuits to today's 13 kV

20   standards.  Another key component of Tampa Electric's plan is

21   its attachment standards and procedures.  I believe these

22   provide the standards and procedures necessary to ensure that

23   proper third-party attachment notification has been given and

24   that every attachment made to a pole has been engineered to be

25   there, which is critical to the safety and reliability of the

FLORIDA PUBLIC SERVICE COMMISSION

254

1   electric system.

2             In summary, Tampa Electric's approach to continue to

3   build to construction Grade B, undertake specific pilot

4   projects to evaluate NESC extreme wind, and upgrade other key

5   components of the electric system provide a reasonable measured

6   multi-pronged approach to storm hardening the company's

7   transmission and distribution system.  This approach should

8   bring about less storm damage to Tampa Electric's system, and

9   thus less restoration time and cost following a major storm

10   event.  As a result, Tampa Electric's plan is prudent,

11   practical, and is being implemented in a cost-effective manner.

12             MR. WILLIS:  I tender the witness.

13             COMMISSIONER CARTER:  Cross.

14             MS. BROWNE:  Yes, Mr. Chairman.  My name is Maria

15   Browne and I have some questions on cross.

16             COMMISSIONER CARTER:  You're recognized.

17                          CROSS EXAMINATION

18   BY MS. BROWNE:

19        Q    I am going to reserve most of my questions for

20   rebuttal where you have actually addressed these issues, in

21   many cases more thoroughly, and in the interest of any further

22   discussions between the parties over the course of tonight.

23        A    Okay.

24        Q    If you could turn to Pages 9 and 10 of your initial

25   testimony, Lines 16 to 7 -- starting at 16 on Page 9 and going

FLORIDA PUBLIC SERVICE COMMISSION

255

1   to 7 on Page 10.  There you discuss TECO's plan to replace

2   sound poles built to Grade C construction with poles built to

3   Grade B.

4        A    That's correct.

5        Q    And can you confirm that TECO began Grade B

6   construction in the 1970s?

7        A    We have documentation that states that the

8   construction standard adopted in the 1970 was the National

9   Electric Safety Code's Grade B.

10        Q    And so poles were built to Grade C prior to that

11   time, correct?

12        A    The documentation doesn't state what the standard was

13   prior to the move to Grade B.

14        Q    It's your understanding, though, that there are poles

15   built to Grade C construction that exist in TECO's footprint?

16        A    There are poles that, you know, would meet Grade C or

17   fail to meet Grade B, so it just depends on what the criteria

18   is you're looking at and what that threshold is.

19        Q    Assuming that poles were built to Grade C

20   construction prior to being built to Grade B construction in

21   the 1970s then, they have been there for quite sometime, up to

22   35 years or so, correct?

23        A    Based on those assumptions that would be correct,

24   yes.

25        Q    And so poles that have been there for that long have

FLORIDA PUBLIC SERVICE COMMISSION

256

1   withstood extreme weather and hurricanes over that period,

2   correct?

3        A    That would be correct, yes.

4        Q    But you still plan to replace those poles if they are

5   not built to Grade B, correct?

6        A    That's correct.

7        Q    And building to Grade B, to confirm, is either

8   shortening existing spans or putting in a stronger class pole,

9   is that correct?

10        A    There are several things you can do to improve the

11   strength of a pole.  It could be guying, it could be relocating

12   facilities off of a heavily loaded pole to an adjacent pole

13   that might be more lightly loaded, it could be putting in a

14   stronger pole, mid-span pole.  So there are several things you

15   can do.

16        Q    And you're going to make the assessment about whether

17   a pole satisfies Grade B construction standards during the

18   ground line inspection, is that correct?

19        A    It's on the same cycle as our pole inspection and

20   ground line, but it is a separate assessment.  It's not done at

21   exactly the same time.

22        Q    Will it be done at the same time as the load

23   analysis?

24        A    That is the load analysis, yes.

25        Q    Okay.  And will it not then be done at the same time

FLORIDA PUBLIC SERVICE COMMISSION

257

1   as the assessment of whether a pole has deteriorated or not?

2        A    Certain information is gathered at that time, but it

3   is a separate crew so to speak that would go out and do the

4   assessment of the loading.

5        Q    Is it clear which will occur first?

6        A    Typically, the ground line inspection would occur

7   first.

8        Q    And so do you have a pay to distinguish then when a

9   pole has been identified as being deteriorated versus

10   overloaded?

11        A    Yes, we do.

12        Q    And if the pole is overloaded and there is no permit

13   for the attaching entity, that attaching entity will be held

14   responsible for the cost of the pole replacement?

15        A    That's correct.

16        Q    Similarly, if the pole is at Grade C, and you put in

17   a Grade B pole, and there is an attacher on the pole that is

18   not permitted, you will hold that attacher responsible for the

19   cost of the pole replacement?

20        A    Could you restate the question, please.

21        Q    If the pole is currently built to Grade C and you're

22   going to replace it with a Grade B construction, and there's an

23   attacher on the pole that is not permitted, will you assess the

24   cost of that pole replacement to that attaching entity?

25        A    If that attaching entity is causing the overload and

FLORIDA PUBLIC SERVICE COMMISSION

258

1   did not gain proper approval to be on the pole, then that

2   attaching entity could have some cost responsibility to

3   mitigate the overload condition.

4        Q    I was actually talking about Grade C versus B, not

5   the overload.

6        A    Well, if it's not meeting Grade B then we are

7   considering it doesn't meet today's construction standards so

8   it would be overloaded.

9        Q    Okay.  So you are equating those as the same.  Can

10   you confirm that you would assess the entire cost of the pole

11   replacement, or is there some apportionment of costs that would

12   be required?

13        A    For example, if all attachers that are on the pole

14   except for one are permitted to be on the pole, and there's one

15   attacher that is causing that pole to be overloaded that is not

16   permitted or did not gain approval to be on the pole, then that

17   last attacher would be responsible for mitigating the overload.

18   Like I said previously, it could be replacing the pole

19   worst-case, it could be a number of other things to relieve the

20   loading on the pole.

21        Q    If you determined that the pole is deteriorated

22   during the ground inspection, TECO will be responsible for

23   replacing that pole?

24        A    That is correct.  If the pole is determined to be

25   deteriorated then we don't do even the loading analysis piece

FLORIDA PUBLIC SERVICE COMMISSION

259

1   of it, because the pole is going to be replaced.

2        Q    And you are asserting that that is actually going to

3   occur before the loading analysis, correct?

4        A    That's correct.

5             MS. BROWNE:  I would like to introduce as an exhibit

6   TECO's responses to FCTA's interrogatories.

7             COMMISSIONER CARTER:  Is that all of them or just

8   selected ones?

9             Staff, has this already been marked as an exhibit?

10             MS. FLEMING:  No.  This will be Exhibit Number 50.

11             COMMISSIONER CARTER:  Exhibit Number 50.

12             MR. WILLIS:  You have two documents here, which one

13   is Exhibit 50?

14             COMMISSIONER CARTER:  What I'm marking as Exhibit

15   50 is the one entitled "Tampa Electric Company's Answer to

16   First Set of Interrogatories Numbers 1 through 30 of Florida

17   Cable Telecommunications Association, Inc."  That's what I'm

18   showing.

19             Staff?

20             MS. FLEMING:  I concur.

21             COMMISSIONER CARTER:  Hold on one second here.  Let's

22   make sure everyone gets a copy and is on the same page.

23             Commissioners, do you all have one?  Okay.  You're

24   recognized.

25             (Exhibit 50 marked for identification.)

FLORIDA PUBLIC SERVICE COMMISSION

260

1   BY MS. BROWNE:

2        Q    Just to clarify, I'm going to reserve my questions

3   that concern the permitting, how you identify whether or not an

4   attachment is permitted for rebuttal.

5        A    Okay.

6        Q    If you will refer to TECO's response to Interrogatory

7   Number 9, FCTA's Interrogatory Number 9, you state there that

8   1,630 poles having joint use attachments annually will be

9   replaced, is that correct, as part of storm hardening?

10        A    That's correct, in total.

11        Q    Annually, though, right?

12        A    Annually.

13        Q    And approximately how much does it cost to replace a

14   pole with a Grade B construction pole?

15        A    In the neighborhood of $1,500 to $2,000.

16        Q    Is that material only or does that include labor?

17        A    That's the total cost.

18        Q    Does that include transfer costs?

19        A    No, that does not include transfer costs.

20        Q    If the pole is moved out of line by 15 feet, would

21   that significantly increase the cost to replace the pole?

22        A    Tampa Electric's cost, not considering transfer

23   costs?

24        Q    Maybe I should ask an interim question.  If an

25   attaching entity is held responsible for the cost of the pole

FLORIDA PUBLIC SERVICE COMMISSION

261

1   replacement, will they also be responsible for the cost of

2   transferring Tampa Electric's facilities?

3        A    If the pole would not be changed out for any reason

4   but what I would call an unauthorized attachment, somebody that

5   is attached to the pole that did not get approval to be there,

6   then that entity would be responsible for all the costs to

7   change that pole out.

8        Q    So the full cost, on average, to replace a pole

9   including Tampa Electric's transfer costs is how much

10   approximately?

11        A    That would be the 1,500 to 2,000.  And it's the same

12   as if the -- you know, if the attaching entity would have

13   gained approval to begin with to attach to the pole, that's

14   what we would call make-ready costs to prepare the pole, you

15   know, to increase the capacity of the pole to accommodate the

16   attacher.

17        Q    If the pole is moved out of line 15 feet,

18   approximately how much would that increase the cost?

19        A    I really couldn't say without knowing the specifics,

20   what's on the pole, you know, and what has to be transferred

21   and that kind of thing.

22        Q    But it could increase significantly, correct?

23        A    It could increase.  I don't know if I would say

24   significantly, but it could increase the cost.

25             MS. BROWNE:  I have no further questions at this

FLORIDA PUBLIC SERVICE COMMISSION

262

1   time.

2             COMMISSIONER CARTER:  Okay.  Let's take a moment

3   here.  Commissioners, at this point in time do any

4   Commissioners have any questions before we ask the other

5   parties if they have any questions?

6             Hearing none, we'll move to staff.

7             MS. FLEMING:  Staff has no questions.

8             COMMISSIONER CARTER:  Okay, then.

9             Mr. Willis.

10             MR. WILLIS:  I have no redirect.

11             We would move the admission of Exhibit Number 8.

12             COMMISSIONER CARTER:  You had an exhibit marked

13   Number 50.

14             MS. BROWNE:  I would like to move that in.

15             COMMISSIONER CARTER:  Any objection, staff?  Any

16   objections by any of the parties?  Show it done.

17             (Exhibit 8 and Exhibit 50 admitted.)

18             COMMISSIONER CARTER:  Ms. Fleming.

19             MS. FLEMING:  I believe the next witness listed here

20   is Slavin, which we noted earlier that Witness Slavin's

21   testimony and exhibits have been withdrawn, so the next witness

22   would be Witness Walker, is that correct?

23             MR. O'ROARK:  Correct.  And.

24             Mr. Chairman, Mr. Walker you will recall is Verizon's

25   witness who has been stipulated, and we would move admission of

FLORIDA PUBLIC SERVICE COMMISSION

263

1   the testimony again recalling that his testimony from Page 4,

2   Line 3 to Page 7, Line 18 has been withdrawn.

3             COMMISSIONER CARTER:  Give me one second here so we

4   can all be on the same page here.

5             Staff, I am looking at the comprehensive exhibit list

6   and I am looking for --

7             MS. FLEMING:  It's my understanding that Witness

8   Walker does not have any exhibits at this point, since he is a

9   stipulated witness just in the Progress docket.  I believe the

10   Verizon attorney is asking to move in Witness Walker's prefiled

11   testimony just as it pertains to the Progress docket, to move

12   it into the record as though read.

13             COMMISSIONER CARTER:  Any objections?  Hearing none,

14   show it done.

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

270

1             COMMISSIONER CARTER:  Next.

2             MS. FLEMING:  The next witness is Witness Smith from

3   AT&T.  He was a previously stipulated witness, but we do have

4   the testimony and exhibits to move into the record for this

5   witness.

6             COMMISSIONER CARTER:  And that would be --

7             MS. FLEMING:  Exhibit Number 27.

8             COMMISSIONER CARTER:  Any objections?  Hearing none,

9   show it done.

10             (Exhibit 27 marked for identification and admitted

11   into the record.)

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

279

1             COMMISSIONER CARTER:  Next.

2             MS. FLEMING:  The next witness I have is FCTA Witness

3   Harrelson.

4             MR. SEIVER:  Mr. Chairman, yes, Mr. Harrelson is the

5   next witness.  And the way I understood the procedure would be

6   is Mr. Harrelson would testify even though he has testimony in

7   three of the four dockets, he would do one docket at a time, be

8   cross-examined and redirect before we moved on to his direct

9   testimony in the next docket.

10             And if Your Honor, Mr. Chairman please, we could

11   begin with his first docket, which I guess is the Tampa

12   Electric docket, if that's the preference.

13             COMMISSIONER CARTER:  Any objection by any of the

14   parties?  Staff.  That makes so much sense.  Let's do it.  That

15   would be logical, let's do that.

16                        MICHAEL T. HARRELSON

17   was called as a witness on behalf of Florida Cable

18   Telecommunications Association, and having been duly sworn,

19   testified as follows:

20                         DIRECT EXAMINATION

21   BY MR. SEIVER:

22        Q    Would you please state your name for the record,

23   please?

24        A    My name is Michael Truett Harrelson.  My nickname is

25   Mickey.

FLORIDA PUBLIC SERVICE COMMISSION

280

1        Q    Mr. Harrelson, were you here today when the witnesses

2   were sworn in?

3        A    I was, yes.

4        Q    And, Mr. Harrelson, did you cause to be filed

5   testimony in the Docket 00 -- I'm sorry, 0702997-EI (sic)

6   concerning the storm hardening plan of Tampa Electric Company,

7   testimony on behalf of the Florida Cable Telecommunications

8   Association?

9        A    Yes, I did.

10        Q    And did you have any additions or corrections to that

11   testimony?

12        A    None.

13        Q    And if I asked you the questions in that testimony

14   today, would your answers be the same?

15        A    Yes.

16        Q    And did you also have some exhibits attached to that

17   testimony?

18        A    I believe there were, yes.

19        Q    Would you please identify those exhibits?

20        A    I'm not certain about the numbers, but in this copy

21   it's MTH-1.  Should I refer to it by a different number?  I'm

22   not sure.

23             MR. SEIVER:  Mr. Chairman, that's Exhibit Number 28.

24        Q    And is that the curriculum vitae, Mr. Harrelson?

25        A    It is, and it includes a list of testimonies.

FLORIDA PUBLIC SERVICE COMMISSION

281

1        Q    And, Mr. Harrelson, would you look at MTH-2, which is

2   on the master exhibit list Number 29, and tell us what that is?

3        A    That is a copy of an affidavit by Doctor Larry

4   Slavin.

5        Q    And then hearing identification Exhibit Number 30,

6   which is MTH-3, would you please explain what that exhibit is?

7        A    That's a copy of the process to engage third-party

8   attachers.

9        Q    And these are the only three exhibits that you have

10   attached to your testimony in the Tampa Electric docket, is

11   that right?

12        A    That's correct.

13             MR. SEIVER:  At this time I would like to move into

14   the record the direct testimony -- I'm sorry.  Mr. Chairman, at

15   this time I would like to move into the record the prefiled

16   direct testimony of Mr. Harrelson.

17             COMMISSIONER CARTER:  The prefiled testimony of Mr.

18   Harrelson will be entered into the record as though read.

19

20

21             (REPORTER NOTE:  Direct Testimony of Michael

22   subsequently withdrawn in Docket 070297-EI.  Transcript

23   continues with Page 282.)

24

25

FLORIDA PUBLIC SERVICE COMMISSION

282

1   BY MR. SEIVER:

2        Q    Mr. Harrelson, could you please give a summary of

3   your testimony.

4        A    Yes.  Tampa Electric has stated that its experience

5   shows that there is no substantial evidence that building

6   distribution structures to extreme wind construction grades

7   will prevent damage from falling trees, tree limbs, flying

8   debris during major storm events.  In my opinion, Grade B

9   construction, which Tampa Electric proposes to continue to

10   build to, is more than adequate to strengthen distribution

11   poles against the effects of extreme winds in the service

12   territory of Tampa Electric.

13             Compliance with the applicable grade of Grade C for

14   poles 60 feet or less will meet the Commission's objectives as

15   long as other initiatives such as vegetation management,

16   increased guying, replacing rotten poles are implemented.

17   However, TECO since the early '70s has used Grade B

18   construction, and the majority of its plant is already built to

19   Grade B.  Accordingly, TECO estimates the increased incremental

20   cost to building to Grade B to be zero.  We feel that the

21   incremental cost of building to Grade B, including changing out

22   some of the sound Grade C poles, will be greater than zero.

23             The three-year pilot project program we agree is

24   prudent, practical, cost-effective, and especially the practice

25   of storm hardening the interstate crossings.  All four of the

FLORIDA PUBLIC SERVICE COMMISSION

283

1   IOUs have identified that as an area worthwhile to either

2   harden to extreme wind standards or place underground as TECO

3   intends to do, and we agree that's worthwhile.  On transition

4   to its Grade B standard, I don't believe that its plans for

5   deploying Grade B are prudent, practical, and cost-effective

6   because I do not agree that all of their poles are now

7   presently at Grade B.

8             TECO's plan relies heavily on its maintenance

9   programs, including its ground line inspection program, by

10   which it intends to identify poles that need to be replaced.

11   This inspection program was required in another docket, but the

12   criteria is identified in this docket.  TECO plans to implement

13   the use of a pole strength evaluating program called Pole

14   Foreman.  I am concerned that Pole Foreman may not take into

15   account all of the relevant criteria for assessing the true

16   strength of poles and its ability to withstand wind and

17   loading.  For example, I don't believe that Pole Foreman takes

18   into account the guying effect of lateral lines on poles

19   without special application procedures.

20             Considering the pole loading calculations with

21   computer software as opposed to the engineering guidelines,

22   tables, and charts that have served very well for electric

23   utility designers is new to TECO and many others.  I believe

24   extra caution should be used to be certain that beneficial as

25   well as the detrimental loading effects on poles should be

FLORIDA PUBLIC SERVICE COMMISSION

284

1   included in these sophisticated calculations.

2             I have concerns about TECO's inspection process to

3   determine the loading effects of third-party attachments on the

4   poles.  First, TECO intends to perform a loading analysis on

5   joint use poles.  A loading analysis shall not be performed on

6   poles with only TECO assets.  This approach is discriminatory.

7   Electric facilities are known to overload poles as well as

8   poles with electric facilities and third-party attachments.

9             Second, TECO intends to assess responsibility for

10   overloading in a discriminatory and arbitrary manner.  TECO

11   states that it will presume that the electric company was the

12   first entity on the pole.  It is always assumed that the

13   company was the first attacher.  It will then attempt to assess

14   responsibility for overloading on the last party to attach to

15   the pole, which it presumes to be the third-party attacher.  In

16   my experience the power company owner is often the last one to

17   put an additional attachment on a pole, such as a transformer,

18   service to a new customer, a streetlight, or things of that

19   nature.

20             Third, TECO intends to assess responsibility for

21   overloading on any party that cannot produce an approved paper

22   copy of a permit.  TECO has asserted that it has not maintained

23   adequate records of pole attachments, accordingly it will look

24   to third-party attachers to prove that they are authorized to

25   be on the pole.  If they cannot produce evidence that they are

FLORIDA PUBLIC SERVICE COMMISSION

285

1   authorized in the form of an approved application, they will be

2   held responsible for any noncompliance and will be responsible

3   to pay for the make-ready that will bring the pole back into

4   compliance.

5             That's my summary.

6             MR. SEIVER:  Thank you, Mr. Harrelson.

7             Mr. Chairman, we tender him for cross.

8             COMMISSIONER CARTER:  Mr. Willis, you're recognized.

9                          CROSS EXAMINATION

10   BY MR. WILLIS:

11        Q    Good after, Mr. Harrelson.

12        A    Good afternoon.

13        Q    I take it that in performing loading analysis up to

14   this point you have just used engineering guidelines and hand

15   calculation methods, which are essentially rules of thumb, is

16   that correct?

17        A    I have used those more than using the computer-based

18   analysis program, but I have used one computer-based program in

19   the past, yes.

20        Q    You haven't used Pole Foreman to conduct load

21   analysis, though, have you?

22        A    I have not actually used Pole Foreman.  I have only

23   had a 30 or 45-minute discussion with Mr. Malcolm Young

24   (phonetic), who markets and, I believe, developed Pole Foreman.

25        Q    Mr. Harrelson, do you agree that the purpose of this

FLORIDA PUBLIC SERVICE COMMISSION

286

1   docket is to determine whether the storm hardening plan of

2   Tampa Electric meets the objectives of enhancing the

3   reliability of electric transmission and distribution service?

4        A    I do; and it should be in a prudent, practical, and

5   cost-effective manner, yes.

6        Q    Okay.  Well, let's look at the first objective first

7   of enhancing the reliability of electric transmission and

8   distribution service.  Will you agree that construction Grade B

9   poles are stronger than construction Grade C poles?

10        A    I generally agree with that.  The strength can be

11   achieved by storm guying and other methods other than simply

12   stronger poles, but the overall line construction is stronger,

13   yes.

14        Q    How much stronger is a construction B pole than a

15   construction C pole in equivalent wind strength?

16        A    Equivalent wind strength is a comparison that has to

17   go through several assumptions.  The National Electrical Safety

18   Code requires that Grade C have nine pounds per square foot of

19   wind pressure applied to the pole and the lines and the

20   equipment.  Grade B also requires the exact same wind pressure.

21   The National Electric Safety Code then applies different

22   strength and loading factors to Grade B, to Grade C, and Grade

23   C actually has a subgrade of Grade C at crossings.

24             So equivalent wind speed can be computed, but it must

25   be done based on whether you're applying those factors to the

FLORIDA PUBLIC SERVICE COMMISSION

287

1   force of wind, to the force of conductors on the pole, to the

2   effect of wind on the pole itself.  So a general answer is the

3   best that can be calculated on that.  Specific answers depend

4   on the exact loading of each individual pole.

5        Q    Will you refer to your testimony on Page 11 at Line

6   3?

7        A    Okay.  Thank you.

8        Q    Could you please read the sentence that begins at the

9   end of Line 3 through the beginning of Line 6?

10        A    The sentence is Grade B design results in an

11   equivalent -- Grade B design results in an equivalent wind

12   strength of approximately 116 miles an hour, and thus stronger

13   than Grade C design which results in an equivalent wind

14   strength of approximately 86 miles per hour.

15        Q    Do you agree that Tampa Electric's distribution

16   facilities already meet and in most cases exceed the minimum

17   requirements of NESC?

18        A    Yes, sir, I do.

19        Q    Do you agree that continuing to build to construction

20   Grade B will produce a system with the equivalent wind strength

21   that a system -- with a greater equivalent wind strength than a

22   system built to construction Grade C?

23             MR. SEIVER:  I'm sorry, I object.  Could you clarify

24   that.

25             COMMISSIONER CARTER:  Yes.  Make it a little clearer

FLORIDA PUBLIC SERVICE COMMISSION

288

1   so we can all understand the question.

2             MR. WILLIS:  All right.

3   BY MR. WILLIS:

4        Q    Would you agree that continuing to build to

5   construction Grade B in Tampa Electric's system will produce a

6   system with a greater equivalent wind strength than a system

7   built to construction Grade C?

8        A    I do.

9        Q    Will you agree that building to construction Grade B

10   will enhance the reliability of Tampa Electric's system?

11        A    I agree that it will under most circumstances.  There

12   are circumstances where I think it will be for the most part

13   irrelevant.

14        Q    Now, you have contended that some of TECO's system is

15   not presently built to construction Grade B standards, correct?

16        A    That's correct.

17        Q    If that's correct, then upgrading the portion of the

18   system that is not built to construction Grade B will provide a

19   greater equivalent wind strength of poles on Tampa Electric's

20   system, won't it?

21        A    Under certain circumstances.  And if I can clarify,

22   in areas which there are many of in Tampa where there are trees

23   and buildings as tall as and near the line, then the

24   performance of Grade B poles I do not think will be

25   significantly superior to Grade C poles.  Those trees shelter

FLORIDA PUBLIC SERVICE COMMISSION

289

1   the lines from the effect of the wind.  Up until the point when

2   the trees start to break off limbs, the trees start to fall

3   over, and when the trees come down they would take down a Grade

4   B line or a C Line almost the same.

5        Q    Would you agree that failing to replace a

6   construction Grade C pole with a construction Grade B pole as

7   those poles are discovered will delay the complete conversion

8   of Tampa Electric's system to a construction Grade B?

9        A    No, I don't.  I think it's a matter of priorities.

10   If you go through and replace sound solid Grade C poles during

11   an eight-year cycle that means that it is still six or seven

12   years before you get around to replacing the deteriorated poles

13   that do not meet Grade C.  And there are a significant number

14   of those, according to your reliability reports, that don't

15   meet the strength requirements.  So I suggest prioritizing the

16   expenditures, replace the rotten poles first, come back on the

17   second pass, replace the solid sound Grade C poles, which many

18   of them have been there for 50 or 60 years.

19        Q    Well, if a pole of 60 feet or less is constructed to

20   construction Grade B, wouldn't it be more reliable against

21   flying debris than a Class C pole?

22        A    Up to a certain point I believe it would be if that

23   small debris would not break both poles.  If the debris is

24   large enough it will break a B or a C or an extreme wind for

25   that matter.

FLORIDA PUBLIC SERVICE COMMISSION

290

1        Q    But there are circumstances where a B will survive

2   better than a C, correct?

3        A    I agree.  I believe there is a window there where it

4   would.

5        Q    Now, let's look at the second prong of the test, that

6   is the prudent and cost-effective manner of enhancing the

7   reliability of the electric transmission and distribution

8   service.  You have agreed, have you not, that based on Tampa

9   Electric's historic use of construction Grade B, that

10   continuing to build to construction Grade B standards with only

11   limited pilot projects for extreme wind loading is a prudent,

12   practical, and cost-effective approach?

13        A    Yes.

14        Q    You contend that Tampa Electric's plan is not prudent

15   because it plans to replace poles that meet construction Grade

16   C, but not construction Grade B, correct?

17        A    I believe that aspect of it would be better adjusted

18   and more prudent to change out the deteriorated poles first,

19   wait until a later date to change out the solid poles that meet

20   Grade C criteria, that's correct.

21        Q    Well, what is the life of a typical wooden pole?

22        A    It is like a typical engineer; it varies a lot.  Some

23   poles really are as solid as the day they were put into the

24   ground and they were put in in the '20s and the '30s.  But, I

25   don't know what the average is.  I do know that some of the

FLORIDA PUBLIC SERVICE COMMISSION

291

1   poles put in in the '60s and '70s have already been replaced,

2   and there are poles out there that were installed in the '30s.

3        Q    Mr. Harrelson, you agree that the NESC requires

4   construction Grade B for distribution poles crossing limited

5   access highways, railroad tracks, and navigable waterways?

6        A    Yes, I do.

7        Q    Isn't the rationale for requiring construction Grade

8   B for limited access highways, railroad tracks, and navigable

9   waterways is that stronger poles are less likely to cause a

10   failure to the pole that would interfere with transportation?

11        A    I think that is true, and it's not simply focused on

12   poles.  A lot of crossings are made strong by the storm guying

13   technique.  In general, if everything is considered equal, the

14   stronger construction is more resilient and more resistant to

15   storm events.  What the code does is specifies strength and

16   conditions.  When one exceeds the code and chooses to for its

17   purposes other than safety, say for instance reliability, if

18   you choose to exceed the code for those purposes, reliability,

19   you are not bound then by the other terms in the code that, for

20   instance, say don't consider where there is a big tree hanging

21   over it.

22             If the code requires Grade C and you choose to use

23   Grade B, then you are also at liberty to look up and see if

24   there is a big tree that will fall and crush that Grade B pole,

25   and you can say, wait, I'll put that Grade B pole in an open

FLORIDA PUBLIC SERVICE COMMISSION

292

1   area where the wind is going to effect it as opposed to putting

2   it in a forest where it will be sheltered by the trees until if

3   the trees come down they break the Grade B pole.  So if you are

4   going to exceed the code, you are at liberty to put in a few

5   other common sense guidelines that are not specified in the

6   code for the places where the code does mandate Grade B.

7        Q    If outages are reduced and restoration times are

8   improved following a major storm event, would you agree that

9   all parties would benefit?

10        A    I do agree that if that happens all parties benefit,

11   and the only qualifier I would add is just let's make it

12   cost-effective, prudent, and practical.

13        Q    You would agree that Tampa Electric's approach to

14   continue to build to construction Grade B for new construction

15   of major planned work, expansion and rebuilds and relocations

16   of its overhead system is prudent, practical, and

17   cost-effective, do you not?

18        A    I do.  And the only qualifier I would put on that is

19   as many years as I have been involved in this, I have always

20   believed that the lines that are attached to the pole, the

21   additional guying effects are part of the consideration of the

22   strength of that pole.  And I'm simply wanting to, I guess,

23   request that TECO take that into consideration and just be sure

24   Pole Foreman does do that.

25        Q    Now, let's talk a minute about the level of detail

FLORIDA PUBLIC SERVICE COMMISSION

293

1   that Tampa Electric has provided to the CATV providers in FCTA.

2   You contend on Page 18, Line 6, that Tampa Electric's plan does

3   not include specific technical design specifications,

4   construction standards, and construction methodologies that

5   will be employed in hardened poles.  Would you agree that Tampa

6   Electric has worked in good faith to provide information to

7   attachers?

8        A    I agree.  And, in addition, that process to engage

9   third-party attachers, I believe, will ultimately provide that

10   information.  But we can't tell what the costs are for

11   transferring until we know which poles you will be doing work

12   on or which poles you will be requiring us to do work on.  And

13   until that process has a chance to work, you don't yet know, so

14   you can't yet tell us.

15        Q    Well, you will agree that Tampa Electric did hold

16   meetings with attachers to discuss its pilot projects, did it

17   not?

18        A    Yes.

19        Q    And maps were provided of the effective routes to the

20   attachers, were they not?

21        A    That's correct.

22        Q    And offers to ride each effective circuit were made

23   to each of the attachers, wasn't it?

24        A    Yes, it was.

25        Q    And did you take advantage of that offer?

FLORIDA PUBLIC SERVICE COMMISSION

294

1        A    Yes, we did to our satisfaction.  We didn't actually

2   ride, but the gentleman who showed us all the plans offered to

3   ride.  He had a meeting for the second half of the day, we were

4   perfectly comfortable in following that map on our own.

5        Q    Okay.

6        A    I might add, the maps and the routes show a few miles

7   of line.  They do not yet state any of the work that will be

8   done on any of the individual poles.  That will have to be

9   developed later when those jobs are actually engineered.

10        Q    And that will be taken care of in the process within

11   the process which has been approved here, correct?

12        A    That's correct.

13        Q    On Page 23 of your testimony, you state that

14   7.7 percent, or 1,359 of 17,700 poles inspected by Tampa

15   Electric failed construction Grade B, is that right?

16        A    That's correct.

17        Q    And that number was derived, wasn't it, from Tampa

18   Electric's 2006 inspection report which shows that reference?

19        A    Yes.

20        Q    Are you familiar with the company's current failure

21   rate stated in response to FCTA's Request for Production of

22   Documents Number 7?

23        A    I can't quote it.  I don't remember if I have seen

24   it.  I believe I have seen it, but I don't remember.

25        Q    I have provided the witness a copy of that discovery

FLORIDA PUBLIC SERVICE COMMISSION

295

1   response of Tampa Electric.  I'd like to ask you, Mr.

2   Harrelson, isn't the historic rate of poles failing loading

3   analysis two percent shown in that report?

4        A    That is what this answer reflects, yes.

5        Q    And that's after some 55,000 poles have been

6   inspected, correct?

7        A    I'm looking at 38,000.

8        Q    Okay.  Well, as the company has had additional

9   experience the pole failure rate has gone down, correct?

10        A    I'm sorry, I just don't follow you.

11        Q    I'll withdraw that; I think it is obvious.

12             MR. SEIVER:  I object to that.  I wanted to know what

13   was put in that was said to be obvious.

14             MR. WILLIS:  Well, the historic rate of poles failing

15   is two percent after at least 38,000 poles have been inspected,

16   whereas Mr. Harrelson's reference was a failure rate of

17   7.8 percent after only 17,000 poles had been inspected.

18             MR. SEIVER:  I'm not sure we can draw any conclusions

19   from that, but now I understand his point.

20             COMMISSIONER CARTER:  Mr. Willis, what you are

21   referring to, is that part of the record?  You just pulled out

22   a page from the record, is that --

23             MR. WILLIS:  I don't believe it is in the record.

24   I'll provide it.

25             COMMISSIONER CARTER:  I think that is probably where

FLORIDA PUBLIC SERVICE COMMISSION

296

1   we are, we're trying to figure out -- you know, that would

2   probably be more helpful and save some objections on that if we

3   can all see what we are talking about at the same time.

4             Before we go further, staff, this looks like a

5   response to an interrogatory.  Can you place this?

6             MS. FLEMING:  Looking at this, this is not part of

7   the staff's stipulated exhibit, so it is not part of the record

8   unless Mr. Willis is intending to identify it as a hearing

9   exhibit.

10             COMMISSIONER CARTER:  So we will need to give this a

11   separate number, then.  This will be Number 51?

12             MS. FLEMING:  Yes, that's correct, Commissioner.

13             COMMISSIONER CARTER:  And give us a title, Mr.

14   Willis.

15             MR. WILLIS:  Tampa Electric's Response to FCTA's

16   First Request for Production of Documents Number 7.

17             (Exhibit Number 51 marked for identification.)

18             COMMISSIONER CARTER:  Hold on one second.  Okay.

19             Witness, have you had an opportunity to look this

20   over yet?

21             THE WITNESS:  Yes.

22             COMMISSIONER CARTER:  Okay.  Mr. Seiver.

23             MR. SEIVER:  I guess I need Mr. Willis to clarify, or

24   maybe the witness can clarify.  I see a percentage for poles

25   failing, loading poles 4.5 percent failing, structural

FLORIDA PUBLIC SERVICE COMMISSION

297

1   analysis, poles replaced annually, which is another number

2   which I think are those first two added.  I don't know if he's

3   comparing one percentage to only one or the combined

4   percentage.  That's why I was kind of confused about what we

5   are comparing.

6             MR. WILLIS:  Well, I asked the witness if the

7   historic rate of poles failing the loading is shown to be 2

8   percent on this report, this response.  It is clear what I

9   asked him about.

10             MR. SEIVER:  I guess maybe I missed.  And the

11   percentage of failing loading was based on a fewer number of

12   poles earlier, is that it?

13             MR. WILLIS:  Mr. Harrelson in his testimony has a

14   7.8 percent number, and I was comparing that with what was

15   later information.

16             MR. SEIVER:  Well, I think the record will speak for

17   itself.

18             Mr. Chairman, I will withdraw my objection to the

19   question.

20             COMMISSIONER CARTER:  Okay.

21   BY MR. WILLIS:

22        Q    Mr. Harrelson, on Page 29 of your testimony, you

23   refer to the 2001 audit, isn't that correct?

24        A    What line, please?

25        Q    It was Page 29, Line 1.

FLORIDA PUBLIC SERVICE COMMISSION

298

1        A    Okay.  Yes.

2        Q    Are you familiar with Tampa Electric's pole

3   attachment audit conducted in 2001?

4        A    I'm somewhat familiar with it, not any particular

5   level of detail.  I've discussed it with one individual.

6        Q    Do you agree that that audit showed that 20 percent

7   of third-party attachments on Tampa Electric's system were

8   unauthorized and unnoticed?

9        A    I think, yes, that determination was made by TECO.

10        Q    And you also note on Page 29, Line 3, that CATV

11   operators paid a significant lump sum to cover back rent for

12   attachments that were not authorized, correct?

13        A    That's correct for attachments that were claimed that

14   they were not authorized.

15        Q    Do you know if any make-ready costs were paid to

16   ensure that the poles met code and company construction

17   standards as a result of that audit?

18        A    I'm not certain.  I don't think there were any

19   make-ready costs assessed.

20        Q    On Page 31, Line 2, you state that Tampa Electric's

21   joint pole attachment audit is really just a billing audit, is

22   that correct?

23        A    Yes.

24        Q    Now, were you referring to the company's audit that

25   is being undertaken as a result of the Commission's order in a

FLORIDA PUBLIC SERVICE COMMISSION

299

1   previous docket?

2        A    That was my understanding, yes.

3        Q    Mr. Harrelson, I want to show you an excerpt of Order

4   Number 06-0351, and ask you a question about that, please, sir.

5             Mr. Harrelson, I want to refer you to the last

6   paragraph on Page 4 of this order.

7             MR. SEIVER:  Excuse me, if I might interpose an

8   objection.  I'm just realizing now that this is an incomplete

9   document.  This is just the front page and Page 4.  There are

10   apparently more pages that are part of this order.

11             COMMISSIONER CARTER:  What's the purpose on this

12   document, Mr. Willis?

13             MR. WILLIS:  Well, Mr. Harrelson indicated that the

14   audit that Tampa Electric was going to conduct was just a

15   billing audit, whereas your order in the final paragraph

16   describes much more than a billing audit.  It describes a

17   number of things that I was going to ask him to refer to.

18             MR. SEIVER:  I think for completion, if we are going

19   to have this as an exhibit, and I know Mr. Willis hasn't marked

20   it as a hearing exhibit yet, that we should have the whole

21   order, at least for reference.

22             COMMISSIONER CARTER:  Hang on a second.

23             MR. WILLIS:  I have a copy if he would like.

24             COMMISSIONER CARTER:  Hang on a second.

25             Ms. Helton.

FLORIDA PUBLIC SERVICE COMMISSION

300

1             MS. HELTON:  Mr. Chairman, it is not our practice to

2   mark Commission orders as exhibits.  It's something that you

3   can officially recognize, although we don't even typically

4   officially recognize it.  I think it's just assumed by everyone

5   that you can use and rely on Commission orders.

6             However, it seems like a valid concern to me that he

7   has that he would like to have the full body of the order

8   before him so that he can look at it and maybe perhaps let his

9   witness look at it.  So, if Mr. Willis has one that he can look

10   at, maybe we could let him do that and then move forward.

11             COMMISSIONER CARTER:  That sounds like a reasonable

12   suggestion to me.  (Pause.)

13   BY MR. WILLIS:

14        Q    Mr. Harrelson, would you read the last paragraph on

15   Page 4 of Order Number 06-0351?

16        A    Yes.  Would you like for me to read it aloud?

17        Q    Yes; please, sir.

18        A    I mean, I will read it to myself.  "Each

19   investor-owned electric utility shall develop a plan for

20   auditing joint use agreements that includes pole strength

21   assessments.  These audits shall include both poles owned by

22   the electric utility to which other utility attachments are

23   made, i.e., telecommunications and cable, and poles not owned

24   by the electric utility to which the electric utility has

25   attached its electrical equipment.  The location of each pole,

FLORIDA PUBLIC SERVICE COMMISSION

301

1   the type and ownership of the facilities attached, the age of

2   the pole, and the attachments to it should be identified.  The

3   utility shall verify that such attachments have been made

4   pursuant to a current joint use agreement.  Stress calculations

5   shall be made to ensure that each joint use pole is not

6   overloaded or approaching overloading for instances not already

7   addressed by Order PSC-06-0144-PAA-EI.

8        Q    That describes much more than just a billing audit,

9   doesn't it?

10             MR. SEIVER:  Objection.  He's trying to characterize

11   what the order says.  It speaks for itself.

12             MR. WILLIS:  All right.  I will withdraw the

13   question.

14             COMMISSIONER CARTER:  Okay.  Let's move on.

15   BY MR. WILLIS:

16        Q    If you will refer to Page 33, Line 24 of your

17   testimony.  You indicate that your experience is that

18   third-party attachments do not significantly increase load on

19   poles and overlashing has only a very small incremental effect

20   on already attached strand and assembly.  Do you see that

21   testimony, Mr. Harrelson?

22        A    Yes.

23        Q    You will agree that CATV attachments and overlashings

24   do place additional loadings on a pole?

25        A    I do.

FLORIDA PUBLIC SERVICE COMMISSION

302

1        Q    And you will agree that it is possible for an

2   overlashed CATV attachment to create an overloaded situation?

3        A    It is possible to increase the load on the pole.

4   It's possible to overload a pole that is not overloaded.  It is

5   possible to add more load to a pole that is already overloaded.

6   So with the recognition that increasing load can cause all of

7   those possible effects, yes.

8        Q    You will agree that cables as large as an inch in

9   diameter can be added and included in an overlash?

10             MR. SEIVER:  I'm sorry, objection.  Included by who

11   and when and what?

12             COMMISSIONER CARTER:  I think there is probably not a

13   foundation for this, Mr. Willis.  So let's -- I mean, let's

14   move on.

15   BY MR. WILLIS:

16        Q    Will you agree that six or more cables can be

17   overlashed into a bundle?

18             MR. SEIVER:  Same objection.

19             COMMISSIONER CARTER:  Mr. Willis, if you want to ask

20   this witness things that are within his area of expertise, then

21   let's do that and kind of let's stay within the confines of the

22   four corners of the record.

23   BY MR. WILLIS:

24        Q    Okay.  Well, Mr. Harrelson, will you refer to your

25   deposition at Page -- do you have a copy of your deposition?

FLORIDA PUBLIC SERVICE COMMISSION

303

1        A    Yes, sir.

2        Q    Would you refer to your deposition at Page 112?

3        A    Oh, the deposition.  I'm sorry, I don't have it.

4             MR. WILLIS:  Okay.  Well, I may come back to that in

5   a minute.

6             COMMISSIONER CARTER:  Staff, do you have a copy that

7   you can provide?

8             MS. FLEMING:  Yes.  Staff would note that that is

9   part of the Staff Composite Exhibit 6, and it should to be your

10   right.  It's Exhibit 6, Tab 4.

11             MR. SEIVER:  I have an extra copy.

12             COMMISSIONER CARTER:  Thank you.  You may proceed.

13             THE WITNESS:  I'm at 112.

14   BY MR. WILLIS:

15        Q    Would you read Line 16 through Line 23?

16        A    On Page 112?

17        Q    Yes.

18        A    Mine starts by saying Page 16 talking about increased

19   storm restoration delays.

20        Q    On your deposition?

21        A    Well, this copy it does.

22             COMMISSIONER CARTER:  Okay.  Hang on a second.  Let's

23   take a minute and -- let's just take a minute to get the proper

24   documents before the witness.  Let's just take a minute.

25             THE WITNESS:  I see two different numbers on the

FLORIDA PUBLIC SERVICE COMMISSION

304

1   page.  There is more than one page on each.

2             COMMISSIONER CARTER:  Off the record.

3             (Off the record.)

4             COMMISSIONER CARTER:  Let's go back on the record

5   here.

6             What I thought we were doing, I was very optimistic

7   looking at the clock, and I see right now we are still knee

8   deep in the tall trees and the deep woods with the ticks, so I

9   think that this is probably a good breaking point, since we are

10   where we are now, looking at documents and things of that

11   nature.

12             I think what we are going to do, Commissioners, if

13   that is okay with you, we will just break for now and pick up

14   again tomorrow at 9:30 and proceed from there and give

15   everybody a good night's sleep and be ready.  And eat your

16   Wheaties in the morning and be ready to roll.

17             Staff, are there any matters that we need to discuss

18   prior to our recess and for the day?

19             MS. FLEMING:  One matter would be Hearing Exhibit 44,

20   which was the Slavin deposition transcript.  We need to get

21   that moved into the record.  I would note that the errata sheet

22   was left off the exhibit, and Ms. Keating is bringing that

23   around to attach to the back of Exhibit 44.

24             COMMISSIONER CARTER:  Okay.  Let me ask you this, I

25   thought that we had already moved 44 in, then we just put down

FLORIDA PUBLIC SERVICE COMMISSION

305

1   each one of the different case numbers, is that -- did we not

2   do that?

3             MS. FLEMING:  Exhibit 44 has not been moved into the

4   record.

5             COMMISSIONER CARTER:  Slavin?

6             MS. FLEMING:  That's correct, and it is only being

7   moved into the record for the FPL docket.

8             COMMISSIONER CARTER:  Okay.  So show that done.

9             (Exhibit Number 44 admitted into the record.)

10             COMMISSIONER CARTER:  Any other preliminary matters?

11             MS. FLEMING:  That's all I'm aware of right now.

12             COMMISSIONER CARTER:  Any preliminary matters from

13   any of the parties?

14             Okay.  See everybody tomorrow bright and early at

15   9:30.

16             MR. WILLIS:  Is it alright if we leave our materials

17   here overnight?

18             COMMISSIONER CARTER:  Yes, we will secure the room.

19   They will secure the room, not we.

20             (The hearing adjourned at 4:50 p.m.)

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

306

1   STATE OF FLORIDA    )

:              CERTIFICATE OF REPORTER

2   COUNTY OF LEON      )

3

I, JANE FAUROT, RPR, Chief, Hearing Reporter Services

4   Section, FPSC Division of Commission Clerk, do hereby certify

that the foregoing proceeding was heard at the time and place

5   herein stated.

6             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

7   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

8   proceedings.

9             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

10   or employee of any of the parties' attorney or counsel

connected with the action, nor am I financially interested in

11   the action.

12             DATED THIS ______ day of October, 2007.

13

14             ___________________________________________

JANE FAUROT, RPR

15                   Official FPSC Hearings Reporter

(850) 413-6732

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION