307

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

In the Matter of:

3

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070297-EI

4   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

5   TAMPA ELECTRIC COMPANY.

---------------------------------------

6   REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070298-EI

STORM HARDENING PLAN FILED PURSUANT TO

7   RULE 25-6.0342, F.A.C., SUBMITTED BY

PROGRESS ENERGY FLORIDA, INC.

8   ----------------------------------------

REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070299-EI

9   STORM HARDENING PLAN FILED PURSUANT TO

RULE 25-6.0342, F.A.C., SUBMITTED BY

10   GULF POWER COMPANY.

---------------------------------------

11   REVIEW OF 2007 ELECTRIC INFRASTRUCTURE    DOCKET NO. 070301-EI

STORM HARDENING PLAN FILED PURSUANT TO

12   RULE 25-6.0342, F.A.C., SUBMITTED BY

FLORIDA POWER & LIGHT COMPANY.

13   ________________________________________/

14

15

16

ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

17                 A CONVENIENCE COPY ONLY AND ARE NOT

THE OFFICIAL TRANSCRIPT OF THE HEARING,

18            THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

19

20                              VOLUME 3

21                        Pages 307 through 489

22

23   PROCEEDINGS:        HEARING

24

25

FLORIDA PUBLIC SERVICE COMMISSION

308

1   BEFORE:             CHAIRMAN LISA POLAK EDGAR

COMMISSIONER MATTHEW M. CARTER, II

2                       COMMISSIONER KATRINA J. McMURRIAN

COMMISSIONER NANCY ARGENZIANO

3                       COMMISSIONER NATHAN A. SKOP

4   DATE:               Wednesday, October 3, 2007

5   TIME:               Commenced at 9:48 a.m.

6   PLACE:              Betty Easley Conference Center

Room 148

7                       4075 Esplanade Way

Tallahassee, Florida

8

REPORTED BY:        LINDA BOLES, RPR, CRR

9                       Official FPSC Reporter

(850) 413-6734

10

APPEARANCES:        (As heretofore noted.)

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

309

1                              I N D E X

2                              WITNESSES

3

NAME:                                                PAGE NO.

4

5   MICHAEL T. HARRELSON

6

Prefiled Direct Testimony Inserted (070298)     315

7        Direct Examination by Mr. Seiver                346

Prefiled Direct Testimony Inserted (070301)     349

8        Cross Examination by Mr. Butler                 399

Cross Examination by Mr. Wright                 417

9        Redirect Examination by Mr. Seiver              421

10

11   PETER J. RANT

12        Direct Examination by Mr. Wright                427

Prefiled Direct Testimony Inserted              430

13

14   R. L. WILLOUGHBY

15        Direct Examination by Mr. Wright                461

Prefiled Direct Testimony Inserted              463

16

17

18

19   CERTIFICATE OF REPORTER                              489

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

310

1                              EXHIBITS

2   NUMBER:                                        ID.    ADMTD.

3   34   PJR-1                                     455     460

4   35   PJR-2                                     455     460

5   36   PJR-3                                     455     460

6   37   RLW-1                                     474     486

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

311

1                         P R O C E E D I N G S

2             (Transcript continues in sequence from Volume 2.)

3             CHAIRMAN EDGAR:  Good morning.  Call the hearing to

4   order this morning.  Thank you all.  Thank you to Commissioner

5   Carter for standing in for me yesterday.  And Commissioner

6   Argenziano is not able to join us this morning.  She may be

7   joining us later today.

8             And I understand that we may have some preliminary

9   matters to address before we go back to testimony from the

10   current witness.

11             MR. WILLIS:  That's correct.  Madam Chairman, we

12   would request that we suspend the cross-examination of Tampa

13   Electric at this juncture and move to other cross-examination

14   of this witness in hopes that we will be able to avoid further

15   cross-examination altogether as we, we're continuing to try to

16   reach an agreement.  So that would be helpful, if that's okay

17   with you.

18             CHAIRMAN EDGAR:  Okay.  So my understanding is that

19   the request from TECO is that we stop the questioning from TECO

20   to FCTA Witness Harrelson at this point in time, with the

21   understanding that you may want to have the opportunity to

22   resume cross, but we'll see how that goes?

23             MR. WILLIS:  Correct.

24             CHAIRMAN EDGAR:  Okay.  Are there, are there

25   questions on cross in this docket from any of the other

FLORIDA PUBLIC SERVICE COMMISSION

312

1   parties?  I'm seeing no, no.  And no questions from staff?

2             MS. FLEMING:  No questions.

3             CHAIRMAN EDGAR:  Commissioners, any questions for

4   this witness on this docket?  And I'm seeing none.

5             Then, Mr. Willis, that sounds like a reasonable

6   request to me.

7             Ms. Fleming.

8             MS. FLEMING:  There are a couple of other preliminary

9   matters that we need to address.  It is not clear in the

10   transcript whether Battaglia's direct testimony was moved into

11   the record yesterday, so I would defer to Mr. Badders to

12   address that.

13             CHAIRMAN EDGAR:  Mr. Badders.

14             MR. BADDERS:  Thank you.  I apologize.  It appears I

15   may not have moved his testimony in.  So at this time I would

16   like to move the direct testimony of Ed Battaglia into the

17   record as though read.

18             CHAIRMAN EDGAR:  Okay.  The direct prefiled testimony

19   of Witness Battaglia will be entered into the record as though

20   read.

21             (REPORTER'S NOTE:  For convenience of the record,

22   Witness Battaglia's prefiled direct testimony was entered into

23   the record in Volume 1, Page 85.)

24             MR. BADDERS:  Thank you.

25             CHAIRMAN EDGAR:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

313

1             Ms. Fleming.

2             MS. FLEMING:  On another matter as far as Witness

3   Harrelson regarding the Progress docket, as you know, the

4   Progress docket was stipulated yesterday and the issues were

5   approved by the Commission.  So staff would suggest that

6   Witness Harrelson's testimony with respect to the Progress

7   docket be stipulated if there are no objections and no

8   Commissioners have any questions.

9             CHAIRMAN EDGAR:  Okay.  Commissioners, any questions

10   for Witness Harrelson in the Progress docket?

11             COMMISSIONER CARTER:  No, ma'am.

12             CHAIRMAN EDGAR:  Seeing none.  Ms. Fleming, no

13   questions.

14             MS. FLEMING:  Okay.  Then when we get to that point,

15   I guess it would be right after we start, we can move in

16   Witness Harrelson's prefiled testimony in the Progress docket

17   and then proceed to his testimony in the FPL docket.

18             CHAIRMAN EDGAR:  Okay.  Are there questions on cross

19   for Witness Harrelson in the Progress docket from any of the

20   other parties?  And I'm also seeing no, seeing none.  So --

21             MR. SEIVER:  Thank you, Madam Chair.  At this point

22   we would then switch to the Progress docket, if we could.  And

23   I would like to move into the record based on the stipulations

24   the prefiled direct testimony of Mr. Harrelson in the Progress

25   docket, which is 070298-EI.

FLORIDA PUBLIC SERVICE COMMISSION

314

1             CHAIRMAN EDGAR:  Okay.  The prefiled testimony of

2   Witness Harrelson will be moved into the record for the

3   Progress docket as though read.

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

346

1             MR. SEIVER:  Thank you.  And we will deal with the

2   exhibits to the Progress testimony as to, with all of

3   Mr. Harrelson's exhibits at the conclusion of the

4   cross-examination in the FPL docket, or, if we resume Tampa, at

5   the conclusion of that docket.

6             CHAIRMAN EDGAR:  Yes.  Thank you.

7             MR. SEIVER:  And since we have withdrawn Gulf Power,

8   I believe the next testimony that we have for Mr. Harrelson is

9   in the Florida Power & Light docket.

10             CHAIRMAN EDGAR:  Yes.

11             MR. SEIVER:  Thank you.

12                        MICHAEL T. HARRELSON

13   was recalled as a witness on behalf of Florida Cable

14   Telecommunications Association and, having been duly sworn,

15   testified as follows:

16                         DIRECT EXAMINATION

17   BY MR. SEIVER:

18        Q    And so, Mr. Harrelson, were you here yesterday when

19   the witnesses were sworn?

20        A    Yes, I was.

21        Q    And you are Michael T. Harrelson?

22        A    Yes, I am.

23        Q    And did you submit testimony in the Florida

24   Power & Light docket, 070301, on behalf of the Florida Cable

25   Telecommunications Association?

FLORIDA PUBLIC SERVICE COMMISSION

347

1        A    Yes, I did.

2        Q    And if I were to ask you the questions in that

3   prefiled testimony today, would your answers be the same?

4        A    Yes.

5        Q    Are there any errors -- any changes or corrections to

6   that?

7        A    Not that I'm aware of, unless -- I heard some

8   discussion about a stipulation that might take some pages out.

9   I'm not sure.

10             MR. SEIVER:  I'm sorry.  We had some changes in the

11   exhibit numbers, but we'll deal with that when we move the

12   exhibits in at the end.

13             CHAIRMAN EDGAR:  Okay.

14   BY MR. SEIVER:

15        Q    Mr. Harrelson, would you please give a summary of

16   your testimony?

17             MR. BUTLER:  Excuse me, Madam Chairman.  Before

18   Mr. Harrelson summarizes his testimony, it was my impression

19   that consistent with the stipulation we had on, on Issue

20   51 that FCTA was going to be withdrawing portions of

21   Mr. Harrelson's testimony, and now seems like the right time to

22   do it, if it's going happen.

23             MR. SEIVER:  I apologize.

24             CHAIRMAN EDGAR:  Okay.  Mr. Butler, thank you for

25   bringing that to our attention.  Can you address that for me,

FLORIDA PUBLIC SERVICE COMMISSION

348

1   please?

2             MR. SEIVER:  Thank you, Madam Chair.  And I

3   apologize, Mr. Butler.  I have the note right here and I still

4   didn't see it.

5             Yes.  Madam Chair, to modify our moving the testimony

6   in, we need to withdraw in Mr. Harrelson's prefiled direct

7   testimony Page 36 beginning with Line 3 through Page 45, Line

8   14.

9             MR. BUTLER:  Thank you.

10             CHAIRMAN EDGAR:  Okay.  So am I -- let me make sure I

11   understand, and we'll work together to get where we need to be.

12   So we are going to enter the prefiled direct testimony of this

13   witness, with the exclusion of Page 36, Line 3 through Page 45,

14   Line 14.

15             MR. SEIVER:  Yes, Madam Chair.  That is correct.

16             CHAIRMAN EDGAR:  So noted for the record.

17             MR. SEIVER:  Thank you.

18             CHAIRMAN EDGAR:  Thank you.

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

395

1   BY MR. SEIVER:

2        Q    All right.  Mr. Harrelson, now would you do your

3   summary?  Thank you.

4        A    Thank you.  Good morning, Madam Chairman and

5   Commissioners.

6             FPL's plan will not meet the objectives of enhancing

7   reliability, reducing restoration costs and outage times in a

8   prudent, practical and cost-effective manner because the plan

9   applies extreme wind loading Grade B to distribution poles and

10   lines less than 60 feet high for critical infrastructure

11   circuits, new construction, critical poles, interstate

12   crossings and major rebuild projects, as well as some of the

13   incremental hardening throughout FPL's entire service territory

14   as opposed to applying EWL in only areas where it is likely to

15   have maximum benefits with minimum negative consequences.

16             FPL's plan ignores or at least fails to incorporate

17   the well-documented effects of open areas and areas near the

18   coast versus areas with concentrations of trees that were

19   described in the KEMA report and analysis of FPL's forensic

20   data from Hurricane Katrina and Wilma in 2005.

21             FPL is required by the rule to determine where, when

22   and how to apply EWL criteria for distribution poles and lines

23   in a prudent, practical and cost-effective manner.  The NESC

24   does not require EWL to be applied to such poles and lines less

25   than 60 feet high; therefore, the NESC does not prescribe any

FLORIDA PUBLIC SERVICE COMMISSION

396

1   guidance for such an application.  FPL must decide if it should

2   consider both the sheltering effects which trees and buildings

3   provide for winds and the danger of wind-blown debris and

4   falling limbs in trees associated with placing more poles and

5   more costly poles such as FPL's plan utilizes in its EWL

6   designs and placing those poles near trees and buildings.

7             Where and when the extreme winds hit, some of the

8   tall trees near FPL's new EWL lines are sure to fall on the

9   lines after being blown down by the very wind speed force for

10   which the EWL lines were designed to withstand.  FPL intends to

11   spend almost $300 million on implementing EWL for distribution

12   lines in its three-year plan.  The cost of one EWL concrete

13   pole can exceed the cost of one Grade B type wood pole by

14   $8,000 per pole.

15             FPL estimates it will replace 2,100 Grade B poles in

16   2007 and add 700 new EWL designed poles between existing pole

17   locations to shorten span lengths.  These numbers will likely

18   double in 2008 and 2009.

19             FPL has done a very large volume of good work to

20   develop engineering guidelines for use by field personnel in

21   application of its EWL standards and incremental hardening

22   design plans; however, there are two major deficiencies.  In

23   addition to not considering trees and buildings near the lines,

24   the engineering criteria did not consider the strengthening

25   effects, which are called the guying effects, of angles in the

FLORIDA PUBLIC SERVICE COMMISSION

397

1   power lines which are guyed, junction poles in the power lines

2   where cables and wires cross such as at intersections, and

3   pull-offs from the power line which are supported by guy wires.

4             As a result, many poles which are actually strong

5   enough to withstand extreme wind are still replaced by FPL at

6   great additional cost and disruption to the public because of

7   the cranes, bucket trucks and other equipment that handle the

8   concrete poles, the equipment that is often used.  FPL lists

9   storm guying, which is placing guy wires and anchors on both

10   sides of straight line power poles, as its first preference and

11   tool in its engineering tool kit to accomplish EWL strength for

12   existing poles.  This is an excellent application,

13   cost-effective.  FPL has committed to determine if and how it

14   can include the other guying effects of the other lines and

15   cables I mentioned.  FPL is also investigating ways to include

16   the effects of buildings and trees near lines into its EWL

17   design.  I believe these can and should be accomplished.

18             Finally, I believe that EWL is justified in

19   interstate power line crossings in Florida.  The NESC requires

20   Grade B, and that's because of the critical importance of the

21   hurricane evacuation and recovery operations for these

22   interstate highways.  Pilot projects for EWL design with

23   instrumentation for good future forensic information gathering

24   and the aggressive application of storm guying because it is so

25   effective and cost-effective are all prudent, practical and

FLORIDA PUBLIC SERVICE COMMISSION

398

1   cost-effective.  However, such a grand scale of implementing

2   extreme wind for distribution poles as is in FPL's plan is, in

3   my opinion, not prudent, practical and cost-effective.  Thank

4   you.

5             CHAIRMAN EDGAR:  Thank you.

6             MR. SEIVER:  Thank you.  If I neglected to move his

7   testimony as modified into the record, I would like to do that

8   at this time.

9             CHAIRMAN EDGAR:  I believe we did, but we will note

10   that for the record to make sure that the prefiled direct

11   testimony with the previously noted lines stricken will be

12   entered into the record as though read.

13             MR. SEIVER:  Thank you, Madam Chair, and I tender the

14   witness for cross-examination.

15             CHAIRMAN EDGAR:  Thank you.

16             Mr. Butler.

17             MR. BUTLER:  Thank you, Madam Chairman.  At the

18   outset, let me note that staff has identified and all of us

19   have stipulated to the introduction of Mr. Harrelson's

20   deposition transcript as part of the evidence in this

21   proceeding, and there are quite a few questions in there.  I

22   commend that to your reading pleasure.  But I'm going to try to

23   keep my cross-examination brief and focused because I won't be

24   rehashing all of the ground that is covered in the deposition

25   transcript.

FLORIDA PUBLIC SERVICE COMMISSION

399

1                          CROSS EXAMINATION

2   BY MR. BUTLER:

3        Q    Mr. Harrelson, good morning.

4        A    Good morning.

5        Q    Have you ever been qualified or have you ever

6   testified as an expert on wind loading issues?

7        A    No, I don't believe I have.

8             (REPORTER'S NOTE:  Commissioner Argenziano entered

9   hearing room.)

10        Q    Is it also true that you have never been qualified

11   and have never testified as an expert on storm hardening

12   issues?

13        A    No, I have not.

14        Q    Is it true that you've never been qualified or

15   testified as an expert on forensic analysis of storm damage to

16   a pole network?

17        A    That's correct.

18        Q    And just to clarify, before this proceeding have you

19   ever testified on the subject of the appropriate way to storm

20   harden electric distribution systems?

21        A    Storm hardening beyond requirements of the National

22   Electric Safety Code I have not.  To my knowledge this is the

23   first time this has come up is in Florida.

24        Q    Have you ever conducted any formal forensic analyses

25   of storm damage to electric utility distribution systems of the

FLORIDA PUBLIC SERVICE COMMISSION

400

1   sort that FPL performed in the 2005 storm season?

2             MR. SEIVER:  I'll just object to that question on

3   what the term "formal forensic analysis" means.  If it's clear

4   to the witness, that's fine.  But I believe that "formal" is a

5   vague term.

6             MR. BUTLER:  I will withdraw the word "formal" from

7   the question.

8   BY MR. BUTLER:

9        Q    Do you recall the question or do I need to restate

10   it?

11             CHAIRMAN EDGAR:  Actually I would request that you

12   restate the question.  Thank you.

13   BY MR. BUTLER:

14        Q    Have you ever performed forensic analysis of

15   storm-related damage to electric distribution system facilities

16   of the sort that FPL performed during the 2005 storm season?

17        A    Not in exactly the same manner.  I do have two years

18   of experience with hurricanes in South Florida in 2004 and '05,

19   and I took a lot of photographs and made some observations, but

20   I did not present a written report or do a formal analysis.  I

21   also have a week or ten days experience in South Carolina with

22   Hurricane Hugo.

23        Q    But I believe you agreed in your deposition that this

24   was kind of an after-the-fact forensic evaluation of what you

25   saw as opposed to a system that was in place in advance to sort

FLORIDA PUBLIC SERVICE COMMISSION

401

1   of gather data specifically with respect to the cause of storm

2   damage?

3             MR. SEIVER:  I want to object to that.  It's assuming

4   some facts that I'm not sure are in evidence, but.

5             THE WITNESS:  Yes, sir.  I don't recall exactly what

6   I said.  But if I could restate my experience, I did the

7   evaluation informally with photographs as it occurred, as I

8   worked in the field.  Then there was a review, but it was also

9   not extensively documented.  It was discussed after the fact.

10   BY MR. BUTLER:

11        Q    Do you know of any entity other than FPL that has

12   conducted the sort of forensic analysis of storm damage to

13   electric distribution systems in Florida that FPL conducted

14   following or during the 2005 storm season?

15        A    No, sir, I don't.

16        Q    Okay.  Mr. Harrelson, is it true that FPL met with

17   third-party attachers in April of 2007 to explain the Storm

18   Hardening Plan that it was intending to file?

19        A    Yes.  And I believe I attended that meeting.

20        Q    That was going to be my next question.  Did you

21   attend it?

22        A    Yes.

23        Q    Okay.  Did you ask questions during that meeting of

24   FPL?

25        A    I did.  Yes.  Yes, sir, I did.

FLORIDA PUBLIC SERVICE COMMISSION

402

1        Q    Okay.  And did FPL respond to your questions?

2        A    They did.  At first the response was they had

3   considered my concerns about the additional strength and guying

4   effects of junction poles and angle poles and that they had

5   determined that it was better to go ahead and put stronger

6   poles in at that point in time.

7        Q    But I think, as you described in your summary, over

8   time FPL has had further discussions with you and has agreed to

9   consider more formally those guying effects; is that correct?

10        A    Yes, that's correct.  I confirmed that in some

11   rebuttal testimony.  That's correct.

12        Q    Okay.  And is it also the case that FPL met

13   specifically with the FCTA in August to further explain its

14   Storm Hardening Plan?

15        A    Yes.

16        Q    And did you attend that meeting?

17        A    I don't remember the dates, but I attended more than

18   one meeting.  I'm almost certain that I did attend that

19   particular meeting.

20        Q    Okay.  And did you ask questions of FPL at that time?

21        A    That's correct.  Yes.  That was a telephone and in

22   person meeting, and I was in person and some others were on

23   there by phone.

24        Q    Okay.  Has the FCTA received detailed engineering

25   drawings for FPL's 2007 storm hardening projects?

FLORIDA PUBLIC SERVICE COMMISSION

403

1        A    Yes.

2        Q    Have you reviewed those?

3        A    I have reviewed certain of those, and I've also

4   reviewed, in not great detail but in some detail, two of the

5   actual construction projects.

6        Q    Okay.  Has FPL accommodated any requests that you've

7   made to participate in such meetings on the actual details of

8   the projects?

9        A    Not entirely, but I think within reason, yes.

10        Q    Okay.  Has the, has the FCTA also received CDs of

11   FPL's route maps for the 2008/2009 projects?

12        A    Yes, I'm sure we have.  I was trying to remember any

13   of the details.  But there are, as you described, route maps

14   which basically show the one line diagram, no poles in

15   particular, but the street backgrounds in the one line diagrams

16   where the circuits affected are located.

17        Q    Do you have any reason to believe that FPL has not

18   provided FCTA information on its hardening projects as that

19   information has become available?

20        A    No, I do not.

21        Q    Do you believe that the process to engage third-party

22   attachers which the Commission has approved provides a useful

23   mechanism for dialogue between electric utilities and

24   third-party attachers about the future projects?

25        A    Yes, I believe that would be useful.

FLORIDA PUBLIC SERVICE COMMISSION

404

1        Q    Uh-huh.  And do you believe that FPL has dealt with

2   the FCTA in good faith regarding the coordination of

3   third-party attachments to its hardening projects?

4        A    Yes, I do.  The only thing I would like to add, it's

5   been a little slower than I had hoped, but I think I

6   understand.

7        Q    Thank you.  Mr. Harrelson, at your deposition you

8   described some, I guess inspection may not be the proper word,

9   but some visits you made or some observations you made of

10   damage that was caused by Hurricane Charley.  Do you remember

11   that?

12        A    Yes.

13        Q    Okay.  And am I correct that you observed damage from

14   Hurricane Charley in, I think it was Arcadia and Lake Wales; is

15   that right?

16        A    I know I did.  Whatever the towns on Highway 27,

17   U.S. Highway 27.  I believe that's Lake Wales.  Sometimes I

18   don't remember the names exactly right.  But it was as I

19   returned northward on Highway, U.S. 27 immediately after

20   Hurricane Charley went through or shortly after Hurricane

21   Charley went through.

22        Q    And is it your understanding that Hurricane Charley

23   entered Florida on the southwest coast and then headed sort of

24   northeast or east/northeast across the state?

25        A    That's correct.  Landfall was at Punta Gorda.

FLORIDA PUBLIC SERVICE COMMISSION

405

1        Q    So it would have hit the coast and then traveled

2   inland before it did the damage you observed at Arcadia and

3   Lake Wales; is that correct?

4        A    That's correct.

5        Q    Okay.  And I think you agreed at your deposition that

6   Arcadia is something more than 25 miles inland; is that right?

7        A    I believe that's correct.  It would be easy to

8   verify.

9        Q    And I think you also agreed that Lake Wales is

10   something more than 50 miles inland; is that right?

11        A    Yes.

12        Q    Okay.  Is it your understanding that FPL's Storm

13   Hardening Plan has three separate wind zones that have

14   different wind speeds to which the EWL hardening is designed in

15   each respective zone?

16        A    Yes, it does.  And additionally I think that's very

17   reasonable.

18        Q    Okay.  And do you happen to recall what the three

19   wind speeds for those zones are?

20        A    I believe it's 145, 130 and 105.

21        Q    Okay.  And would you agree that the wind speed, I

22   mean, or the wind force to which poles would have to be

23   designed in the 145-mile-per-hour zone is approximately twice

24   as strong as the wind force in the 105-mile-per-hour zone?

25        A    It is as required by the National Electrical Safety

FLORIDA PUBLIC SERVICE COMMISSION

406

1   Code for poles and attachments greater than 60 feet in height.

2   So in general the answer is yes, but the code applies it to

3   60 feet and greater.

4        Q    Okay.  Now do you recall from FPL's wind zones, are

5   the, the areas that are within the 145-mile-per-hour zone

6   predominantly on the east and sort of lower southwestern

7   coastal areas of Florida?

8        A    That's correct.

9        Q    Okay.  And the area of the 105-mile-per-hour wind

10   zone is pretty much in the north central part of FPL's service

11   territory?

12        A    Yes.

13        Q    So the design of FPL's poles for EWL hardening

14   purposes in this north central inland area would only have to

15   withstand approximately half as much wind force as the poles

16   designed for the coastal areas that are in the

17   145-mile-per-hour wind zone; correct?

18        A    Yes, I think that's correct.  And I know it's also

19   been stated that Grade B is equivalent to different wind speeds

20   by different people testifying, but roughly equivalent to

21   105 miles per hour or greater.  So it's a puzzle why Grade B

22   poles are changed out in places like Lake City where the

23   applicable wind speed is 105.

24        Q    During your observations of hurricane damage in the

25   2004 and 2005 hurricane season, I believe you've testified at

FLORIDA PUBLIC SERVICE COMMISSION

407

1   your deposition that you saw instances of cascading pole

2   failures; is that right?

3        A    Yes.  Many of them.

4        Q    Okay.  And is it true that you saw some instances of

5   cascading poles that it appeared those events were initiated by

6   wind only, that there wasn't any evidence of debris or trees

7   falling on the pole to initiate the cascade?

8        A    That's correct.  I'm sure I saw some instances of

9   that.  And I did certainly see some instances that were also

10   initiated by deteriorated poles.  I saw other instances were

11   definitely initiated by either broken or weakened guy wires

12   that pulled up and started the cascading event.  And then

13   another issue that I observed is very important:  The poles

14   that the cascading event stopped on was usually one of the

15   guyed poles, angle poles or junction poles where there was

16   additional strength to that particular pole by these other

17   effects that FPL is now considering.

18        Q    You anticipated my next question, but let me just

19   clarify.

20             Is it your understanding that FPL's storm hardening

21   design guidelines include the use of storm guys for, among

22   other purposes, to shore up poles along line -- pole lines

23   along -- along long pole lines to try to minimize the potential

24   for cascading?

25        A    I think I'm beginning to understand that better.  I

FLORIDA PUBLIC SERVICE COMMISSION

408

1   don't think it was stressed in the plan so that I understood it

2   from my first reading of the plan, but I agree.

3        Q    I'd like you to turn, please, to Page 34 and 35 of

4   your testimony.

5        A    What's that stamp number on the page?

6        Q    I'm sorry?

7        A    Could you tell me the stamp, Bate stamp number?

8        Q    I don't know that it has a Bate stamp number.

9        A    Okay.  I can find it.  I can find it.

10        Q    It's your prefiled testimony Page 34.  It says 34 at

11   the bottom of it.

12        A    What line?

13        Q    I'm sorry?

14        A    What line on 34?

15        Q    Well, I'm getting there.  I just -- right now just

16   get to Page 34.  Do you have it in front of you?

17        A    I think I do.

18             MR. SEIVER:  Mr. Harrelson, it's your testimony, not

19   the deposition.

20             THE WITNESS:  I think I don't.

21   BY MR. BUTLER:

22        Q    This should start with the words "With Grade B

23   standards" at the very top of the page.

24        A    It does.  Thank you.

25        Q    You have a list of what you consider to be prudent,

FLORIDA PUBLIC SERVICE COMMISSION

409

1   practical and cost-effective measures to storm hardened systems

2   that starts on Line 13 of Page 34.  Do you see that?

3        A    I do.  Yes.

4        Q    Okay.  The first item here is small conductor

5   replacement projects.  Do you see that?

6        A    I do.

7        Q    Okay.  Do you know whether FPL is conducting small --

8   an unfortunate choice of words -- is implementing small

9   conductor replacement as part of its Storm Hardening Plan?

10        A    I believe I do now.  I know I've been informed of

11   that recently.  I do not think it was pointed out as part of

12   their plan.

13        Q    Do you know whether FPL -- excuse me.  Do you know

14   whether FPL is attempting to implement right-of-way access

15   improvement projects where it has secured the right to do so,

16   the legal right to do so?

17        A    I don't, I don't know any details.  I would think

18   that they could if they chose to increase emphasis on that,

19   whatever they're doing.  But I'm just saying in general those

20   are very effective practices and I don't know what FPL is

21   actually doing.

22        Q    From reviewing the rebuttal testimony of FPL's

23   witnesses, do you know whether FPL is using specialized

24   equipment and contractors for work in difficult right-of-way

25   conditions, off-road or swampy areas?

FLORIDA PUBLIC SERVICE COMMISSION

410

1        A    Yes, I do now, and I believe it's part of their

2   recovery plan.

3        Q    Turning to Page 35, continuing the list of bullet

4   items, the next item is pole inspection.  Do you know whether

5   FPL has a sort of expanded or more aggressive pole inspection

6   program as part of its overall hardening initiatives?

7        A    I do observe from the reliability report that they're

8   spending a very large increase on pole inspections and

9   remediation.  I'm not certain the details of their inspection,

10   incorporation of inspections of the associated guy wires.  If

11   not, I think that's something they should consider.

12        Q    Okay.  Your next bullet refers to installation of

13   storm guying, and I think we discussed this earlier.  Is it

14   true that your, your understanding is FPL's design guidelines

15   for its storm hardening incorporates the use of storm guying?

16        A    Yes, it does.  I was, I think, trying to point out

17   that I did not see, or alluding to the fact that I did not see

18   it in the plan that they had identified special particular

19   storm guying projects for existing lines in places such as

20   swampy areas, soft soil, agricultural areas where the storm

21   guying alone could be very effective in incremental hardening.

22        Q    Your next two bullets deal with the subject of

23   sectionalizing the electric system so it's possible basically

24   to restore a portion of it while other portions are still

25   damaged; is that correct?

FLORIDA PUBLIC SERVICE COMMISSION

411

1        A    Yes.  And, in fact, part of what FPL had included in

2   its interstate highway crossing strategy reminded me that

3   that's a very effective practice.  So I knew they were doing it

4   on their interstate highway crossing application.  I just

5   didn't see it in the plan about a wider application.

6        Q    Okay.  But based on FPL's rebuttal testimony, is it

7   your understanding that FPL is actively pursuing the use of

8   sectionalization where appropriate?

9        A    Well, I know they're pursuing it, and I suppose where

10   appropriate would be a matter of priorities and budgeting and

11   engineering discretion.

12        Q    But there is -- I agree that one can always debate

13   how much is appropriate.  But you would agree that FPL is

14   actively pursuing that topic?

15        A    Yes.  Yes, I do.

16        Q    Okay.  The next item is bullet point starting on Line

17   15 about increasing distribution system voltage from 12 or 13

18   kV up to 25 kV.  Do you see that?

19        A    Yes.

20        Q    And do you recall from your deposition our discussion

21   of this topic?  And I think I could characterize your answer

22   accurately as saying that you thought this is something that

23   would be applicable in sort of long-run lines in rural areas

24   where there's a real opportunity to increase the power carrying

25   capability of that line?

FLORIDA PUBLIC SERVICE COMMISSION

412

1        A    Yes.  That was one example.  That's correct.  And I

2   read as well I think in some rebuttal testimony that certain

3   parts of Florida Power & Light's distribution system is, in

4   fact, operating at 25 kV rather than 13 or 12.

5        Q    Would you agree that most of FPL's service territory

6   is not in the sort of rural conditions where this particular

7   measure would be applicable?

8        A    Right.  That's, that's the example I gave.  But I do

9   believe that it's in the testimony that the open areas that

10   were affected first by Hurricane Wilma were 25 kV circuits or

11   at least part of them were.

12        Q    Okay.  And the last bullet point is about improved

13   procedures to avoid cutting of fiber-optic cables by debris

14   clearing and electric repair crews.  Do you see that?

15        A    Yes.

16        Q    And are you aware of instances where FPL's storm

17   restoration activities resulted in cutting or otherwise

18   damaging fiber-optic cables of FCTA members in a way that you

19   feel could have been avoided?

20        A    No, I'm not specifically, not with FPL and, and not

21   specifically with anyone.  But I have heard discussions of the

22   fact that immediately after some of these severe storms they

23   have a technique of checking their fiber-optic cables with a

24   light and it's functional, and then in pursuing days unknown

25   parties clearing roadways, clearing debris and in some cases

FLORIDA PUBLIC SERVICE COMMISSION

413

1   with bolt cutters cut those fiber-optic cables, perhaps not

2   knowing the consequences or the cost to repair.  So it's an

3   issue that I think has great potential for our working

4   together.  I didn't mean to imply that FPL was negligent in

5   that.

6        Q    Thank you.  One final topic I wanted to cover with

7   you, Mr. Harrelson.  Would you turn to your Exhibit MTH-4?

8        A    I'm there, and it's a poor copy.  Let me get a

9   different book.

10             MS. FLEMING:  If I may interject.

11             CHAIRMAN EDGAR:  You may, because I think I have the

12   same question.

13             MS. FLEMING:  I believe Mr. Harrelson's exhibits have

14   been renumbered because there were duplicate exhibits in

15   different dockets, and I believe FCTA had an errata sheet of

16   those exhibits.  So, John, if you could be specific as to

17   which -- if you're discussing --

18             MR. BUTLER:  It's the Slavin affidavit, and if that's

19   been renumbered --

20             THE WITNESS:  Slavin.  Okay.

21             MS. FLEMING:  That would be MTH-2.

22             MR. BUTLER:  It's 2 now?

23             MS. FLEMING:  Yes.

24             THE WITNESS:  In my copy.  I'm there.

25             CHAIRMAN EDGAR:  So, Mr. Butler, you were attempting

FLORIDA PUBLIC SERVICE COMMISSION

414

1   to draw our attention to the, what's labeled "Affidavit of Dr.

2   Lawrence Slavin"?

3             MR. BUTLER:  That's correct.  One thing I would

4   observe is that the package I have, unless they've been

5   withdrawn, there is an MTH-2 and an MTH-3.  They were pictures

6   of power facilities.  Are those now no longer exhibits?

7             THE WITNESS:  They're exhibits but the number is

8   different, I think.

9             MS. FLEMING:  If I may interject.  As we stated

10   previously, an errata sheet, I believe, was provided to all

11   parties by FCTA, as well as to all the Commissioners.

12   Mr. Harrelson provided testimony, four separate sets of

13   testimony in four dockets.  The exhibits were duplicative.  So

14   in order to enter only one exhibit in each docket, we

15   consolidated the exhibits and renumbered the exhibits so that

16   it would flow better for purposes of the hearing.  The correct

17   identification of the exhibits is entailed in staff's

18   Comprehensive Exhibit List.  So to the extent that it's

19   possible, if parties can refer to the exhibit as it's

20   designated on the Comprehensive Exhibit List, that would be

21   helpful.

22             CHAIRMAN EDGAR:  Okay.  And there again, we'll work,

23   work through it together.

24             MR. BUTLER:  Yeah.  Okay.  Then MTH-2 is what I'm

25   referring to apparently.  That's the affidavit of Dr. Slavin;

FLORIDA PUBLIC SERVICE COMMISSION

415

1   correct?

2             MS. FLEMING:  Yes.  That's correct.

3             CHAIRMAN EDGAR:  It is.  And that is, just for

4   purposes of the record, labeled as Number 29 on the list.

5             MR. BUTLER:  Thank you.

6   BY MR. BUTLER:

7        Q    Mr. Harrelson, what is the date of the affidavit of

8   Dr. Slavin that you've attached to your testimony?

9        A    Can you help me find it?

10        Q    Yes.  I'm referring to the filing date.  It's up in

11   the style of the document above the title "Filed August 11,

12   2006."  Do you see that?

13        A    August 11th, 2006.

14        Q    Yes.  Okay.  Would you agree that that date is well

15   before FPL filed its Storm Hardening Plan in May 2007?

16        A    Yes.

17        Q    Okay.  In fact, would you agree that Dr. Slavin's

18   affidavit that you've attached to your testimony is actually

19   directed at a rule proposal that was current at that time that

20   would have required each utility to adopt, to the extent

21   cost-effective, EWL hardening within its system?

22        A    It was a rulemaking process.  I'm not sure I could

23   even understand it completely.  But would you restate?

24        Q    Well, let me go with what you just said.  Do you know

25   what the, the nature of the rulemaking process was for which

FLORIDA PUBLIC SERVICE COMMISSION

416

1   Mr. Slavin or Dr. Slavin's affidavit was originally submitted?

2        A    It was my understanding that the Commission and staff

3   was developing a rule to address the reliability and resilience

4   of the electric distribution system in Florida during extreme

5   weather events.

6        Q    But you don't know the specifics of the rule to which

7   Dr. Slavin's affidavit was addressed, the rule proposal?

8        A    The proposed rule?

9        Q    Right.

10        A    I have copies of it but I can't quote it to you now.

11   I was here when he made that presentation.

12        Q    Do you know whether the rule was adopted as, as it

13   was proposed, you know, at the time that Dr. Slavin filed this

14   affidavit?

15        A    It was not.

16        Q    Okay.  What role did you play in preparing

17   Dr. Slavin's affidavit?

18        A    None.

19        Q    Are you personally a member of any NESC committee or

20   subcommittee?

21        A    No, I'm not.

22             MR. BUTLER:  Okay.  Thank you, Mr. Harrelson.  That's

23   all the questions that I have.

24             CHAIRMAN EDGAR:  Mr. Wright.

25             MR. WRIGHT:  Thank you, Madam Chairman.  I have

FLORIDA PUBLIC SERVICE COMMISSION

417

1   limited cross-examination for Mr. Harrelson.

2             CHAIRMAN EDGAR:  Okay.

3                          CROSS EXAMINATION

4   BY MR. WRIGHT:

5        Q    Good morning, Mr. Harrelson.

6        A    Good morning.

7        Q    Are you capable of testifying only about cable

8   telecommunication -- cable television facilities, or if I were

9   to ask you a question that says cable and telephone or cable

10   and telecommunications facilities, would that throw you off?

11        A    I'd have to hear the question, but I do have some

12   experience in both those areas.

13        Q    Thank you.  As a preliminary matter, are you familiar

14   with FPL's Storm Secure Plan?

15        A    Only I'm aware of it that it was approved for early

16   2006.

17        Q    Okay.  As a general matter, will you agree that

18   telecommunications and cable television facilities that are

19   installed underground are less vulnerable to direct wind damage

20   than overhead facilities?

21             MR. BUTLER:  I'm going to object to this question as

22   not relating to Mr. Harrelson's direct testimony.

23             MR. WRIGHT:  He testifies about FPL's plan.  FPL's

24   plan includes undergrounding.  I want to ask him about it.

25             MR. BUTLER:  Well, he testifies about particular

FLORIDA PUBLIC SERVICE COMMISSION

418

1   things.  He objects to the particular way that we're going to

2   apply extreme wind loading to our overhead system.  I don't

3   think there is a single reference to under -- to FPL's plan as

4   it relates to underground facilities, and so I really think

5   this goes beyond the scope of Mr. Harrelson's direct testimony.

6             MR. WRIGHT:  I'll move on.

7   BY MR. WRIGHT:

8        Q    Mr. Harrelson, do I understand your testimony

9   correctly in that it criticizes FPL's plan for adopting extreme

10   wind loading criteria?

11        A    Certain aspects of FPL's adoption and implementation

12   of extreme wind loading criteria I do disagree with.

13        Q    Well, for example, at Page 9 of your testimony you

14   testify that the Commission should not find that FPL's plan

15   meets the desired objectives of enhancing reliability and

16   reducing restoration costs and outage times.  Are you familiar

17   with that part of your testimony?

18        A    That's correct.  Yes.

19        Q    And again at Page 12 you testify that the company's

20   plan does not meet the desired objectives of enhancing

21   reliability and reducing restoration costs and outage times in

22   a prudent, practical and cost-effective manner.  Are you

23   familiar with that part of your testimony?

24        A    Yes, I am.  That's correct.  And my intention there

25   is to state that the entire plan as it's stated should not be

FLORIDA PUBLIC SERVICE COMMISSION

419

1   approved.

2        Q    And my question for you is have you performed any

3   cost-effectiveness or benefit cost analysis of FPL's plan as

4   it -- of FPL's plan?

5        A    Nothing I would characterize as a cost analysis, no.

6   But I'm not an economist either.

7        Q    Well, and nothing coming within the scope of a

8   benefit cost or cost-effectiveness analysis as you understand

9   those terms; correct?

10        A    Correct.

11        Q    Thank you.  At Page 31 of your testimony,

12   Mr. Harrelson, you make this statement.  "From the information

13   I have seen thus far, I do not see a corresponding benefit to

14   third-party attachers resulting from the majority of these

15   storm hardening activities."  Are you familiar with that part

16   of your testimony?

17        A    Yes.

18        Q    Okay.  Now my question for you is -- well, a couple

19   of preliminary questions.

20             Have you made any study of storm restoration cost

21   savings that might be realized through FPL's storm hardening

22   activities as set forth in its plan with regard to cable

23   television or telecommunications facilities?

24        A    No.

25        Q    Have you made any study of any other benefits; for

FLORIDA PUBLIC SERVICE COMMISSION

420

1   example, reduced lost revenues as a possible benefit from storm

2   hardening as set forth in FPL's plan?

3        A    No studies, no.

4        Q    Okay.  So would it be a fair characterization of your

5   testimony that you testify FPL hasn't demonstrated

6   cost-effectiveness to your satisfaction, but you haven't done

7   any analysis of cost-effectiveness either?

8        A    I'm sorry.  I might not have been paying attention.

9   I didn't follow you.

10        Q    I'm sorry.  That was a little longer than I try to

11   make my questions.

12             You testified you don't believe that FPL's Storm

13   Hardening Plan is cost-effective.

14        A    That's correct.

15        Q    Okay.  But you haven't done any analysis to show

16   whether it is or not; correct?

17        A    I would not characterize my observations based on my

18   experience and based on a review of their plan as an analysis.

19   It is my professional opinion.

20        Q    But you haven't made, you haven't made any estimate

21   of the benefits to cable telecommunications providers or cable

22   television providers or telecommunications service providers

23   from storm hardening as per FPL's plan, have you?

24        A    It's my opinion -- the answer is no.  And it's my

25   opinion that there's not sufficient information to do a

FLORIDA PUBLIC SERVICE COMMISSION

421

1   detailed analysis.  And I'm not certain I'd be the best person

2   to do an economic analysis, but it is my opinion that there's

3   not enough information there to make that analysis.

4             MR. WRIGHT:  Thank you.  That's all I have.

5             CHAIRMAN EDGAR:  Thank you.  Are there questions on

6   cross from any of the other parties?  I'm seeing the answer as

7   no.  Are there questions, are there questions from staff?

8             MR. TEITZMAN:  Staff has no questions for the

9   witness.

10             CHAIRMAN EDGAR:  Okay.  Thank you.  Are there

11   questions on redirect?

12             MR. SEIVER:  Just a few, Madam Chair.  Thank you.

13             CHAIRMAN EDGAR:  Okay.

14                        REDIRECT EXAMINATION

15   BY MR. SEIVER:

16        Q    Mr. Harrelson, you might recall that Mr. Butler had

17   asked you about the 2007 engineering and the projects.  Do you

18   recall that line of questioning?

19        A    Yes, I do.

20        Q    And I think you said you had actually looked at, you

21   had looked at two actual construction projects?

22        A    I have.  Yes.

23        Q    And which two are those?

24        A    It was one in Lake City to upgrade the circuits to

25   the Veterans Memorial Hospital in Lake City to EWL, and I

FLORIDA PUBLIC SERVICE COMMISSION

422

1   believe it also included the Shands Hospital on the north side

2   of town and a large sewage plant on the south side of the

3   veterans hospital.  So there were actually three perhaps

4   critical infrastructures involved in that upgrade.  I looked at

5   that and took photographs and also put together a PowerPoint

6   presentation of my observations of that partially completed

7   project.  FPL had completed its pole work.  The cable,

8   telephone and TV and whatever other third-party attachments had

9   not yet been transferred.

10        Q    And had you come to any conclusions about that

11   project after viewing it?

12        A    There were a number of concrete poles installed in

13   Lake City, there was a large number of poles that had

14   strengthening guying effects that I believe could have been

15   taken into consideration and in a few instances were taken into

16   consideration, and there was a lot of poles changed out.  Lake

17   City, of course, has a lot of tall pine trees similar to

18   Tallahassee, a lot of large oak trees, and I believe that if a

19   105-mile-an-hour wind comes through Lake City, a lot of that

20   work there will be torn down by those large trees falling into

21   those lines.

22        Q    Mr. Harrelson, did you include photographs and a

23   discussion of what you saw at Lake City in your testimony?

24        A    I do.  I have two photographs.

25        Q    And did you look at another project?  Did you say

FLORIDA PUBLIC SERVICE COMMISSION

423

1   there was a second project?

2        A    Yes.  When I was traveling to the meeting in Miami, I

3   stopped at a project in Fort Myers.  It was an EWL upgrade of

4   the circuit to, I believe, the Lee County Memorial or -- I

5   don't recall exactly the name of the hospital, but it was in

6   Fort Myers.  And I observed and photographed a very large

7   number of concrete poles that had been installed on that job;

8   some concrete poles replacing other concrete poles which were

9   not designed to the strength level that was, was used to

10   replace them.

11        Q    And did you come to any conclusions about that

12   project after you viewed it?

13             MR. BUTLER:  I'm going to object to this line of

14   questioning.  I don't think that it's redirect of anything I

15   asked about.  My question to Mr. Harrelson was really

16   confirming that he had received and had an opportunity to look

17   at data, you know, going to the subject of the cooperation, the

18   degree of exchange of information between FPL and the cable

19   industry.  This is not addressing that subject at all.  It's

20   just using it as a pretext to get Mr. Harrelson into the

21   subject of opining about specific facilities that he reviewed.

22             MR. SEIVER:  I'll withdraw the question and

23   substitute another.

24   BY MR. SEIVER:

25        Q    Mr. Harrelson, did you discuss the Lee County/Fort

FLORIDA PUBLIC SERVICE COMMISSION

424

1   Myers project in your testimony?

2        A    To some extent I did, yes.

3             MR. SEIVER:  That's all I have.  Madam Chair.  Thank

4   you.

5             CHAIRMAN EDGAR:  Thank you.  Let's take up exhibits.

6             MR. SEIVER:  We were going to -- if we could have

7   indulgence for a moment because we were going to move to TECO.

8             MS. FLEMING:  Madam Chairman, if I may, I would

9   suggest that FCTA identify the errata sheet regarding the

10   exhibits as a hearing ID, please, and I have it as Exhibit

11   Number 52.  I don't know if copies have been handed out to all

12   the parties or the Commissioners.

13             CHAIRMAN EDGAR:  Of the errata sheet?

14             MS. FLEMING:  Of the errata sheet regarding the

15   change of testimony exhibits.

16             CHAIRMAN EDGAR:  Okay.  Commissioners, okay, I

17   believe the errata sheet was passed out here at the bench

18   yesterday.  We did not, at least during the time I was here we

19   did not identify it, and I don't readily see it on the exhibit

20   list in front of me.  So unless I am corrected that we did,

21   we can go ahead and mark that as 52, the errata sheet as

22   Exhibit 52.  And if there are parties that need copies, I'm

23   sure that we can accommodate that.

24             MR. SEIVER:  Thank you, Madam Chair.  Yes, it was not

25   marked, so --

FLORIDA PUBLIC SERVICE COMMISSION

425

1             CHAIRMAN EDGAR:  Okay.  We will label it as 52, and

2   the heading is Errata to the Testimony of Michael T. Harrelson

3   filed October 2nd, 2007.

4             MR. SEIVER:  And I would ask then that we move that

5   into the dockets in which Mr. Harrelson has his direct

6   testimony, which are the Tampa Electric docket, the Gulf Power

7   docket -- I'm sorry, the Progress docket and the Florida Power

8   & Light dockets.

9             CHAIRMAN EDGAR:  I'm sorry.  Could you say that for

10   me one more time?

11             MR. SEIVER:  I would ask that the errata sheet,

12   hearing Exhibit 52, be moved into the record in Docket 070297

13   with regard to Tampa Electric Company, into Docket 070298 with

14   respect to Progress Energy, and Docket 070301 with respect to

15   Florida Power & Light.

16             CHAIRMAN EDGAR:  Okay.  Okay.  I'm with you now.

17   Thank you.

18             (Exhibit 52 marked for identification and admitted

19   into the record.)

20             Mr. Willis, how would you like to proceed with your

21   cross regarding the 297 docket?

22             MR. WILLIS:  What I'd like to do is take a short

23   break so I could confer with FCTA, Madam Chairman.

24             CHAIRMAN EDGAR:  Okay.  Let's --

25             MR. BUTLER:  Madam Chairman, before we take a break,

FLORIDA PUBLIC SERVICE COMMISSION

426

1   did I miss it?  Did FCTA move into the record the exhibits of

2   Mr. Harrelson other than that errata sheet?

3             CHAIRMAN EDGAR:  We have not moved the exhibits yet.

4             MR. BUTLER:  And we're going to do that at the end of

5   all of the cross-examination.

6             CHAIRMAN EDGAR:  We are.  I got a little ahead of

7   myself.  I apologize.  Never forgetting but needing to come

8   back to Mr. Willis and TECO to see how we want to proceed with

9   that.  So, no, we have not yet entered the exhibits and we will

10   take that up collectively.  So let's take -- let's come back at

11   the top of the hour and then we will finish up with this

12   witness.  Thank you.

13             (Recess taken.)

14             Okay.  We are going to go back on the record.  And

15   when -- do you need another moment?

16             MR. WILLIS:  What we would suggest doing is continue

17   to postpone -- I'd asked the witness whether he would rather,

18   which way he would rather do, and I think he'd rather stand

19   down in hopes that we can finalize this agreement.  So with

20   that, I think we should postpone.

21             CHAIRMAN EDGAR:  Okay.  Well, I would -- looking at

22   the time, I would certainly like to forge ahead and continue to

23   conduct as much business as we can go ahead and get done here

24   for the next little while.  So is there any objection or

25   concern from any of the participants if we ask this witness to

FLORIDA PUBLIC SERVICE COMMISSION

427

1   not be excused, to stay in the room, but to basically take a

2   break while we continue and we go on to the next witness?  Is

3   there any concern or objection to that?

4             MR. SEIVER:  None from FCTA.

5             CHAIRMAN EDGAR:  No.  No.  Okay.  Well, then thank

6   you, sir.  And, again, we will be calling you back, so please

7   stay with us through the proceedings, but we will move on to

8   the next witness.

9             THE WITNESS:  Yes.  Thank you.

10             CHAIRMAN EDGAR:  Thank you.

11             And, Mr. Wright, the next witness is your witness.

12             MR. WRIGHT:  Thank you, Madam Chairman.

13             The City of Panama City Beach and the Panama City

14   Beach Community Redevelopment Agency call Mr. Peter J. Rant.

15                            PETER J. RANT

16   was called as a witness on behalf of the City of Panama City

17   Beach and the Panama City Beach Community Redevelopment Agency

18   and, having been duly sworn, testified as follows:

19                         DIRECT EXAMINATION

20   BY MR. WRIGHT:

21        Q    Good morning, Mr. Rant.

22        A    Good morning.

23        Q    Please state your name and address for the record.

24        A    My name is Peter J. Rant.  My address is 1609

25   Heritage Commerce Court, Wake Forest, North Carolina.

FLORIDA PUBLIC SERVICE COMMISSION

428

1        Q    Mr. Rant, you've been present for the entire

2   proceeding since yesterday morning; is that correct?

3        A    Yes, I have.

4        Q    And so you took the oath of witnesses yesterday

5   morning?

6        A    Yes, I did.

7        Q    Thank you.  And are you the same Peter J. Rant who

8   prepared and caused to be filed in this, in this proceeding

9   direct testimony consisting of 24 pages?

10        A    Yes.

11        Q    Do you have any changes or corrections to make to

12   that testimony?

13        A    Yes, I do.  I have one change.  On Page 7, Line 5,

14   after the word "equipment" add a close paren.

15        Q    Thank you.  And if I were to ask you the same

16   questions contained in your prefiled direct testimony today,

17   would your answers be the same?

18        A    Yes, they would.

19        Q    And do you then adopt this testimony as your sworn

20   testimony before the Florida Public Service Commission today?

21        A    Yes, I do.

22             MR. WRIGHT:  Madam Chairman, if there are no

23   objections, I would request that Mr. Rant's testimony be

24   entered into the record as though read.

25             CHAIRMAN EDGAR:  The prefiled testimony will be

FLORIDA PUBLIC SERVICE COMMISSION

429

1   entered into the record as though read, with the correction

2   noted by the witness.

3

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

454

1   BY MR. WRIGHT:

2        Q    Thank you.  And, Mr. Rant, did you also prepare and

3   cause to be filed -- or prepare, compile and cause to be filed

4   in this proceeding three exhibits which are attached to your

5   testimony and identified therein as PJR-1, 2 and 3?

6        A    Yes, I did.

7             MR. WRIGHT:  Madam Chairman, I believe these have

8   been marked for identification as Exhibits 34, 35 and 36 in

9   what is now Exhibit 1.

10             CHAIRMAN EDGAR:  I'm sorry.  Mr. Wright, 34, 35 and

11   36, and I missed that last --

12             MR. WRIGHT:  Yeah.  In Exhibit 1 -- I believe that

13   the exhibit list is now Exhibit 1 to the --

14             CHAIRMAN EDGAR:  Yes.  Yes.  Okay.  I understand.

15             MR. WRIGHT:  Okay.

16             CHAIRMAN EDGAR:  Got you.  Yes.  That is correct.

17             MR. WRIGHT:  Thank you.  And so with the exhibits

18   marked for identification and Mr. Rant's testimony entered, I

19   would ask that he summarize his testimony for the Commission.

20             CHAIRMAN EDGAR:  Okay.  Actually I did not enter the

21   exhibits.

22             MR. WRIGHT:  I think I just said they were marked for

23   identification.

24             CHAIRMAN EDGAR:  They're just marked.  Okay.  I'm

25   sorry.  We are just not communicating right now, Mr. Wright.

FLORIDA PUBLIC SERVICE COMMISSION

455

1   Okay.  The exhibits are so marked as you have described.  We

2   will take them up at the conclusion of the testimony, and we

3   look forward to the witness's summary.

4             (Exhibits 34, 35 and 36 marked for identification.)

5             MR. WRIGHT:  Thank you, Madam Chairman.

6   BY MR. WRIGHT:

7        Q    Mr. Rant, proceed.

8        A    Thank you, Madam Chairman, Commissioners.

9             Gulf Power has taken a significant step forward with

10   its Storm Hardening Plan and included ten-point initiatives.

11   The plan is clearly focused on improving the overhead portion

12   of Gulf's system beyond what is strictly required by the NESC

13   in order to improve storm restoration and system reliability.

14   However, the plan falls short with regard to its analysis of

15   potential targeted undergrounding of distribution lines.  It is

16   my professional opinion that the Commission should not approve

17   the plan as submitted.  The Commission should request that Gulf

18   revisit undergrounding based upon data that is currently

19   available to them.

20             Gulf should include this analysis and continue with

21   its other efforts to capture and utilize data regarding the

22   costs and benefits of undergrounding in its efforts to improve

23   storm restoration and reliability.  The potential benefits of

24   targeted undergrounding include reduced system wind damage,

25   improved storm response by freeing up crews for overhead

FLORIDA PUBLIC SERVICE COMMISSION

456

1   restoration, preserve revenues from avoided outages, reduce

2   vegetation management costs, reduce pole inspection costs, and

3   reduced exposure to legal costs due to contact accidents.

4             Underground construction is normally more expensive

5   than overhead construction.  Targeting underground conversion

6   projects to areas which yield the most reliability gains

7   results in an optimized system performance result.  Gulf should

8   consider this within the context of its Storm Hardening Plan.

9             I've drawn these conclusions based upon my experience

10   designing overhead and underground electric distribution lines

11   over the last 14 years.  Specifically from 2000 to 2004 I

12   managed a storm hardening project for Brunswick EMC, a

13   cooperative utility in coastal North Carolina.  The project

14   consisted of undergrounding all of the remaining overhead lines

15   on each of four barrier islands served by the cooperative.

16   This part of North Carolina was hit directly by Hurricanes

17   Bertha, Fran and Bonnie in the mid 1990s.  The cooperative

18   experienced major damage to its overhead lines along the coast

19   and determined the necessity to harden its system.

20             In reviewing storm restoration efforts, Brunswick

21   management made the key observation that portions of the system

22   that were already underground faired much better during major

23   and minor storm events.  They focused their efforts toward

24   undergrounding areas that were the most problematic to restore.

25   Following a review of the recurring restoration costs, the

FLORIDA PUBLIC SERVICE COMMISSION

457

1   cooperative, supported in its efforts by FEMA, developed its

2   own undergrounding initiative, including the part of the plan

3   which I managed.

4             Since completing this project, Brunswick has been hit

5   directly by Tropical Storm Ernesto in 2006, which resulted in

6   outages to thousands of their customers in overhead served

7   areas and no outages in its recently undergrounded areas.

8   Additionally, on a daily basis even during summer thunderstorms

9   Brunswick experienced greater reliability on its underground

10   system.

11             The key point is that Gulf's Storm Hardening Plan

12   should include undergrounding to a greater extent than it does

13   as submitted.  Gulf's own data related to Hurricane Dennis in

14   2005 suggests that Panama City Beach, a high underground

15   percentage area with direct Gulf exposure, faired better and

16   was restored more quickly than Pensacola, which experienced

17   similar weather conditions but which is served mostly by

18   overhead lines.

19             Specifically the differences were dramatic.  The peak

20   number of outages experienced during Hurricane Dennis were

21   respectively 14 percent of Gulf's customers in Panama City

22   Beach and 96 percent of Gulf's customers in Pensacola.  These

23   areas are certainly not identical, but this data taken in the,

24   in the context of the general body of knowledge certainly

25   suggests that targeting, targeted undergrounding should be

FLORIDA PUBLIC SERVICE COMMISSION

458

1   considered as a component in the Storm Hardening Plan.

2             Should undergrounding be done on a blanket basis?

3   Absolutely not.  However, I do believe that Gulf's plan as

4   amended does not adequately include evaluation and

5   incorporation of undergrounding.  The plan presents significant

6   savings derived from its adoption of NESC Grade B overhead

7   standards, which does not fully present potential savings

8   derived from undergrounding.  The plan includes substantial

9   data collection efforts going forward on this issue, which we

10   fully support.

11             Gulf has data available at present to evaluate costs

12   and benefits of targeted undergrounding and should include

13   undergrounding in its Storm Hardening Plan as other utilities

14   have done.

15             Based upon the current body of knowledge with regard

16   to underground construction technology, costs, savings and

17   performance, this Commission should reject Gulf's plan and

18   require it to resubmit the plan with a more detailed

19   consideration of undergrounding.  If Gulf's plan is approved as

20   amended, it will result in delayed and/or reduced use of

21   undergrounding in its hardening measures most likely for years

22   to come while Gulf further studies data from additional storms.

23             Gulf's customers in areas that could be undergrounded

24   will continue to experience outages that might otherwise be

25   avoided.  And FPL has identified in its efforts costs and

FLORIDA PUBLIC SERVICE COMMISSION

459

1   benefits of targeted undergrounding and included the shared

2   cost approach to communities desiring underground electric

3   facilities through its GAF credit in its approved tariff.  Gulf

4   Power has access to similar data on its system and should

5   include a full consideration of targeted undergrounding in its

6   Storm Hardening Plan now.

7             Undergrounding provides substantial benefits and

8   those benefits have real value to utilities and their customers

9   both in terms of reduced storm restoration time and other

10   benefits that should be considered in the context of Gulf's

11   Storm Hardening Plan.

12             CHAIRMAN EDGAR:  Thank you.

13             MR. WRIGHT:  Madam Chairman, Mr. Rant is available

14   for cross-examination.

15             CHAIRMAN EDGAR:  Thank you.  Are there questions on

16   cross from Gulf?

17             MR. BADDERS:  At this point we do not have questions,

18   but we would like to reserve the right, if questions do come

19   from the bench or from other parties, to possibly respond to

20   that.

21             CHAIRMAN EDGAR:  Okay.  Are there questions from any

22   of the other parties in this case on cross?

23             MR. SEIVER:  FCTA has no questions.

24             CHAIRMAN EDGAR:  No questions.  AT&T, no questions.

25   No questions.  Embarq, no questions.  No questions.  Questions

FLORIDA PUBLIC SERVICE COMMISSION

460

1   from staff.

2             MS. FLEMING:  No questions.

3             CHAIRMAN EDGAR:  No questions from staff.  Questions

4   from Commissioners.  No questions.  Mr. Badders, no questions.

5             MR. BADDERS:  No questions.

6             CHAIRMAN EDGAR:  No questions.  Okay.

7             MR. WRIGHT:  Thank you, Madam Chairman.  And I would

8   move the admission of Exhibits 34, 35 and 36 into the record of

9   the case.

10             MR. BADDERS:  No objection.

11             CHAIRMAN EDGAR:  Okay.  Seeing no objection, Exhibits

12   34, 35 and 36 will be moved into the record.

13             (Exhibits 34, 35 and 36 admitted into the record.)

14             MR. WRIGHT:  Thank you.  And I believe that Mr. Rant

15   may be excused.

16             CHAIRMAN EDGAR:  The witness may be excused.  Thank

17   you.

18             MR. WRIGHT:  Thank you, Madam Chairman.

19             Next the City of Panama City Beach and the Panama

20   City Beach Community Redevelopment Agency call Mr. R. L.

21   Willoughby.

22                          R. L. WILLOUGHBY

23   was called as a witness on behalf of the City of Panama City

24   Beach and the Panama City Beach Community Redevelopment Agency

25   and, having been duly sworn, testified as follows:

FLORIDA PUBLIC SERVICE COMMISSION

461

1                         DIRECT EXAMINATION

2   BY MR. WRIGHT:

3        Q    Good morning, Mr. Willoughby.  Will you please state

4   your name and address for the record?

5        A    R. L. Willoughby, 1609 Heritage Commerce Court, Wake

6   Forest, North Carolina.

7        Q    Mr. Willoughby, you were sworn in along with all the

8   other witnesses yesterday morning, were you not?

9        A    Yes, I was.

10        Q    Thank you.  Are you the same R. L. Willoughby who

11   prepared and caused to be filed in this proceeding prefiled

12   direct testimony consisting of 11 pages?

13        A    Yes.

14        Q    Do you have any changes or corrections to make to

15   that testimony?

16        A    I do not.

17        Q    If I were to ask you the same questions contained in

18   that testimony today, would your answers be the same?

19        A    Yes.

20        Q    And do you then adopt this testimony as your sworn

21   testimony before the Florida Public Service Commission today?

22        A    I do.

23        Q    Thank you.

24             MR. WRIGHT:  Madam Chairman, if there are no

25   objections, I would request that Mr. Willoughby's testimony be

FLORIDA PUBLIC SERVICE COMMISSION

462

1   entered into the record as though read.

2             CHAIRMAN EDGAR:  The prefiled direct testimony will

3   be entered into the record as though read.

4             MR. WRIGHT:  Thank you.

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

474

1   BY MR. WRIGHT:

2        Q    And, Mr. Willoughby, did you also attach to your

3   prefiled direct testimony one exhibit consisting of your resume

4   and designated as RLW-1?

5        A    I did.

6        Q    Thank you.

7             MR. WRIGHT:  Madam Chairman, I believe that exhibit

8   has been marked as Exhibit Number 37.

9             CHAIRMAN EDGAR:  Yes.

10             (Exhibit 37 marked for identification.)

11             MR. WRIGHT:  Thanks.  And I would, with your

12   indulgence, ask Mr. Willoughby to summarize his testimony for

13   the Commission.

14             THE WITNESS:  Madam Chairman, Commissioners, I was

15   asked by Panama City Beach and Panama City Beach Community

16   Redevelopment Agency to give my opinions regarding Gulf Power's

17   Storm Hardening Plan.  I state this opinion based on my 40

18   years of experience in operations and management of electric

19   transmission and distribution systems.  The first 15 to 20

20   years of my career was primarily with construction and

21   maintenance of underground and overhead facilities.  I had

22   quite a bit of hands-on experience with actual power

23   restoration during minor storms, major storms and just routine

24   events.  The last 20 years or so I've been in administration

25   and management.

FLORIDA PUBLIC SERVICE COMMISSION

475

1             Early in my career as a power lineman and also later

2   as a utility director I have personally experienced the

3   frustrations of extended power outages during minor and major

4   storm events, and later as city manager I had to deal with the

5   financial and the political issues of operating a local

6   distribution system.  Since then and during my tenure in this

7   business, technology has improved a great deal with

8   undergrounding as well as improved training for the employees

9   that place the underground facilities in, and with this it's

10   becoming a normal and typical application for most utilities.

11   In fact, the utilities I work with, probably over 95 percent of

12   all new construction was underground and most of the clients

13   that we currently work for now, most of their utilities are

14   going underground.

15             I've worked in many minor and major storm events in

16   my career.  While I was a manager in Washington, North

17   Carolina, I had specific experience with five named hurricanes

18   or five named storms, one of them was a tropical storm when it

19   hit Washington, and it confirmed the value of undergrounding

20   facilities when properly designed, properly installed and

21   properly maintained as suffering minimal damage from, from

22   flooding and from other storm-related events.

23             In the storms that we experienced, in these five

24   storms that we experienced, extensive damage was done to our

25   overhead system through wind and wind-blown debris, and we also

FLORIDA PUBLIC SERVICE COMMISSION

476

1   had extensive flooding.  The underground -- the overhead

2   facilities faired poorly during the, during the storm events

3   but our underground facilities faired very well.  The only

4   underground outages we had were where we had live front

5   equipment and the flooding came and got above the energized bus

6   so that we had to de-energize the equipment.  But when the

7   waters receded, we were able to energize the facilities right

8   away and those came back up.  We had no wind-related problems

9   to our underground system.  The only extended outages we had on

10   the underground was where an underground section might be

11   served from an overhead line.  The overhead would be on the

12   source side, if you will.  And if the overhead was out for an

13   extended while, we couldn't get the underground back on, but

14   the underground was ready for energization in these events.

15             Today I have no specific criticism of Gulf Power's

16   overhead storm hardening recommendations.  In addition, their

17   hardening design specification for their underground has

18   positive enhancements.  I do believe, however, that Gulf Power

19   should take a more definitive approach to evaluating

20   underground as a greater component of their Storm Hardening

21   Plan.  I am not recommending blanket undergrounding of

22   everything.  But it has been my experience, as I said earlier,

23   properly designed, installed and maintained underground

24   facilities have, have no more operation, excuse me, operation

25   and maintenance costs than overhead, and quite often less costs

FLORIDA PUBLIC SERVICE COMMISSION

477

1   and operation and maintenance costs.  And in addition, during

2   minor and major storm events they've proven to be more reliable

3   and time, time saved and cost, cost savings, too.

4             I believe Gulf Power's overhead Storm Hardening Plan

5   is a positive approach to improving reliability.  However, I

6   believe they should take a more proactive approach to

7   underground as a component of the Storm Hardening Plan.

8   Sufficient information should be available to analyze the

9   benefits and costs for undergrounding and should be readily

10   available to Gulf Power.  I believe they should use this data

11   as well as data from other utilities as necessary to actively

12   evaluate the reliability and cost benefits of undergrounding

13   and include this as a part of their underground storm -- as

14   part of their Storm Hardening Plan.  That concludes my summary.

15             MR. WRIGHT:  Thank you, Mr. Willoughby.

16             Madam Chairman, Mr. Willoughby is available for

17   cross-examination.

18             CHAIRMAN EDGAR:  Thank you.

19             Mr. Badders, let me come back to you in a moment, if

20   I may.

21             Commissioner Carter, did you have a question?

22             COMMISSIONER CARTER:  Thank you, Madam Chairman.  I

23   was listening both to Mr. Rant and Mr. Willoughby, and I think

24   that you said that notwithstanding undergrounding, were the

25   source in terms of the connectivity from the power source, if

FLORIDA PUBLIC SERVICE COMMISSION

478

1   that goes out, then all the power is out.  That's what you

2   said; right?

3             THE WITNESS:  Quite often the overhead line serves

4   the underground because the overhead is closer to the source

5   quite often, and if that's off, the underground is off.

6   However, if you have your forces and crews working on the

7   overhead and get it on, as soon as it's on, the underground is

8   on.  Of course, that lends itself to putting more underground

9   in, you would think.  But that is some of the dilemma with

10   underground because quite often it's served from an overhead

11   feeder.

12             COMMISSIONER CARTER:  Madam Chairman, if you'd permit

13   to follow up.

14             Do you know of any system anywhere in the country

15   where the actual source is underground as well?

16             THE WITNESS:  I guess it depends on what you call the

17   source.  In this context I'm calling the source the substation.

18             COMMISSIONER CARTER:  Let me define it for you.  Let

19   me define it for you.

20             THE WITNESS:  Okay.

21             COMMISSIONER CARTER:  The connectivity so that you

22   can get some juice.

23             THE WITNESS:  Well, again, that would depend, is it a

24   generating plant, is it a transmission line or is it

25   distribution?  But not trying to be facetious, but

FLORIDA PUBLIC SERVICE COMMISSION

479

1   traditionally at a distribution level we would determine, we

2   would, I would identify it as directly out of the substation.

3   Now you could have overhead transmission lines serving the

4   substation, but most often transmission lines aren't affected

5   quite as much because of maintenance and tree trimming and that

6   sort of thing.  However, I do know of a few places, I can't

7   recall off the top of my head, that directly out of the

8   substation the facilities are underground.  Quite often those

9   are in downtown areas with network systems and things such as

10   that, but there are some places likes that.  It doesn't mean

11   there couldn't be more.

12             COMMISSIONER CARTER:  But no, no direct -- Madam

13   Chairman.  But a substation in and of itself is not the source

14   of the power.  It's a place where the power is distributed from

15   the, the plant itself to go to different sections.

16             THE WITNESS:  The substation is the source of the,

17   typically the source of the distribution power.

18             COMMISSIONER CARTER:  Right.

19             THE WITNESS:  That's where distribution and

20   transmission typically are separated.

21             COMMISSIONER CARTER:  Madam Chairman.  You understand

22   what I'm asking you?

23             THE WITNESS:  Yes, sir.

24             COMMISSIONER CARTER:  Because I hear what you're

25   saying, and I appreciate that, about undergrounding.  We've had

FLORIDA PUBLIC SERVICE COMMISSION

480

1   tremendous discussion about that.  The fact of the matter is if

2   the source is overhead and you're connecting to an underground,

3   you lose the source overhead, you're still out of power.

4             THE WITNESS:  Until that component is fixed.  And

5   when that's fixed, then you don't have any -- you should not

6   have any additional work to do to get the distribution up

7   because it's underground.  But your point is well-taken, yes,

8   sir.

9             COMMISSIONER CARTER:  And because -- Madam Chairman.

10   And because we've had so much discussion about undergrounding,

11   I was wondering if there were a situation anywhere in the

12   country where they had gone the extraordinary step to connect

13   with the source for the undergrounding.  Because it seems like

14   to me, excuse me, it seems like to me it's, you're still

15   halfway there.  If you've got the, the connectivity to the

16   residential units or commercial units underground but the

17   source from the plant is coming overhead, you still, that's

18   still the Achilles' heel, wouldn't you agree?

19             THE WITNESS:  I would agree that that is additional

20   exposure.  Yes, sir.

21             COMMISSIONER CARTER:  Thank you.

22             CHAIRMAN EDGAR:  Commissioner Argenziano.

23             COMMISSIONER ARGENZIANO:  Well, Commissioner Carter,

24   I heard the same thing and I wrote the question down because

25   that sparked my interest because I hadn't thought of that.  But

FLORIDA PUBLIC SERVICE COMMISSION

481

1   yet in the discussion I think -- at some point I guess, and I

2   don't know if you can give me this, this number, I guess -- how

3   many or what percentage of underground lines are serviced by

4   aboveground?  I guess they all are to some degree.  But also

5   in, in what Commissioner Carter was asking you, even though

6   it's still an Achilles' heel, you still have that whole

7   underground line that does not have to be put back up once you

8   get the aboveground up.

9             THE WITNESS:  That's correct.  That's absolutely

10   correct.

11             COMMISSIONER ARGENZIANO:  So that would then expedite

12   services along that whole underground line also.

13             THE WITNESS:  And in addition to that, instead of

14   having crews working on the underground section that could be

15   overhead, they've got all their resources allocated to their

16   overhead section.  So you can allocate your resources, more of

17   your resources to those smaller areas the more you underground.

18             COMMISSIONER ARGENZIANO:  And one other -- and I

19   would imagine that if you had taken the time and the money to

20   put in underground lines, that the aboveground lines that are

21   servicing the underground lines would be hardened first.

22             THE WITNESS:  One would hope that would be an

23   integral part of the plan.

24             COMMISSIONER ARGENZIANO:  Well, that -- I'd hope so.

25   Okay.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

482

1             CHAIRMAN EDGAR:  Commissioner Skop.

2             COMMISSIONER SKOP:  Thank you, Madam Chair.

3             Just along those lines of questioning as a quick

4   follow-up.  What is your experience with existing

5   undergrounding to the extent that -- you know, I think that you

6   have admitted in your testimony that it's traditionally more

7   expensive than overhead.  But I think that in some of the

8   hearings that we've held, and we've got some, again, additional

9   information, it seems like undergrounding, there are some

10   inherent problems to the extent of service restoration with --

11   like, if it were in a coastal region and you had storm surge,

12   that it would be covered with huge volumes of sand and/or

13   flooding or other issues, and I just wanted to get you to

14   briefly speak to that, if you could, please.

15             THE WITNESS:  If you have some major erosion or, or

16   beach wash or backwash, those things could happen.  The areas

17   I've been experienced with and worked with, that's been very

18   minimal.  That's not to say it couldn't happen.  But even said

19   that, that's still typically, in my opinion, typically less

20   time-consuming to get that resolved than be putting poles and

21   wires and that sort of thing up and getting trees cleared out

22   of the way.

23             COMMISSIONER SKOP:  Thank you.

24             CHAIRMAN EDGAR:  And there are no questions from

25   staff or from the other parties.  I will come back to you,

FLORIDA PUBLIC SERVICE COMMISSION

483

1   Mr. Badders.

2             MR. SEIVER:  No questions.

3             CHAIRMAN EDGAR:  No questions.  No questions.  No

4   questions.  Mr. Badders.

5             MR. BADDERS:  No questions.

6             CHAIRMAN EDGAR:  No questions.

7             Questions on redirect?

8             MR. WRIGHT:  No thank you, Madam Chairman.  We

9   appreciate it.

10             CHAIRMAN EDGAR:  Okay.  Oh, Commissioner Carter.

11             COMMISSIONER CARTER:  Just kind of following up on

12   what Commissioner Argenziano was saying is that it would seem

13   to me to make sense that if you're connecting to underground,

14   that you would want to harden the overhead structures maybe to,

15   like you're saying, coming to the substations.  I guess that

16   would be more of a distribution line or a transmission line,

17   and, you know, reinforce that greatly because you know the

18   power from that substation goes to the entire area,

19   geographical area.  Has that been your experience, what you've

20   found in areas --

21             THE WITNESS:  I would absolutely agree.  That should

22   be part of the overall plan to have the segments that can be

23   put in underground reasonably and that customers may be willing

24   to pay a premium for that.  And the overhead lines serving it,

25   you would absolutely want that part of your overall plan to

FLORIDA PUBLIC SERVICE COMMISSION

484

1   improve reliability.

2             CHAIRMAN EDGAR:  Commissioner Argenziano.

3             COMMISSIONER ARGENZIANO:  Just another question.  Out

4   of curiosity, how deep are the lines underground?  How deep do

5   you have to go?

6             THE WITNESS:  It varies with the voltage, and a lot

7   of times it varies with the other utilities around because

8   traditionally your high voltage, your high voltage -- when I

9   say high voltage, distribution high voltage from 7 kV to 15 kV,

10   something like that -- is three to four feet.  Most people try

11   to go within four feet there.  And it depends on whether it's

12   in conduit or not.  And quite often they go deeper than that

13   just to get clearance from other like water lines, sewer lines,

14   telephone cables, that sort of thing.

15             COMMISSIONER ARGENZIANO:  If you're going deeper, I

16   would imagine some of the cost calculations would be if you

17   encounter lime rock?

18             THE WITNESS:  It can be.  And the unknowns of going

19   deeper.  Directional boring has been a very beneficial addition

20   to the technology of undergrounding.  And in my opinion, even

21   though directional boring can be more expensive than opening a

22   trench, quite often it can be less expensive because of the

23   disruptive -- lack of disruption to the aboveground trees and

24   shrubbery, that sort of thing, as well as, you know, to go

25   through some of these areas you would hit some unusual.

FLORIDA PUBLIC SERVICE COMMISSION

485

1             COMMISSIONER ARGENZIANO:  And I guess the reason I'm

2   asking is I wonder if you start to underground, if you all of

3   the sudden come up with a whole batch of lime rock, of course

4   the costs are going to go up to get through that lime rock.  Is

5   there any kind of echo sonar or whatever they call it that's

6   done ahead of time or is that -- or do you calculate that ahead

7   of time in undergrounding?

8             THE WITNESS:  You can.  I would think most utilities

9   that are doing work in certain areas -- you could have a spot

10   that's just, you don't recognize is there, but most of them

11   probably have the experience in working in areas, they know

12   about what the soils are in certain areas.  And you could -- I

13   don't think that's a major problem.  It can on a site-specific

14   case be a problem.  But on the grand scheme of undergrounding I

15   don't see it as being a big deal.  It can be in a spotted

16   location, yes.

17             COMMISSIONER ARGENZIANO:  Okay.  Madam Chair.  The

18   only reason I mentioned that, I was wondering, I know that when

19   they're laying water lines throughout the state a lot of times

20   they hit lime rock and it brings up the cost quite a bit than

21   what's anticipated upfront and then you could start something

22   and then later wind up having a greater, greater cost.  So I

23   didn't know if that was taken into consideration before the

24   lines are laid.

25             THE WITNESS:  And you could, excuse me, and you could

FLORIDA PUBLIC SERVICE COMMISSION

486

1   do soil borings ahead of time if you were concerned about

2   things like that to get a better idea of it.

3             COMMISSIONER ARGENZIANO:  Okay.  Thank you.

4             CHAIRMAN EDGAR:  Thank you.

5             Okay.  Let's take up the exhibit.

6             MR. WRIGHT:  Thank you.  We would move the admission

7   of Exhibit 37, Madam Chairman.

8             CHAIRMAN EDGAR:  Okay.  Seeing no objection, Exhibit

9   37 will be entered into the record, and the witness is excused.

10   Thank you very much.

11             MR. WRIGHT:  Thank you.

12             (Exhibit 37 admitted into the record.)

13             CHAIRMAN EDGAR:  Mr. Willis --

14             MR. WILLIS:  We would --

15             CHAIRMAN EDGAR:  -- what is your pleasure?

16             MR. WILLIS:  We would suggest that you take --

17   proceed to the rebuttal witnesses but take Regan Haines after

18   Manny Miranda.  What I would anticipate doing is that after

19   Manny Miranda completes his rebuttal, to then come back to

20   Mr. Harrelson, if necessary, and then to Mr. Haines, if

21   necessary.

22             CHAIRMAN EDGAR:  Okay.  So I just want to make sure

23   I've got it straight.  Okay.  So realizing that you have shared

24   with us that TECO and FCTA are still in discussions, so --

25             MR. WILLIS:  Correct.

FLORIDA PUBLIC SERVICE COMMISSION

487

1             CHAIRMAN EDGAR:  -- you're asking that we hold on

2   Witness Haines.  And, Ms. Fleming, thoughts?

3             MS. FLEMING:  I'm processing this information.  We

4   recognize that we would like to encourage stipulation among the

5   parties.  I think it would -- if it doesn't confuse the record

6   for any of the parties, we can move forward with the rebuttal

7   testimony if that's the Commission's pleasure.

8             CHAIRMAN EDGAR:  Can I ask you, Mr. Willis, and as

9   Ms. Fleming has stated, of course, I agree that we do try to

10   encourage these sorts of discussions and certainly want to do

11   anything we can to facilitate or not throw up burdens.

12   However, it is a little, of course, unusual to move into

13   rebuttal testimony with direct still hanging out there.  So can

14   you give me a feel for about what your time frame you think

15   you're looking at?  And, of course, part of the reason I'm

16   asking, other than just general curiosity, is, you know, we

17   could take an early lunch break and then come, come back after

18   lunch and see where we're at if you think that that might be

19   productive.

20             MR. WILLIS:  We have an agreement that we're willing

21   to sign that is, has been presented to FCTA, and they're

22   checking with their client basically is what I think the

23   situation is.

24             MS. BROWNE:  That's correct, Madam Chair.  And I

25   think that if we broke and came back after an early lunch, that

FLORIDA PUBLIC SERVICE COMMISSION

488

1   would likely be enough time for us to reach a resolution or

2   not, to have an answer.

3             CHAIRMAN EDGAR:  Okay.  Commissioners, any concerns

4   if we go ahead and take an earlier lunch break, give the

5   parties additional time?

6             Okay.  Then let's go ahead, we will take a slightly

7   early break.  It is about 20 to 12:00.  Let's come back at

8   1:00.  Does that work, Commissioners?  Does that work?

9             Okay.  We are on lunch break, and we will be back at

10   1:00.  Thank you.

11             MS. BROWNE:  Thank you, Madam Chair.

12             (Lunch recess taken.)

13             (Transcript continues in sequence with Volume 4.)

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

489

1   STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2   COUNTY OF LEON      )

3

4             I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing proceeding was

5   heard at the time and place herein stated.

6             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

7   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

8   proceedings.

9             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

10   or employee of any of the parties' attorneys or counsel

connected with the action, nor am I financially interested in

11   the action.

12              DATED THIS ______ day of October, 2007.

13

14                  ________________________________

LINDA BOLES, RPR, CRR

15                  FPSC Official Commission Reporter

(850) 413-6734

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION