176

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

DOCKET NO. 070183-WS

3   In the Matter of:

4   PROPOSED ADOPTION OF RULE 25-30.4325,

F.A.C., WATER TREATMENT PLANT USED

5   AND USEFUL CALCULATIONS.

6   _____________________________________/

7

8

9

ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

10                 A CONVENIENCE COPY ONLY AND ARE NOT

THE OFFICIAL TRANSCRIPT OF THE HEARING,

11            THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

12                              VOLUME 2

13                        Pages 176 through 339

14   PROCEEDINGS:        HEARING

15   BEFORE:             CHAIRMAN MATTHEW M. CARTER, II

COMMISSIONER LISA POLAK EDGAR

16                       COMMISSIONER KATRINA J. MCMURRIAN

COMMISSIONER NANCY ARGENZIANO

17                       COMMISSIONER NATHAN A. SKOP

18   DATE:               Tuesday, January 22, 2008

19   TIME:               Commenced at 9:30 a.m.

Concluded at 4:06 p.m.

20

PLACE:              Betty Easley Conference Center

21                         Room 148

4075 Esplanade Way

22                       Tallahassee, Florida

23   REPORTED BY:        JANE FAUROT, RPR

Official FPSC Reporter

24                       (850) 413-6732

25   APPEARANCES:        (As heretofore noted.)

FLORIDA PUBLIC SERVICE COMMISSION

177

1                              I N D E X

2                              WITNESSES

3

NAME:                                               PAGE NO.

4

FRANK SEIDMAN, P.E.

5

Direct Examination by Mr. Friedman               182

6        Prefiled Direct Testimony Inserted               184

Cross Examination by Mr. Reilly                  228

7        Cross Examination by Mr. Hoffman                 240

Cross Examination by Mr. Jaeger                  244

8

VAN HOOFNAGLE, P.E.

9

Prefiled Direct Testimony Inserted               250

10

DWIGHT T. JENKINS, P.G.

11

Prefiled Direct Testimony Inserted               254

12

RICHARD P. REDEMANN, P.E.

13

Direct Examination by Mr. Gervasi                265

14        Prefiled Direct Testimony Inserted               267

Cross Examination by Mr. Reilly                  286

15        Cross Examination by Mr. Hoffman                 303

16   ANDREW T. WOODCOCK, P.E., M.B.A.

17        Prefiled Rebuttal Testimony Inserted             310

18   JOHN F. GUASTELLA, P.E.

19        Direct Examination by Mr. Hoffman                326

Prefiled Surrebuttal Testimony Inserted          328

20        Cross Examination by Mr. Reilly                  331

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

178

1                              EXHIBITS

2   NUMBER:                                      ID.    ADMTD.

3   8 through 12                                         248

4   13                                                   249

5   14 through 21                                        308

6   22                                                   337

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

179

1                         P R O C E E D I N G S

2             CHAIRMAN CARTER:  We'll go back on the record.  And I

3   think the last time that we left here, we were taking the last

4   train to Clarksville.

5             COMMISSIONER SKOP:  I think it was Memphis.

6             CHAIRMAN CARTER:  That shows you about how old I am.

7             Was it to Memphis?

8             COMMISSIONER SKOP:  Yes.

9             CHAIRMAN CARTER:  Okay.  I think, Mr. Friedman -- Mr.

10   Hoffman, we finished with you, right, with your witnesses?

11             MR. HOFFMAN:  Yes.

12             CHAIRMAN CARTER:  Well, not with you personally, but

13   (laughter) --

14             MR. HOFFMAN:  That remains to be seen, I guess.

15             CHAIRMAN CARTER:  I'm working on the dialogue.  Give

16   me a week or so to get back in the saddle there.

17             MR. HOFFMAN:  Mr. Chairman, I do have one preliminary

18   matter.  I think Mr. Seidman is up next.

19             With respect to Mr. Woodcock's rebuttal, I think that

20   we can, unless the Commissioners have questions, stipulate his

21   rebuttal into the record.

22             CHAIRMAN CARTER:  Oh, that sounds refreshing.

23             Mr. Friedman, are you cool with that, too?

24             MR. FRIEDMAN:  I'm cool with that.

25             CHAIRMAN CARTER:  All right.  Mr. Reilly, let's hear

FLORIDA PUBLIC SERVICE COMMISSION

180

1   from you on that.

2             MR. REILLY:  It catches me slightly by surprise.

3             CHAIRMAN CARTER:  You beat them down.

4             MR. REILLY:  Well, I mean, he can certainly decide

5   whether he wants to ask cross-examination questions, so there

6   is nothing I have to comment on that.  I guess we would yield

7   to staff.

8             MS. GERVASI:  We don't have questions on rebuttal,

9   either.

10             CHAIRMAN CARTER:  Well, see, I was right from the

11   very beginning.

12             MR. REILLY:  I thank the parties.

13             CHAIRMAN CARTER:  So Mr. Woodcock can still go home,

14   can't he?

15             MR. REILLY:  No, he needs to sit here and help me.

16   He's not excused.

17             CHAIRMAN CARTER:  I was trying to help you out, you

18   know.  You are welcome to stay.  Okay.

19             MR. JAEGER:  Chairman Carter, just before we broke, I

20   think Commissioner Argenziano had a question about Rule 62.

21             CHAIRMAN CARTER:  One second.  We will get back to

22   that in a minute.  Let's kind of take care of the preliminary

23   matters.

24             Ms. Gervasi, is there anything that we need to do on

25   this, since the parties are in agreement on the stipulation?

FLORIDA PUBLIC SERVICE COMMISSION

181

1             MS. GERVASI:  No, sir, other than to have his

2   Rebuttal Testimony offered up into the record as though read at

3   the appropriate time, which I'm sure Mr. Reilly will do.

4             CHAIRMAN CARTER:  Okay.  That will be --

5             MR. REILLY:  I'll be happy to do it now, whatever

6   your pleasure.

7             MS. GERVASI:  Probably for the record to read

8   correctly, we ought to wait on that.

9             CHAIRMAN CARTER:  Let's kind of give Mr. Reilly a

10   heads up when we get to that point, all right?

11             MS. GERVASI:  Yes, sir.

12             CHAIRMAN CARTER:  Okay.  Mr. Jaeger.

13             MR. JAEGER:  Yes.  Rule 62-555.348, titled Planning

14   for Expansion of Public Water System Source Treatment or

15   Storage Facilities.  That was effective August 28th, 2003.

16   There has been no changes since then.  I checked -- well, the

17   staff helped me check the Florida Administrative Code, there is

18   nothing in the works for amending it.  I also called my DEP

19   sources, and they said there is nothing in the works for

20   amending this rule.

21             CHAIRMAN CARTER:  Commissioner Argenziano.

22             COMMISSIONER ARGENZIANO:  Thank you, because I wasn't

23   sure if it was that rule.  I know something stuck out about

24   that, and I don't know if we are -- just finding that out makes

25   me feel more comfortable.  I appreciate that.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

182

1             CHAIRMAN CARTER:  Thank you.  I think, Mr. Friedman,

2   you are up next.

3             MR. FRIEDMAN:  Thank you very much.  Utilities, Inc.

4   calls Frank Seidman.

5             CHAIRMAN CARTER:  Mr. Seidman, you are recognized.  I

6   know you have already been sworn.  I saw you in here this

7   morning.

8             THE WITNESS:  Yes, I have been sworn.

9                            FRANK SEIDMAN

10   was called as a witness on behalf of Utilities, Inc., and

11   having been duly sworn, testified as follows:

12                         DIRECT EXAMINATION

13   BY MR. FRIEDMAN:

14        Q    Would you please state your name and business

15   address?

16        A    Frank Seidman, Post Office Box 13427, Tallahassee,

17   Florida.

18        Q    And, Mr. Seidman, did you prefile Direct Testimony in

19   this docket on behalf of Utilities, Inc. consisting of 42 pages

20   and five exhibits?

21        A    That's correct.

22        Q    And do you have any corrections to your testimony?

23        A    Yes, I have one correction.

24        Q    Could you point that out for us, please?

25        A    That would be on Page 21, Line 20.  And in that line

FLORIDA PUBLIC SERVICE COMMISSION

183

1   there is a Paren 5, it should read Paren 4.  That is the only

2   correction.

3        Q    And, Mr. Seidman, if I were to ask you the questions

4   in your prefiled testimony with that one change, would your

5   answers be the same?

6        A    Yes, they would.

7             MR. FRIEDMAN:  I would like to ask that Mr. Seidman's

8   prefiled testimony be submitted into the record as those read.

9             CHAIRMAN CARTER:  The prefiled testimony will be

10   entered into the record as though read.

11             MR. FRIEDMAN:  And, for the record, Mr. Seidman's

12   exhibits have been designated by the staff on Exhibit 1 as 8,

13   9, 10, 11, and 12.  And we will offer those at the appropriate

14   time.

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

226

1   BY MR. FRIEDMAN:

2        Q    Mr. Seidman, would you briefly summarize your

3   prefiled Direct Testimony?

4        A    Yes, thank you.  My Direct Testimony presents the

5   position of Utilities, Inc. and its Florida subsidiaries with

6   regard to this rulemaking.  And that basic position of

7   Utilities, Inc. is that it supports the rule as proposed in its

8   entirety, including the stipulations.  It supports it even

9   though it may not agree with every part of the rule, but it

10   supports it because it represents a compromise resulting from

11   the concerted efforts of the Commission staff and the

12   interested parties.  And, more importantly, it codifies

13   decisions of this Commission that have been developed,

14   solidified during the course of many evidentiary hearings, or

15   occurring over many years before many sets of Commissioners.

16             Our testimony consists of two parts.  The first part

17   lays out some background and history regarding the regulatory

18   concept of used and useful, and the second part consists of

19   comments on specific changes proposed by the Office of Public

20   Counsel to the proposed rule.  I have included this background

21   and history for a couple of reasons.  In general, I thought it

22   was important for everyone to have an understanding of the

23   roots of the concept in regulatory law, its uniqueness and also

24   its vagueness.

25             Although the purpose of used and useful is commonly

FLORIDA PUBLIC SERVICE COMMISSION

227

1   understood to be the means by which we determine which assets

2   of the utility are going to be included in rate base, there is

3   not a clue in any regulatory law as to how that should be

4   accomplished.  Specifically, with regard to regulation of water

5   and wastewater utilities in Florida, I thought it was important

6   to understand that this Commission has been examining, and

7   testing, and reexamining, and proposing methods of calculating

8   and standardizing the calculation of used and useful for over

9   35 years.  So there is an awful lot of history behind what is

10   being presented to you today in the staff's proposal and it

11   should not be taken lightly.  This is not something that was

12   just developed over a few weeks or even over the two years that

13   were devoted specifically to this rulemaking.  These are not

14   hastily conceived sets of rules, but they are rather well

15   thought out codifying conclusions of these many evidentiary

16   hearings which are referred to and they have been subjected to

17   arguments for and against and to cross-examination and ruled on

18   in other rate cases.

19             With regard to the second part of my testimony

20   wherein I comment on proposed changes of the proposed rule, I

21   believe these comments that you have in hand speak for

22   themselves, and I'm not going to use up your time going over

23   them.  I'm just hopeful that they will be useful to you in

24   reaching your final decisions.

25             And I just want to conclude my summary by reiterating

FLORIDA PUBLIC SERVICE COMMISSION

228

1   that the purpose of used and useful analysis is not to

2   determine a used and useful percentage, but rather to determine

3   what assets are going to be included in rate base.  Determining

4   a percentage is a means to an end and not the end itself.  The

5   resulting rule should enable the utility the opportunity to

6   recover the cost of providing the facilities which make it

7   possible to operate a system in an economical manner,

8   protective of the environment, and intended to assure that the

9   customers get a continuously reliable level of service.

10             Thank you.

11             MR. FRIEDMAN:  We would tender Mr. Seidman for

12   cross-examination at this time.

13             CHAIRMAN CARTER:  Thank you.  And, Mr. Reilly, you

14   are recognized.

15                          CROSS EXAMINATION

16   BY MR. REILLY:

17        Q    Good afternoon, Mr. Seidman.

18        A    Good afternoon.

19        Q    Could I have you refer to your testimony on Page 19,

20   Lines 5 and 6.  I believe on these lines it is your testimony

21   that you state that Mr. Woodcock's peak demand for water

22   storage ignores the necessity for emergency storage, is that

23   correct?

24        A    That's correct.

25        Q    So for identical service areas, one served by a water

FLORIDA PUBLIC SERVICE COMMISSION

229

1   treatment plant with no storage and one served by a water

2   treatment plant with storage, is there a differing standard for

3   emergency volume in your judgment?

4        A    Would you repeat that?

5        Q    We have identical service areas, one served by a

6   water treatment plant with no storage and one with storage.  In

7   your judgment would that create a differing standard for

8   emergency volume considerations?

9        A    No, because the emergency volume is related to the

10   storage.  If there's no storage, there is obviously no

11   emergency volume contained in a storage facility.

12        Q    So the customers without storage would not get the

13   benefit, obviously, of emergency storage.  I mean, there is no

14   provision for emergency for such a system.

15        A    They are without the benefit of any storage.

16        Q    Are you aware of FDEP requirements to include design

17   requirements for water treatment systems that provide for

18   continued operation in emergency situations?

19        A    And what rule is that?

20        Q    I'm asking are you familiar with any FDEP rule that

21   includes design requirements for water treatment systems that

22   provide for continued operation in emergency situations?

23        A    I'm not familiar with anything specific.  I think the

24   overall design requirements of DEP through their Rule

25   62-555 covers basically all situations.

FLORIDA PUBLIC SERVICE COMMISSION

230

1        Q    Would you say that the concept of firm reliable

2   capacity which involves sizing a plant to meet demands in the

3   event the largest capacity well is required to be out of

4   service is an example of a requirement to cover an emergency?

5        A    Yes, it is.

6        Q    And is the firm reliable capacity concept embodied in

7   the used and useful rule proposed by staff?

8        A    I'm sorry?

9        Q    Is firm reliable capacity, the concept of this

10   embodied in the used and useful rule proposed by staff?

11        A    If you are referring to the extent that leaving one

12   well out of service gives you some buffer, yes.

13        Q    Are you aware of the FDEP requirements regarding

14   standby power generators to allow water treatment plants to

15   operate in the event of power outages?

16        A    Yes.

17        Q    So FDEP has several design requirements for water

18   treatment facilities to maintain service in the event of an

19   emergency, but does not require any emergency volume for system

20   storage, isn't that correct?

21        A    I don't think it necessarily requires emergency

22   storage, but I don't think that has anything to do with the

23   fact that emergency storage is a consideration, and it is well

24   documented in literature for the design of water treatment

25   plants, water treatment systems.

FLORIDA PUBLIC SERVICE COMMISSION

231

1        Q    But FDEP's effort to help address potential

2   emergencies, it does require standby power, but it does not

3   require quote, unquote, emergency storage, is that correct?

4   Per se, water storage?

5        A    I will defer for what you said, sure.

6        Q    Okay.  Shifting subjects, have you read Mr.

7   Hoffnagle's testimony?

8        A    Yes, I have read it.

9        Q    Do you have it handy?

10        A    Yes.

11        Q    I would direct your attention to Page 2 of that

12   testimony, Lines 13 through 19.

13        A    Okay.

14        Q    Do you agree with Mr. Hoffnagle's testimony regarding

15   how FDEP rules relate to Florida Public Service Commission

16   practices?  Do you believe his statement is accurate, and do

17   you agree with it?

18        A    If you are referring to the last sentence --

19        Q    I think I'm referring to those Lines 13 through 19.

20   DEP sets/establishes standards of practice and care for the

21   industry to ensure water quality.

22        A    I agree with that.

23        Q    To those lines, okay?

24        A    I agree with that.

25        Q    And that this responsibility remains -- as to

FLORIDA PUBLIC SERVICE COMMISSION

232

1   quantity, remains with the state's water management districts?

2        A    Yes, I agree with that.  I don't have any problem

3   with his answer.

4        Q    Okay.  And referring to the same testimony on Page 2,

5   Lines 6 through 9, if I could have you just look at that?

6        A    Page 2 --

7        Q    Same page, Lines 6 through 9.  It starts Subparagraph

8   .320, and this is speaking of the general purpose for FDEP Rule

9   62-555.320.  Do you likewise --

10        A    Yes, that's fine.

11        Q    And you do agree with that testimony?

12        A    Sure.

13        Q    Okay.  Thank you.  Moving to another subject

14   regarding that issue of 12 hours of well pumping.  Would you

15   say that a water treatment plant that is twice as big as what

16   is needed to serve its customers base at build-out is prudently

17   designed?

18        A    A system that's twice as big as it needs to be at

19   build-out?

20        Q    Right; would be, in your judgment, prudently

21   designed?

22        A    I think that depends on what the design criteria were

23   at the time that it was designed.  We are talking about design

24   conditions here, so at one time when the system was designed,

25   there were certain parameters that were used to determine the

FLORIDA PUBLIC SERVICE COMMISSION

233

1   size.  Now, if it -- okay, at build-out.  If it builds out to

2   the full system and it's -- yes, it would be excess.

3        Q    And the answer is you wouldn't consider that prudent?

4        A    No, I wouldn't.  No.  If you designed it to have only

5   12 hours operation, I don't think that would be prudent.  But I

6   don't think that is what we are talking about here in this

7   rulemaking.  I don't think anybody has suggested that a system

8   be designed to use the pumps only 12 hours a day.  What is

9   being suggested in these rules is for the purposes of used and

10   useful determination, the 12-hour criteria is a good one

11   because it envelops a lot of other things besides just the

12   requirement to meet the peak demand.  Requirements that Mr.

13   Redemann has addressed very well, I think.

14        Q    Do you know of any design criteria that states wells

15   must be designed based on 12 hour a day pump time?

16        A    No.  Again, that is not what I see as the issue here.

17   We are not designing plants here.  The Commission isn't asking

18   anybody to -- isn't looking at the design of plants in this

19   particular setting here.  The design of plants and whether or

20   not they are designed properly is the purview of the DEP.  What

21   we are looking at here is how are we going to recoup money that

22   is prudently invested through the rates.

23        Q    But would it be -- and, again, this is an issue of

24   just prudence from an engineering standpoint, and you say this

25   has nothing to do with used and useful, but would it be prudent

FLORIDA PUBLIC SERVICE COMMISSION

234

1   for an engineer to design a well field to pump for only 12

2   hours a day when it could be designed to operate at 24 hours a

3   day?

4        A    No, I don't think it is prudent to design it for 12

5   hours a day.  I think I already said that.

6        Q    Have you read Mr. Jenkins' testimony?

7        A    Mr. Whose?

8        Q    Mr. Jenkins, the water management district witness.

9        A    I glanced at it.  I've got it here.

10        Q    I just want to verify whether you concur with him

11   with regard to some of his testimony.  If you could get a copy

12   of it.

13        A    I've got it.

14        Q    And I will refer you to Page 9, Lines 10 through 13.

15   In fact, I might just have you -- it is so short, maybe you

16   could just read it, and then think, and I will ask you a

17   question about it.

18        A    Lines 10 through 13 on Page 9.

19        Q    Correct.

20        A    "And the bottom line is that there is typically no

21   benefit to operating wells or a well field for a period of 12

22   hours versus 24 hours in Florida, since localized steady state

23   drawdown conditions are quickly reached and impacts are often

24   caused by regional cumulative withdrawals.  However, in some

25   cases, such as where there are localized resource impacts,

FLORIDA PUBLIC SERVICE COMMISSION

235

1   interference with existing legal uses, or saline water

2   intrusion, short-duration operation of wells can be used to

3   avoid or minimize the impacts."

4        Q    Sir, just 10 through 13.

5        A    I'm sorry.

6        Q    So, I guess if you could just look at 10 through 13

7   and just confirm whether you concur with that statement?

8        A    No, I think there are benefits.  I think that's a

9   pretty broad statement.  He says that there are no benefits,

10   and I think there are benefits.  And as I said, Mr. Redemann

11   has addressed this more directly than I have, but I certainly

12   see benefits to operating those wells on a rotating basis.

13        Q    But wouldn't the benefits and the need for such

14   reduced pumping depend on the specific system and particular

15   aquifer conditions of that area?  There may be no benefits or

16   there may be benefits depending on the specific engineering and

17   environmental considerations?

18        A    Certainly, the benefits are going to vary according

19   to the system and how it's operated and how it's designed.  But

20   what we are looking here again in this rule is a way to capture

21   the legitimate costs of a prudent design under a used and

22   useful concept, that is how do you recover the money that the

23   utility has prudently spent.  And it's not a design criteria.

24   Again, I'm saying that again.  I don't think anybody here has

25   indicated that we should design systems to operate only at 12

FLORIDA PUBLIC SERVICE COMMISSION

236

1   hours.

2        Q    Well, given Mr. Jenkins' discussion about the

3   complexities of well impacts in Florida and the numerous

4   special conditions that comprise a typical consumptive use

5   permit issued by the districts, does it not seem likely that if

6   there was a concern of over-pumpage of a well field that it

7   would be addressed as a condition of the consumptive use

8   permit?

9        A    It may or may not.  Conditions may change after the

10   permit is issued.

11        Q    Is not the water management district with their

12   expertise and staff best positioned to make those kinds of

13   judgments?

14        A    Well, they may be, but they are not in a position to

15   determine how the dollars associated with putting those wells

16   in the ground and the monies spent on those pumps is going to

17   be recovered.  That is not their bailiwick, either.  That is

18   what this Commission is doing.  And that is what I'm saying in

19   this particular case, I think when you say that -- I mean, the

20   opposite of this is what Mr. Woodcock has proposed is to base

21   it on 24 hours, and I think that is way out of line on the

22   other side.  And as I indicated in my Direct Testimony, I think

23   when you look at the consideration that has been given to other

24   factors by staff in proposing the 12-hour basis, that it goes

25   much further towards promoting a good efficient operation of

FLORIDA PUBLIC SERVICE COMMISSION

237

1   the system and recovering the dollars that are specifically

2   invested by the utility.

3        Q    If a well field is sized to meet max day demand of a

4   service area, how frequently will that well field even be

5   operating 24 hours a day, the entire well field?

6        A    I don't know.

7        Q    Likely not be?

8        A    Operating 24 hours a day every day?

9        Q    Right.

10        A    No, it won't be operating 24 hours a day every day,

11   but I don't know what the daily usage will be.

12        Q    And if a well field is designed to provide the max

13   day demand with the largest well out of service, there will

14   always be at least one well pump not operating on max day, is

15   that correct?

16        A    That's correct.

17        Q    And obviously even less pumpage on an average day?

18        A    Yes.

19        Q    All right.  All right.  I direct your attention to

20   your testimony on Page 35, and I'm looking at Lines 18 through

21   20.

22        A    Yes.

23        Q    And I think this is where you speak of staff's

24   recommendation recognizes that there are costs incurred for

25   purposes other than delivering water, and that that is the cost

FLORIDA PUBLIC SERVICE COMMISSION

238

1   of protecting the water supply, is that correct?

2        A    Yes.

3        Q    In your opinion, is the Florida Public Service

4   Commission charged with protecting the state's water supply?

5        A    Indirectly, yes, I think so.

6        Q    And in what regard?

7        A    There are criteria that utilities have to meet in

8   designing their system, and I believe that Chapter

9   367.111 indicates that utilities have to meet those criteria as

10   part of what is required of them in providing service.  So,

11   indirectly, the Commission is saying that you have to do these

12   things, whatever they are, protect the environment, provide

13   safe water, provide adequate service are all part of the things

14   that you have to do in order to meet the regulatory

15   requirements of this Commission, even though they themselves

16   are not the agency that is going to determine whether those

17   criteria are met.

18        Q    Is it not reasonable to consider the water management

19   districts with their permitting authority diligently work to

20   protect the water supply to the extent that permits issued may

21   contain specific limitations on pumping?

22        A    Sure.

23        Q    Are you aware of the water management districts

24   routinely issuing permits that limit pumping to 12 hours a day?

25        A    No, I'm not aware of what they do routinely.

FLORIDA PUBLIC SERVICE COMMISSION

239

1        Q    To change the subjects here, if we could look at Page

2   39, Lines 6 through 9.  Here you recommend that OPC's

3   recommendation to eliminate Section (7)(a) 3. and (7)(a)(b)

4   (sic) because you do not believe the proposed method is valid

5   for all size and character of systems, is that correct?

6        A    Yes.  Could I look at that?  Let me look at that part

7   of the rule.  I've got it here.

8             Right.  Those parts of the rule are the part where it

9   says if actual or max day flow data is not available,

10   1.1 gallons per minute per ERC would be used.

11        Q    And you believe that is inappropriate?

12        A    I think the 1.1 gallons per minute is pretty low,

13   because in most cases this is going to be applying to systems,

14   small systems probably don't have storage are going to be

15   having to meet, you know, peak hour or instantaneous flows.

16   And with small systems, I think that number of 1.1 is pretty

17   low, and rather than have that tied in there as a basis, I

18   would rather see it knocked out.

19             The other thing is I think there is a concern if

20   there is no maximum flow data for a utility, I think there are

21   other things that are really of more concern.  In other words,

22   I'm pretty skeptical of a situation where a utility does not

23   have maximum day flow data.

24        Q    Is one of your concerns given the vast difference

25   between systems of one size fits all as far as a default?

FLORIDA PUBLIC SERVICE COMMISSION

240

1        A    One size fits all, yes, for that particular instance

2   where we are looking at more of a peak hour instantaneous flow.

3             MR. REILLY:  Okay.  I have no further questions.

4             CHAIRMAN CARTER:  Mr. Hoffman.

5             MR. HOFFMAN:  Thank you, Mr. Chairman.

6                          CROSS EXAMINATION

7   BY MR. HOFFMAN:

8        Q    Good afternoon, Mr. Seidman.

9        A    Good afternoon.

10        Q    I'm Ken Hoffman.  I represent Aqua Utilities Florida.

11   Doesn't the Public Service Commission protect the state's water

12   supply through its rate structure authority, including the

13   authority to establish various forms of conservation rates?

14        A    Yes.  In fact, it has to do that in concert with the

15   water management districts.

16        Q    Okay.  Would you say that the Public Service

17   Commission's water and wastewater rules, including their

18   customer service billing rules and metering rules which require

19   meter accuracy within certain parameters also help to preserve

20   state water supply?

21        A    Yes.  The more metering and the more accurate the

22   metering, the better idea we have of what the flows are and can

23   control them.

24        Q    Okay.  Thank you.  Let me ask you a few questions

25   about this issue of max day demand in Subsection 7 of the

FLORIDA PUBLIC SERVICE COMMISSION

241

1   proposed rule, which you talk about on Pages 36 through 38 of

2   your testimony.  Let me let you turn to that.

3             Now, this notion of an actual maximum day as it is

4   laid out in the proposed rule, that is still less than an

5   engineer's maximum day estimate that would be used to design a

6   water treatment system, isn't that true?

7        A    That would be correct.  An engineer's design would be

8   based on a design maximum day.

9        Q    Now, in addition, for design purposes, isn't the

10   estimated maximum day rate of flow used in designing the plant

11   there to account for growth?

12        A    Please repeat that.

13        Q    Does the estimated maximum day rate of flow that an

14   engineer develops in designing a plant, does that account for

15   customer growth and operating cushion, as well as an operating

16   cushion?

17        A    Yes, because if you are designing for either a new

18   utility or an addition to a utility, you are obviously

19   designing for something in excess of what you are already

20   serving, or you wouldn't need to make the addition or you

21   wouldn't to need have the utility.  So it always has to be

22   forward-looking.

23        Q    Now, let me ask you a question based on a very simple

24   hypothetical which is assume for the purpose of this next

25   question that you have a 2007 test year and your max day is

FLORIDA PUBLIC SERVICE COMMISSION

242

1   900,000 gallons per day in 2007.  That's your test year for a

2   rate case.

3             Now, assume that two years before that in 2005 you

4   had a higher max day of 930,000.  Are you with me so far?

5        A    Yes.

6        Q    Is there ever any real justification, in your

7   opinion, for using anything less than that 930,000 gallon per

8   day maximum rate of flow in determining used and useful for a

9   water treatment plant?

10        A    I wouldn't think so.  I mean, I have been involved in

11   a lot of rate cases and this issue is something that comes up,

12   I wouldn't say very often, but it comes up often.  What do we

13   do when we have already reached a peak that is higher than the

14   peak in the test year?

15             In my way of thinking, if you have already reached a

16   peak, that means that the customers have shown a demand that

17   had to be met.  And therefore whatever, say, used and useful

18   came out as a result of that indicates what's the maximum that

19   has been put on that system to date.  Going into a test year

20   subsequently to that that has a lower demand means you are

21   going to be lowering the used and useful below an amount you

22   have already indicated was necessary.  So it kind of -- you

23   know, it leaves you backing off when you have already indicated

24   that the expenditures the utility has made were necessary.

25        Q    Is that opinion that you have just stated similar to

FLORIDA PUBLIC SERVICE COMMISSION

243

1   the notion or the fact that this Commission in the past has

2   made determinations in a rate case that a water treatment plant

3   is 100 percent used and useful, and then in a subsequent rate

4   case the demand has dropped due to the institution of

5   conservation programs, but not lowered that 100 percent used

6   and useful finding from the previous case?

7        A    Yes.  If I'm understanding you correctly, are you

8   asking me has the Commission in some cases gone ahead and

9   recognized that a drop in demand due to conservation shouldn't

10   result in a drop in used and useful?

11        Q    Yes.

12        A    Yes, I agree with that.

13        Q    Do you agree that the design criteria for a water

14   treatment plant is not dependent on a rate setting test year?

15        A    Oh, definitely not, no.

16        Q    I'm sorry?

17        A    Design is not dependent on a ratemaking test year,

18   definitely not.

19        Q    Let me ask you another hypothetical.  If you assume a

20   water system has a 6-inch diameter well that can produce

21   1,200 gallons per minute, it is a one-well system with no

22   storage.  If a four-inch diameter well will produce 500 gallons

23   per minute, but the peak demand of the customers is 600 gallons

24   per minute.  Those are the assumed set of facts.  Would it have

25   been prudent for the utility to install the 6-inch diameter

FLORIDA PUBLIC SERVICE COMMISSION

244

1   well?  Let me restate that.

2             Wouldn't it have been prudent for the utility to

3   install the 6-inch diameter well, even though the ratio of the

4   demand to capacity would be only 50 percent?

5        A    I'm going to ask you to repeat it.  I think I lost

6   something in there.

7        Q    Okay.  I think I'm going to withdraw that.

8        A    Okay.

9             MR. HOFFMAN:  That concludes my questions.

10             Thank you, Mr. Chairman.

11             CHAIRMAN CARTER:  Commissioners, any questions?

12             Staff.

13             MR. JAEGER:  Just a few questions, Chairman.

14                          CROSS EXAMINATION

15   BY MR. JAEGER:

16        Q    Mr. Seidman, could you turn to Page 19 of your

17   testimony.  And instead of me reading it, would you read Lines

18   24 through 25, and then go on to the next page and just finish

19   your answer for that, starting "on that basis."

20        A    "On that basis, one could set minimum storage

21   capacity, other than the fire flow at about 50 percent of

22   maximum day demand, with 25 percent being for equalization and

23   25 percent for emergency demand."

24        Q    Go ahead and finish the paragraph.

25        A    "Again, this is a minimum."  How far do you want me

FLORIDA PUBLIC SERVICE COMMISSION

245

1   to read?

2        Q    To the end of that answer.

3        A    "I believe Mr. Woodcock's recommendation, therefore,

4   is inadequate for purposes of calculating used and useful and

5   the proposed rule recommendation of 100 percent of maximum day

6   demand, though higher than the minimum requirement is not

7   unreasonable."

8        Q    Thank you.

9             Are you aware that lime softening reverse osmosis

10   also known as membrane softening, microfiltration, and ion

11   exchange water treatment plants need backwash water and are

12   operated for an extended period of time?

13        A    Yes.

14        Q    Would you apply the 50 percent maximum day storage to

15   these water treatment plants?

16        A    As opposed to what?

17        Q    As opposed to a higher storage, since they are --

18        A    Well, I think a higher storage for systems like that

19   would be helpful, but I don't know, you know, without knowing

20   the specifics of the system, whether it should come from

21   storage or something else.

22        Q    Going back to Page 39, I believe at the top there on

23   Line 2 you are talking about taking out (7)(a) 3., is that

24   correct?

25        A    Yes.

FLORIDA PUBLIC SERVICE COMMISSION

246

1        Q    And (7)(a)3., is that if the actual maximum day flow

2   data is not available, 1.1 gallons per minute per equivalent

3   residential connection should be used, 1.1 times ERCs, is that

4   correct?

5        A    Right.

6        Q    What do you do if there are no monthly operating

7   reports, what do you use?

8        A    Excuse me?

9        Q    What do you do if there are no monthly operating

10   reports?

11        A    I guess if I'm the DEP, I cite the utility.

12        Q    What do you do if you are the Commission and you are

13   doing a rate case?

14        A    That's a tough one.  I have never had a client in

15   that situation.  I don't know what to advise the Commission in

16   something like that.

17        Q    Wouldn't it be better to have some kind of default

18   set there in case there are not any operating reports?

19        A    It's better than nothing.  But my guess is, knowing

20   what this staff has done in other cases, if you don't provide

21   sufficient information to back up your filing, they're going to

22   deny it.

23             MR. JAEGER:  Staff has no further questions.

24             CHAIRMAN CARTER:  Commissioners?

25             Commissioner Argenziano.  A question for staff.

FLORIDA PUBLIC SERVICE COMMISSION

247

1             COMMISSIONER ARGENZIANO:  To the question, I guess,

2   of the reverse osmosis plant.  How often is it, in your

3   understanding, that the membranes need to be backwashed?

4             MR. JAEGER:  Is that question for me, Commissioner?

5   I'm sorry, I'm not used to being a witness.  I would have to

6   defer to engineers on that.  But reverse osmosis, I just know

7   that it's pretty constant, it's pretty steady.  The membranes

8   keep clogging up with filtered particles, so it's a constant

9   struggle to keep those membranes clean.

10             COMMISSIONER ARGENZIANO:  Right.  And that goes to my

11   question, wanting to figure out, I think in a smaller plant,

12   like let's say Dunedin, a reverse osmosis plant, how often --

13   that's a pretty small plant compared to others, how often that

14   backwashing would take place?  To get an understanding, because

15   the gist of your question meant something, and then to

16   understand how often they are backwashed would mean additional

17   information, additional use of that water.  I can wait.

18             CHAIRMAN CARTER:  Let's see if one of the engineers

19   can back Mr. Jaeger up on this and help him out.

20             MS. GERVASI:  Mr. Seidman, perhaps, has an answer to

21   that.  Also, Mr. Redemann will come to the stand shortly and

22   may be able to answer or address that question, as well.

23             COMMISSIONER ARGENZIANO:  The reason I ask is because

24   it adds to the question that was asked, how often -- the

25   frequency that water needs to be there.

FLORIDA PUBLIC SERVICE COMMISSION

248

1             CHAIRMAN CARTER:  Do you want to also ask --

2             COMMISSIONER ARGENZIANO:  Yes, I would love to do

3   that.  Since he is the witness right now, it would be great for

4   him to --

5             CHAIRMAN CARTER:  Fire away.

6             THE WITNESS:  With reverse osmosis, it's basically a

7   continuous operation of backwashing.

8             COMMISSIONER ARGENZIANO:  I'll wait for staff.

9             CHAIRMAN CARTER:  Thank you.

10             Commissioners, any further questions?

11             Staff, any further questions?

12             I think we are back to Mr. Friedman.

13             MR. FRIEDMAN:  Yes.  We have no redirect.  I would

14   like to move Mr. Seidman's exhibits, which are designated on

15   the Comprehensive Exhibit List as 8, 9, 10, 11, and 12 into

16   evidence.

17             CHAIRMAN CARTER:  Any objections?

18             MR. REILLY:  No objections.

19             CHAIRMAN CARTER:  Hearing known, Exhibits 8, 9, 10,

20   11, and 12 are moved in.

21             (Exhibits 8 through 12 admitted into the record.)

22             CHAIRMAN CARTER:  Any further questions for this

23   witness?  I will just say hang loose, Mr. Seidman.

24             MR. FRIEDMAN:  That's the only witness being

25   presented by Utilities, Inc.

FLORIDA PUBLIC SERVICE COMMISSION

249

1             CHAIRMAN CARTER:  Thank you, Mr. Friedman.

2             Staff, you are recognized.

3             MS. GERVASI:  Thank you, Mr. Chairman.

4             At this time staff would request that Mr. Van

5   Hoofnagle's testimony, prefiled Direct Testimony be inserted

6   into the record as though read.

7             CHAIRMAN CARTER:  And we have no objections on that,

8   do we, by either party?  Show it done.

9             MS. GERVASI:  Thank you.  And he did not have any

10   prefiled exhibits.

11             And at this time I would also request that the

12   prefiled Direct Testimony of Dwight Jenkins be inserted into

13   the record as though read.

14             CHAIRMAN CARTER:  Any objections?

15             MR. HOFFMAN:  No objections.

16             MR. REILLY:  None.

17             CHAIRMAN CARTER:  Show it done.

18             MS. GERVASI:  Thank you.  Mr. Jenkins had one

19   exhibit, and at this time I would like to offer into evidence

20   Exhibit 13.

21             CHAIRMAN CARTER:  Any objections?

22             MR. HOFFMAN:  None.

23             MR. REILLY:  None.

24             CHAIRMAN CARTER:  Show it done.

25             (Exhibit 13 admitted into the record.)

FLORIDA PUBLIC SERVICE COMMISSION

265

1             MS. GERVASI:  Staff then calls Mr. Richard Redemann

2   to the stand.  Oh, he is already there.

3             Mr. Redemann, have you been sworn?

4             THE WITNESS:  Yes, I have.

5             MS. GERVASI:  Thank you.

6                      RICHARD P. REDEMANN, P.E.

7   was called as a witness on behalf of the Staff of the Public

8   Service Commission, and having been duly sworn, testified as

9   follows:

10                         DIRECT EXAMINATION

11   BY MS. GERVASI:

12        Q    Could you please state your full name for the record?

13        A    Richard Paul Redemann, P.E.

14        Q    Have you submitted prefiled Direct Testimony in this

15   case consisting of 38 pages?

16        A    Yes.

17        Q    Do you have any changes to make to that prefiled

18   testimony?

19        A    No.

20        Q    If I were to ask you the same questions as contained

21   in your prefiled Direct Testimony today, would your answers be

22   the same?

23        A    Yes, they would.

24             MS. GERVASI:  I would like to request that the

25   prefiled Direct Testimony of Mr. Redemann be inserted into the

FLORIDA PUBLIC SERVICE COMMISSION

266

1   record as though read.

2             CHAIRMAN CARTER:  The prefiled testimony will be

3   accepted into the record as though read.

4             MS. GERVASI:  Thank you.

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

284

1   BY MS. GERVASI:

2        Q    Mr. Redemann, did you prefile or cause to be prefiled

3   Exhibits RPR-1 through RPR-8 along with your prefiled

4   testimony?

5        A    Yes.

6        Q    Do you have any changes to make to any of your

7   prefiled exhibits?

8        A    Yes.  I have one correction to make in two places on

9   my prefiled Exhibit RPR-8.  I have prepared a corrected

10   exhibit.

11             CHAIRMAN CARTER:  Hang on one second.  That is RPR-8?

12             THE WITNESS:  RPR-8, which has been handed out to the

13   parties and the Commission.

14             CHAIRMAN CARTER:  Okay.

15             THE WITNESS:  The correction is as follows on Exhibit

16   RPR-8, Page 3 of 5, the middle column, Paragraph (7)(a).  I

17   have replaced the words "change '30-day period' to 'maximum

18   month'" to "no change recommended."  Also on Exhibit RPR-8,

19   Page 4 of 5, middle of the column, Paragraph (7)(b), I replaced

20   the words "change '30-day period' to 'maximum month'" to "no

21   change recommended."

22   BY MS. GERVASI:

23        Q    Thank you.  Does that conclude the changes to your

24   prefiled exhibits?

25        A    Yes.

FLORIDA PUBLIC SERVICE COMMISSION

285

1        Q    Have you prepared a brief summary of your testimony?

2        A    Yes, I have.

3        Q    Could you please present that to the Commission at

4   this time?

5        A    Yes.  Over the years, a number of different methods

6   have been used to calculate water treatment plant used and

7   useful.  This has resulted in a substantial amount of staff,

8   utility, and ratepayer advocate time and litigation.  The

9   litigation results in substantial rate case expense, which

10   results in higher rates.

11             In 2003, in Docket 020071-WS, which was a rate case

12   for Utilities, Inc. of Florida, I testified to the Commission's

13   policy at that time on the water treatment plant used and

14   useful.  There was also testimony from the utility and Public

15   Counsel in that case.  The proposed Rule 25-30.4325 is designed

16   to codify the Commission's policy and streamline the water

17   treatment plant used and useful calculations.

18             MS. GERVASI:  Thank you.  Staff tenders the witness

19   for cross-examination.

20             CHAIRMAN CARTER:  Mr. Reilly, you're recognized.

21             MR. REILLY:  Thank you.  I'm having my engineer

22   witness just pass out a two-page Citizens' cross-examination

23   exhibit.  It is just a copy of two rules of the PSC, and I'm

24   just going to ask him a question or two about those two rules,

25   and how they might apply to our proceeding.

FLORIDA PUBLIC SERVICE COMMISSION

286

1             CHAIRMAN CARTER:  Okay.

2                          CROSS EXAMINATION

3   BY MR. REILLY:

4        Q    Mr. Redemann, I was just going to ask you very few

5   questions on this rule.  Are you familiar with this rule?

6        A    Yes, but I don't have it in my prefiled testimony.

7        Q    But I still would like to ask you a question.

8             MS. GERVASI:  Staff would like to voice an objection

9   at this point in time based on these questions having to do

10   with the AFPI rule or the service availability rule go beyond

11   the scope of the witness' prefiled testimony.

12             CHAIRMAN CARTER:  Mr. Reilly.

13             MR. REILLY:  We can just brief the rule and that's

14   fine.  It was my desire to bring before the Commissioners that

15   there is a mechanism for utilities to seek recovery of plant

16   that is not deemed used and useful, and that was the reason for

17   these one or two questions.

18             CHAIRMAN CARTER:  The objection is that it's outside

19   the scope of the rule.

20             MR. REILLY:  And in response to that, if the

21   Commission doesn't give me leave to ask a question, we will

22   just brief it in our brief.

23             CHAIRMAN CARTER:  Why don't we do that.  Let's try to

24   stay close to home base.  I mean, we kind of got off.  Let's

25   stay close to home base on this one.  You have got his

FLORIDA PUBLIC SERVICE COMMISSION

287

1   testimony, his Direct Testimony, you have got his exhibits,

2   and --

3             MR. REILLY:  The rules speak for themselves.

4             CHAIRMAN CARTER:  Okay.

5   BY MR. REILLY:

6        Q    Mr. Redemann, staff's version of the rule includes a

7   provision for using peak hour design criteria of 1.1 gallons

8   per minute per ERC for systems that do not have adequate FDEP

9   monthly operating reports?

10        A    Yes, that's correct.

11        Q    How would you define ERC?

12        A    An equivalent residential connection.

13        Q    And what does that mean to you?

14        A    That's the customer demand that is placed on the

15   system by one residential connection.

16        Q    And if you had a mobile home park with 200 ERC

17   connections and no records, this would be the provision of the

18   rule that you would use?

19        A    For a mobile home park, I would multiply it by .8.

20        Q    .8, okay.  And is that provision of applying .8 in

21   the rule or what would be the basis of making such a

22   calculation?

23        A    I believe it's in our 25-30 rule.

24        Q    So that would apply in that situation?

25        A    Yes.

FLORIDA PUBLIC SERVICE COMMISSION

288

1        Q    And, likewise, with regard to the provision using for

2   maximum day design criteria of 787.5 gallons per day per ERC of

3   actual flows, you would --

4        A    Multiply it by .8.

5        Q    For a system?

6        A    With mobile homes.

7        Q    Okay.  If I could have you refer to your testimony on

8   Page 7, Lines 24 through 25, and Lines 1 and 2 on the following

9   Page 8.  You state excluding fire flow from peak hour demand is

10   not consistent with sound engineering design, but is based on

11   FDEP permitting rules.  Is that correct?

12        A    Yes.

13        Q    Does that mean that you do not consider FDEP design

14   criteria as presented in Chapter 62-555.320 to embody sound

15   engineering design principles?

16        A    Remember, we're calculating used and useful for

17   plant, so we need to consider the design criteria, yes, but we

18   are also trying to establish a used and useful plant that is

19   put into rate base.

20        Q    But would you not assume that the DEP rules do at

21   least embody sound engineering?

22        A    We have a Commission policy and orders on the correct

23   amount of used and useful as detailed in my testimony.

24        Q    Repeat that again.

25        A    I have Commission orders and references and incipient

FLORIDA PUBLIC SERVICE COMMISSION

289

1   policy in my testimony on the proper method of used and useful.

2        Q    And that is -- and how is that responsive to the

3   question that, in fact, that constitutes sound engineering

4   principles?

5        A    Repeat your question?

6        Q    I asked you in your statement in your testimony does

7   that mean that you do not consider FDEP design criteria

8   presented in their rule to embody sound engineering principles?

9        A    Yes.  DEP does have engineering design criterion that

10   are sound engineering principles.

11        Q    Including the particular one I mentioned, which is

12   62-555.320?

13        A    Can you read the rule to me?

14        Q    That is the rule that is for design and construction

15   of public water systems.

16             CHAIRMAN CARTER:  Mr. Reilly, just let him look at it

17   and see if he is familiar with the rule, but I think we are

18   really once again getting far afield.  That's a DEP rule.  But

19   if you want to ask him about is he familiar with the rule, then

20   we will go from that.  I think you can get the same thing that

21   you are trying to accomplish by --

22             MR. REILLY:  Do you have a copy of the rule?  And in

23   his testimony he makes reference -- well, let's just take a

24   look at it here.

25             CHAIRMAN CARTER:  Do you have a copy of that rule?

FLORIDA PUBLIC SERVICE COMMISSION

290

1             THE WITNESS:  Not with me.

2             CHAIRMAN CARTER:  Staff, can you get him a copy of

3   it?

4             MS. GERVASI:  Yes, sir.

5             CHAIRMAN CARTER:  Let's take a moment here.  If we're

6   going to ask a witness a question, we need to give him some

7   information so he can respond to it.  So let's just take about

8   two minutes here and everyone just kind of exhale a little bit.

9   This may be a good point to stretch.  Let's take five minutes.

10             (Recess.)

11             CHAIRMAN CARTER:  Okay.  We are back on the record.

12             And when we left, Mr. Reilly was going to provide the

13   witness with a copy of the rule.

14             MR. REILLY:  Yes.

15   BY MR. REILLY:

16        Q    And have you had an opportunity to look at it?

17             And the limited scope, the nature of this question,

18   I'm not asking detailed questions about this DEP rule, it's

19   just the testimony that says OPC's proposal is not consistent

20   with sound engineering practices.  And then the very next

21   sentence says, "Nevertheless, it is based on DEP's permitting

22   rules regarding the capacity of the system."

23             So my simple straightforward question is do you not

24   believe that the FDEP rule embodies sound engineering

25   principles?  I guess that's the nature of it.

FLORIDA PUBLIC SERVICE COMMISSION

291

1        A    Well, the DEP rules include minimum designs.  You

2   need also to use the engineering references and guidance

3   documents attached to the DEP rule.

4             MR. REILLY:  Okay.  Enough on the DEP rule.

5             CHAIRMAN CARTER:  I'm with you.

6             MR. REILLY:  I sense that.

7   BY MR. REILLY:

8        Q    Mr. Redemann, are you aware of the likelihood of a

9   fire occurring on the annual peak demand hour of a water

10   system, that is the highest hour out of 24 hours on the highest

11   day of the 365 days?

12        A    I am not aware of that happening.

13        Q    It is highly unlikely?

14        A    Not highly unlikely because many water treatment

15   plants have the same peak day every day, so it could very

16   easily happen.

17        Q    It could very easily happen that a fire would occur

18   on the peak hour of the entire year?

19        A    Well, the peak days sometimes aren't really peak days

20   that much.  I mean, the pattern develops and the peak days

21   aren't really that -- there isn't that much change over a year,

22   of a yearly period.

23        Q    But you are not aware of any instance where that has

24   ever happened?

25        A    Not that I can recall.

FLORIDA PUBLIC SERVICE COMMISSION

292

1        Q    If there were to be a fire in the water system

2   service area, would you expect that the fire demands would tend

3   to suppress simultaneous peak demands?

4        A    If there is a fire that happens, the well pump -- I

5   mean, the pumper trucks would pull from the fire hydrants, and

6   the demand would be slightly less, because they are going to

7   put out the fire.

8        Q    Real quickly, I'm going to ask you the same questions

9   I asked Mr. Seidman if you have handy Mr. Hoofnagle's

10   testimony.

11        A    I don't have it with me right here.

12        Q    Could he be given one real quickly?

13             CHAIRMAN CARTER:  One second.  We will take one

14   second.

15             Staff, if you could provide that information to the

16   witness.  Also, while he is asking that, Mr. Hoofnagle and Mr.

17   Jenkins also, is that right, do you want them to have both of

18   those?

19             MR. REILLY:  I believe so.  I think on this witness I

20   am only asking Mr. Hoofnagle.

21             CHAIRMAN CARTER:  Oh, really?

22             MR. REILLY:  Yes.  I think it's a good idea.  Let me

23   get Mr. Jenkins' testimony just so we can all sing kum-ba-yah.

24             CHAIRMAN CARTER:  I was just anticipating.

25             THE WITNESS:  I have Mr. Hoofnagle's testimony.

FLORIDA PUBLIC SERVICE COMMISSION

293

1   BY MR. REILLY:

2        Q    And, again, I think we are looking at Page 2, Lines

3   13 through 19.  And I guess if you could just read that and

4   determine if you concur with that statement?

5        A    Thirteen through 19?

6        Q    Yes, sir.

7        A    Page 2?

8        Q    Yes, sir.

9        A    "DEP sets/establishes standards of practice and care

10   for the industry to ensure water quality.  Issues of adequacy

11   of supply related to this overriding goal of water safety and

12   quality as it might impact operating pressure and such concerns

13   as fire flow.  We do not directly oversee water supply or

14   quantity as such.  This responsibility remains with the state's

15   water management districts.  As I understand the role of the

16   PSC, it is the agency that oversees rates, customer service and

17   economic issues affecting private utilities under its

18   jurisdiction."

19        Q    And you are okay with that statement?

20        A    Yes.

21        Q    And the last question on Page 2, Lines 6 through 9,

22   this is where -- if you would just take a look at that, it

23   begins Subparagraph .320?

24        A    Subparagraph .320 is an extensive rule governing

25   design and operation of public water systems and addresses

FLORIDA PUBLIC SERVICE COMMISSION

294

1   treatment plants, pumping facilities, materials' standards,

2   ancillary well features, storage, power, tankage, distribution

3   system and plant operational issues, and safety.

4        Q    And you concur as well with that statement?

5        A    Yes.

6        Q    All right.  Changing the subject to high service

7   pumps.  Under your proposal including high service pumping with

8   storage for used and useful calculations, the capacity of the

9   high service pumps relative to system demand is not considered,

10   is that correct?

11        A    Yes.  I did a spreadsheet of pumping costs and

12   storage costs, and the pumping costs was very minimal compared

13   to storage cost.

14        Q    And define that for me, if you would?

15        A    Well, I think it was about .3 percent.

16        Q    Of total?

17        A    Pumping cost, 311.4, versus storage cost, Account

18   330.4.  So it was just minimal.

19        Q    So you just feel it is de minimis?

20        A    I don't feel like it is needed because it's a lot of

21   work and you are not getting, you know, very much value out of

22   it.

23             MR. REILLY:  Just one second.

24             CHAIRMAN CARTER:  Take your time.

25   BY MR. REILLY:

FLORIDA PUBLIC SERVICE COMMISSION

295

1        Q    In your analysis, would you believe that's really

2   true in every case concerning this cost of high service

3   pumping?

4        A    Well, apparently what's happening is either they are

5   putting them on the storage cost, or they are putting them in

6   311.2, which is the well cost, which is also pumps.  So it's

7   just not a cost-effective solution to multiply or to do the

8   high service pump calculation.  You could apply it to the

9   storage calculation.

10        Q    Let me have you refer to your testimony on Page 16,

11   Lines 18 through 19.

12        A    Has the Commission previously used the 12-hour day to

13   determine well capacity?  Yes.

14        Q    Okay.  You state in this testimony that the single

15   well system should be considered 100 percent used and useful

16   unless it appears to be oversized?

17        A    Yes, that's correct.

18        Q    How would you determine if a well is oversized?

19        A    I would need to see the calculations.  But,

20   basically, what I have done is I looked on line for well

21   capacity, and from about 80 gallons per minute to 325 gallons

22   per minute, the wells cost the same.

23        Q    And determining whether it is oversized, would be one

24   way is to look at the well's capacity relative to the system

25   demands?

FLORIDA PUBLIC SERVICE COMMISSION

296

1        A    Yes, that would be one way to do it.  You probably

2   would need to consider economies of scale.  Well, for one well,

3   we would consider that to be 100 percent used and useful.

4        Q    But if there was still some question of being

5   oversized, wouldn't you make allowances for growth, excessive

6   unaccounted for water, and, if provided, fire flow?

7        A    Well, that would all be looked at in the calculation,

8   of course.

9        Q    To determine whether it was oversized or not?

10        A    Yes.

11        Q    And those would be other factors that you would

12   consider?

13        A    Yes.

14        Q    Is that not the used and useful calculation?

15        A    That is the used and useful calculation.

16        Q    Okay.  Thank you.  Moving on to another subject.

17   This 100 percent used and useful for build-out systems.  I

18   would refer you to, I guess, the same page, 16, Lines 3 through

19   6.  Here you say that water systems that are built out with no

20   apparent potential expansion in the surrounding areas should be

21   considered 100 percent used and useful if designed prudently,

22   is that correct?

23        A    That's correct.

24        Q    How do you determine if there was no apparent

25   expansion of the service area?

FLORIDA PUBLIC SERVICE COMMISSION

297

1        A    If they had an amendment case application in.

2        Q    Excuse me?

3        A    If there was an amendment application in.  Most of

4   the systems that we see out there are fixed systems, meaning

5   they have been there for 20 or 30 years, and just are not

6   growing.  They are fully developed and built out.

7        Q    If an area is built out at least in its current

8   service territory, however, if in the surrounding area there is

9   large amount of acreage where the system has the potential to

10   grow, if and when development is economically feasible in those

11   areas, would that not still constitute a potential growth for

12   that system?

13        A    Well, I would have to see the exact area.  I mean,

14   certainly if the neighboring communities are all growing right

15   there, you might want to consider it.  But in most cases, most

16   of the utility systems, they are not growing, and the

17   agricultural land next to them has been agriculture for many,

18   many years.

19        Q    So it might depend on the zoning and the whole growth

20   patterns?

21        A    If you wanted to change the zoning, you would have to

22   get it approved by the county, of course.

23        Q    Right.  As part of evaluating if a system is

24   prudently designed, this prudent standard you mention in your

25   system, would you not also look to see if it was substantially

FLORIDA PUBLIC SERVICE COMMISSION

298

1   oversized for the service area which is now built out?

2        A    Yes.

3        Q    Now, on the subject of 24 hours versus -- a subject

4   we have talked about a lot -- 24 hours versus 12 hours, would

5   you say that a water treatment plant that is twice as big as

6   what is needed to serve its customer base at build-out is

7   prudently designed?

8        A    Twice as big?  No.  But remember, the usage patterns

9   of most customers indicate that they are not using the water 24

10   hours a day.  The water management districts, both the

11   Southwest Florida and South Water Management District, each

12   have one day watering.  So watering -- irrigation is just not

13   occurring like it used to anymore.

14        Q    Could you make -- I appreciate the clarification, but

15   was that a yes or a no on the question of whether if at the end

16   of the day and you have a built-out system and it is twice as

17   big as it needs to be, would that be an indication of it being

18   prudently designed?

19        A    Well, you would have to look at the specific

20   components of the water system.  You might have to do an

21   economies of scale adjustment, that's a possibility.

22        Q    But this would raise a question in your mind as to

23   whether it was prudently designed if that was the final result

24   at the build-out?

25        A    I would have to think about the specific situation,

FLORIDA PUBLIC SERVICE COMMISSION

299

1   but, yes, I would think about it.

2        Q    Do you know of any design criteria that states wells

3   must be designed based on 12 hours per day of pumping time?

4        A    No, but the reason that I'm using the 12 hours is

5   these systems have storage, and the water quality is generally

6   poor, they usually have an aerator on.  There is hydrogen

7   sulfide in the water.  And continually pumping that water 24

8   hours will just deteriorate the water quality.  So I'm

9   recommending that it is prudently -- it would be prudent to

10   rest the well for 12 hours to replenish the water supply to get

11   better quality of water service to the customers.

12        Q    I misspoke.  My engineer, in fact, does have a

13   question about Mr. Jenkins' testimony.  So we will do this real

14   quickly.  If you could refer to it.  And, again, I will just

15   refer you to the same area of questioning as Mr. Seidman.  I

16   guess we are looking at Page 9, Lines 10 through 13.  You don't

17   have to read it out, but just if you could refer to it and just

18   tell me whether you can agree with the statement?

19        A    I don't agree with the statement.  Because, as I

20   indicated earlier, most of the water systems that you would use

21   the 12 hours have storage, and the water quality is poor, and

22   you need aeration generally for hydrogen sulfide.  And the

23   concentration of the water, pumping it 24 hours would just

24   deteriorate the water quality.  It's really a water quality

25   issue.

FLORIDA PUBLIC SERVICE COMMISSION

300

1        Q    And is that not the type of issue that -- water

2   quality issue you say?

3        A    Water quality.  That would be the Florida Department

4   of Environmental Protection.

5        Q    Okay.  Given Mr. Jenkins' discussion about the

6   complexities of well impacts in Florida and the numerous

7   special conditions that comprise a typical consumptive use

8   permit issued by the district, does it not seem likely that if

9   there was any concern about pumpage in terms of quantity now,

10   that it would be addressed in a condition of the consumptive

11   use permit?

12        A    Yes, that would be addressed in the consumptive use

13   permit if there is saltwater intrusion.

14        Q    Now, if a well field is sized to meet the maximum day

15   demand of a service area, how frequently will that well field

16   be operating at 24 hours a day?

17        A    Probably not very frequently at all.

18        Q    And if a well field is designed to provide max day

19   demand with the largest well out of service, there will always

20   be at least one well pump not operating on the max day, is that

21   correct?

22        A    Well, the reason we take the one well out is during

23   periods of time over the years the well will need to be

24   replaced and so there may not be two wells there, there may

25   only be one well for a period of time.

FLORIDA PUBLIC SERVICE COMMISSION

301

1        Q    So the answer is -- what is the yes or no answer to

2   that?

3        A    Repeat the question?

4        Q    And if a well field is designed to provide the

5   maximum day demand with the largest well out of service, there

6   will always be at least one well pump not operating on the max

7   day, is that correct?

8        A    If one well is out of service, you will only have one

9   well, if it's a two-well system.

10        Q    Right, if it's a two-well system.  That's right,

11   obviously it has to be -- maybe my question is two or more

12   wells.

13        A    If there are two or more wells, then you would have

14   one less than however many wells you have.

15        Q    Okay.  Could you explain how water quality and

16   aerators affect well pumping?

17        A    The aerator for water quality, depending on what the

18   problem is, if it's hydrogen sulfide, the water will flow over

19   the aerator and the aerator will release the hydrogen sulfide.

20        Q    But how does it affect well pumping?

21        A    The water quality -- as you pump a well, you have a

22   draw down of the well and it concentrates the components of

23   what is inside the well, and then you get a higher

24   concentration if you continually pump the well.

25        Q    Would you say that's true for all systems everywhere?

FLORIDA PUBLIC SERVICE COMMISSION

302

1        A    No, probably that's not true for all systems.

2        Q    What about storage without aerators?

3        A    There's very few of those, but there are probably

4   some.  I can't think of any right now.  Generally speaking, the

5   reason why you have storage is because of the water quality

6   issue, particularly in the Central Florida area.

7        Q    You said you had storage because of water quality

8   issues, not because of pressure demands and --

9        A    Well, you could have it for both, yes.

10        Q    Excuse me?

11        A    You could have storage for both.

12             MR. REILLY:  Bear with us just one quick second.

13   BY MR. REILLY:

14        Q    Here is the question:  For a system that has lime

15   softening and storage, and no aeration, how does that affect

16   well pumping for 12 hours?

17        A    Well, for example, Florida Cities Water Company,

18   which is the only system I know that has lime softening, they

19   had used some of the wells some of the time, they couldn't use

20   them all at once.  That is the only lime softening plant I'm

21   aware of.

22        Q    I understand you are aware of that system, but how

23   does it affect well pumping?

24        A    Well, in that particular system, they couldn't use

25   all the wells at one time.  That had to alternate them.  The

FLORIDA PUBLIC SERVICE COMMISSION

303

1   water management district required them to do that, I believe.

2        Q    But that was done by the water management districts

3   because of the specific circumstances of that case?

4        A    Yes.

5             MR. REILLY:  Thank you.

6             That concludes my questions of Mr. Redemann.

7             CHAIRMAN CARTER:  Okay.  I believe Mr. Hoffman is

8   next.

9             MR. HOFFMAN:  Thank you, Mr. Chairman.

10                          CROSS EXAMINATION

11   BY MR. HOFFMAN:

12        Q    Good afternoon, Mr. Redemann.

13        A    Good afternoon.

14        Q    Let me ask you a question first about unaccounted for

15   water, which is on Page 11?

16             CHAIRMAN CARTER:  Excuse me, Mr. Hoffman.  I had one

17   of my over-50 moments.

18             Commissioner Argenziano, the question that you had, I

19   forgot it, but I did remember that you had a question.

20             COMMISSIONER ARGENZIANO:  Thank you.  Just to find

21   out, and I'm sure it varies from plant-to-plant, whether it's

22   ocean seawater or brackish, but do you have an estimate on how

23   often a plant -- and I'm sure the gallonage has to be

24   incorporated in there, also -- how often the reverse osmosis

25   membranes need to be backwashed?

FLORIDA PUBLIC SERVICE COMMISSION

304

1             THE WITNESS:  I don't recall exactly, but probably --

2   usually they are set on timers and stuff, or when the pressure

3   builds up, then they have to go into automatic backwash.  So I

4   would estimate maybe 10 percent of the water, maybe 15 percent,

5   if I recall correctly.

6             COMMISSIONER ARGENZIANO:  How often?

7             THE WITNESS:  Well, they are on a pressure cycle, so

8   when the pressure builds up, it turns on and off.  So, maybe

9   what you are asking is how much time they are --

10             COMMISSIONER ARGENZIANO:  No.  No.  I think in the

11   interim I found out the answer myself, and it really depends on

12   what type of facility.  There is a plant in -- the Diablo plant

13   in California, which has also reverse osmosis, or seawater

14   desalination for drinking water as well as cooling water, and

15   I'm finding out, and I'm going to place a call to them, and

16   finding out they haven't even backwashed their filters yet.

17   There was no need.

18             But, yet, the City of Dunedin, I think, uses about

19   130 gallons to backwash every 48 hours.  So it is just

20   dependent.  But, that is what I really wanted to know was the

21   frequency, and I guess it depends on what type of plant, where

22   it is located, and what technology, whether it is new or older

23   technology.

24             Thank you.

25             CHAIRMAN CARTER:  Thank you, Commissioner.

FLORIDA PUBLIC SERVICE COMMISSION

305

1             Mr. Hoffman, sorry to interrupt, but I had one of my

2   over-50 moments there.

3             MR. HOFFMAN:  Thank you, Mr. Chairman.

4   BY MR. HOFFMAN:

5        Q    Mr. Redemann, a question about unaccounted for water,

6   which is addressed at least in part on Page 11 of your prefiled

7   testimony.

8        A    Yes.

9        Q    Okay.  On Page 11, Lines 2 through 5, there is a

10   sentence there that states, "For those water system with

11   unaccounted for water in excess of 10 percent, where the

12   utility has not taken steps to reduce the water loss, a

13   reduction in peak demand and chemical and electrical expenses

14   and purchased water should be made."

15             My question is, would you agree that where

16   unaccounted for water is in excess of 10 percent, and the

17   utility has taken such steps to reduce the water loss, that a

18   reduction in peak demand and chemical and electrical expenses

19   and purchased water should not be made?

20        A    Yes, that's correct.  What I'm really looking for is

21   for the utility to contact the Florida Rural Water Association,

22   and they have circuit riders around the state that help the

23   utilities find unaccounted for water.  Other times it's a

24   metering issue, or they actually have the equipment to find the

25   leaks along with the water management district.  So before you

FLORIDA PUBLIC SERVICE COMMISSION

306

1   come in for a rate case, it would be a good idea for those

2   systems that are over 10 percent to have the water management

3   district -- I mean, the Florida Rural Water Association find

4   the leaks and make a recommendation on the system and what

5   needs to be done.

6        Q    And your testimony is that when a utility has taken

7   those steps under these circumstances that there should not be

8   a reduction in peak demand and chemical and electric expenses

9   and purchased water, correct?

10        A    That would probably be correct.  It all depends on

11   what the Florida Rural Water Management recommends.  It may be,

12   you know, replacement meters or something like that, so it just

13   depends on what they recommend.

14        Q    Let me ask you a question or two about peak day and

15   how that is determined under the proposed rule.  That is

16   Subsection 7 of the proposed rule, and you talk about it on

17   Page 5 of your testimony.  Just a couple of questions on this.

18             Would you agree that if the maximum day has an

19   unusual occurrence, that for consistency the Commission should

20   turn to the next highest day that does not have an unusual

21   occurrence?

22        A    Well, I have done that before.  I have used the

23   second highest day if there was no unusual occurrence.

24   Recently we have just used the five-day maximum average, but I

25   have used that in the past.

FLORIDA PUBLIC SERVICE COMMISSION

307

1        Q    And in your expert opinion, then, either methodology

2   would be appropriate?

3        A    Yes, either methodology would be reasonable.

4        Q    And would you agree that when a five-day average is

5   used, and this is simply a matter of math, when a five-day

6   average is used, the utility will not recover the cost for the

7   max day in the test year?

8        A    It all depends if there was a previous rate case and

9   the system was 100 percent used and useful the last time, then

10   I would recommend that it be 100 percent again.  It just

11   depends on the situation.

12        Q    Okay.  Let me try a hypothetical with you that sort

13   of addresses Subsection 4 of the rule, which is the instances

14   where a water treatment system is considered 100 percent used

15   and useful, and you get into this on Page 16 of your testimony.

16             Are you with me, Mr. Redemann?

17        A    Yes.

18        Q    If you would assume that a utility's water system has

19   a peak demand of 600 gallons per minute; and then assume,

20   secondly, that a four-inch well has a peak capacity of

21   500 gallons per minute.  So that is less than the peak demand

22   of the customers.  And then assume that a six-inch well has a

23   peak capacity of 1,200 gallons per minute.  Those are my three

24   facts for my hypothetical.

25             Now, you would agree, would you not, that in order

FLORIDA PUBLIC SERVICE COMMISSION

308

1   for the utility to meet its obligation to serve it would have

2   to use that six-inch well, correct?

3        A    Yes.

4        Q    And would you agree that under the proposed rule,

5   which you support Subsection (4)(a), that that six-inch well

6   would be 100 percent used and useful?

7        A    That is correct.

8             MR. HOFFMAN:  Thank you.  Those are all the questions

9   I have.

10             Thank you, Mr. Chairman.

11             CHAIRMAN CARTER:  Mr. Friedman.

12             MR. FRIEDMAN:  I have none.

13             CHAIRMAN CARTER:  Commissioners?  Staff?

14             MS. GERVASI:  We have no redirect.

15             CHAIRMAN CARTER:  Okay.  Then let's take care of some

16   housekeeping matters.

17             MS. GERVASI:  Staff would move Exhibits 14 through

18   20, and Exhibit 21 as revised.

19             CHAIRMAN CARTER:  Any objections?  Hearing none,

20   Exhibits 13, 14, 15, 16, 17, 18, 19, 20, and 21, correct?

21             MS. GERVASI:  And 21 as revised, yes, sir.

22             CHAIRMAN CARTER:  Show it done.

23             MS. GERVASI:  Thank you.

24             (Exhibits 14 through 20, and 21 as revised, admitted

25   into the record.)

FLORIDA PUBLIC SERVICE COMMISSION

309

1             MS. GERVASI:  And it appears at this time this would

2   be the appropriate time for Public Counsel to move in the

3   Rebuttal Testimony of Mr. Woodcock.

4             MR. REILLY:  I do so move.

5             CHAIRMAN CARTER:  No objections?  Show it done.  That

6   would be exhibit -- I guess we will need to start on another

7   list, then.

8             MS. GERVASI:  That would be Rebuttal Testimony, and I

9   don't believe he had any exhibits to his rebuttal, is that

10   correct?

11             MR. REILLY:  That is correct.

12             CHAIRMAN CARTER:  Okay.

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

326

1             MS. GERVASI:  So that brings us to the Surrebuttal

2   Testimony of Mr. Guastella.

3             CHAIRMAN CARTER:  Hang on one second.  Let me get my

4   notes together here.

5             MS. GERVASI:  Sure.

6             CHAIRMAN CARTER:  Mr. Hoffman, you are recognized,

7   sir.

8             MR. HOFFMAN:  Thank you, Mr. Chairman.  Aqua

9   Utilities Florida would recall Mr. Guastella.

10                          JOHN F. GUASTELLA

11   was called as a surrebuttal witness on behalf of Aqua Utilities

12   Florida, and having been duly sworn, testified as follows:

13                         DIRECT EXAMINATION

14   BY MR. HOFFMAN:

15        Q    Good afternoon, Mr. Guastella.

16        A    Good afternoon.

17        Q    Are you the same John Guastella who prefiled prefiled

18   Direct Testimony in this proceeding?

19        A    Yes.

20        Q    And did you prepare and cause to be filed three pages

21   of prefiled Surrebuttal Testimony in this proceeding?

22        A    Yes.

23        Q    Do you have any changes to your Surrebuttal

24   Testimony?

25        A    No.

FLORIDA PUBLIC SERVICE COMMISSION

327

1        Q    If I asked you the questions that were contained in

2   your prefiled Surrebuttal Testimony this afternoon, would your

3   answers be the same?

4        A    Yes.

5             MR. HOFFMAN:  Mr. Chairman, I would ask that Mr.

6   Guastella's prefiled Surrebuttal Testimony be inserted into the

7   record as though read.

8             CHAIRMAN CARTER:  Your prefiled Surrebuttal Testimony

9   will be entered into the record as though read.

10             MR. HOFFMAN:  Thank you, Mr. Chairman.

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

331

1   BY MR. HOFFMAN:

2        Q    Mr. Guastella, have you also attached one exhibit to

3   your Surrebuttal Testimony?

4        A    Yes.

5        Q    And that is Exhibit JFG-4?

6        A    Correct.

7             MR. HOFFMAN:  Mr. Chairman, I believe that this

8   particular Exhibit JFG-4 has been premarked for identification

9   as Exhibit 22.

10             CHAIRMAN CARTER:  You're correct.

11   BY MR. HOFFMAN:

12        Q    Mr. Guastella, do you have a brief summary of your

13   prefiled Surrebuttal Testimony?

14        A    Yes.  Basically my testimony simply covers fire flow

15   requirements and sources for those determinations.

16             MR. HOFFMAN:  Thank you.  The witness is available

17   for cross.

18             CHAIRMAN CARTER:  Mr. Reilly, you are recognized.

19             MR. REILLY:  Yes, sir.

20                          CROSS EXAMINATION

21   BY MR. REILLY:

22        Q    Just a few questions where I'm going to try to

23   understand any differences and compare your JFG-2 exhibit filed

24   with your Direct Testimony versus this JFG-4, which was filed

25   with your Rebuttal Testimony.  Just so that I can make sure I

FLORIDA PUBLIC SERVICE COMMISSION

332

1   understand how these two references work with each other, is it

2   true that JFG-2 is considering population, the level of

3   population amounts in determining fire flow rates?

4        A    That's one of the tables that is included in JFG-2.

5        Q    And if I'm going to the right place, would that be

6   on -- well, this is an excerpt, but it would be Page 16 of

7   JFG-2?  It looks to be a table.

8        A    Yes.  The Page 16 you are referring to is the Page 16

9   out of the standard schedule for grading cities and towns.

10        Q    Just one of the excerpts.  Now, this JFG-2, it's a

11   1956 National Board of Fire Underwriters reference, is that

12   correct?

13        A    That was the latest edition at that time, yes.

14        Q    Now, if I could have you look at this most recent

15   exhibit, JFG-4, and is it titled -- let's see, it says AMMA.

16   Is that actually AWWA you mean to say?  Is that a

17   typographical --

18        A    Yes, that is a typographical error.

19        Q    And that's excerpts from M-5 manual?

20        A    That's correct.

21        Q    And my question, if I could direct your attention to

22   a certain page on there so you could help me understand where

23   this later reference, how it affect your first reference.  And

24   I believe I need to direct your attention to -- I guess it's

25   Page 22, but it is also an excerpt.  And it's the page dealing

FLORIDA PUBLIC SERVICE COMMISSION

333

1   with fire flow requirements, is that correct?  Are you on that

2   page?

3        A    Page 22?

4        Q    It's in the top left corner of the page, and it is

5   right after -- well, it is many pages back, but it's just --

6   well, it's Chapter 4 dealing with fire protection.

7        A    Well, there are two.  In Exhibit JFG-4 there are two.

8   One of them is water utility management manual for AWWA, which

9   has a Chapter 4, and then there was a subsequent water

10   management report by AWWA.  So that in both AWWA water

11   management training course in water management, one refers to

12   the grading schedule and another refers to an updating of the

13   fire flow requirements by ISO.

14        Q    Okay.  The first part of your JFG-4, and it is on the

15   second page right after your cover page, it says water utility

16   management, AWWA.  That's an excerpt, and what is the date?

17   The date on that is 19 -- I'm sorry.

18        A    1959 copyright date.

19        Q    That is the second page, and I didn't speak

20   correctly.  That's a training course in water utility

21   management.  That's the first part, is that correct?

22        A    That's one of the excerpts that I'm including which

23   refers to the standard schedule for grading cities and towns,

24   which is JFG-3, as one of the most generally accepted standards

25   for public fire protection.

FLORIDA PUBLIC SERVICE COMMISSION

334

1        Q    And if you move from your cover page to the third

2   page over, there is a Chapter 4, fire protection.  And what is

3   the date of this little excerpt that you have pulled out and

4   underlined all of this language?  What is the date of this

5   particular part of your JHG-4?

6        A    The first page is a training course in water utility

7   management, and that extends from the first, second, third,

8   fourth, fifth, sixth, seventh, and eighth pages, so that's all

9   part of the first reference by AWWA to the standard schedule

10   that is shown in my Exhibit JFG-3.  And then there is a second

11   part to Exhibit 4, which states water utility management, AWWA

12   Manual M-5, and that also consists of a number of pages.  That

13   refers to Exhibit JFG-2 that I included in my Direct Testimony.

14   So the American Water Works Association has recognized both the

15   older grading schedule in JFG-3 and the more recent schedule of

16   ISO in Exhibit JFG-2.

17        Q    I might be able to help you to an answer on this.  I

18   just saw here the copyright 1959 on that second page of the

19   first reference.

20        A    Correct.

21        Q    And then later attached to this is apparently a much

22   newer reference, and it is, in fact, also talking about the

23   same chapter, Chapter 4, fire protection, is that correct, but

24   it just seems to be a lot newer?

25        A    Well, this is copyright 1999.  So the AWWA has

FLORIDA PUBLIC SERVICE COMMISSION

335

1   recognized the older version in the 1959 copyright, and the

2   more recent version of ISO requirements in the 1999 copyright.

3        Q    But this later one is, in fact, the far newer one as

4   compared to 1959?

5        A    1999 is newer than 1959.

6        Q    And now that we have established that, if you could

7   just move on to the second reference, the newer reference, AWW.

8   There is a couple of sentences in there I just want you to help

9   explain to me.  And, of course, it is right on our subject,

10   fire flow requirements.  And it's found on -- well, it is

11   excerpted Page 22, the top left corner.  And what I'm drawing

12   your attention to is the first couple of sentences that follow

13   the word fire flow requirements.  And if you could read those

14   first two sentences.

15        A    "Another important change in the schedule is the

16   method of estimating required fire flow.  The formula, based on

17   population, included in the schedule since it was first

18   published has been eliminated.  The calculation" --

19        Q    That's good enough.  Just those two sentences.  My

20   question is is, in fact -- or give me your interpretation of

21   what that sentence means to you, concerning the applicability

22   of population as being a valid basis?

23        A    Well, the grading schedule -- this recognized that

24   over the course of many years, scores of years, the

25   population -- the table containing fire flows for various

FLORIDA PUBLIC SERVICE COMMISSION

336

1   populations were a good reliable estimate.  As times have

2   changed, the ISO has gone to a specific formula for specific

3   buildings.  So whether you use the population as a guide or

4   whether you use the specific formula regardless of population,

5   you still come up with a reasonable level of required fire

6   flow.

7             In both instances the AWWA states that it

8   specifically generally recognizes as the most acceptable

9   standard for fire flow requirements is the ISO or its

10   predecessor.  This is what I rely on in performing many fire

11   flow requirements and studies.  That's accepted generally

12   around the country as the most generally and widely accepted

13   method is using the ISO formula, whether it is the older one or

14   the newer one.

15        Q    I appreciate that clarification of your position, but

16   my narrow question is by virtue of this language, am I

17   interpreting it correctly to mean that this has been eliminated

18   as one of the factors, the population?

19        A    That's correct.  They no longer use population, they

20   use a different formula.

21             MR. REILLY:  Okay.  Thank you.

22             CHAIRMAN CARTER:  Okay.  Mr. Friedman.

23             MR. FRIEDMAN:  I have no questions.

24             CHAIRMAN CARTER:  Thank you.

25             Commissioners, any questions?  Staff.

FLORIDA PUBLIC SERVICE COMMISSION

337

1             MR. JAEGER:  Staff has no questions.

2             CHAIRMAN CARTER:  Mr. Hoffman.

3             MR. HOFFMAN:  No redirect.

4             CHAIRMAN CARTER:  Okay.  Let's take care of our

5   housekeeping chores here.

6             MR. HOFFMAN:  Mr. Chairman, Aqua would move Exhibit

7   22.  We would note the correction to the title of the cover

8   page to AWWA M-5 manual excerpts, and ask that that be admitted

9   into the record.

10             CHAIRMAN CARTER:  Any objection?

11             MR. REILLY:  No objections.

12             CHAIRMAN CARTER:  Show it done.

13             MR. HOFFMAN:  Thank you.

14             (Exhibit 22 admitted into the record.)

15             CHAIRMAN CARTER:  Staff.

16             MS. GERVASI:  Staff knows of no other matters that

17   need to be attended to at this time.  I would simply note that

18   the transcript of today's hearing is due on February 5th,

19   followed by post-hearing briefs on February 19th for a

20   post-hearing agenda of April the 8th.

21             CHAIRMAN CARTER:  Okay.  Let me, first of all, thank

22   the attorneys and the witnesses for their courtesy and the

23   professionalism that you conducted yourself today here in our

24   hearing.

25             Commissioners, anything for the good of the order?

FLORIDA PUBLIC SERVICE COMMISSION

338

1             Any other matters, staff?

2             MS. GERVASI:  None that we are aware of.

3             CHAIRMAN CARTER:  Hearing none, we are adjourned.

4             (The hearing concluded at 4:06 p.m.)

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

339

1   STATE OF FLORIDA    )

2                       :              CERTIFICATE OF REPORTER

3   COUNTY OF LEON      )

4

I, JANE FAUROT, RPR, Chief, Hearing Reporter Services

5   Section, FPSC Division of Commission Clerk, do hereby certify

that the foregoing proceeding was heard at the time and place

6   herein stated.

7             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

8   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

9   proceedings.

10             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

11   or employee of any of the parties' attorney or counsel

connected with the action, nor am I financially interested in

12   the action.

13             DATED THIS 29th day of January, 2008.

14

15             ___________________________________________

JANE FAUROT, RPR

16                   Official FPSC Hearings Reporter

(850) 413-6732

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION