283

1                              BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3       In the Matter of:

DOCKET NO. 090505-EI

4

REVIEW OF REPLACEMENT FUEL COSTS

5       ASSOCIATED WITH THE FEBRUARY 26,

2008 OUTAGE ON FLORIDA POWER &

6       LIGHT'S ELECTRICAL SYSTEM.

________________________________/

7

8                               VOLUME 3

9                        Pages 283 through 506

10              ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

11               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

12

13       PROCEEDINGS:     HEARING

14       COMMISSIONERS

PARTICIPATING:   CHAIRMAN NANCY ARGENZIANO (via phone)

15                        COMMISSIONER LISA POLAK EDGAR

COMMISSIONER NATHAN A. SKOP

16                        COMMISSIONER DAVID E. KLEMENT

COMMISSIONER BEN A. "STEVE" STEVENS III

17

DATE:            Thursday, March 18, 2010

18

TIME:            Commenced at 9:30 a.m.

19                        Concluded at 12:35 p.m.

20       PLACE:           Betty Easley Conference Center

Room 148

21                        4075 Esplanade Way

Tallahassee, Florida

22

REPORTED BY:     LINDA BOLES, RPR, CRR

23                        JANE FAUROT, RPR

Official FPSC Reporters

24                        850-413-6734/850-413-6732

25       APPEARANCES:     (As heretofore noted.)

FLORIDA PUBLIC SERVICE COMMISSION

284

1                              I N D E X

2                              WITNESSES

3

NAME:                                   PAGE NO.

4

5       TERRY J. KEITH

6       Direct Examination by Mr. Ross            289

Prefiled Direct Testimony Inserted        291

7       Cross Examination by Ms. Kaufman          297

8       DAVID E. DISMUKES

9       Direct Examination by Mr. Beck            300

Prefiled Direct Testimony Inserted        303

10       Errata Sheet to Prefiled Direct Inserted  343

Cross Examination by Mr. Butler           350

11       Cross Examination by Ms. Bennett          381

Redirect Examination by Mr. Beck          396

12

J.A. STALL

13

Direct Examination by Mr. Ross            401

14       Prefiled Rebuttal Testimony               403

Cross Examination by Ms. Bradley          408

15       Cross Examination by Ms. Kaufman          416

Cross Examination by Mr. Young            417

16       Redirect Examination by Mr. Ross          438

17       GERARD J. YUPP

18       Direct Examination by Mr. Butler          439

Prefiled Rebuttal Testimony Inserted      442

19       Cross Examination by Mr. Beck             446

Cross Examination by  Ms. Bradley         448

20       Cross Examination by Ms. Kaufman          448

Cross Examination by Mr. Young            452

21       Redirect Examination by Mr. Butler        458

22       WILLIAM E. AVERA

23       Direct Examination by Mr. Butler          460

Prefiled Rebuttal Testimony Inserted      463

24       Cross Examination by Mr. McGlothlin       481

Cross Examination by Ms. Bradley          485

25       Cross Examination by Mr. Young            488

FLORIDA PUBLIC SERVICE COMMISSION

285

1                              WITNESSES

2

NAME:                                           PAGE NO.

3

4       TERRY J. KEITH

5       Direct Examination by Mr. Ross                    491

Prefiled Rebuttal Testimony Inserted              493

6       Cross Examination by Ms. Kaufman                  501

7

8

9

10

11

12

13

14

15

16       CERTIFICATE OF REPORTER (Boles)                   505

17       CERTIFICATE OF REPORTER (Faurot)                  506

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

286

1                              EXHIBITS

2       NUMBER:                                 ID.    ADMTD.

3       11  DED-1                               302       399

4       12  DED-2                               302       399

5       13  DED-3                               302       399

6       14  DED-4                               302       399

7       15  DED-5                               302       399

8       16  DED-6                               302       399

9       17  DED-7                               302       399

10       18  DED-8                               302       399

11       19  DED-9                               302       399

12       20  DED-10                              302       399

13       21  DED-11                              302       399

14       22  DED-12                              302       399

15       23  GJY-10                              441       460

16       24  GJY-11                              441       460

17       25  GJY-12                              441       460

18       39                                      359       400

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

287

1                         P R O C E E D I N G S

2                 (Transcript follows in sequence from

3       Volume 2.)

4                 COMMISSIONER SKOP:  Good morning.  I'd like to

5       reconvene this hearing.  And I believe Chairman

6       Argenziano is joining us by phone.  Can you hear us,

7       Chairman Argenziano?

8                 CHAIRMAN ARGENZIANO:  Yes, I can.  Thank you.

9       Good morning.

10                 COMMISSIONER SKOP:  I hope you're feeling

11       better.

12                 Where we left off, Commissioners, yesterday,

13       we had finished with the direct testimony of Dr. Avera,

14       and I believe that leaves us one additional witness,

15       Witness Keith.  I think Commissioner Stevens had some

16       additional questions that may require recalling a panel

17       of witnesses, so we'll take it from there.

18                 And just for planning purposes, I'm hopeful

19       that we can break for lunch from 12:00 to 1:00 and

20       conclude the hearing in a reasonable time in early

21       afternoon.  So with that, Mr. Butler, you're recognized

22       to call your next witness.

23                 MR. BUTLER:  Thank you.  Commissioner Skop,

24       before we introduce Mr. Keith, I was going to make a

25       brief statement about kind of the division between

FLORIDA PUBLIC SERVICE COMMISSION

288

1       Dr. Avera and Mr. Yupp on this question of the

2       eight-hour system average calculation.  It sounds like

3       you may be envisioning a panel of them, in which case it

4       will be moot.  If you are going to do the panel, I won't

5       bother you with the division of labor.  If you are not

6       planning on the panel but asking them separately, I'd

7       like to make just a brief statement about the division

8       between the two.

9                 COMMISSIONER SKOP:  You're recognized for the

10       statement, and I'll yield to my colleagues as to whether

11       they want to have a panel to ask their questions.  But

12       you're recognized.

13                 MR. BUTLER:  Thank you.  Let me just briefly

14       describe what, you know, how we intend that Dr. Avera's

15       and Mr. Yupp's testimony divide that subject up.

16                 Dr. Avera addresses questions about the policy

17       rationale for FPL's use of system average rather than

18       nuclear avoided cost.  He can also address the rationale

19       for limiting the calculation to the period following the

20       Flagami transmission event when the transmission

21       disturbance had significantly impacted FPL's ability to

22       operate its generating system to meet customer load.

23                 Mr. Yupp addresses questions about why eight

24       hours is the proper measure of how long it took for

25       FPL's generating system to stabilize operationally after

FLORIDA PUBLIC SERVICE COMMISSION

289

1       the Flagami transmission event, and he also addresses

2       how FPL performed the system average calculation for

3       those eight hours to derive a replacement power cost of

4       of $2,024,035.  Hopefully that distinction will help.

5       And of course if the Commission's preference is to have

6       a panel of the two, we'll certainly accommodate that.

7                 Thank you.

8                 COMMISSIONER SKOP:  Thank you, Mr. Butler.

9       And then also just one additional housekeeping matter.

10       Yesterday you extended the professional courtesy I

11       believe to Ms. Bradley from the AG to ask additional

12       questions of Mr. Stall when he comes back on rebuttal,

13       so hopefully we can take care of that.  I know

14       Ms. Bradley is going to be joining us a little bit late

15       today.  So with that, if you could call your next

16       witness.

17                 MR. BUTLER:  Thank you.

18                 MR. ROSS:  FPL calls Terry Keith.  Mr. Keith

19       is in the witness chair.  He was sworn yesterday.

20                 COMMISSIONER SKOP:  Very well.

21                            TERRY J. KEITH

22       was called as a witness on behalf of Florida Power &

23       Light Company and, having been duly sworn, testified as

24       follows:

25                          DIRECT EXAMINATION

FLORIDA PUBLIC SERVICE COMMISSION

290

1       BY MR. ROSS:

2            Q.   Would you please state your name and business

3       address?

4            A.   Terry J. Keith, 9250 West Flagler Street,

5       Miami, Florida 33174.

6            Q.   Mr. Keith, have you prepared and caused to be

7       filed direct testimony in this proceeding totaling five

8       pages?

9            A.   Yes, I did.

10            Q.   Do you have any changes or corrections to your

11       direct testimony?

12            A.   One correction.  On Page 1, Line 5, it now

13       reads January 13th, 2009.  It should be January 13th,

14       2010.

15            Q.   Mr. Keith, if I asked you the questions

16       contained in your direct testimony as you just corrected

17       it, would your answers be the same?

18            A.   Yes, it would.

19                 MR. ROSS:  Mr. Chairman, I request that the

20       direct testimony of Mr. Keith as corrected be entered

21       into the record as if read.

22                 COMMISSIONER SKOP:  The prefiled testimony of

23       the witness will be entered into the record as though

24       read.

25

FLORIDA PUBLIC SERVICE COMMISSION

296

1       BY MR. ROSS:

2            Q.   Mr. Keith, have you prepared a summary of your

3       direct testimony?

4            A.   Yes.

5            Q.   Would you please provide that summary to the

6       Commission?

7            A.   Sure.  Good morning, Commissioners.  My

8       testimony encourages you to consider the long-standing

9       fuel adjustment clause process which allows for

10       fluctuations in costs, including refunds, to flow

11       through the true-up mechanisms without the need for a

12       one-time refund.  This process has served customers and

13       utilities fairly over the years without prejudice, it

14       limits changes to customer bills and it's very

15       efficient.

16                 On the other hand, if you decide in this case

17       a one-time refund to customers is more appropriate, in

18       order to implement the refund as soon as possible, I

19       recommend that the refund should be issued to customers

20       of record during the first billing cycle beginning

21       60 days after the credit amount is determined.  This

22       concludes my summary.  Thank you.

23                 MR. ROSS:  We tender the witness for

24       cross-examination.

25                 COMMISSIONER SKOP:  Thank you, Mr. Ross.

FLORIDA PUBLIC SERVICE COMMISSION

297

1                 Mr. McGlothlin, you're recognized for

2       cross-examination.

3                 MR. McGLOTHLIN:  OPC has no questions for this

4       witness.

5                 COMMISSIONER SKOP:  Excuse me?  I'm sorry.

6                 MR. McGLOTHLIN:  No questions.

7                 COMMISSIONER SKOP:  All right.  Thank you.

8                 Ms. Kaufman, you're recognized.

9                 MS. KAUFMAN:  Thank, you, Commissioner.  Good

10       morning.

11                          CROSS EXAMINATION

12       BY MS. KAUFMAN:

13            Q.   Mr. Keith, I just have one question for you.

14       You would agree with me, wouldn't you, that if the

15       Commission requires a one-time refund within 60 days

16       after the issuance of the order, that the customers

17       would receive whatever amount the Commission deems

18       appropriate more quickly than if that amount is rolled

19       into the fuel adjustment proceedings?

20            A.   Yes.  I would agree.

21                 MS. KAUFMAN:  Thank you.

22                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

23                 And, again, I don't know if the AG will be

24       joining us, so we'll go out of sequence.  Staff, any

25       questions for the witness?

FLORIDA PUBLIC SERVICE COMMISSION

298

1                 MR. YOUNG:  No questions.

2                 COMMISSIONER SKOP:  Okay.  Commissioners?

3                 COMMISSIONER STEVENS:  Just one.

4                 COMMISSIONER SKOP:  Commissioner Stevens,

5       you're recognized.

6                 COMMISSIONER STEVENS:  On Page 2 of the

7       testimony on Line 6 you state that "This is the most

8       efficient means to implement a one-time credit."  What's

9       the fairest means?

10                 THE WITNESS:  Commissioner, I think either way

11       that you would do the one-time credit there's the

12       potential for, the unintended potential for some, one

13       customer to benefit versus another customer.  So I'm not

14       sure that there's necessarily a fairness issue, and

15       that's why I result to what's the quickest way to get

16       the money back to the customer if you want to do a

17       one-time credit.

18                 COMMISSIONER STEVENS:  Do you know how many

19       customers this will be credited to, how many accounts?

20                 THE WITNESS:  Approximately 4.5 million

21       accounts.

22                 COMMISSIONER STEVENS:  So it would be all of,

23       all of FPL accounts?

24                 THE WITNESS:  Yes, sir.

25                 COMMISSIONER STEVENS:  All of the customers

FLORIDA PUBLIC SERVICE COMMISSION

299

1       were affected by this outage?

2                 THE WITNESS:  No.  That's not quite the way

3       the fuel adjustment clause works.

4                 COMMISSIONER STEVENS:  So we look at it

5       through the fuel adjustment because all the customers

6       were affected by that cost.

7                 THE WITNESS:  Right.  That's correct.

8                 COMMISSIONER STEVENS:  Okay.  Thank you.

9                 THE WITNESS:  What -- okay.

10                 COMMISSIONER SKOP:  Thank you, Commissioner.

11       Any additional questions from the bench?  Hearing none,

12       Mr. Ross, you're recognized for redirect.

13                 MR. ROSS:  No redirect.

14                 COMMISSIONER SKOP:  Thank you.  And I believe

15       we have no exhibits for this witness.

16                 MR. ROSS:  That's correct.

17                 COMMISSIONER SKOP:  So, Mr. Keith, you're free

18       to step down and we'll see you for rebuttal.

19                 THE WITNESS:  Thank you.

20                 COMMISSIONER SKOP:  All right.  I think that

21       brings us to the close of FPL's witnesses' direct

22       testimony.  And I think, Commissioner Stevens, at your

23       discretion, I think you had additional questions

24       yesterday.  And if you'd like to recall one or more

25       witnesses, you're free to do so at this time.

FLORIDA PUBLIC SERVICE COMMISSION

300

1                 MR. BUTLER:  Commissioner Skop, I'm sorry.  I

2       just, I would offer that we certainly, if it's more

3       efficient, can have Commissioner Stevens ask the

4       questions of those witnesses on rebuttal or recall them

5       now, whichever is your preference.

6                 COMMISSIONER SKOP:  Okay.

7                 COMMISSIONER STEVENS:  Rebuttal is fine.

8                 COMMISSIONER SKOP:  Okay.  I'll defer to that.

9       Any additional questions from the bench?

10                 Okay.  Hearing none, Public Counsel, you're

11       recognized to call your witness.

12                 MR. BECK:  Thank you, Commissioner.  The

13       citizens call Dr. David Dismukes.

14                 COMMISSIONER SKOP:  And, Dr. Dismukes, have

15       you been sworn previously?

16                 THE WITNESS:  Yes, sir.

17                 COMMISSIONER SKOP:  All right.  Thank you.

18                          DAVID E. DISMUKES

19       was called as a witness on behalf of the Citizens of the

20       State of Florida and, having been duly sworn, testified

21       as follows:

22                          DIRECT EXAMINATION

23       BY MR. BECK:

24            Q.   Dr. Dismukes, would you please state your full

25       name.

FLORIDA PUBLIC SERVICE COMMISSION

301

1            A.   David E. Dismukes.

2            Q.   By whom are you employed?

3            A.   I'm an independent consultant.

4            Q.   And have you prepared direct testimony in this

5       case consisting of 40 pages?

6            A.   Yes, sir, I have.

7            Q.   And do you have an errata sheet to your

8       testimony?

9            A.   Yes, sir.

10            Q.   If I were to ask you the same questions that

11       are contained in your testimony with the changes noted

12       in the errata sheet, would your answers be the same?

13            A.   Yes, sir, they would be.

14                 MR. BECK:  I would ask that Dr. Dismukes'

15       testimony be inserted into the record as though read.

16                 COMMISSIONER SKOP:  The prefiled testimony of

17       the witness will be entered into the record as though

18       read.

19       BY MR. BECK:

20            Q.   And, Dr. Dismukes, you also have 12 exhibits

21       accompanying your testimony, do you not?

22            A.   Yes, sir, I do.

23            Q.   And those have been marked -- or you have them

24       in your testimony as DED-1 through 12?

25            A.   Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

302

1                 MR. BECK:  And, Commissioners, those have been

2       marked as Exhibits 11 through 22 in the staff's

3       Comprehensive Exhibit List for identification.

4                 (Exhibits 11 through 22 marked for

5       identification.)

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

344

1       BY MR. BECK:

2            Q.   Have you prepared a summary of your testimony?

3            A.   Yes, sir, I have.

4            Q.   Would you please provide it?

5            A.   Yes, sir.

6                 Good morning, Commissioners.  The purpose of

7       my testimony is to address one of the two issues you

8       heard about at the beginning of the proceeding, which is

9       the estimation and calculation of the replacement cost

10       credit that is due to FPL's ratepayers from the February

11       outage.  And I think it's important to draw that out

12       early and to make that, that differentiation.  This

13       isn't a prudence recommendation.  This isn't a

14       disallowance.  This is an appropriately determined

15       credit that will go back to FP&L's customers as a

16       consequence of those February outages.

17                 Now as you've, you've discerned probably from

18       the testimony yesterday and having read the testimony of

19       the company's witnesses, there's a significant

20       difference in the calculations of those credits.  The

21       company is proposing roughly about $2 million.  My

22       estimate is somewhere around $15.9 million, $16 million.

23                 The difference in that has to do with two

24       primary reasons.  One is the duration of the outage

25       period that you're looking at for the replacement cost

FLORIDA PUBLIC SERVICE COMMISSION

345

1       credit.  The second has to do with the avoided fuel that

2       you're looking at to assess and determine what that

3       credit is.

4                 The company, as you've heard from yesterday,

5       would like you to make a decision based on a system

6       average cost in determining that credit.  My

7       recommendation is that you would do it as you

8       traditionally would do it, and that is looking at the

9       avoided fuel cost for the unit that was out, which would

10       be the nuclear fuel cost.

11                 Now the company's defense for this is really,

12       it's not that big a difference, I think as you heard

13       yesterday from some of the cross-examination and some of

14       the questions about the numbers.  I mean, the numbers

15       kind of fall out in very similar fashions.  There's not

16       a lot of disagreement in terms of what the purchased

17       power amount is.  There's not a lot of disagreement in

18       terms of what the peaking units were for the eight

19       hours.  There's not a lot of disagreement in terms of

20       how to determine what that system average cost is.

21       There's not a lot of differences in terms of figuring

22       out what the avoided nuclear fuel cost is.  It's really

23       an issue of how you put those things together to

24       determine the replacement cost credit.

25                 The company would like to use a system average

FLORIDA PUBLIC SERVICE COMMISSION

346

1       for determining that credit based on two primary

2       defenses:  One is a fairness issue and the other is on

3       what it believes to be sound economic and regulatory

4       principles.  And my testimony addresses both of those

5       issues I think at length.  I think the better half of my

6       prefiled testimony addresses both those issues in

7       detail.

8                 I mean, clearly on its face the issue of

9       fairness certainly is questionable.  I mean, to have an

10       estimate that's $16 million and to offer to pay only

11       $2 million of that I think certainly challenges a

12       fairness and equity issue.  I mean, 50/50 may have some

13       grounds to that, maybe 75/25 may have some grounds to

14       fairness.  But to, to suggest that you're only going to

15       make a credit payment of about 12.5 percent is certainly

16       not along the lines of being fair, particularly to

17       FP&L's ratepayers.

18                 If you look at sound economics and regulatory

19       policy, I don't think either of, any of the company's

20       suggestions would match up with either of those.  If you

21       think about this from a, from an economics perspective

22       and just from an efficiency perspective and you consider

23       the fact that, that customers have paid more than normal

24       in a prior period because of the outage, their

25       consumption has been reduced as a consequence of that

FLORIDA PUBLIC SERVICE COMMISSION

347

1       and they've lost consumer welfare for that.  And what

2       your job is to do in the second period is to provide a

3       credit that makes them whole for that amount.

4                 Now if my consumption has been reduced in this

5       period and I don't get the full benefit for it in the

6       second period, there's a loss in consumer welfare there

7       and there's a cost to society.  And there's no

8       efficiency gain there and there's nothing consistent

9       with economic principles by doing something like that.

10                 The second thing and a more contemporaneous

11       idea in economic principles would be this idea that I

12       talk about in my testimony in terms of moral hazard.

13       And moral hazard fits into the area of risk and

14       uncertainty and information economics, and it's one upon

15       which a lot of performance-based regulatory principles

16       are based.  And if you go in -- and the basic

17       fundamental principles behind this are that if you

18       provide insurance to a party, they will behave

19       differently with that insurance than without that

20       insurance.  And you may have some familiarity with this

21       with the banking crisis recently, the too big to fail

22       issues where some have argued that going in and

23       providing the bailouts to big banks further stimulates

24       the types of risky activities that they got themselves

25       in trouble with to begin with.

FLORIDA PUBLIC SERVICE COMMISSION

348

1                 So if you think about this from a regulatory

2       perspective, do you want to provide insurance to a

3       company for outages and costs that they will not incur

4       because of those outages and to encourage that type --

5       or to reduce the cost of those types of outages on a

6       forward-going basis and what are the regulatory

7       implications associated with that?

8                 The other thing in terms of regulatory policy,

9       you heard some discussion yesterday about the fuel

10       adjustment clause, and I think a grossly

11       mischaracterized representation of how that process

12       works to suggest the fact that, that, that it's all

13       benefits for ratepayers and no benefits to the company.

14                 I think anybody that's familiar with natural

15       gas prices and the movement that they've had since 2005

16       knows that there's benefits associated with fuel

17       adjustment clauses.  It insulates the utilities from the

18       risk of bearing those costs and those shifts in

19       commodity, in commodity prices that they use for the

20       fuel that they pass through to their ratepayers.  So

21       there is a very significant benefit to the company by

22       having that fuel adjustment clause in place, and it's

23       certainly not one-sided.

24                 In addition, ratepayers pay for those lower

25       cost fuel assets through their base rates and they

FLORIDA PUBLIC SERVICE COMMISSION

349

1       provide the company a return on and of that investment.

2       You can't look at the fuel clause and the fuel rates

3       alone without thinking about its corresponding cost in

4       base rates as well.  So there is a, there is a price

5       that's paid for those lower cost fuel assets, and those

6       are through your base rates.  And there's certainly

7       benefits for the company associated with having that as

8       well.

9                 The other big issue that the company has

10       raised is that this would provide disincentives

11       associated with developing nuclear and renewable fuels.

12       When you think about nuclear power plants, they are very

13       capital intensive assets.  A small replacement credit

14       cost of $16 million relative to an eight plus billion

15       dollar investment is a small amount.  In my opinion and

16       my experience, I have never heard replacement cost

17       issues come up as an issue associated with making

18       generation planning decisions, particularly with regards

19       to nuclear power plants.

20                 When you think about renewable power, you have

21       the same types of issues.  I've never heard replacement

22       power come up as an issue associated with these assets

23       as well.  And for most of these assets, they have a

24       number of other economic attributes that create

25       challenges from a regulatory perspective that go well

FLORIDA PUBLIC SERVICE COMMISSION

350

1       beyond the issues that are in this proceeding today.

2       And a lot of that has to do with how you're going to

3       make up that uneconomic differential between traditional

4       assets and a renewable asset.  So that's the first

5       hurdle that would ever have to be crossed if you're

6       talking about investments in renewable energy.

7                 That concludes my summary, and I'd be happy to

8       answer any questions, Mr. Chairman.

9                 MR. BECK:  Dr. Dismukes is tendered for

10       cross-examination.

11                 COMMISSIONER SKOP:  Thank you, Mr. Beck.

12                 FPL is recognized for cross-examination.

13                 MR. BUTLER:  Thank you, Mr. Chairman.

14                          CROSS EXAMINATION

15       BY MR. BUTLER:

16            Q.   Good morning, Dr. Dismukes.

17            A.   Good morning.

18            Q.   I'll start by asking you a few questions about

19       your background.  Are you trained as a nuclear engineer?

20            A.   No, sir.

21            Q.   I'm sorry.  I didn't hear you.

22            A.   No, sir.

23            Q.   No, sir?  Okay.  And have you ever worked at a

24       nuclear power plant?

25            A.   No, sir.

FLORIDA PUBLIC SERVICE COMMISSION

351

1            Q.   Okay.  You don't hold any licenses from the

2       Nuclear Regulatory Commission to operate a nuclear power

3       plant, do you?

4            A.   No, sir.

5            Q.   Okay.  And have you ever been responsible for

6       managing the operation of a nuclear power plant?

7            A.   No, sir.

8            Q.   Okay.  Did you speak to any of FPL's plant

9       operators regarding the, either the nuclear units coming

10       down following the Flagami transmission event or work

11       done to bring those units back online after the event?

12            A.   No, sir.

13            Q.   Okay.  And I believe you have not visited

14       FPL's Turkey Point nuclear power plant; is that right?

15            A.   That is correct.

16            Q.   Okay.  You also haven't visited FPL's Flagami

17       transmission substation?

18            A.   No, sir.

19            Q.   Excuse me.  In connection with your deposition

20       I asked you to bring copies of any testimony you filed

21       or previously provided that addresses the manner of

22       calculating a utility's replacement power or replacement

23       fuel cost.  And am I correct that you have no documents

24       responsive to that request?

25            A.   That's correct.

FLORIDA PUBLIC SERVICE COMMISSION

352

1            Q.   And are you making any claim in your testimony

2       that the Turkey Point nuclear units were operated

3       imprudently?

4            A.   No, sir.  And I don't think that's the issue

5       in this case.  It's really determining what the

6       replacement cost credit should be to ratepayers.  It's

7       not a prudence investigation and my recommendation is

8       not based upon a disallowance.

9            Q.   Based on the information you have received,

10       understanding your just answer -- the answer you just

11       gave, do you have any reason to believe that the Turkey

12       Point nuclear units could have been safely returned to

13       service more rapidly than they were following the

14       Flagami transmission event?

15            A.   I do not.  And, again, the purpose of my

16       testimony isn't to recommend a prudence disallowance to

17       the Commission.

18            Q.   Okay.  Understood.  I'm just wanting to

19       establish for the record and for the benefit of the

20       Commissioners kind of the parameters of what you are and

21       aren't asserting.

22                 Do you have personally any information to base

23       an objection to FPL's decision that it would repair the

24       Turkey Point Unit 3 rod position indicator system during

25       the outage that was initiated by the Flagami

FLORIDA PUBLIC SERVICE COMMISSION

353

1       transmission event?

2            A.   I do not have a position.  And, again, the

3       purpose of my testimony wasn't to go in and micromanage

4       what the, what the company did during those outages.  It

5       was to determine what the appropriate replacement cost

6       credit should be for ratepayers.

7            Q.   In connection with your deposition, I also

8       asked you to bring copies of any orders or opinions in

9       which a regulatory body has concluded that a utility is

10       responsible for replacement power costs associated with

11       the full duration of a power plant outage without regard

12       to whether imprudence on the part of the utility caused

13       the entire outage.  Do you remember that?

14            A.   Yes, sir, I do.

15            Q.   Am I correct that you are aware of no such

16       documents?

17            A.   That is correct.

18            Q.   Excuse me.  Are you aware of any cases where

19       the Florida Public Service Commission has disallowed

20       replacement power costs for an outage at a power plant

21       when there has been no finding of imprudence with

22       respect to the operation or maintenance of that power

23       plant?

24            A.   I'm not aware of any orders.

25            Q.   I would ask you the same question with respect

FLORIDA PUBLIC SERVICE COMMISSION

354

1       to utility regulatory commissions in other states.  Are

2       you aware of any case where a utility regulatory

3       commission in another state has disallowed replacement

4       power costs for an outage at a power plant when there

5       has been no finding of imprudence with respect to the

6       operation or maintenance of that plant?

7            A.   I'm not aware of any orders.

8            Q.   Okay.  The NRRI article that you cite in your

9       testimony states on Page 3 that, and I quote, regulators

10       are legally bound to allow costs -- or, I'm sorry, allow

11       utilities the opportunity to recover prudently incurred

12       costs.  Prudent costs reflect utility management that

13       makes rational and well-informed decisions, end quote.

14       Am I correct that you agree with that statement?

15            A.   I do.  But the purpose of my testimony isn't

16       to offer a prudence disallowance.  It's to offer a

17       replacement cost credit.

18            Q.   Are you familiar with the Commission's, this

19       Commission's order Number 23232?

20            A.   I don't have the numbers memorized, so can you

21       help me and let me know what that is about?

22            Q.   I see Ms. Bennett is about to do what I had

23       hoped she would, which is to pass out copies of it.

24       Thank you, Ms. Bennett.

25                 COMMISSIONER SKOP:  Mr. Butler, are we going

FLORIDA PUBLIC SERVICE COMMISSION

355

1       to be marking this as Exhibit Number --

2                 MR. BUTLER:  It is an order of this

3       Commission.  I don't feel a need to mark it as an

4       exhibit, if others don't.  I think it's readily

5       accessible.

6                 COMMISSIONER SKOP:  Okay.  Very well.  Thank

7       you.

8       BY MR. BUTLER:

9            Q.   Now having the order before you, seeing that,

10       seeing what it says, are you familiar with this order

11       that involved a, an outage of Turkey Point nuclear units

12       in 1989?

13            A.   Yes, sir, I'm familiar with it.

14            Q.   Okay.  Excuse me.  Would you agree that in

15       Order 23232 the Commission directed FPL to refund to

16       customers replacement power costs associated with Turkey

17       Point Unit 3 being offline for the period March 21 to

18       31, 1989?

19            A.   It's my understanding there was a disallowance

20       associated with the operation of the plant.

21            Q.   You're not familiar with the time period of

22       the disallowance or of the nuclear plants, the sort of

23       total duration of the outage that was in question?

24            A.   I know that it was for part of the period that

25       the plant was out, but not the entire period.

FLORIDA PUBLIC SERVICE COMMISSION

356

1            Q.   Well, would you accept, subject to check, that

2       Turkey Point Unit 3 did not actually return to service

3       until June 24, 1989?

4            A.   I can agree to that, subject to check.

5            Q.   Actually, let me do this.  It's probably

6       better.  If you'll turn to Page 4.  If you'll look at

7       the paragraph that somebody has helpfully marked with a

8       line down the right side.  So that's good.  It helps.

9       Thank you, Ms. Bennett.  There is a reference to Unit 3

10       returning to service on June 24, 1989.  Do you see that?

11            A.   I do.

12            Q.   Okay.  So would you agree that in this case

13       the Commission limited the refund that it required FPL

14       to make to customers to a period of three days out of a

15       nearly two-month long outage?

16            A.   I can agree to that, subject to check.

17            Q.   And are you aware that the Commission gave as

18       a reason for limiting the refund to that three-day

19       period that, quote, even though management was

20       responsible for the outage, replacement fuel costs were

21       prudently incurred commencing April 1?

22            A.   I can agree to that, subject to check.  That's

23       my understanding.

24            Q.   Okay.  So would you agree that in that order

25       at least the Commission parsed the outage, disallowed

FLORIDA PUBLIC SERVICE COMMISSION

357

1       replacement power costs with respect to a period of

2       time, three days, in which it found that the company was

3       responsible for the replacement power costs because it

4       had not acted prudently, but then did not disallow fuel

5       costs for the period thereafter, from April 1 through

6       June 24, 1989?

7            A.   Yes, sir, I agree.  But the circumstances in

8       this proceeding are different than those.  I mean, that

9       was a prudence investigation associated with the

10       operation of the plant.  This is an investigation

11       associated with determining the replacement cost credit

12       that goes to ratepayers and how that credit will be

13       assessed to those ratepayers.

14            Q.   And as I believe you said earlier, your

15       testimony is the same irrespective of any finding with

16       respect to prudence; is that right?

17            A.   My testimony is not based on an imprudence

18       finding and it's not recommending a disallowance.  It's

19       recommending an appropriately determined replacement

20       cost credit to ratepayers.

21            Q.   Are you also familiar with the Commission's

22       Order Number PSC-09-0024-FOF-EI, which I'm going to

23       refer to that as Order 0024 for simplicity?

24            A.   Yes, sir.

25                 MR. BUTLER:  Okay.  And, Ms. Bennett, do you

FLORIDA PUBLIC SERVICE COMMISSION

358

1       have a copy of --

2                 THE WITNESS:  I have a copy, Mr. Butler.

3       BY MR. BUTLER:

4            Q.   Do you have a copy of it?

5            A.   Yeah.  Go ahead.

6            Q.   Okay.  Thank you.

7                 And this is the order that dealt with what's

8       been referred to yesterday as the drilled hole incident;

9       is that right?

10            A.   That is correct.

11            Q.   Would you agree that in Order 0024 the

12       Commission required FPL to refund replacement power

13       costs associated with a five-day extension of a planned

14       refueling outage due to what I'll, what we're calling

15       the drilled hole incident?

16            A.   Yes, sir.

17            Q.   So, conversely, would you agree that Order

18       0024 did not allow -- disallow any of the outage time

19       prior to the five-day extension?

20            A.   That's my understanding.

21            Q.   Okay.  Are you aware of any decisions of this

22       Commission requiring FPL to refund replacement power

23       costs other than Order 23232?  I'm sorry.  I put one too

24       many numbers in there, I think.  Order 23232 and Order

25       0024.

FLORIDA PUBLIC SERVICE COMMISSION

359

1            A.   I'm not aware of any.

2            Q.   Okay.  Are you familiar with the Louisiana and

3       Texas order, orders for which Public Counsel has asked

4       this Commission to take official notice?

5            A.   Yes, sir.

6                 MR. BUTLER:  Okay.  Mr. Chairman, I have an

7       excerpt from the Louisiana order that I think it

8       probably would be useful to identify as an exhibit just

9       for clarification.

10                 COMMISSIONER SKOP:  Very well.  I think the

11       exhibit number will be 39.  And a short title, please.

12                 MR. BUTLER:  Short title is Excerpt from

13       Louisiana PSC Decision.

14                 COMMISSIONER SKOP:  Thank you.

15                 (Exhibit 39 marked for identification.)

16       BY MR. BUTLER:

17            Q.   Dr. Dismukes, before focusing on the excerpt

18       that I handed you, I'd like to ask you just more

19       generally, based on your familiarity with the, excuse

20       me, these orders, is it your understanding that both

21       orders arose out of the same series of outages at the

22       River Bend nuclear power plant operated by Gulf States

23       Utilities?

24            A.   Yes, sir.

25            Q.   Two separate regulatory jurisdictions in which

FLORIDA PUBLIC SERVICE COMMISSION

360

1       power was provided in both jurisdictions, so they had

2       decisions based on the same outage; correct?

3            A.   Yes, sir.  That's correct.

4            Q.   Okay.  Do you know if any of the River Bend

5       outages that are the subject of those two orders was the

6       result of an off-site transmission disturbance?

7            A.   It's my understanding the transmission-created

8       outage was onsite.

9            Q.   All right.  Okay.  That's a good segue to the

10       excerpt that I had provided you.  If you would look in

11       what's been marked as Exhibit 39 and focus on what's

12       marked at the top as Page 26 of 33.

13            A.   Okay.

14            Q.   And this describes the explosion of a B

15       preferred transformer.  Do you see that?

16            A.   Yes.

17            Q.   And is that the event you were just referring

18       to as an onsite transmission disturbance?

19            A.   Yes, sir.

20            Q.   Okay.  I think you already said this, but just

21       let me clarify or confirm.  You would agree that the B

22       preferred transformer was located on the River Bend

23       power plant site; correct?

24            A.   Yes, sir.  That's correct.

25            Q.   Okay.  Is it your understanding that the

FLORIDA PUBLIC SERVICE COMMISSION

361

1       B preferred transformer was not used in day-to-day

2       operations of the River Bend power plant, but rather had

3       a specific role in providing startup power to the plant?

4            A.   That's my understanding, that it's used for

5       plant use.

6            Q.   Okay.  So would you agree that the B preferred

7       transformer served a specialized function that was

8       directly tied to operation of the River Bend plant?

9            A.   That's my understanding, but I don't know with

10       certainty if that is the case.

11            Q.   Okay.

12            A.   I mean, it may, it may have additional

13       purposes there for the area around the town.  I don't

14       know.  I think the order would suggest that's the case.

15       I'm not trying to be argumentative, but I just don't

16       know.

17            Q.   Would you agree that in evaluating

18       consequences of the B preferred transformer explosion,

19       the Louisiana PSC did not disallow replacement power

20       costs for the full time that the River Bend plant was

21       offline following the explosion, but rather disallowed

22       replacement power costs for half of the outage duration?

23            A.   I would agree it was some, some portion of the

24       outage period.  Again, I think this differs from the

25       proceeding that we're engaged in today, which is to look

FLORIDA PUBLIC SERVICE COMMISSION

362

1       at a replacement cost credit.  It's not a prudence

2       investigation.  It wasn't my understanding from the

3       company's testimony that its $2 million recommendation

4       was a finding of imprudence on its behalf.

5            Q.   Would you agree that it was very broadly

6       characterized or summarized FPL's testimony that FPL is

7       seeking to achieve or strike a fairness balance in the

8       allocation of the replacement power costs between

9       customers and the utility, shareholders?

10            A.   I would agree that that's the, that's the goal

11       of the company's recommendation, but that has nothing to

12       do with prudence.

13            Q.   Would you turn to Page 28 of 33 in the

14       Louisiana PSC order.

15            A.   Okay.

16            Q.   I'd like to ask you about the paragraph, the

17       short paragraph that is immediately above Topic C,

18       impact of River Bend outages, where it starts, "The

19       Commission finds that Gulf States' imprudence."  Do you

20       see that?

21            A.   Yes, sir.

22            Q.   Excuse me.  I'd like you to read the last

23       sentence of that paragraph, the second sentence.

24                 (Pause.)

25                 I'm sorry. I meant to read aloud.

FLORIDA PUBLIC SERVICE COMMISSION

363

1            A.   Oh, okay.  "The Commission finds that Gulf

2       States' imprudence caused one-half the delay resulting

3       from the B transformer explosion.  This ruling

4       adequately balances the competing considerations in this

5       issue."  Where the competing considerations, as I

6       understand it, were the differences of opinion on what

7       was prudent and what was imprudent associated with the

8       transformer outage.

9            Q.   Thank you.

10                 Your testimony has some discussion about

11       pricing signals sent to customers.  I want to ask you

12       just a few questions about the subject of realtime

13       pricing.  Excuse me.  We covered this in your

14       deposition.  I'm trying to summarize this to not take a

15       lot of time.

16                 Is it your understanding that under the

17       Florida fuel adjustment clause, the fuel factors for

18       what I'll call year three reflect projected fuel cost

19       for year three, and estimated/actual true-up of fuel

20       cost for year two, and a final true-up of fuel cost for

21       year one?

22            A.   That's correct.

23            Q.   Okay.  And isn't it also correct that the fuel

24       factors under the Florida fuel adjustment clause are

25       uniform or levelized over the year in which they apply?

FLORIDA PUBLIC SERVICE COMMISSION

364

1            A.   That's correct.

2            Q.   And so wouldn't you agree that the fuel

3       factors under the Florida fuel adjustment clause are

4       substantially removed from the concept of realtime

5       pricing for fuel at any particular point in time within

6       the year when the factors are applied?

7            A.   That's correct.  I don't think they're

8       designed to be a realtime pricing signal.

9            Q.   Okay.  I'd like to turn to the subject briefly

10       of, excuse me, incentives and disincentives created by

11       fuel adjustment mechanisms and their application.

12                 Would you agree that a utility regulatory

13       commission's decision on what types of costs it will

14       allow to be recovered through a fuel adjustment clause

15       will influence utility decisions?

16            A.   What do you mean by utility decisions?  That's

17       pretty broad.

18            Q.   The utility's management decisions in how it's

19       going to operate, you know, build and operate its

20       system.

21            A.   I'm not aware of how fuel adjustment clause

22       decisions impact generation planning decisions.  I'm not

23       aware of anything of that nature.

24            Q.   Would you turn to -- do you have a copy of

25       your deposition available?

FLORIDA PUBLIC SERVICE COMMISSION

365

1            A.   I do.

2            Q.   Would you turn to Page 28 in the transcript of

3       it?  If you'll look on Line 12 in the deposition, I

4       asked you the question, "If a regulatory commission has

5       a particular approach to determining whether fuel costs

6       that are subject to a cost tracker are going to be

7       disallowed, will the way that the Commission decides

8       whether or not costs will be disallowed, is that

9       something that could be an incentive or a disincentive

10       to the utility's decision?"  And you answered, "I would

11       stand by my prior answer.  I mean, to the extent that

12       the utility commission defines the rules by which the

13       fuel cost to recover in a tracker is going to influence

14       utility decisions."  Do you see that?

15            A.   I do.

16            Q.   Do you disagree with the answer that you gave

17       at your deposition?

18            A.   I don't see that that has anything to do with

19       generation planning decisions.  Can you help me where,

20       where we discussed that in the prior parts of those

21       questions?  Because I think that was the nature of the

22       question you asked me earlier.

23            Q.   When you answered the question, because I was

24       using your words, "influence utility decisions," in the

25       deposition, how were you using the term?

FLORIDA PUBLIC SERVICE COMMISSION

366

1            A.   Well, I think if you go up to Line 4 and 5, we

2       were talking about trackers from a general perspective

3       and I was referring to that answer, and I said that

4       regulatory parameters define how cost trackers will work

5       and influence utility decisions.

6                 I think if you go to the prior page, we had

7       similar discussions and we were talking mostly about

8       fuel and how utilities would make expenditures relative

9       to fuel.  I don't think we were discussing anything

10       about how utilities would make generation planning

11       decisions, and that was the premise of the question that

12       you asked me earlier.

13            Q.   So when you answered this question in your

14       deposition, in spite of the context of this case, you

15       didn't understand your answer about utility decisions to

16       include decisions with respect to operation and

17       construction of power plants and fuel that are consumed

18       in them?

19            A.   Mr. Butler, you asked me earlier about

20       generation planning decisions.  And I answered the

21       questions in this deposition and I'm answering the

22       questions now as you ask them to me, and they had

23       nothing to do with generation planning.

24            Q.   Okay.  So what did you have in mind when you

25       were referring to influence or being an incentive or a

FLORIDA PUBLIC SERVICE COMMISSION

367

1       disincentive to the utility's decisions?  I mean those

2       are your words.  Those decisions --

3            A.   Those are my words.

4            Q.   I'm sorry.

5            A.   We were talking about decisions associated

6       with fuel expenditures.

7                 MR. BUTLER:  Excuse me.  Mr. Chairman, I had

8       not completed my question.

9                 COMMISSIONER SKOP:  Okay.  Mr. Butler, you can

10       complete your question.  And I'd ask the parties to

11       relax and we'll get to the bottom of this.  You're

12       getting a little testy there.

13                 MR. BUTLER:  Thank you.

14       BY MR. BUTLER:

15            Q.   Dr. Dismukes, you know, your words are that,

16       excuse me, you know, the Commission defines the rules by

17       which fuel cost to recover in a tracker is going to

18       influence utility decisions.  I'm just asking you what

19       did you mean by "utility decisions" when you used the

20       term in your deposition?

21            A.   In how it purchased and procured fuel.

22            Q.   Nothing about how it would actually consume

23       the fuel then?

24            A.   Excuse me?  I didn't hear that.

25            Q.   I said nothing about how it would actually

FLORIDA PUBLIC SERVICE COMMISSION

368

1       consume the fuel then?

2            A.   Well, you purchase fuel to consume it.

3            Q.   Okay.  I'd ask you -- now I'd like to change,

4       switch subjects about, still in the area of incentives

5       and disincentives, and ask you to compare a utility's

6       risk of disallowance for a replacement power cost

7       between a nuclear unit and a combined cycle unit.  Would

8       you agree that in general it takes longer to bring a

9       nuclear unit back online after an unplanned outage than

10       is the case for a combined cycle unit?

11            A.   Yes, sir.  That's the case.

12            Q.   Would you also agree that in general the net

13       replacement power cost, meaning the difference between

14       the cost for replacement power on a unit that is offline

15       and the avoided cost of fuel not consumed for the

16       offline unit, is higher for a nuclear unit than for a

17       combined cycle unit?

18            A.   Yes, sir.  On a fuel cost basis that would be

19       the case.

20            Q.   Would you agree that both of these factors,

21       the longer time to return a nuclear unit to service

22       after an unplanned outage and the higher net replacement

23       power cost for a nuclear unit, are added vulnerabilities

24       that a utility has to accept if it decides to build

25       nuclear units?

FLORIDA PUBLIC SERVICE COMMISSION

369

1            A.   Yes, sir.

2            Q.   Now I'd like to ask you a, to consider a

3       hypothetical.  Suppose that a utility is deciding

4       whether to build a nuclear unit or a combined cycle

5       unit.  It's in a regulatory jurisdiction where the

6       utility will be allowed to recover the capital costs for

7       either type of unit.  But if the unit goes offline for

8       any reason, there's a 50/50 chance that the utility

9       won't be able to recover the net replacement power costs

10       for that unit, recognizing in advance this is a pretty

11       abstract hypothetical.

12                 In that hypothetical situation, would you

13       agree that the utility's incentive would be to build a

14       combined cycle unit so that the amount of net

15       replacement power costs that are at risk would be lower?

16            A.   I think the utility would have an obligation

17       to develop in a regulatory environment the resource that

18       provided the least cost net present value revenue

19       requirement.

20            Q.   Okay.  Would you agree that a business, any

21       business including a utility that's looking at a

22       calculus of what the revenue requirements for various

23       options might be needs to take into account the risks

24       associated with the various options?

25            A.   Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

370

1            Q.   Are you aware of any experts who have taken

2       the view that high net replacement power costs

3       attributable to low fuel cost generation does not affect

4       investor perception of risk associated with a utility's

5       future investments in that type of generation?

6            A.   Can you start with that, the beginning part of

7       that question?  Am I aware of experts that have argued

8       that position?

9            Q.   I'm sorry.  I'll reread it.

10                 Are you aware of any experts who have taken

11       the view that high net replacement power costs

12       attributable to low fuel cost generation does not affect

13       investor perception of risk associated with a utility's

14       future investments in that type of generation?

15            A.   I haven't done a survey of expert witness

16       positions to be able to tell you.

17            Q.   Okay.  Are you aware of any financial rating

18       agencies that have taken that same view?

19            A.   Again, I haven't done any surveys.  I can't

20       answer that question.

21            Q.   Would your answer be the same with respect to

22       financial analysts?

23            A.   Yes, sir.

24            Q.   And would your answer be the same with respect

25       to equity investors in electric utilities?

FLORIDA PUBLIC SERVICE COMMISSION

371

1            A.   Yes, sir.

2            Q.   Okay.  Would you agree that fuel adjustment

3       clauses which allow utilities to pass through their

4       actual fuel costs to reduce the risk to the utility of

5       underrecovering fuel costs -- I'm sorry.  Let me start

6       over again.  Strike that.

7                 Would you agree that fuel adjustment clauses

8       which allow utilities to pass through their actual fuel

9       costs reduce the risk to the utility of underrecovering

10       fuel costs in the event that fuel costs turn out to be

11       higher than expected?

12            A.   Yes, sir.

13            Q.   Would you also agree that such a fuel cost

14       isolates the utility from any potential benefits of

15       recovering more than its actual cost if fuel costs turn

16       out to be lower than expected?

17            A.   Utilities do not gain from fuel adjustment

18       clauses generally.  In some instances, fuel clauses have

19       performance incentives embedded in them associated with

20       fuel use or generator performance like the PSC has here,

21       or they may have a provision where they can share the

22       gains on off-system sales like the Commission does here

23       in Florida.  So there are some opportunities for gain,

24       for gains in those, in those clauses.

25            Q.   But subject to those two fairly narrow

FLORIDA PUBLIC SERVICE COMMISSION

372

1       exceptions, would you agree generally that if a

2       utility's fuel costs in Florida go down, it returns the

3       benefit of that in the sense of charging the lower

4       actual fuel costs to customers?

5            A.   I would agree that when fuel costs go down,

6       the utility is expected to pass those along to its

7       ratepayers.

8            Q.   Okay.  Now in contrast, isn't it true that if

9       a company owns a nuclear unit and sells its output on a

10       merchant basis at market prices, the company would be

11       able to profit from those sales any time that the low

12       nuclear fuel cost is below the market price at which it

13       sells?

14            A.   Can you ask that again?  That was -- I didn't

15       get the first part of that.

16            Q.   Sorry.  Yeah.  Certainly.  Isn't it true that

17       if a company owns a nuclear unit and sells its output on

18       a merchant basis at market prices, the company would be

19       able to profit from those sales any time that the low

20       nuclear fuel cost is below the market price at which it

21       sells?

22            A.   Merchant plants tend to make a gain when their

23       internal costs are less than the market clearing price.

24            Q.   And would you agree that fuel costs for

25       nuclear plants have been well below the marginal power

FLORIDA PUBLIC SERVICE COMMISSION

373

1       cost for most, excuse me, for most power markets over

2       the last several years?

3            A.   Yes, sir.  That's the case.

4            Q.   Does a regulated utility that provides its

5       nuclear generated power to retail customers under a

6       pass-through fuel clause have a comparable opportunity

7       to profit from the difference between the low nuclear

8       fuel cost and the higher marginal power cost?

9            A.   Only to the extent they make an off-system

10       sale and are allowed to share gains in that.

11            Q.   Let me ask you a couple of questions about

12       your testimony on moral hazard.

13            A.   Yes, sir.

14            Q.   Are you aware of any instance in which FPL

15       acted irresponsibly with respect to taking Turkey Point

16       Units 3 and 4 offline following the Flagami transmission

17       event?

18            A.   No, sir.  And the purpose of my testimony

19       wasn't to do a prudence evaluation of the company's

20       operation during the outage.  It was to estimate a

21       replacement cost credit.

22            Q.   Do you agree that the Nuclear Regulatory

23       Commission has a wide range of authority to ensure that

24       nuclear operations are safe and well managed at

25       utilities such as FPL?

FLORIDA PUBLIC SERVICE COMMISSION

374

1            A.   Yes, sir.  That's my understanding.

2            Q.   Okay.  Do you also agree that the North

3       American Reliability -- I have this as Council.  I heard

4       the other day corporation.  I'm not sure what the C

5       stands for, but whichever.

6            A.   I think it's, I think they changed it to

7       corporation.

8            Q.   Changed it to corporation?  Okay.  I -- thank

9       you.

10                 So do you also agree that the North American

11       Reliability Corporation has substantial authority to

12       ensure that transmission systems such as FPL's are

13       operated safely and reliably?

14            A.   Yes, sir.  I agree.

15            Q.   Your testimony discusses at Page 25 the recent

16       banking and financial crisis leading to large bailouts.

17       You used this as an example of moral hazard.

18                 Are you suggesting any comparison between

19       FPL's operation of its nuclear units and the management

20       of the banks and financial institutions that led to that

21       crisis?

22            A.   No, sir.  It was provided as an example of

23       moral hazard.

24            Q.   Similarly, are you suggesting in your

25       testimony on moral hazard that FPL would cut corners or

FLORIDA PUBLIC SERVICE COMMISSION

375

1       not operate its system as reliably and effectively if

2       the Commission were to adopt FPL's approach to

3       calculating replacement power costs for the Flagami

4       transmission event?

5            A.   No, sir, that's not my testimony.

6            Q.   Okay.

7                 COMMISSIONER SKOP:  Mr. Butler, can you hold

8       on for one second, too?  It looks like we may have lost

9       our telephone link.  And if Chris is available.

10                 MR. BUTLER:  It was a propitious moment for a

11       break.  Let me ask this.  I am going to ask Dr. Dismukes

12       a couple of questions about Interrogatory Number 42, and

13       that is on the CD as Page 318, Bates Number 318 at the

14       bottom and 319.  I have extra copies of the

15       interrogatory and can distribute it, if anybody needs

16       it.

17                 COMMISSIONER SKOP:  Okay.  Are you suggesting

18       we need a few minute break to get to that interrogatory?

19       All right.  Why don't we take a five-minute break and

20       we'll reconvene at -- man, my eyesight is getting bad.

21       Let's reconvene at 10:25.

22                 (Recess taken.)

23                 COMMISSIONER SKOP:  Okay.  At this point we

24       will go back on the record.  Mr. Butler, you're

25       recognized for additional questioning.

FLORIDA PUBLIC SERVICE COMMISSION

376

1                 MR. BUTLER:  Thank you, Commissioner Skop.

2       BY MR. BUTLER:

3            Q.   Doctor Dismukes, I am going to ask you a few

4       questions about FPL's answer to Staff Interrogatory 42.

5       And just for the record, I will note that this is part

6       of Staff's Stipulated Exhibit 31, is that right?  I'm

7       sorry, it would be the response to -- yes, the

8       stipulated Exhibit 27, and it is Bates numbered as

9       319 -- I'm sorry, 318 and 319 at the bottom.  But I

10       handed you a paper copy of the same interrogatory and

11       answer just for the sake of convenience.

12                 Are you familiar with this interrogatory

13       response?

14            A.   Yes, sir, generally.

15            Q.   And is it your understanding that this

16       response reflects FPL's calculation of replacement power

17       costs under four different outage duration scenarios

18       using the production costing simulation approach?

19            A.   Yes, sir.

20            Q.   And the fourth scenario designated as D, as in

21       dog, excuse me, represents outage time of 158 hours for

22       Unit 3 and 107 hours for Unit 4, correct?

23            A.   Yes, sir.

24            Q.   And that corresponds to the outage duration

25       that the Office of Public Counsel is asking this

FLORIDA PUBLIC SERVICE COMMISSION

377

1       Commission to have FPL be responsible for, is that

2       correct?

3            A.   That is correct.

4            Q.   And the calculation of the dollar amount for

5       the replacement power costs under that -- or in that

6       scenario under this production cost simulation modeling

7       is $14,557,536, correct?

8            A.   Yes, sir.

9            Q.   Do you agree, Doctor Dismukes, that the

10       production cost simulation approach that is reflected in

11       Interrogatory 42 is appropriate for the Commission to

12       use in determining the dollar amount of replacement

13       power costs under the scenarios that are identified in

14       Interrogatory 42?

15            A.   I think it is one method that the Commission

16       could consider.  The problem with this method is that

17       it's only -- the ability to replicate it and to test its

18       accuracy rests with the company and the company only.

19       There is no way I can go in and actually go in and test

20       whether or not this model creates the outputs that it

21       says it does under these particular scenarios.  So I am

22       generally familiar with production cost models.  I don't

23       have any objection to the premise of using them, but

24       there is no way of verifying this number for anybody

25       outside of Florida Power and Light.

FLORIDA PUBLIC SERVICE COMMISSION

378

1            Q.   Do you know if you or the Office of Public

2       Counsel asked for the opportunity to review the model

3       and verify its results?

4            A.   I don't believe that anybody asked for this

5       from Public Counsel.  I'm not aware of that.

6            Q.   And you didn't personally, is that correct?

7            A.   There is no way I could run it.  I don't own

8       the software.  I think it is several hundred thousand

9       dollars to use this kind of software, and I don't have

10       the resources to purchase that kind of multi-area

11       dispatching software.

12            Q.   Did you ask to participate with FPL in using

13       its copy of the software to replicate the results?

14            A.   No, I didn't.  I mean, what would I have done

15       with it?  It was well past the testimony filing date.

16       We got this on a Friday, as I recall, very late.  I

17       don't remember what the circumstances were in the

18       process.  It was pretty late in the game when we got

19       this.

20            Q.   Okay.

21            A.   In fact, I think the discovery date time had

22       already passed, but I'm not certain about that.

23            Q.   Let me ask you about the -- well, in any

24       event, you would agree that -- subject to the objections

25       or concerns that you just expressed -- that the approach

FLORIDA PUBLIC SERVICE COMMISSION

379

1       of calculating replacement power costs using production

2       costing simulation would be an appropriate approach to

3       use in this proceeding, is that correct?

4            A.   Dispatch modeling can be an appropriate

5       approach.  Some commissions have used it.  The problem

6       with dispatch modeling in my experience has been what I

7       talked about earlier in that it is very difficult for

8       other parties, including Commission staffs, to verify

9       the accuracy of those models because they don't have

10       access or the resources to the software to be able to

11       execute them.

12            Q.   Let me ask you about the four scenarios that

13       are reflected here, or some of those scenarios.

14       Focusing to start with on Scenario D, I believe you

15       confirmed are earlier that this is representative of the

16       full outage duration for both Turkey Point Unit 3 and

17       Turkey Point Unit 4, correct?

18            A.   Yes, sir, that's my understanding.

19            Q.   And are you aware of any decisions of the

20       Florida Public Service Commission in which it has

21       disallowed the full outage duration for outages at power

22       plants without a finding that all of that outage

23       duration was a result of imprudence?

24            A.   I'm not aware of any, and my recommendation in

25       this proceeding is not for a prudence disallowance, it

FLORIDA PUBLIC SERVICE COMMISSION

380

1       is for replacement cost credit.

2            Q.   So whether or not FPL were found to be

3       imprudent with respect to any of the hours of operation

4       for Turkey Point Unit 3 or Turkey Point Unit 4, your

5       recommendation would be the same, which is that the

6       outage duration used for the replacement power cost

7       calculation would be as shown in Subpart D here, 158

8       hours for Unit 3 and 107 hours for Unit 4, correct?

9            A.   Yes, sir, that's correct.  But for the

10       transmission outage, those units would not have been out

11       of service.  They weren't scheduled to be out of service

12       and, therefore, the opportunity costs of the outage

13       associated with the full duration and the avoided

14       nuclear costs associated with those resources.

15            Q.   Am I correct that in your summary you stated

16       that a 50/50 split of replacement power costs between

17       FPL's customers and its shareholders would, in your

18       mind, be fairer than FPL's $2 million replacement power

19       cost refund proposal?

20            A.   I think that my summary said that it would

21       have some semblance of equity or fairness.  There wasn't

22       even an attempt -- the point I was trying to make was

23       there wasn't an attempt to even try to equitably and

24       fairly distribute those costs.  It wasn't to suggest or

25       make a recommendation that they should be split on a

FLORIDA PUBLIC SERVICE COMMISSION

381

1       50/50 basis.

2            Q.   You would agree that that would represent a --

3       reflect a balance of interests between customers and

4       shareholders, wouldn't you?

5            A.   Mathematically, 50/50 would be an equal split

6       and a balance, yes.

7                 MR. BUTLER:  Commissioner Skop, indulge me for

8       just a moment.  I need to confirm what additional

9       questions I have.

10                 COMMISSIONER SKOP:  Very well.

11                 (Pause.)

12                 MR. BUTLER:  No further questions.

13                 Thank you, Doctor Dismukes.

14                 THE WITNESS:  You're welcome.

15                 COMMISSIONER SKOP:  Thank you, Mr. Butler.

16       Staff is recognized.

17                 MS. BENNETT:  Thank you.

18                          CROSS EXAMINATION

19       BY MS. BENNETT:

20            Q.   Doctor Dismukes, my name is Lisa Bennett, I'm

21       an attorney with the Public Service Commission staff.  I

22       just have a few questions for you.

23                 I kind of get the understanding from your

24       testimony, and I think from Doctor Avera's testimony

25       that this is basically a policy decision for the

FLORIDA PUBLIC SERVICE COMMISSION

382

1       Commission.  Do you agree?

2            A.   Yes, ma'am, I would.

3            Q.   Is this a case of first impression for the

4       Commission, meaning that they have never had something

5       like this before them before to decide?

6            A.   Yes, ma'am.  Based on my understanding it

7       would certainly be that way.

8            Q.   And as I understand from your testimony, you

9       have given us several reasons not to agree with FPL's

10       recommendation on policy, and that's correct in your

11       testimony; correct?

12            A.   Yes, ma'am.

13            Q.   But in your opening statement you talked about

14       there might be a 50/50 split.  Are there any times when

15       from a policy standpoint the Commission should shift the

16       risk to the consumers of the product?

17            A.   There may be.  I don't know that I have got a

18       listing of situations where that may or may not occur.

19            Q.   That was my next question.  Are you aware of

20       any of those situations?

21            A.   Yes.  I mean, there have been instances where

22       those types of decisions have been made in the history

23       of utility regulation.  I just don't have a list right

24       now and can tell you which ones would be appropriate or

25       which ones have an analogue to what's going on in this

FLORIDA PUBLIC SERVICE COMMISSION

383

1       particular proceeding.

2            Q.   Well, let me back up.  I talked about 50/50.

3       Are there times when a portion of the risk should be

4       shifted to the consumer of the product?  And when I'm

5       talking the product, I'm talking about electric service.

6            A.   There may be.  I can't say specifically what

7       those may be.

8            Q.   Could this be considered a factual case and

9       not a policy driven case, in your mind?

10            A.   What do you mean by that?

11            Q.   Let's back up and say instead of a policy

12       decision, would the Commission -- is there any reason

13       for the Commission to make this as a factual decision

14       instead of a policy decision?

15            A.   Well, I think it could.  I mean, the facts are

16       you have a fixed period for outages, you have a fixed

17       series of costs that you can determine what the

18       replacement costs are, and you can come up with a fixed

19       number.  So from those set of facts you can render a

20       decision.  And I'm making that from a policy perspective

21       and an economist perspective.  I don't know from a legal

22       perspective if that's allowable or not, so I would

23       caveat that answer.

24            Q.   In making a policy decision, I'm going back to

25       the policy, is this an unusual event?  Will the

FLORIDA PUBLIC SERVICE COMMISSION

384

1       Commission see this type of policy often?

2            A.   I don't know that it's an unusual event in the

3       sense that a Commission has to make a decision on

4       replacement costs.  I think the circumstances -- the

5       technical circumstances around it make it a unique

6       event, but the actual regulatory decision part of

7       assessing a replacement cost is not an unusual event.

8            Q.   And I think I'm going specifically to this

9       event, a transmission-related event.  Is that unique to

10       the Commission decision-making to require replacement

11       power costs based on a transmission-related event

12       outage?

13            A.   For the Florida Commission?

14            Q.   Yes.

15            A.   Yes, ma'am.

16            Q.   What about for other commissions?

17            A.   I believe that there have been some other

18       decisions in that area.  But, again, many of those have

19       revolved around findings of prudence, prudence

20       investigations.

21            Q.   Okay.  I want you to turn to that 1990 order,

22       23232, for the next couple of questions.

23            A.   Okay.

24            Q.   And I think we have heard that the Commission

25       only required FPL to refund for three days of an outage

FLORIDA PUBLIC SERVICE COMMISSION

385

1       that extended well over a month, is that correct?  Is

2       that your understanding of that case?

3            A.   Yes, ma'am.

4            Q.   And the Commission found that in this

5       docket -- I'm sorry, in this docket OPC is asking that

6       the Commission require FPL to refund for the full time

7       that the power was out at the nuclear plants, correct?

8            A.   Yes, ma'am.

9            Q.   Would you explain why the Commission should

10       treat this docket differently than the 1980 order?

11            A.   Well, I think it's based on the premise of

12       this whole proceeding.  And under the proposed

13       resolution of issues in this case, Florida Power and

14       Light agreed to assume the responsibility for the event.

15       And I don't recall looking in that stipulation that

16       there were any conditions on that.  Part of the event,

17       half of the event, one quarter of the event, they said

18       that they would assume responsibility for the event.

19       Therefore, the entire outage time associated with the

20       event and the opportunity costs associated with the

21       event is the basis upon which the replacement cost

22       credits should be assessed.

23                 MS. BENNETT:  No further questions.

24                 COMMISSIONER SKOP:  Thank you.

25                 Questions from the bench.  Commissioner

FLORIDA PUBLIC SERVICE COMMISSION

386

1       Stevens, you're recognized.

2                 COMMISSIONER STEVENS:  Thank you, Mr. Chair.

3                 Doctor Dismukes, do you know what time of day

4       this outage occurred?

5                 THE WITNESS:  I do not recall.  I think it was

6       in the afternoon.

7                 COMMISSIONER STEVENS:  In your experience,

8       have you ever seen a penalty imposed on a utility

9       company in the amount of $25 million?

10                 THE WITNESS:  In looking at the penalties --

11       no, sir.  In looking at the penalties that have been

12       assessed by the Federal Energy Regulatory Commission

13       under the new provisions after the Energy Policy Act of

14       2005, they have got a list on their home page and you

15       can look at those, and that $25 million agreement is far

16       and away higher than anything that's listed on that

17       page.

18                 COMMISSIONER STEVENS:  Okay.  On the first

19       page of the -- or second under DED-2, which is the

20       stipulation and consent agreement on Page 7 of 21 of

21       Exhibit DED-2, Roman Numeral II, Number 2, a lot of

22       customers were affected.  Do we know how many of these

23       customers were commercial enterprises?

24                 THE WITNESS:  I do not know.  I think the way

25       they are approximated would be proportional to the share

FLORIDA PUBLIC SERVICE COMMISSION

387

1       of commercial customers that FPL serves.

2                 COMMISSIONER STEVENS:  And all we're looking

3       at in this process is a replacement cost credit, is that

4       correct?

5                 THE WITNESS:  Yes, sir.  A credit back to

6       ratepayers for the replacement cost of the outage.

7                 COMMISSIONER STEVENS:  So we haven't looked at

8       anything having to do with the economic impact to any of

9       the customers of FPL.

10                 THE WITNESS:  No, sir, not at all.  And to

11       clarify, I mean, again, looking back, I think it's

12       important in making the decision and looking at the

13       context of this case to look at that proposed resolution

14       of issues, and that resolution of issues clearly

15       articulates that Florida Power and Light is going to

16       assume full responsibility for this outage.  They are

17       not going to admit imprudence, and I would interpret

18       liability, either, and those issues are off the table

19       here.  What is the appropriate replacement costs?  So we

20       haven't even gotten into those issues.

21                 COMMISSIONER STEVENS:  Okay.  Yesterday,

22       during Doctor Avera's testimony, I had asked about the

23       calculation of where the eight hours came from, and his

24       testimony says it's subjective, and Mr. Yupp had worked

25       on that, and Mr. Butler had commented to that this

FLORIDA PUBLIC SERVICE COMMISSION

388

1       morning.  Are any of your calculations based on

2       subjective numbers?

3                 THE WITNESS:  No, sir.  They are all based on

4       numbers the company has filed.

5                 COMMISSIONER STEVENS:  Thank you, Mr.

6       Chairman.

7                 COMMISSIONER SKOP:  Thank you, Commissioner

8       Stevens.

9                 Additional questions from the bench.  Seeing

10       none, I have a few.  Good morning, Doctor Dismukes.  How

11       are you doing?

12                 THE WITNESS:  Good morning.  Good.

13                 COMMISSIONER SKOP:  I just wanted to start

14       by -- again, this is a different function for me.  I

15       have to spend a lot of time looking at what's going on

16       instead of looking at the fine print here.  But on Page

17       9 of your prefiled testimony, you discussed the

18       company's net replacement purchase -- replacement power

19       cost credit.  And you discussed that methodology

20       alluding to an eight-hour period that was used in the

21       company's calculation versus your contention that the

22       nuclear units were off-line for 158 hours and 107 hours

23       respectively.  I guess -- and then going on to, I'm

24       sorry, Page 15, where you discuss your alternate

25       replacement power cost calculation or recommendations,

FLORIDA PUBLIC SERVICE COMMISSION

389

1       did your analysis account for the FPL assertion that the

2       Turkey Point 3 nuclear generating unit could not be

3       returned to service until the control rod indicator

4       repair was complete pursuant to an agreement with the

5       Nuclear Regulatory Commission?

6                 THE WITNESS:  No, sir.

7                 COMMISSIONER SKOP:  Okay.  So that is not

8       factored into your calculation?

9                 THE WITNESS:  No, sir.  If you look at those

10       issues trying to go in and separate and piece-part --

11       well, for starters, I didn't think it was relevant,

12       because, again, going back to the stipulation, the issue

13       is assuming the responsibility for the outage and the

14       units were out but for the outage.

15                 However, following up on that, going in and

16       piece-parting out all these individual pieces and saying

17       this one was a day, and this one is two days, and this

18       one was three days gets back to, I think, some of the

19       questions that Commissioner Stevens has about the

20       subjectivity of how much of that was created by the

21       replacement rod indicator, how much of this was the

22       steam generator problem, how much of this was the

23       general confusion of having two million customers out

24       and transmission lines down all over the state, and

25       people running into each other.  You know, how much of

FLORIDA PUBLIC SERVICE COMMISSION

390

1       that do you account for in this, and where do you make

2       those fine differentiations.  When you do that, you

3       start getting into a lot of subjectivity.

4                 COMMISSIONER SKOP:  And I just would recognize

5       that this, in terms of the testimony from both sides,

6       seems to be a more challenging policy question than the

7       hole drilling incident that the Commission dealt with

8       previously.  That's why I'm trying to take the time to

9       better understand the position of the parties.

10                 Mr. Butler had asked you a series of questions

11       related to a hypothetical where if there were an outage

12       and there is a 50/50 chance that the company is going to

13       have to basically be held accountable for that outage,

14       and asked you to elaborate upon that a little bit.  In

15       asking that question, I didn't fully hear the company

16       provide the standard for what caused the outage at the

17       plants, and I was wondering, you know, if certain

18       instances, whether it be human error that is alluded to

19       in the Gulf States case, or, you know, a willful act, or

20       negligence, or gross negligence, should that, in your

21       opinion, come into the determination on who should be

22       assessed the cost of replacement power, whether it be

23       the consumers or whether it be the company?

24                 THE WITNESS:  Well, not in this situation

25       because the company has already agreed to assume the

FLORIDA PUBLIC SERVICE COMMISSION

391

1       responsibility for it.  So, I mean --

2                 COMMISSIONER SKOP:  But the amount is in

3       question.  And, again, it seems to be, you know,

4       obviously there was a cause of the event and the outage,

5       but the amount of the hours of the outage, I guess, is a

6       material fact in dispute between the parties.  So I'm

7       trying to gain an understanding from your perspective as

8       to, you know, what should be looked at.  I guess the

9       company has proposed an eight-hour period for when the

10       transmission grid was back to a point of equilibrium

11       where customers were being served and things were

12       normal.

13                 But also I think the company has mentioned

14       that typically when you have a reactor shutdown, it's

15       typically about 48 hours to bring those reactors back

16       into service and get them back on-line.  Whereas, in

17       your analysis you used the -- and correct me if I'm

18       wrong -- the 158 and 107 hours respectively, I think, to

19       make that calculation on the nuclear.  So I'm trying to

20       gain a better perspective, assuming that the proximate

21       cause of the Turkey Point 3 and 4 turbine generator

22       trips and reactor plant shutdown was related to, you

23       know, an active employee at a substation for the sake of

24       discussion, what is the appropriate benchmark?  Is it

25       the 48 hours that the plants would be normally returned

FLORIDA PUBLIC SERVICE COMMISSION

392

1       to come on-line, or is it the extreme example that I

2       think that you are referencing in your analysis, or did

3       you consider variations of that within your

4       documentation that you provided?

5                 THE WITNESS:  Well, I don't know that you can

6       get into those issues because based on the stipulation

7       the company said that it would assume the full

8       responsibility for the outage, and we didn't piece-part

9       that.  And so now if you were to go down that road, you

10       would have to start getting into an analysis of the

11       prudence of various operations and whether or not they

12       should or should not have occurred.

13                 Should the replacement rod indicator problem

14       have occurred?  What about the steam generator issue?

15       Which one was prudent, which one was not prudent?  We

16       waived all of those prudence issues off the table, as I

17       understood it, in this particular proceeding.  And so

18       the starting point for my analysis was not going in and

19       looking at the prudence of individual actions, because I

20       didn't think they were relevant based on the facts and

21       the issues in this case.  Calculate the replacement

22       costs and figure out who pays for it, and that is really

23       the premise.  So if that is the starting point, that's

24       how you would calculate it.

25                 COMMISSIONER SKOP:  Okay.  And I respect that,

FLORIDA PUBLIC SERVICE COMMISSION

393

1       and I know you take the case as you find it.  There was

2       a stipulation between the parties, you know, where

3       prudency was, I believe, I don't have the agreement, but

4       I think FPL contended that their actions would not be

5       deemed imprudent.  I don't have the exact words, but,

6       you know, obviously there's a difference.  If you

7       support your calculation, the numbers is higher, but I

8       believe, unless I am wrong, that those calculations are

9       based on the entire time period that both nuclear units

10       were out of service irrespective of any intervening

11       events or any preexisting agreements that would require

12       that unit to stay down by the NRC the next time the

13       plant came down.

14                 THE WITNESS:  That's right, but for the outage

15       they were out.

16                 COMMISSIONER SKOP:  Okay.  And then if I could

17       ask you to turn to your Exhibit DED-2, please.  And this

18       is just to touch upon a question that Commissioner

19       Stevens asked.  I assume that you have read the FERC

20       order approving the stipulation and consent agreement,

21       is that correct?

22                 THE WITNESS:  Yes, sir.

23                 COMMISSIONER SKOP:  Subject to check with

24       respect to the $5 million that may be spent on BES

25       reliability enhancement measures, subject to check,

FLORIDA PUBLIC SERVICE COMMISSION

394

1       would you agree that the FERC order has no express

2       requirements to make that investment in Florida to the

3       extent that FPL may have other transmission facilities

4       outside the state?

5                 THE WITNESS:  Subject to check, yes, I believe

6       that is the case.  I don't recall anything in here being

7       explicit to Florida.

8                 COMMISSIONER SKOP:  Okay.  And I'm sure FERC

9       did not intend that, but, again, the language in

10       Paragraph 2 suggests that 5 million may be spent as part

11       of the settlement agreement on BES reliability

12       enhancement.  Would you also agree, subject to check,

13       that neither the FRCC or the Florida Public Service

14       Commission has any say in where those improvements may

15       go to the extent that the improvements are subject to

16       approval by FERC Commission staff and NERC staff

17       approval?

18                 THE WITNESS:  Based on my understanding from a

19       policy analyst perspective, that is the case.  Yes, sir,

20       you're right.  The FRCC nor the Florida Public Service

21       Commission would have any say-so in that.

22                 COMMISSIONER SKOP:  Okay.  And I'm not

23       suggesting anything, I just know it is not expressly

24       stated.  That may be the implied intent that it would be

25       made in Florida.  I would expect it to be for the

FLORIDA PUBLIC SERVICE COMMISSION

395

1       benefit of FPL's ratepayers, but if staff could follow

2       up on this.  It is not germane to this proceeding, but

3       it would be good to get some insight into what

4       improvements regarding the BES reliability enhancements

5       that FPL intends to make and if, in fact, those -- which

6       I expect they would -- would be made in Florida.  So, as

7       a side issue for follow-up.  But I think that is all the

8       additional questions I have.

9                 Commissioner Klement, you're recognized.

10                 COMMISSIONER KLEMENT:  Thank you.

11                 Doctor Dismukes, I want to follow up on

12       Commissioner Skop's -- a couple of his questions.  It

13       has to do with the rod replacement and the additional

14       time down.  You said you did not consider that in making

15       your recommendation.  My question is why?

16                 THE WITNESS:  Again, as I indicated to the

17       Hearing Officer, the issue in this case was to determine

18       an appropriate replacement cost associated with the

19       outage.  But for the outage, these units would not have

20       been down.  They weren't scheduled to be down.  And so

21       all the other factors, while interesting and important,

22       have no bearing on the calculation for the replacement

23       costs.

24                 COMMISSIONER KLEMENT:  Okay.  Thank you.

25       That's all.

FLORIDA PUBLIC SERVICE COMMISSION

396

1                 COMMISSIONER SKOP:  Thank you, Commissioner.

2                 Mr. Beck, you're recognized for redirect if

3       there is no further questions from the bench.

4                 MR. BECK:  Thank you, Commissioner.

5                         REDIRECT EXAMINATION

6            BY MR. BECK

7            Q.   Doctor Dismukes, do you recall the

8       hypothetical that Mr. Butler gave you about the company

9       decision whether to build a gas turbine or a nuclear

10       plant?

11            A.   Yes, sir.

12            Q.   In that hypothetical, would it make a

13       difference whether the company would receive different

14       regulatory treatment for recovery of costs on a gas

15       turbine versus a nuclear plant?

16            A.   Yes, sir, it would.

17            Q.   Do you know whether Florida gives special

18       regulatory treatment to construction of nuclear plants?

19            A.   Yes, sir, they do.  They provide a number of

20       positive cost-recovery provisions associated with

21       preconstruction dollars, as well as cash earnings on

22       construction work in progress, or CWIP.

23            Q.   You have been asked some questions about the

24       settlement agreement, the proposed resolution of issues

25       in this case?

FLORIDA PUBLIC SERVICE COMMISSION

397

1            A.   Yes, sir.

2            Q.   In that Florida Power and Light did not admit

3       imprudence, is that right?

4            A.   That's my understanding, yes, sir.

5            Q.   They simply said that they would be

6       responsible for -- I'm paraphrasing it, the replacement

7       costs, is that right?

8            A.   Yes, sir.

9            Q.   Had they not had the agreement, would there

10       have been an issue of imprudence in the case?

11            A.   I think had the agreement not existed those

12       would have been areas that the parties would have had to

13       explore is the prudence of the outage and the duration

14       of the outage and the various components contributing to

15       that.

16            Q.   But the imprudence would have focused on the

17       Flagami event, not the bringing back of the unit, or

18       bringing back the nuclear power units, is that right?

19            A.   Yes, sir.

20            Q.   You were asked some questions about the

21       production cost model interrogatory response by the

22       company?

23            A.   Yes, sir.

24            Q.   Did the company refer to that in either their

25       direct or rebuttal testimony?

FLORIDA PUBLIC SERVICE COMMISSION

398

1            A.   No, sir, they did not.

2            Q.   It fact, it came in after their testimony was

3       filed, was it not?

4            A.   Yes, sir.

5            Q.   Was it minutes before the deposition staff

6       scheduled of their witness -- of FPL Witness Yupp?

7            A.   As I recall that was the case, yes, sir.

8            Q.   Finally, I want to make clear, you are not

9       recommending a 50/50 split of the replacement power

10       costs between the company and customers, are you?

11            A.   No, sir, I am not.  I was just trying to make

12       a reference to issues associated with fairness and

13       equity and just the fact that this was so far out of

14       line with what you would normally see in some kind of

15       split that it doesn't connote in any way any type of

16       fairness.

17            Q.   If the Commission were to do some sort of

18       split, would the necessary consequence of that be that

19       customers would pick up some of the extra costs that

20       were incurred as part of the outage?

21            A.   Yes, sir, they would.

22                 MR. BECK:  Thank you.  That's all I have.

23                 COMMISSIONER SKOP:  Thank you, Mr. Beck.

24                 Ms. Bradley and to Ms. Kaufman, again, the

25       Commission tries to limit friendly cross, but I do want

FLORIDA PUBLIC SERVICE COMMISSION

399

1       to ask if you had questions for the witness, and we'll

2       go back and allow cross-examination or redirect as

3       appropriate if you have questions at this point.

4                 MS. BRADLEY:  Not at this time.  Thank you.

5                 COMMISSIONER SKOP:  Thank you.  Ms. Kaufman.

6                 MS. KAUFMAN:  I do not.

7                 Thank you, Commissioner.

8                 COMMISSIONER SKOP:  Great.  Thank you.  It

9       worked out as I expected.

10                 Okay.  All right.  So that takes us to

11       exhibits.  And, Mr. Beck, you're recognized.

12                 MR. BECK:  Yes, Commissioner.  We would move

13       in Exhibits 11 through 22.

14                 COMMISSIONER SKOP:  Okay.  Any objection to

15       the admission of Exhibits 11 through 22 into the record?

16                 MR. BUTLER:  No objection.

17                 COMMISSIONER SKOP:  All right.  Hearing none,

18       those are entered into the record.

19                 (Exhibit Numbers 11 through 22 admitted into

20       the record.)

21                 COMMISSIONER SKOP:  And, Mr. Butler, I believe

22       you have Exhibit 39.  Do you wish to move to enter that

23       at this time?

24                 MR. BUTLER:  Yes.  Thank you, Commissioner.

25                 I would move the admission of Exhibit 39 into

FLORIDA PUBLIC SERVICE COMMISSION

400

1       the record.

2                 COMMISSIONER SKOP:  Any objection?  Hearing

3       none, Exhibit 39 will be entered into the record.

4                 (Exhibit Number 39 admitted into the record.)

5                 COMMISSIONER SKOP:  Okay.  I believe that

6       brings us to rebuttal testimony from FPL, and Mr. Stall

7       is the next witness.

8                 So, Mr. Butler, you're recognized.

9                 MR. BUTLER:  Thank you.

10                 While Mr. Stall is taking the stand, I feel

11       the need just to comment very briefly on the proposed

12       resolution of issues that Doctor Dismukes had referred

13       to.  And it speaks for itself, but certainly FPL's

14       understanding of it is that the whole issue of how to

15       calculate replacement power costs, the proper measure of

16       it, et cetera, fully left open for the parties to take

17       different positions, and the resolution specifically

18       says that, that all parties to this PRI and staff may

19       each take any position that it wishes concerning the

20       proper measure of replacement power costs, if any, that

21       FPL should refund to customers as a result of the

22       Flagami Transmission Event.  And I just wanted to

23       clarify, that's our understanding and the basis on which

24       we have presented testimony in this proceeding.

25                 COMMISSIONER SKOP:  Thank you for that.

FLORIDA PUBLIC SERVICE COMMISSION

401

1                 And, again, I think that the Commission based

2       on the record evidence will give the appropriate weight

3       to the respective witness testimony as it deems

4       appropriate.

5                 MR. BUTLER:  Thank you.

6                 COMMISSIONER SKOP:  You're recognized.

7                 MR. ROSS:  Mr. Stall was sworn yesterday.

8                             J. A. STALL

9       was called as a witness on behalf of Florida Power &

10       Light Company and, having been duly sworn, testified as

11       follows:

12                          DIRECT EXAMINATION

13       BY MR. ROSS:

14            Q.   Good morning, Mr. Stall.

15            A.   Good morning.

16            Q.   Have you prepared rebuttal testimony totaling

17       five pages to be filed in this proceeding?

18            A.   I have.

19            Q.   And did you cause an errata to your rebuttal

20       testimony to be filed on March 2nd, 2010?

21            A.   Yes.

22            Q.   Do you have any other changes or corrections

23       to your rebuttal testimony?

24            A.   No.

25            Q.   If I asked you the questions contained in that

FLORIDA PUBLIC SERVICE COMMISSION

402

1       corrected rebuttal testimony today, would your answers

2       be the same?

3            A.   Yes.

4                 MR. ROSS:  Mr. Chairman, I request that the

5       rebuttal testimony of Mr. Stall as amended by the errata

6       be entered into the record as if read.

7                 COMMISSIONER SKOP:  The rebuttal testimony as

8       amended by the errata sheet of the witness will be

9       entered into the record as though read.

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

409

1            BY MR. ROSS:

2            Q.   Mr. Stall, have you prepared a summary of your

3       rebuttal testimony?

4            A.   I have.

5            Q.   Would you please provide that summary to the

6       Commission?

7            A.   Yes, I will.

8                 Good morning, Commissioners.  My rebuttal

9       testimony refutes the Office of Public Counsel Witness

10       Dismukes' assertions regarding the opportunity for a

11       moral hazard with regard to the operation of FPL's

12       nuclear power plants if FPL's proposals in this docket

13       are adopted.

14                 In every refueling outage at FPL's nuclear

15       units, our employees are driven to complete outages as

16       safely and quickly as possible.  We have an entire

17       separate organization that has only one responsibility,

18       the safe and efficient performance of our outages.  Our

19       employees continuously critique our outage performance,

20       and lessons learned are implemented across our entire

21       fleet to improve outage performance.

22                 Furthermore, FPL operates its nuclear power

23       plants pursuant to a complex set of Nuclear Regulatory

24       Commission requirements.  Even if a licensee were

25       inclined to allow its performance to lag in response to

FLORIDA PUBLIC SERVICE COMMISSION

410

1       a moral hazard, it would be impossible to do so without

2       a significant regulatory response from the NRC.  Doctor

3       Dismukes' assertions regarding a theoretical moral

4       hazard fail to recognize these facts.

5                 I also address the position implicit in Doctor

6       Dismukes' replacement power cost calculation that the

7       full duration of the outages at Turkey Point Units 3 and

8       4 following the Flagami Transmission Event resulted from

9       that event and thus should be used to measure

10       replacement power costs.  A conservative measure of the

11       outage time resulting from the Flagami Transmission

12       Event is 48 hours for each unit, since a nuclear unit

13       will typically be restarted from an unplanned shutdown

14       within 48 hours.  None of the outage time at Turkey

15       Point Units 3 or 4 beyond the 48-hour time frame was the

16       result of any inappropriate or imprudent actions on

17       FPL's part.

18                 This concludes my summary.

19                 MR. ROSS:  We tender the witness for cross.

20                 COMMISSIONER SKOP:  Thank you, Mr. Ross.

21       Mr. Beck, you're recognized.

22                 MR. BECK:  No questions, Commissioner.

23                 COMMISSIONER SKOP:  All right.  Thank you.

24                 Ms. Bradley.  And I know that from yesterday

25       Mr. Butler had extended a professional courtesy to allow

FLORIDA PUBLIC SERVICE COMMISSION

411

1       you to ask questions regarding Mr. Stall's Direct

2       Testimony.  So, you're recognized.

3                 MS. BRADLEY:  Thank you.  I appreciate it.

4                          CROSS EXAMINATION

5       BY MS. BRADLEY:

6            Q.   Mr. Stall, I understand Mr. Yupp prepared this

7       response to Interrogatory Number 42 that has different

8       hours and all on it.  Are you familiar with that?

9            A.   I'll have to see if I have that particular one

10       in my book.  No.  Could I have a copy, please?  No, I

11       have not seen this particular interrogatory before this

12       moment in time.

13            Q.   Well, let me ask you this:  Mr. Yupp gave a --

14       for some of the questions, an outage time for Turkey

15       Point 3 of 158 hours.  Is that your understanding?

16            A.   That is correct.

17            Q.   And that is the total time that your customers

18       were paying for replacement fuel costs?

19            A.   Well, I can't attest to whether it was the

20       total time that the customers were paying for

21       replacement fuel costs.  However, I can attest to that

22       being the duration of the outage for Turkey Point Unit

23       3.

24            Q.   Could the replacement fuel costs have extended

25       beyond 158 hours?

FLORIDA PUBLIC SERVICE COMMISSION

412

1            A.   I am the wrong person to answer that question.

2       My function is solely in regard to operation and

3       maintenance of the nuclear power plants.  I have no

4       roles or responsibility with regard to the calculation

5       of replacement power costs.

6            Q.   Who would be responsible for that?

7            A.   Witness Yupp.

8            Q.   Okay.  And for Turkey Point 4, the total

9       outage time was 170 -- 107 hours?

10            A.   107 hours, that is correct.

11            Q.   Okay.  And during that period of time the

12       nuclear plants were unavailable for usage?

13            A.   That is correct.

14            Q.   Now, in Page -- it looks like 1 of your

15       rebuttal testimony, down on my copy somewhere around

16       Line 21 and 22, do you see where I'm talking about?

17            A.   I do.

18            Q.   Okay.  On my copy you seem to be saying that

19       customer -- I mean, that Florida Power and Light should

20       refund to customers events or time that's attributable

21       to the event, correct?

22            A.   Let me make sure I'm following exactly where

23       you are.

24            Q.   Okay.  I'm down at the bottom where it is

25       talking about, second, I address the position implicit

FLORIDA PUBLIC SERVICE COMMISSION

413

1       in Doctor Dismukes' replacement power cost calculation

2       that the full outages -- duration of outages at Turkey

3       Point Units 3 and 4 that were initiated by this

4       Flagami -- I'm probably pronouncing that wrong --

5       transmission event are attributable to the event and

6       thus should be used to measure the RPC that FPL refunds

7       to customers.

8            A.   Yes, I can speak to the basis for the

9       statement in there that the full duration of the outages

10       of Turkey Point Unit 3 and 4 should not be used as a

11       basis or input for the calculation with regard to total

12       replacement power costs.  He would have done the

13       calculation, so if we would like to talk about discrete

14       events during those outages and whether or not they were

15       prudent, then I'm the witness for that.

16            Q.   Let me ask you this.  Do you feel like events

17       that are -- or things that are related or attributable

18       to the event should be paid for by or should be the

19       responsibility of Florida Power and Light?

20            A.   I think that the company has accepted

21       responsibility for the event.  However, I think that the

22       parsing or the discussion with regard to how many of the

23       hours that the units were out of service, or unavailable

24       as you indicated, is a more complex discussion that

25       needs to be discussed in light of other circumstances

FLORIDA PUBLIC SERVICE COMMISSION

414

1       around those outages.

2                 For example, on Unit 3, the requirement that

3       we had to do the rod position indication repair.  As I

4       stated yesterday to give an example of why I think that

5       the entire duration of these outages is inappropriate

6       for calculating the replacement power costs, let me use

7       that again as an example.  We had an obligation to the

8       Nuclear Regulatory --

9                 MS. BRADLEY:  Mr. Chairman, I hate to

10       interrupt, but I asked him a very limited brief, and he

11       has gone way beyond that and off into other areas, and I

12       would ask that I be allowed to go ahead with my

13       questions.

14                 COMMISSIONER SKOP:  Ms. Bradley, if you could

15       restate the question.  I ask the witness to answer it

16       and then elaborate, and then you can move on to your

17       next question.

18                 MS. BRADLEY:  I had asked him if he agreed

19       that things that were attributable to the Flagami

20       Transmission Event should be the responsibility of

21       Florida Power and Light, and he said, you know, and then

22       kept going.

23                 COMMISSIONER SKOP:  Okay.  Mr. Stall, if you

24       could answer yes or no and then explain your answer to

25       the question that would be appreciated.

FLORIDA PUBLIC SERVICE COMMISSION

415

1                 THE WITNESS:  I think -- I thought I had

2       answered that several times already, including

3       yesterday.  I believe that the items that are directly

4       attributable to the Flagami event we accept

5       responsibility for at Turkey Point.  However, that does

6       not encompass the entire duration of the outages of

7       Units 3 and 4, and if you would like an explanation I

8       could provide one.

9                 MS. BRADLEY:  No.  I would like to go on to my

10       next questions, since your attorney has gone into your

11       position a number of times.

12       BY MS. BRADLEY:

13            Q.   Were you involved at all in the stipulation

14       and consent agreement with FERC?

15            A.   No, I was not.

16            Q.   Have you read about it or been briefed on it?

17            A.   No, I have not.

18            Q.   You don't have any knowledge of that?

19            A.   Beyond what was in the general press, that is

20       the extent of my knowledge of that agreement.

21            Q.   Who of the witnesses here were familiar with

22       that and were involved with that and could be questioned

23       about it?

24            A.   I'm not certain that there is any particular

25       witness here who has the detailed knowledge of that

FLORIDA PUBLIC SERVICE COMMISSION

416

1       particular settlement agreement.

2            Q.   Did you have sufficient knowledge to know

3       whether that was approved by your company?

4            A.   Yes.

5            Q.   And it was approved by Mr. Olivera?

6            A.   I'm not certain who the signatory authority

7       was on the document.

8            Q.   But it was approved by the company?

9            A.   That is correct.

10            Q.   And so anything in there would be as the

11       agreement states, correct?

12            A.   I believe the agreement stands on its own

13       merits.

14                 MS. BRADLEY:  All right.  No further

15       questions.

16                 COMMISSIONER SKOP:  Thank you, Ms. Bradley.

17       Ms. Kaufman, you're recognized.

18                 MS. KAUFMAN:  Thank you, Commissioner.

19                          CROSS EXAMINATION

20       BY MS. KAUFMAN:

21            Q.   Good morning, again, Mr. Stall.

22            A.   Good morning.

23            Q.   I want to look at that same sentence that Ms.

24       Bradley was asking you about on Page 1.  And I really

25       just have one question, and that is that if the Flagami

FLORIDA PUBLIC SERVICE COMMISSION

417

1       Transmission Event had not occurred on February 26th,

2       2008, the Turkey Point units would not have gone down at

3       that time and you would not have engaged in any of the

4       activities that you have told us about these pass two

5       days, is that correct?

6            A.   That's correct.

7                 MS. KAUFMAN:  Thank you.

8                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

9                 Staff.

10                 MR. YOUNG:  Thank you, sir.

11                          CROSS EXAMINATION

12       BY MR. YOUNG:

13            Q.   Good morning, Mr. Stall.  How are you?

14            A.   Good morning, Mr. Young.

15            Q.   I just have some brief questions.  Some

16       concerns of the errata sheet that you filed with your

17       testimony.  And that errata sheet, it relates to the

18       outage of the automatic turbine shutdown at Turkey Point

19       4, correct?  Turkey Point Unit 4, correct?

20            A.   Let me make sure that I'm on the same document

21       as you.  Are you referring to the reverse power relay

22       trip, Mr. Young?

23            Q.   Yes, sir.

24            A.   Yes.

25            Q.   Can you please discuss the shutdown as relates

FLORIDA PUBLIC SERVICE COMMISSION

418

1       to the -- and that's one of the two shutdowns, correct?

2            A.   That is correct.  And yesterday we -- the

3       other shutdown being the steam generator, level control

4       shutdown that we discussed at length yesterday.

5            Q.   Okay.  Can you please discuss the shutdown,

6       the automatic turbine shutdown that's unrelated to the

7       water level in the steam generator?

8            A.   Yes, I would be pleased to do that.  We had --

9       as we were beginning the start-up sequence of Turkey

10       Point Unit 4, we experienced what's called a reverse

11       power relay trip as we synced the generator to the line.

12       Within 7 milliseconds, which is 7/1000ths of a second of

13       closing the output breaker, we had a reverse power trip.

14                 We had no actual physical reverse power

15       condition that occurred, so we initiated a work order

16       and trouble-shooting, and our relay engineers went out

17       into the plant to diagnose the failure.  We sent the

18       relay to a laboratory, our laboratory, and our

19       laboratory technicians determined that a set of

20       mechanical contacts in that relay had failed closed.

21                 So let me back up and sort of talk about how

22       that protection scheme works and what we discovered from

23       that event.  That relay is a dual function relay, if you

24       will.  It is divided into two parts.  One part of it,

25       the upper half has a set of mechanical contacts in it

FLORIDA PUBLIC SERVICE COMMISSION

419

1       that are normally open and would close on a reverse

2       power condition.  The lower half has a timer in it that,

3       in this particular case, is set for 30 seconds.

4                 The way the protection scheme is designed for

5       this particular relay is that in order to have a reverse

6       power trip of the turbine, two events must occur.  A,

7       the mechanical contacts must be closed for 30 seconds

8       for the contact to make up the timer.  And, B, the

9       output breaker must be closed, otherwise you wouldn't

10       have this reverse power trip.

11                 Initially, when we did our condition report,

12       there was some thought that the vibration from the dual

13       unit trip caused these contacts to go closed and caused

14       this condition to occur.  We talked about that in my

15       deposition, and, frankly, I was troubled by that because

16       it did not make sense to me personally for several

17       reasons.  One is that we have the identical relay in

18       service on Unit 3, and we did not have a similar event

19       occur on Unit 3.  And this is some news that I think

20       Mr. Young is probably hearing for the first time today,

21       as well.

22                 So I asked our engineers to provide me with

23       the computer printout from our sequence of events

24       recorder for that trip, and I took that home last

25       weekend and looked at it over the weekend.  And what I

FLORIDA PUBLIC SERVICE COMMISSION

420

1       learned and what I saw, which was new information, was

2       that within 32 milliseconds of the dual unit trip, which

3       is 32/1000ths of a second, which is instantaneously for

4       all practical purposes, we did, in fact, have a reverse

5       power condition occur and a turbine trip from that.  So

6       those mechanical contacts actually closed at that point

7       in time.  That produced a generator lockout condition.

8                 Subsequent to the trip, before they were

9       restarting the unit, they went to reset that lockout

10       condition and it would have reset except the contacts

11       were still in the failed condition.  So what ended up

12       happening in this particular case is that when they

13       began the restart sequence that culminated in the

14       turbine trip, and they, what we call, flashed a field,

15       began to apply voltage to the generator, that timer

16       restated again because those contacts were closed, and

17       in 30 seconds that timer timed out, and that relay

18       sealed in, if you will.

19                 So now they went -- and there would be no

20       alarm in the control room for that condition, because

21       there wasn't a reverse power trip demanded because the

22       output breaker hadn't been closed yet.  Then they went

23       to close the output breaker, and here is where it was

24       obvious.  Within 7 milliseconds that output breaker

25       tripped on reverse power.  So I think that now we fully

FLORIDA PUBLIC SERVICE COMMISSION

421

1       understand the sequence of events that that relay

2       actually failed independent of the vibration from the

3       Flagami trip, and it would have failed at the next

4       opportunity when we had a shutdown, as well.  So I think

5       that hopefully that explains the sequence of events

6       around that.  And that whole evolution took about eight

7       hours to replace and test that relay.

8            Q.   Okay.  Thank you for that.

9                 Now, let me ask you, were you aware of the

10       plant needing to be shutdown because of this kind of

11       issue while the plant was in Mode 1, Model 1 generation?

12       Mode 1 generation -- operation, excuse me?

13            A.   Well, let me clarify that.  I think I know

14       what you are asking me.  In this particular case,

15       although the plant was in Mode 1, the plant was less

16       than 10 percent power, and there is what is called a

17       P10 inner-lock associated with the reactor that says

18       that if power is less than 10 percent, if the turbine

19       trips the reactor will not trip.  So the turbine

20       tripped, but the reactor stayed critical.

21                 That particular event was not reportable to

22       the Nuclear Regulatory Commission because it is not an

23       actuation of a safety system.  So there was

24       no requirement for notification of the Chief Nuclear

25       Officer, myself in this particular case.  So I became

FLORIDA PUBLIC SERVICE COMMISSION

422

1       aware of this on or about March 1st when we went back a

2       second time and looked at the entire sequence of that

3       outage and discovered that that event was in there.

4            Q.   Now, I think -- let me see if I understand

5       this.  Is it your position or the company's position

6       that the repair -- looking at the -- moving to the RPI

7       repair, is it the company's position that the repair or

8       the RPI -- because of the repair of the RPI system, thus

9       that's the cutoff between what the ratepayers must bear

10       and what the company must be responsible for?

11            A.   Well, I think I'd like to answer that question

12       in two parts if it is okay with you.  I'd like to

13       address Unit 3 and the RPI.  In that I think it is a

14       clear cut case of the RPI should be excluded from this.

15            Q.   And that's because you had to -- because of

16       the NRC order that you had to repair, correct?

17            A.   Because we had to do that repair.  And had we

18       done that repair in October, it would have taken longer.

19       Took an opportunity to go to the Nuclear Regulatory

20       Commission to preserve nuclear generation for our

21       customers.  And to penalize us now for doing the right

22       thing for the customers, I think, would send a very

23       chilling signal to us.

24            Q.   Okay.  But as you alluded to in your Direct

25       Testimony, FPL didn't have any planned outages to do the

FLORIDA PUBLIC SERVICE COMMISSION

423

1       repair, correct?

2            A.   That's correct.

3            Q.   Okay.  And is it based -- the company's

4       position, is that based because partly on the

5       Commission's decision, and I think Mr. Butler alluded to

6       Doctor Dismukes in Order Number 23232, which the

7       Commission stated that the company should only be

8       responsible for three days, three days outage in that

9       case?

10            A.   I can't speak to that.  I think that as far as

11       I'm concerned it's based on common sense, that we would

12       have had to do that repair.  We did the right thing for

13       the customers in October by avoiding it.  It would have

14       taken much longer to do it in October.  We wouldn't have

15       been having a discussion around it today had it been

16       done in October.  And to penalize the company for doing

17       the right thing, I think, is sending a horrible signal.

18                 MR. YOUNG:  No further questions.

19                 COMMISSIONER SKOP:  Thank you, Mr. Young.

20                 Commissioners, questions from the bench?

21       Commissioner Klement, you're recognized.

22                 COMMISSIONER KLEMENT:  Thank you.

23                 Can I just follow up on that, your last

24       statement to say why would it have taken longer if you

25       had waited until October and the plant shutdown?

FLORIDA PUBLIC SERVICE COMMISSION

424

1                 THE WITNESS:  Mr. Commissioner, perhaps I

2       wasn't clear.  It was in October of 2007 when we were

3       ascending in power from a refueling outage that this

4       problem first revealed itself to us, and we knew that we

5       were quite vulnerable.  If another one would have

6       failed, we would have been into a forced shutdown.  At

7       that point in time we had to make a decision on whether

8       to continue with power ascension and operate or shut the

9       reactor back down and go to fix this.

10                 So we knew that if we were to shut the reactor

11       back down and go fix it at that point in time that it

12       would have taken a very long time to do because we

13       didn't have the parts, we didn't have the work order, we

14       hadn't done any advance planning or testing to localize

15       the nature of the problem.  So the engineers developed

16       an alternative methodology that we went to the NRC and,

17       frankly, spent some regulatory margin to get their

18       approval to allow us to continue to operate because it

19       was the right thing for the customers to do that.

20                 Along came the Flagami event, and we were now

21       obligated to do it, and we did it in much less time than

22       it would have been in October.  And to be penalized for

23       doing the right thing for the customers is just, I

24       think, the wrong signal.

25                 COMMISSIONER KLEMENT:  Well, perhaps I should

FLORIDA PUBLIC SERVICE COMMISSION

425

1       have refreshed my memory, but I was thinking I was

2       remembering from yesterday that there was a scheduled

3       shutdown for the fall of 2008.  That is the October I

4       thought I was referring to.  No?

5                 THE WITNESS:  No, the next refueling outage

6       would have been 18 months from October of 2007, which

7       would have been March of 2009.

8                 COMMISSIONER KLEMENT:  March of 2009.

9                 THE WITNESS:  Now, what we talked about

10       yesterday, just to clarify perhaps the record on that,

11       is that we did have a forced outage in June of 2008.

12       However, the reactor was maintained in what we call Mode

13       2, which was a critical state while we did some

14       balancing on an exciter turbine bearing.  And what I was

15       suggesting yesterday, and absolutely what we would have

16       done, had we not had the Flagami event, we would not

17       have kept the reactor in Mode 2 at that time.  We would

18       have shut the reactor down and done that repair at that

19       point in time because it's not a comfortable spot to be

20       in not have the operators with their full attendant

21       instrumentation.  And our policy is generally to give

22       them every opportunity to have everything available.

23                 COMMISSIONER KLEMENT:  And how do you respond

24       to Doctor Dismukes' earlier statement that it didn't --

25       it is almost irrelevant that in the consideration of the

FLORIDA PUBLIC SERVICE COMMISSION

426

1       cost of replacement fuel that you chose to do it -- that

2       you did do it during this unplanned outage?

3                 THE WITNESS:  Well, if I understood Doctor

4       Dismukes' testimony properly, I don't think he was

5       rendering an opinion necessarily on whether or not the

6       outages were -- the right things were done in the

7       outages.  As a matter of fact, I think he generally

8       agreed that, you know, we handled those outages

9       prudently.  So he was given a set of numbers to do a

10       bookend calculation on, which he simply did, and he

11       wasn't necessarily rendering an opinion on the merits of

12       whether or not in this case, for example, the rod

13       position indication repair was the right thing to do or

14       not the right thing to do because he didn't have

15       visibility into that.

16                 COMMISSIONER KLEMENT:  And just to be clear,

17       FPL asserts that they had no choice from a NRC

18       regulatory point of view whether to replace that rod

19       then or wait until your 2009 shutdown, planned shutdown?

20                 THE WITNESS:  No.  We had a legal commitment

21       in writing that obligated us to perform that repair at

22       the next shutdown, which in this particular case was the

23       February 26th shutdown.

24                 COMMISSIONER KLEMENT:  Okay.  Thank you.

25       That's all, Mr. Chairman.

FLORIDA PUBLIC SERVICE COMMISSION

427

1                 COMMISSIONER SKOP:  Thank you, Commissioner.

2                 Any additional questions?  Commissioner

3       Stevens, you're recognized.

4                 COMMISSIONER STEVENS:  Thank you, Mr.

5       Chairman.

6                 Mr. Stall, you stated that you're in charge of

7       the operation and maintenance of the nuclear plants as

8       the Vice-President of Nuclear Transition, is that

9       correct?

10                 THE WITNESS:  I was in charge of -- directly

11       responsible for the operation and maintenance until

12       January 1st of 2009, when I moved into this role of

13       transition and my successor was named.

14                 COMMISSIONER STEVENS:  Okay.  Was this event

15       preventable?

16                 THE WITNESS:  Which particular event are we

17       talking about now, the RPI event?

18                 COMMISSIONER STEVENS:  Yes.

19                 THE WITNESS:  No, I don't believe it was

20       preventable.

21                 COMMISSIONER STEVENS:  Will it happen again?

22                 THE WITNESS:  I have no reason to believe it

23       would happen again.  But, you know, these plants are

24       extremely complex units.  There are hundreds of

25       thousands of parts and components in them, so I could

FLORIDA PUBLIC SERVICE COMMISSION

428

1       never say never.

2                 COMMISSIONER STEVENS:  When you were in charge

3       of the operation and maintenance of the plants, how many

4       employees did you have under you?

5                 THE WITNESS:  That's a --

6                 COMMISSIONER STEVENS:  A round number is fine.

7                 THE WITNESS:  Around 5,000.

8                 COMMISSIONER STEVENS:  Okay.  Were any of

9       these employees responsible for the monitoring of the

10       electric power generated and transmitted to the

11       customers?

12                 THE WITNESS:  Only to the extent that we

13       monitor the individual generator voltage and var output

14       at each of the nuclear plants.  But, with regard to the

15       bulk electric system, no.

16                 COMMISSIONER STEVENS:  Okay.  Thank you, Mr.

17       Chairman.  Thank you, Mr. Stall.

18                 COMMISSIONER SKOP:  Any additional questions

19       from the bench?  Hearing none, I just have a few.

20                 Mr. Stall, I guess it would be beneficial to

21       me because you're, I guess, FPL's nuclear expert, to

22       gain a better understanding of exactly what happened

23       within the plant resulting from the substation event

24       that caused the unplanned outage of the Turkey Point 3

25       and 4 units.  So could you speak to that in terms of,

FLORIDA PUBLIC SERVICE COMMISSION

429

1       you know, what happened when the turbine generator sets

2       tripped as a result of the --

3                 THE WITNESS:  With regard to the transient

4       response of the units in particular?

5                 COMMISSIONER SKOP:  Yes.  And then what the

6       state of the reactors were.  Did they scram, or was it a

7       manual shutdown, and were they in, you know, hot

8       standby, cold restart, or just elaborate on that.

9                 THE WITNESS:  Okay.  Let me attempt to walk

10       through that, if I can, at a high level.  If you back up

11       to just moments before the transient that was initiated

12       in the Flagami substation, both Turkey Point Unit 3 and

13       4 were at 100 percent power in what we call a steady

14       state condition, normal operating condition.

15                 At T=0 when the transmission event occurred

16       and the fault was introduced into the system, our

17       protection system, undervoltage protection system

18       associated with Units 3 and 4 detected an undervoltage

19       condition of less than 70 percent nominal voltage that

20       lasted for a duration of one second or more.  That is

21       the set point of the relays that introduced the

22       undervoltage protection.  That generated a reactor trip

23       signal to the reactor trip breakers, which are the

24       devices that hold the control rods elevated above the

25       reactor core.  So the reactor trip breakers had a signal

FLORIDA PUBLIC SERVICE COMMISSION

430

1       to open, and they did within milliseconds of the event

2       occurring, followed shortly thereafter by 32

3       milliseconds by this reverse power turbine trip signal

4       that I talked about with Mr. Young a few minutes ago.

5                 All the safety systems on both units responded

6       as designed.  There were no malfunctions, there were no

7       operator errors, or any concerns with regard to that.

8       We then performed a detailed analysis, as you have to do

9       anytime there is a transient like this in the plant

10       where we looked at every single relay that actuated,

11       every pump and motor that started, operator response to

12       the event.  Did they follow the procedures properly,

13       were they in the right sequence, all of that.  And

14       everything responded, including the operators, the way

15       they were trained and the equipment the way it was

16       designed to do.

17                 There was one particular undervoltage relay

18       that we found that was slightly out of calibration, but

19       still within the technical specification limits of the

20       license, and we dealt with that.  The transient response

21       was normal.  Had that event lasted longer than it did,

22       we could have found ourselves on the emergency diesels,

23       but because the power was restored fairly quickly to the

24       switchyard like it's designed to do, when the normal

25       station service transformers that supply power as we

FLORIDA PUBLIC SERVICE COMMISSION

431

1       call them -- in other words, when the generators are in

2       service we tap off of that power to supply what we call

3       the in-house or hotel loads.

4                 When that generator tripped, the power to

5       power all of the safety equipment is going to come from

6       one of two places, off-site power or the emergency

7       diesels.  In this case, we swapped over to the reserve

8       service transformers properly, and we had off-site

9       power, so the diesel generators never were required to

10       start and load.  So we didn't have that occur.

11                 And from that point on, Commissioner, it

12       was -- of course it was hectic with two units down

13       simultaneously, but the Nuclear Regulatory Commission

14       responded to the control room, and in their inspection

15       report they said that we had done a very good job with

16       handling that transient.

17                 COMMISSIONER SKOP:  Okay.  With respect to

18       Page 5 of your errata sheet, which is in your rebuttal

19       testimony, you talk about an outage time of 48 hours

20       that's typically necessary to bring a reactor plant back

21       on-line from an unplanned shutdown, is that correct?

22                 THE WITNESS:  That's correct.

23                 COMMISSIONER SKOP:  Okay.  Now, in the

24       instance of what happened as you have just explained,

25       and I won't try and paraphrase, typically -- and this

FLORIDA PUBLIC SERVICE COMMISSION

432

1       was probably a little bit more than a typical trip and

2       then having to standby and then restart or get back up

3       to power.  But when this event happened, did FPL go

4       immediately -- was it FPL's intent to restart the

5       reactors as quickly as possible thereby keeping the

6       plants in a hot standby condition, or did FPL

7       subsequently decide that, no, we have got to bring them

8       down completely cold because of what happened?

9                 THE WITNESS:  On Unit 3, we knew that we had a

10       rod position indication system repair, as we have talked

11       about to complete, and initially it was not clear until

12       we were able to get crews out to their reactor head area

13       whether or not we were going to have to do extensive

14       work.  For example, replacing a coil on top of the

15       reactor head, which would have meant dismantling the

16       missile shield, and that would have caused us to take

17       the unit to cold shutdown as you suggest.

18                 In this particular case, we had anticipated

19       that because we did have the time to plan this job, and

20       we were able to get out there within eight hours and

21       start work.  And we were able to determine that just by

22       lifting the coil a little bit up and getting some

23       measurements under there we were able to determine that

24       that coil was, in fact, satisfactory and that we could

25       maintain the unit in a hot standby condition and do that

FLORIDA PUBLIC SERVICE COMMISSION

433

1       work.  So we stayed in hot standby on that unit.

2                 On Unit 4, there was no necessary maintenance

3       or requirement that would have caused us to take the

4       unit to cold shutdown, so we maintained that unit in a

5       hot standby condition, as well.

6                 COMMISSIONER SKOP:  On Unit 4, because, again,

7       on Unit 3 there was the issue of the control rod

8       indicator, and with respect to that in a question that

9       Commissioner Klement asked you, you mentioned that there

10       was a legal agreement in writing regarding the need to

11       do that maintenance item prior to restart, is that

12       correct?

13                 THE WITNESS:  Yes, sir.

14                 COMMISSIONER SKOP:  Okay.  Do you know if that

15       legal agreement was provided within any of the exhibits

16       or testimony that FPL provided in this case?

17                 THE WITNESS:  I believe it was.

18                 COMMISSIONER SKOP:  Okay.  All right.  And I

19       will ask Mr. Butler or Mr. Ross if you could speak to

20       that briefly.  And I just have one or two more

21       questions.

22                 MR. BUTLER:  Commissioner Skop, we'll get you

23       the number.  It is a discovery response that has been

24       made an exhibit in the staff stipulated exhibits.  We

25       just have to confirm which one it is.

FLORIDA PUBLIC SERVICE COMMISSION

434

1                 COMMISSIONER SKOP:  All right.  Thank you.

2                 So, Mr. Stall, I think my final question deals

3       with Unit 4 and your rebuttal testimony on Page 5.

4       Certainly in an unplanned outage, according to your

5       testimony, you stated that the 48-hour time frame was

6       reasonable to bring both plants on-line.  But there was

7       an additional delay with the restart of Unit 4 as a

8       result of the discussion that we had yesterday, and I

9       guess the question I have is but for the unscheduled

10       outage, FPL would not have had to restart Unit 4.  So is

11       it appropriate in light of what happened with the delay

12       and the additional time that Unit 4 was out not to

13       consider the impact of that in terms of the consumers?

14                 THE WITNESS:  Let me make sure I understand.

15       You're referring to specifically the steam generator

16       water level trip?

17                 COMMISSIONER SKOP:  The 30 additional hours.

18       You said typically when plants go off-line for an

19       unscheduled outage, 48 hours is the maximum time

20       typically necessary to bring those plants back up absent

21       some additional issues that, you know, may have existed

22       with Turkey Point 3.  With respect to 4 that was delayed

23       an additional, I guess, 30 hours, apparently, based on

24       what we were discussing yesterday, and I'm trying to

25       understand whether those 30 hours, it would not be

FLORIDA PUBLIC SERVICE COMMISSION

435

1       appropriate to include that additional loss time also

2       based on what happened?

3                 THE WITNESS:  I don't believe that it is

4       appropriate to include that 30 hours.  And yesterday we

5       had a lot of detailed discussion around that, but just

6       to summarize the basis for my response is I think that

7       you have to back up and look at the performance of these

8       units in the aggregate.  When we look at 2008, you know,

9       we have two nuclear units down there that outperformed

10       the industry average by over 4 percent in capacity

11       factor, which gave the customers a benefit of about 25

12       days of extra generation that they wouldn't have had if

13       we had just performed at that average.

14                 And so I think that it is dangerous when we

15       begin to sort of cherry pick at things that don't go

16       well, and say, well, that could have been done better.

17       That didn't have to happen, therefore, you know, we

18       should penalize the company for that, and we ignore the

19       bigger picture of all of the benefits that have accrued

20       because of superior operations.

21                 And I think also equally important that you

22       begin to creep towards the standard of nothing but

23       perfection is acceptable in operating these big nuclear

24       units, and they are just so complex and there is so much

25       to them that we are never going to be perfect.  Nobody

FLORIDA PUBLIC SERVICE COMMISSION

436

1       is.  These events are going to happen from time to time,

2       but if you weigh it in the balance, the preponderance of

3       the evidence is that the customers are benefiting

4       enormously.

5                 COMMISSIONER SKOP:  I understand, and I do

6       recognize FPL on its operational performance, your

7       operational performance is above industry average, as

8       has been documented in other instances.

9                 To your point about penalties and what have

10       you, I don't think -- you know, certainly I'm here to

11       listen to the record evidence and make a fair judgment

12       based on the facts that come into evidence.  I mean, the

13       whole notion of a penalty, I think, is a little

14       farfetched.  It's important to look at things critically

15       and to have a better understanding as to the details,

16       and that's why I have asked you to answer some of the

17       questions that may have got lost in the details so I can

18       make my own independent judgment when we get to that

19       point.

20                 So I think that's all the questions that I

21       have for you.  I do want to clarify one point to

22       counsel, with respect to the FERC order that I

23       previously spoke to, my concern with that is on the

24       stipulation and consent agreement, Paragraph 25, there

25       seems to be a little bit of a disagreement between the

FLORIDA PUBLIC SERVICE COMMISSION

437

1       FERC order and the FPL consent order about the $5

2       million shall be remitted and that to enhance

3       reliability of the BES, it doesn't really speak to -- it

4       is a little bit vague there and ambiguous, and then

5       contrasting that to the FERC order, Paragraph 2, and

6       Paragraph 18 and 21.  Twenty-one is actually the most

7       specific where it says additional reliability

8       protections on the FPL portion of the BES, but, again,

9       that still does not say peninsular Florida for the

10       benefit of FPL's ratepayers.

11                 MR. BUTLER:  We are looking into getting an

12       answer to that question based on your earlier comment on

13       it, Commissioner, and should be able to today before we

14       conclude.

15                 COMMISSIONER SKOP:  I appreciate that.  And,

16       again, it is a tangential issue, but it is important to

17       ensure value for FPL's ratepayers in Florida.  Because

18       this event was a Florida event, and I am reasonably

19       certain that the FERC Commissioners had that intent.

20       Commissioner Wellinghoff, Spitzer, and Commissioner

21       Moeller, I'm sure, would uphold state interests and

22       rights in reaching that conclusion, also.  But I don't

23       want to speak for them.

24                 But that takes us to exhibits, which I think

25       we have none.

FLORIDA PUBLIC SERVICE COMMISSION

438

1                 MR. ROSS:  Mr. Chairman.

2                 COMMISSIONER SKOP:  Mr. Ross.

3                 MR. ROSS:  I have one item for redirect.

4                 COMMISSIONER SKOP:  Yes.  Redirect.

5                 MR. ROSS:  Thank you.

6                         REDIRECT EXAMINATION

7            BY MR. ROSS:

8            Q.   Mr. Stall, the 70 percent set point that you

9       mentioned in response to Commissioner Skop's question,

10       where is that found?  Where is that requirement found?

11            A.   That is found in our technical specifications

12       which form a part of our operating license from the

13       Nuclear Regulatory Commission.

14            Q.   So is that a mandatory requirement that that

15       70 percent set point actuation, that's a mandatory

16       requirement from the NRC?

17            A.   Yes.

18                 MR. ROSS:  That's all the redirect I have.

19                 And, Commissioner, in response to your

20       question about the NRC license amendment which imposed

21       the condition to repair the RPI at the next outage is in

22       Staff Exhibit 31, which is admitted into evidence, and

23       the specific document starts at Bates number 385.

24                 COMMISSIONER SKOP:  Thank you, Mr. Ross.

25                 And that concludes the redirect.  There are no

FLORIDA PUBLIC SERVICE COMMISSION

439

1       exhibits for this witness for his rebuttal testimony.

2                 MR. ROSS:  That's correct.

3                 COMMISSIONER SKOP:  So I believe that will

4       allow Mr. Stall to be excused.  Thank you, Mr. Stall.

5                 THE WITNESS:  Thank you.

6                 COMMISSIONER SKOP:  All right.  Call your next

7       witness, please.

8                 MR. BUTLER:  Thank you, Commissioner Skop.  We

9       would call Mr. Yupp.

10                            GERARD J. YUPP

11       was called as a witness on behalf of Florida Power and

12       Light Company, and having been duly sworn, testified as

13       follows:

14                         DIRECT EXAMINATION

15       BY MR. BUTLER:

16            Q.   Mr. Yupp, you have been previously sworn,

17       correct?

18            A.   Yes, I have.

19            Q.   Would you please state your name and business

20       address for the record?

21            A.   Gerard J. Yupp, 700 Universe Boulevard, Juno

22       Beach, Florida 33408.

23            Q.   And by whom are you employed and in what

24       capacity?

25            A.   I am employed by Florida Power and Light

FLORIDA PUBLIC SERVICE COMMISSION

440

1       Company as Senior Director in the Energy Marketing and

2       Trading Division.

3            Q.   Have you prepared and caused to be filed in

4       this docket four pages of prefiled Rebuttal Testimony on

5       February 24, 2010?

6            A.   Yes.

7            Q.   Do you have any changes or revisions to your

8       prefiled rebuttal testimony?

9            A.   No, I do not.

10            Q.   If I asked you the questions contained in your

11       prefiled rebuttal testimony, would your answers be the

12       same today?

13            A.   They would.

14                 MR. BUTLER:  Commissioner Skop, I would ask

15       that the prefiled rebuttal testimony of Mr. Yupp be

16       inserted into the record as though read.

17                 COMMISSIONER SKOP:  The prefiled rebuttal

18       testimony of the witness will be entered into the record

19       as though read.

20                 MR. BUTLER:  Thank you.

21       BY MR. BUTLER:

22            Q.   Mr. Yupp, you also are sponsoring Exhibits

23       GJY-10 through GJY-12, which are attached to your

24       prefiled Rebuttal Testimony?

25            A.   Yes, I am.

FLORIDA PUBLIC SERVICE COMMISSION

441

1            Q.   And were those prepared by you or your

2       direction, supervision, or control?

3            A.   Yes, they were.

4                 MR. BUTLER:  Commissioner Skop, I would note

5       that those exhibits have been premarked for

6       identification as Exhibits 23 to 25.

7                 (Exhibits 23, 24 and 25 marked for

8       identification.)

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

446

1       BY MR. BUTLER:

2            Q.   And with that I would ask Mr. Yupp to

3       summarize his rebuttal testimony.

4            A.   Good morning, Commissioners.  My rebuttal

5       testimony in this docket responds to the assertion in

6       the Direct Testimony of OPC Witness David Dismukes that

7       FPL has earned approximately $4.7 billion over the past

8       37 years on its investment in the Turkey Point nuclear

9       units.  Doctor Dismukes fails to give a comparative

10       figure reflecting the benefits that FPL's customers have

11       received on that same investment.

12                 My rebuttal testimony shows that since 1990,

13       FPL's customers have received approximately $7.7 billion

14       in fuel savings because of the operation of Turkey Point

15       Units 3 and 4.  This figure represents $3 billion more

16       than the investment that Doctor Dismukes refers to in

17       his Direct Testimony in just over half the time period.

18                 And that concludes my summary.  Thank you.

19                 MR. BUTLER:  Thank you, Mr. Yupp.  I tender

20       the witness for cross-examination.

21                 COMMISSIONER SKOP:  Thank you, Mr. Butler.

22                 Mr. Beck, you're recognized for

23       cross-examination.

24                 MR. BECK:  Thank you, Commissioner.

25                          CROSS EXAMINATION

FLORIDA PUBLIC SERVICE COMMISSION

447

1       BY MR. BECK:

2            Q.   Good morning, Mr. Yupp.

3            A.   Good morning, Mr. Beck.

4            Q.   Your calculation for the replacement power

5       costs for 48 hours, that does not include power

6       ascension, does it not?

7            A.   In my rebuttal testimony, no, it does not.

8            Q.   And is it not FPL's position that 48 hours is

9       the typical time to bring a single nuclear plant back

10       on-line?

11            A.   I believe that is the case, and this

12       calculation here on 48 hours was done to support the

13       testimony of Witness Stall.  I'm not 100 percent sure on

14       the difference between bringing one and two.  I know we

15       referenced, or Mr. Stall referenced 48 hours in his

16       testimony, and so that was the basis for my calculation.

17            Q.   But did not Mr. Stall yesterday say that the

18       typical time to bring on two reactors at the same time

19       was three to five days?

20            A.   I don't recall specifically.  I do remember

21       hearing something along those lines, so, yes, I would

22       agree.

23                 MR. BECK:  Thank you.  That's all I have.

24                 COMMISSIONER SKOP:  Thank you, Mr. Beck.

25                 Ms. Bradley, you're recognized.

FLORIDA PUBLIC SERVICE COMMISSION

448

1                 MS. BRADLEY:  Thank you.

2                          CROSS EXAMINATION

3       BY MS. BRADLEY:

4            Q.   Sir, I think we are back to you for the

5       question.  The 158 hours for Turkey Point Unit 3 and the

6       107 hours for Turkey Point 4, were your customers paying

7       replacement costs for that period of time or was it

8       longer than that?

9            A.   Our customers were paying replacement power

10       costs for that period of time.  And I'll term it this

11       way; that was once the nuclear units were returned,

12       those two units were lost as a result of the outage, the

13       nuclear units returned, all of the gas-fired generation

14       that had come off the line in response to the outage had

15       also been returned within that time period.  So there

16       were no additional replacement fuel costs past 158 and

17       107 hours.

18                 MS. BRADLEY:  No further questions.  Thank

19       you.

20                 COMMISSIONER SKOP:  Thank you, Ms. Bradley.

21                 Ms. Kaufman, you're recognized.

22                 MS. KAUFMAN:  Thank you, Commissioner Skop.

23                          CROSS EXAMINATION

24            BY MS. KAUFMAN

25            Q.   Good morning, Mr. Yupp.

FLORIDA PUBLIC SERVICE COMMISSION

449

1            A.   Good morning.

2            Q.   On the first page of your rebuttal testimony,

3       and I think you mentioned this in your summary, you talk

4       about the statement of Doctor Dismukes that FPL has

5       earned -- what FPL has earned on its investment in

6       Turkey Point.  I think this is starting at Line 16.  Do

7       you see that, Page 1?

8            A.   Yes, I do.

9            Q.   You certainly don't dispute that Florida Power

10       and Light has earned a return on the Turkey Point

11       assets, do you?

12            A.   I would not dispute that, no.

13            Q.   And those assets are included in FPL's rate

14       base and have been for many years, correct?

15            A.   That is my understanding.

16            Q.   And ratepayers have paid for those assets as

17       well as a return as long as those assets have been in

18       rate base?

19            A.   That is my understanding, also, yes.

20            Q.   And you would also agree, would you not, and I

21       think we have heard some testimony about this already,

22       that nuclear units are highly capital intensive as

23       compared to other types of generating units?

24            A.   That's my understanding, yes.

25            Q.   And I think you have also testified that

FLORIDA PUBLIC SERVICE COMMISSION

450

1       customers have seen substantial fuel savings from the

2       nuclear units, correct?

3            A.   Correct.

4            Q.   Would you not expect the customers to see

5       savings from these highly capital intensive units, and

6       isn't that why FPL proposed them as the appropriate

7       generating choice at the time?

8            A.   No, I would fully expect to see those types of

9       savings from a low cost generation resource such as

10       nuclear.  And I think, you know, to clarify why this is

11       in my testimony, I think, in the Direct Testimony of

12       Doctor Dismukes only one side of the equation was given,

13       and that was the return on the investment of Turkey

14       Point 3 and 4.

15                 I think it was important to at least have a

16       comparative figure just as a reference to just what you

17       are speaking of, the enormous amount of savings that

18       these units have provided to FPL's customers over the

19       years.

20            Q.   Thank you.

21                 And you would agree that certainly that is the

22       reason that FPL proposed that it construct these units

23       and that ratepayers pay for them because they expected

24       to see the ratepayers recognize some substantial fuel

25       savings.

FLORIDA PUBLIC SERVICE COMMISSION

451

1                 MR. BUTLER:  I'm sorry, excuse me.

2       Clarification to the question.  Are you asking about

3       FPL's original decision to build Turkey Point Units 3

4       and 4 that went into service in 1972?

5                 MS. KAUFMAN:  Yes.

6                 MR. BUTLER:  Okay.  So I would just instruct,

7       to the extent the witness knows.

8                 COMMISSIONER SKOP:  Thank you.

9                 Ms. Kaufman, you may proceed.

10       BY MS. KAUFMAN:

11            Q.   Do you need me to repeat?  Did you understand

12       the question, Mr. Yupp?

13            A.   No, I don't.  I guess I would answer it this

14       way:  I don't know what our thought process was in 1972.

15       Again, these units have provided more and more fuel

16       savings over the years as fuel prices, particularly gas

17       and oil, have become extremely volatile and have been

18       high in the last recent years.  So the time frame in

19       1972 was different.  I don't have any specific knowledge

20       of why we would have decided to build the units at that

21       time.

22            Q.   Let me ask it this way, how long have you been

23       with Florida Power and Light?

24            A.   Since 1989.

25            Q.   Okay.  So a few years.

FLORIDA PUBLIC SERVICE COMMISSION

452

1            A.   Yes.

2            Q.   Would it be fair to say that you would not

3       expect your company to have made a proposal to construct

4       generation that would not have provided benefits to the

5       ratepayers, would you?

6            A.   Let me make sure I answer it correctly using

7       yes or no.  No, I would expect the company to make those

8       decisions based on what is the best benefit for our

9       customers, yes.

10                 MS. KAUFMAN:  Thank you.

11                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

12                 Staff.

13                 MR. YOUNG:  Thank you, sir.

14                          CROSS EXAMINATION

15            BY MR. YOUNG:

16            Q.   Mr. Yupp, what is the philosophy behind the

17       48-hour time frame that Mr. Stall alluded to in his

18       Direct and Rebuttal Testimony to bring the plants up

19       normally for one unit?

20            A.   I'm sorry, the philosophy behind the 48 hours?

21            Q.   Yes.

22            A.   I'm not sure I understand.

23            Q.   Do you know the philosophy behind it?  Do you

24       know why it would take 48 hours to bring them up?

25            A.   No.  I'm not in nuclear operations and I do

FLORIDA PUBLIC SERVICE COMMISSION

453

1       not work at a nuclear plant.

2            Q.   Okay.  What is the philosophy behind the eight

3       hours?

4            A.   The eight hours, and hopefully this will

5       clarify any confusion that we had on it.  The eight

6       hours in my testimony was my -- I won't say guess, but

7       was my determination of the time period that the Flagami

8       Transmission Event impacted the stability of FPL's

9       system.  In other words, the policy behind that and

10       behind the Company's approach is what was the time

11       period that the Flagami event affected the stability of

12       FPL's system.  And so when I testified yesterday in my

13       determination in looking at all of the data being able

14       to see the realtime output of all of our generating

15       units on our energy management system, that time frame

16       was eight hours.

17                 So, in other words, at 1:10 p.m. on

18       February 26th the event occurred.  By approximately

19       9:10 that night we had -- everything that had been

20       brought on in response to the event had been shut down,

21       and that is predominately the peaking units that we

22       discussed yesterday.  So all of the peaking units

23       brought on, and we did bring all of them on in response

24       to the event, had been shut down approximately 9:00 to

25       9:15 time frame.  All of the purchased power that we

FLORIDA PUBLIC SERVICE COMMISSION

454

1       bought in response to the event specifically had been

2       sent back to the customers that we had procured it from.

3                 A majority of the gas-fired plants that had

4       come off the line also in response to the event had been

5       brought back on-line.  And keep in mind there was

6       roughly 1,600 megawatts of gas-fired generation that

7       came off.  Most of that had been brought back on within

8       that eight-hour period.

9                 So in looking at the system being able to

10       return to a normal economic dispatch, that is the

11       determination I made that at that eight-hour mark the

12       system had become stable again and we had recovered from

13       the transmission event at Flagami.

14            Q.   You just mentioned the word normal, the system

15       returned to a normal state.  What is your definition of

16       normal, or is the definition recognized -- and is that

17       definition recognized by the electric industry?

18            A.   Can you repeat that last part?

19            Q.   What is your definition of normal?  When you

20       say the system returned to a normal state, what is your

21       definition of normal?

22            A.   When I look at our system operating in a

23       normal state it is that most of our units that have not

24       fully loaded up to the top are in automatic.  In other

25       words, they are controlling with the load of the system.

FLORIDA PUBLIC SERVICE COMMISSION

455

1       As the load is coming up or as the load is coming down

2       our system is pulsing.  Our units that are in automatic,

3       they are responding to that load to match generation

4       with load.  That is a normal operating condition on

5       Florida Power and Light's system, and that is where we

6       returned to at that point in time, approximately that

7       point in time that evening.

8            Q.   Is that your personal definition or is that an

9       industry standard definition?

10            A.   I honestly do not know what an industry

11       standard definition would be of normal.  That is my

12       definition.  And I believe, though, if I were to look at

13       it across the board, if any company's system was

14       operating with its units on-line in automatic responding

15       to load, that would be considered normal.  I'm not an

16       expert to make that claim, it is my opinion, but that is

17       my definition of normal.

18                 COMMISSIONER SKOP:  Mr. Young, can you yield

19       for a moment?  I'd like to get a clarification.

20                 Mr. Yupp, you mentioned normal economic

21       dispatch and that that state had occurred approximately

22       eight hours after the event in question, is that

23       correct?

24                 THE WITNESS:  Yes.

25                 COMMISSIONER SKOP:  Okay.  You would agree,

FLORIDA PUBLIC SERVICE COMMISSION

456

1       would you not, that nuclear is the lowest cost

2       dispatchable unit on FPL's generating system, is that

3       correct?

4                 THE WITNESS:  Yes, I would agree with that.

5                 COMMISSIONER SKOP:  But both nuclear units

6       were not on-line within eight hours, is that correct?

7                 THE WITNESS:  That is correct, also.

8                 COMMISSIONER SKOP:  And Witness Stall has

9       testified that it would normally take an unplanned

10       shutdown at least 48 hours to bring those units back

11       on-line, is that correct?

12                 THE WITNESS:  That is correct.

13                 COMMISSIONER SKOP:  Thank you.

14                 THE WITNESS:  And maybe one point of

15       clarification on that, Commissioner Skop --

16                 COMMISSIONER SKOP:  You're recognized.

17                 THE WITNESS:  -- with your question is that,

18       again, economic dispatch based on the units that were

19       available to run.

20                 COMMISSIONER SKOP:  And that's an important

21       clarification.  Thank you.

22                 Mr. Young, you're recognized.

23                 MR. YOUNG:  No further questions.

24                 COMMISSIONER SKOP:  Thank you.

25                 From the bench, Commissioners, any questions?

FLORIDA PUBLIC SERVICE COMMISSION

457

1       Commissioner Klement.

2                 COMMISSIONER KLEMENT:  Yes.

3                 Mr. Yupp, looking at your testimony on Page 3,

4       starting with Line 14, the question that refers to

5       other -- the question generates some additional cost

6       projections by you, and then it goes to Exhibit GJY-12

7       where the net -- let me see if I have it right.  The net

8       fuel replacement cost is changed from the previous

9       projections.  You have projected a $6 million projection

10       at the rate of calculation according to Mr. Dismukes,

11       and a 3 million according to FPL's average.  I'm trying

12       to understand why those -- why that set of projections

13       was included here.

14                 THE WITNESS:  Basically, the intent of

15       including these numbers within my rebuttal testimony

16       were to provide support to the Rebuttal testimony and

17       Direct Testimony, for that matter, of Mr. Stall.  We

18       have talked a lot about the typical time frame to return

19       a unit, a nuclear unit to service is 48 hours.  And I

20       think the point of it in my rebuttal was to give this

21       Commission at least an idea of, you know, compared to

22       the $2 million that we are proposing, and I know is

23       15.9 million that OPC has in this.  What does 48 hours

24       look like from a cost perspective, not only based on

25       nuclear avoided, but also on a system average.  So,

FLORIDA PUBLIC SERVICE COMMISSION

458

1       purely for reference.

2                 COMMISSIONER KLEMENT:  Thank you.  That's all

3       I have.

4                 COMMISSIONER SKOP:  Thank you, Commissioner.

5                 Any additional questions from the bench?

6                 Hearing none; Mr. Butler, you're recognized

7       for redirect.

8                 MR. BUTLER:  Thank you, Commissioner Skop.

9                         REDIRECT EXAMINATION

10       BY MR. BUTLER:

11            Q.   Mr. Yupp, would you turn to Page 1 in your

12       rebuttal testimony following up on a question by Ms.

13       Kaufman.  On Line 21 you present a fuel savings figure

14       of $7.7 billion, and then you have parenthetically

15       $3 billion more than estimated return.  Do you see that?

16            A.   Yes, I do.

17            Q.   Would it be fair to characterize the 3 billion

18       figure as being sort of a net fuel savings to customers

19       above and beyond what they have had to pay for the

20       nuclear units?

21            A.   Yes, that would be a fair characterization.

22            Q.   Commissioner Skop asked you a couple of

23       questions about the definition of normal operations, or

24       returning to a stable automatic control position, and

25       you had mentioned clarifying to his questions that on

FLORIDA PUBLIC SERVICE COMMISSION

459

1       February 26th when you were seeing a return to that

2       condition after eight hours that it was, you know,

3       economic dispatch given the units that were available to

4       provide service at that time, correct?

5            A.   Correct.

6            Q.   Is that normally the way that FPL would look

7       at economic dispatch is given the units that are

8       available to operate at any particular point in time?

9            A.   Yes.  Our normal mode of operation on a day to

10       day basis is economic dispatch operating with units

11       responding to load in automatic, and on any given day

12       there may be units out of service.  So it does apply to

13       the units that are available we operate in economic

14       dispatch.

15                 MR. BUTLER:  Thank you.  That's all the

16       redirect that I have.

17                 COMMISSIONER SKOP:  Thank you, Mr. Butler.

18                 That takes us to exhibits, and I believe we

19       have Exhibits 23 through 25.

20                 MR. BUTLER:  Yes.  I would move Exhibits 23

21       through 25.  Thank you.

22                 COMMISSIONER SKOP:  Any objections from the

23       parties?  Hearing none, show Exhibits 23 through 25

24       entered into the record.

25                 And, Mr. Yupp, you are excused.

FLORIDA PUBLIC SERVICE COMMISSION

460

1                 THE WITNESS:  Thank you.

2                 MR. BUTLER:  Thank you.

3                 (Exhibit Number 23 through 25 admitted into

4       the record.)

5                 COMMISSIONER SKOP:  And, Commissioners, just

6       for planning purposes, we had hoped to break for lunch

7       at 12:00.  We had had a request from a Commissioner to

8       delay that until at least 12:30, so I'd like to continue

9       moving forward with witnesses, but this would be good

10       time to take a five-minute break.  So we will stand

11       adjourned.

12                 (Recess.)

13                 COMMISSIONER SKOP:  Okay.  We're going to go

14       back on the record.  And, Mr. Butler, call your next

15       witness.

16                 MR. BUTLER:  Thank you, Commissioner Skop.  We

17       call Dr. Avera, who has been previously sworn.

18                          WILLIAM E. AVERA

19       was called as a witness on behalf of Florida Power &

20       Light Company and, having been duly sworn, testified as

21       follows:

22                          DIRECT EXAMINATION

23       BY MR. BUTLER:

24            Q.   Dr. Avera, would you please state your name

25       and business address for the record?

FLORIDA PUBLIC SERVICE COMMISSION

461

1            A.   William E. Avera, 3907 Red River, Austin,

2       Texas.

3            Q.   And by whom are you employed and in what

4       capacity?

5            A.   I'm the President of FINCAP, Incorporated.

6            Q.   Thank you.  Have you caused to be prepared and

7       filed in this docket 17 pages of rebuttal testimony?

8            A.   Yes, sir.

9            Q.   Okay.  Do you have any changes or corrections

10       to your rebuttal testimony?

11            A.   I have one change to make it consistent with

12       Dr. Dismukes' errata.

13                 On Page 11 at Line 22, the number that appears

14       in that line at the end of the line should be

15       13,950,020.  13,950,020.

16            Q.   Thank you.  Is that the only change to your

17       testimony?

18            A.   Yes, sir.

19            Q.   With that change, if I asked you the questions

20       contained in your prefiled rebuttal testimony, would

21       your answers be the same today?

22            A.   They would be.

23                 MR. BUTLER:  Commissioner Skop, I ask that

24       Dr. Avera's prefiled rebuttal testimony be inserted into

25       the record as though read.

FLORIDA PUBLIC SERVICE COMMISSION

462

1                 COMMISSIONER SKOP:  The prefiled rebuttal

2       testimony of the witness will be entered into the record

3       as though read.

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

480

1                 MR. BUTLER:  Thank you.  And Dr. Avera's

2       rebuttal testimony has no exhibits to it.  So with that,

3       I would ask that he summarize his rebuttal testimony.

4                 THE WITNESS:  Good afternoon, Commissioners.

5       My rebuttal responds to the economic and policy

6       arguments in Dr. Dismukes' testimony.  Dr. Dismukes

7       concludes his testimony with the statement, "The

8       company's proposal does not reflect the actual cost of

9       energy associated, replacement cost of energy associated

10       with the transmission-created outage of February 2008."

11                 Despite his recognition that the Flagami

12       transmission event was not caused by imprudent nuclear

13       operations, his recommended calculation of replacement

14       energy treats the outage as if it were nuclear created.

15       In other words, the replacement power cost calculation

16       proposed by Dr. Dismukes is identical to that which

17       would be made if the nuclear units had been operated

18       imprudently, and thus substantially overstates the

19       appropriate amount of RPC attributable to the Flagami

20       transmission event.

21                 Dr. Dismukes claims that the company's

22       proposal is not consistent with sound economic

23       principles and regulatory policy.  In fact, separation

24       of cost based on causation is a fundamental tenet of

25       sound economics and good regulatory policy.  Failing to

FLORIDA PUBLIC SERVICE COMMISSION

481

1       distinguish between transmission-related costs and

2       generated-related, generation-related costs would be

3       unsound economics and counterproductive regulatory

4       policy because it overstates replacement power credit

5       and undermines existing incentives in Florida to

6       encourage energy efficiency.  That completes my rebuttal

7       summary.

8                 MR. BUTLER:  Thank you, Dr. Avera.  I tender

9       the witness for cross-examination.

10                 COMMISSIONER SKOP:  Thank you, Mr. Butler.

11                 Mr. Beck, you're recognized, or

12       Mr. McGlothlin.  Sorry.

13                          CROSS EXAMINATION

14       BY MR. McGLOTHLIN:

15            Q.   Dr. Avera, you've mentioned in your summary

16       your distinction between transmission-related costs and

17       generation-related costs.  And those distinctions appear

18       several times in your rebuttal testimony, do they not?

19            A.   Yes, sir.

20            Q.   And for purposes of my question, I'm looking

21       at Page 9, Line 17, in which you, where you say in part,

22       you assert that Dr. Dismukes' approach completes the

23       transmission-related costs with generation-related

24       costs.  Do you see that sentence?

25            A.   Yes.

FLORIDA PUBLIC SERVICE COMMISSION

482

1            Q.   You would agree with me, sir, would you not,

2       that transmission events can cause generation impacts?

3            A.   Yes.  Transmission events can cause generation

4       impacts.

5            Q.   And in terms of measuring that, you are here

6       to support for policy reasons the, the calculations that

7       Mr. Yupp provided in his testimony, do you not?

8            A.   That's correct.  Because I believe it properly

9       separates transmission cost from the subsequent

10       generation cost.

11            Q.   And as part of that rationale, you and your

12       client assert that there was no imprudence associated

13       with taking the nuclear units offline; correct?

14            A.   That is correct.  And I believe I heard

15       Dr. Dismukes not disagree with that.  He certainly

16       doesn't in his testimony and he didn't in his live

17       testimony.

18            Q.   Now the calculation provided by Witness Yupp

19       that you endorse includes as one component the use of

20       heat rates, does it not?

21            A.   Yes.  That's how we arrive at the adjusted

22       system cost, or how Mr. Yupp arrived at that.

23            Q.   And would you agree with me that heat rates

24       are an aspect of generators, not transmission lines?

25            A.   That is correct.  The heat rate is the

FLORIDA PUBLIC SERVICE COMMISSION

483

1       transformation of, of fuel to electric energy.  That can

2       only be done in generators.  Transmission convey the

3       energy across the system.

4            Q.   Another component of the calculation is fuel

5       cost; correct?

6            A.   Yes.

7            Q.   And there the calculation refers to fuel costs

8       of generators, not transmission lines.

9            A.   That is correct.  Because in order to insulate

10       the transmission-related cost we had to use the system

11       average cost.  Because during that eight-hour period, as

12       Mr. Yupp testified, there was not the availability of

13       the normal economic dispatch of generators.

14            Q.   Including the Turkey Point nuclear generators,

15       they were unavailable during that time frame and beyond;

16       correct?

17            A.   That is correct.  As well as fossil fuel

18       generators.  I believe 4,300 megawatts was unavailable

19       instantly and then they started coming back.

20            Q.   Now with respect to the 4,300 megawatts of

21       generation that was unavailable, that includes Turkey

22       Point 3 and 4 plus other units; correct?

23            A.   Yes, sir.

24            Q.   And some of those other units have been

25       incorporated into the calculation of system average

FLORIDA PUBLIC SERVICE COMMISSION

484

1       costs?

2            A.   Yes, sir.  I believe what Mr. Yupp did is went

3       back and reconstruct system average cost as if all units

4       had been available, including Turkey Point.  And that

5       becomes the, the baseline from which you compare the

6       actual cost during the eight hours of the transmission

7       disturbance.

8            Q.   And with respect to the units other than

9       Turkey Point 3 and 4 that are incorporated in that

10       calculation, there has been no issue of imprudence in

11       the way they were taken offline in terms of the

12       operation of those units, has there?

13            A.   That is correct.  Just as there's not been for

14       Turkey Point.

15            Q.   Now throughout the case some of the witnesses

16       have referred to the acronym RPC.  You're familiar with

17       that?

18            A.   Yes.

19            Q.   What does the R stand for in RPC?

20            A.   Replacement.

21                 MR. McGLOTHLIN:  That's all the questions I

22       have.

23                 COMMISSIONER SKOP:  Thank you, Mr. McGlothlin.

24                 Ms. Bradley, you're recognized.

25                          CROSS EXAMINATION

FLORIDA PUBLIC SERVICE COMMISSION

485

1       BY MS. BRADLEY:

2            Q.   Sir, can you tell me if we exclude the nuclear

3       plants, what was the generation loss associated with

4       this event?

5            A.   Well, I believe the nuclear plants were

6       1,400 megawatts, and the generation loss was 4,300.  So

7       the difference would be the other generation that for

8       some period of time or another was, was impacted.

9            Q.   Where did you get those figures?

10            A.   I think the figures are in the FERC report.

11            Q.   Where does it say that the generation loss

12       excluding the nuclear plants was 4,300?

13            A.   It doesn't say that.  It says 4,300.  I know

14       from other sources that the Turkey Point units were

15       1,400 together.  So the FERC report does not distinguish

16       between the nuclear units and other generation.

17            Q.   So you just decided to subtract that?

18            A.   Well, I think I was trying to respond to your

19       question.  4,300 is in the FERC report.  Other sources

20       tell me the Turkey Point generation.  So if the question

21       is how much generation other than Turkey Point, you do

22       the subtraction.

23            Q.   But the FERC report does not say that the

24       4,300 excludes the nuclear plants, does it?

25            A.   It does not.  It explicitly says all -- that

FLORIDA PUBLIC SERVICE COMMISSION

486

1       is their measure of all of the generation that was

2       affected.

3            Q.   So you just made that assumption based upon

4       your opinion; correct?

5            A.   Well, I think it's a reasonable -- if that's

6       the total amount and we know that included in that

7       amount was Turkey Point, and if the question is how much

8       megawatts other than Turkey Point, you would subtract

9       Turkey Point from the 4,300.

10            Q.   Okay.  So the 4,300 includes Turkey Point?

11            A.   Yes, it does.

12            Q.   Okay.  I misunderstood what you said.  I

13       apologize.

14            A.   Well, maybe I -- I'm glad we're on the same

15       page.

16                 MS. BRADLEY:  Thank you.  No further

17       questions.

18                 COMMISSIONER SKOP:  Thank you, Ms. Bradley.

19                 Ms. Kaufman, you're recognized.

20                 MS. KAUFMAN:  Commissioner, I have no

21       questions.

22                 COMMISSIONER SKOP:  Thank you.

23                 Staff?

24                 MR. YOUNG:  Mr. Chairman, if I can indulge, if

25       I can bear your indulgence for one minute.

FLORIDA PUBLIC SERVICE COMMISSION

487

1                 COMMISSIONER SKOP:  Very well.  I'll move on

2       to one other question.  To Mr. Butler, I guess they had

3       previously, in response to my question regarding the

4       legal agreement from the NRC, they pointed to a Bates

5       number, and I've subsequently had the opportunity to

6       look at that.  Can they specifically identify exactly on

7       what page and what paragraph the requirement as to at

8       the next shutdown you have to do the repairs?

9                 MR. BUTLER:  I'm going to ask Mr. Ross to

10       address that.  He's more familiar with the agreement

11       than I.

12                 MR. ROSS:  Do you have it in front of you,

13       Commissioner Skop?

14                 COMMISSIONER SKOP:  I do.

15                 MR. ROSS:  If you turn to Bates Number 395.

16                 COMMISSIONER SKOP:  Okay.  And which

17       paragraph?

18                 MR. ROSS:  It's -- at the bottom of the page

19       there is a footnote indicated by two asterisks.

20                 COMMISSIONER SKOP:  Okay.  All right.  I'll

21       just look at that.  If I have additional questions --

22       thank you.

23                 MR. ROSS:  Okay.

24                 COMMISSIONER SKOP:  Mr. Young, are you ready

25       to go, or do you need a few minutes?

FLORIDA PUBLIC SERVICE COMMISSION

488

1                 MR. YOUNG:  I'm ready, sir.

2                 COMMISSIONER SKOP:  All right.  You're

3       recognized.  Thank you.

4                          CROSS EXAMINATION

5       BY MR. YOUNG:

6            Q.   Dr. Avera, you heard Ms. Bennett's questions

7       to Dr. Dismukes this morning; correct?

8            A.   Yes.

9            Q.   Do you agree that this is a, that this is a

10       policy decision for the Commission?

11            A.   Yes.  I think it's a significant policy

12       decision.

13            Q.   Are there any times, are there any times when

14       risks of a transmission event should be borne only, only

15       by the utility?

16            A.   Well, I believe that the calculation that we

17       presented sorts out the transmission-related cost, and I

18       think FPL has agreed to bear those costs.  So I believe

19       the $2,024,035 that Mr. Yupp has calculated represents

20       the transmission-related costs from the Flagami outage

21       that should be borne by the company.

22            Q.   But let me ask it again.  And if you can

23       answer yes, no, and then explain your answer.

24                 Are there any times when risk of a

25       transmission event should be borne only by the utility?

FLORIDA PUBLIC SERVICE COMMISSION

489

1            A.   Yes.

2            Q.   Okay.  When?

3            A.   When it is found that the utility has

4       improperly managed their responsibilities or when they

5       agree to it.  Yesterday Mr. McGlothlin gave me a series

6       of documents where investors are told that companies may

7       not be able to recover costs when there is a finding of

8       imprudence or improper behavior.

9            Q.   We're going to come back, come back to that.

10                 Dr. Avera, do you know of any case similar to

11       this case?

12            A.   No, not that has exactly the same fact

13       patterns where you have a transmission event for which

14       the company is responsible and then the issue is

15       replacement power costs that would extend to a nuclear

16       plant.

17            Q.   So this case is very uncommon.

18            A.   It is.  It's the first -- 40 years of

19       experience, and this is number one for me.

20                 MR. YOUNG:  All right.  No further questions.

21                 COMMISSIONER SKOP:  Thank you.  Questions from

22       the bench?

23                 Commissioner Klement, you're recognized.

24                 COMMISSIONER KLEMENT:  Thank you.

25                 This reveals my lack of knowledge of nuclear

FLORIDA PUBLIC SERVICE COMMISSION

490

1       that the acting Chairman may have more of than I, but

2       it's to Mr. Butler or FPL.  In regard to that, the

3       answer to his question at the bottom of Page 395 and the

4       bracketed double asterisk at the bottom, what does Mode

5       3 mean, please?

6                 MR. BUTLER:  Mode 3 is the mode in which the

7       unit is no longer making nuclear power.  The reaction,

8       the critical reaction has stopped.  And so basically, as

9       I understand it, I was actually just talking to Mr. Ross

10       about this during the questioning, this could be in a

11       planned outage, could be in an unplanned outage, just

12       whenever the unit is brought down to that point.  And I

13       would note just as an aside that clearly if it's a

14       planned outage where you're refueling, you have to bring

15       it down not only to Mode 3 but below that to get it to

16       the cold conditions that you would actually be moving

17       fuel in and out.

18                 But the Mode 3 is sort of the break point.  If

19       you go into that mode where the reactivity in the

20       reaction, excuse me, in the reactor has been terminated,

21       then that would be the triggering event for having to do

22       these repairs.

23                 COMMISSIONER KLEMENT:  Thank you.  That's all

24       I have, Chairman.

25                 COMMISSIONER SKOP:  Thank you, Commissioner.

FLORIDA PUBLIC SERVICE COMMISSION

491

1       Any other questions?

2                 Okay.  I guess that brings us to redirect,

3       Mr. Butler or Mr. Ross.

4                 MR. BUTLER:  It is I, and I have no redirect.

5                 COMMISSIONER SKOP:  Thank you.  And there's no

6       exhibits for this witness, so.

7                 MR. BUTLER:  No exhibits.

8                 COMMISSIONER SKOP:  Dr. Avera, you're excused.

9                 THE WITNESS:  Thank you.

10                 COMMISSIONER SKOP:  Mr. Butler, call your next

11       witness.

12                 MR. BUTLER:  Thank you.  That would be

13       Mr. Keith, our final witness.

14                 COMMISSIONER SKOP:  Commissioners, I think

15       we'll get through this relatively quickly, I'm hopeful,

16       so we'll see.  If not, we'll adjourn, but --

17                            TERRY J. KEITH

18       was called as a witness on behalf of Florida Power &

19       Light Company and, having been duly sworn, testified as

20       follows:

21                          DIRECT EXAMINATION

22       BY MR. ROSS:

23            Q.   Good afternoon, Mr. Keith.

24            A.   Good afternoon.

25            Q.   Have you prepared and caused to be filed in

FLORIDA PUBLIC SERVICE COMMISSION

492

1       this proceeding rebuttal testimony totaling six pages?

2            A.   I have.

3            Q.   Do you have any changes or corrections to that

4       testimony?

5            A.   I do not.

6            Q.   If I asked you the questions contained in your

7       rebuttal testimony today, would your answers be the

8       same?

9            A.   Yes, it would.

10                 MR. ROSS:  Mr. Chairman, I'd request that the

11       rebuttal testimony of Mr. Keith be entered into the

12       record as if read.

13                 COMMISSIONER SKOP:  The rebuttal testimony of

14       the witness will be entered into the record as though

15       read.

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

499

1       BY MR. ROSS:

2            Q.   Mr. Keith, have you prepared a summary of your

3       rebuttal testimony?

4            A.   Yes, I did.

5            Q.   Would you please provide that summary to the

6       Commission?

7            A.   Sure.  Good afternoon, Commissioners.  My

8       rebuttal testimony responds to Dr. Dismukes' claim that

9       FPL should be responsible for the replacement power

10       costs of the entire duration of the Turkey Point

11       outages.  I remind the Commission of its well-founded

12       practice to limit disallowances of replacement power

13       costs to the portion of outages that are directly

14       related to imprudent actions of a utility.

15                 In this case there is no testimony that claims

16       imprudent actions at Turkey Point's nuclear power plant

17       during or after the transmission event.  In fact, FPL

18       witness Stall testifies that FPL actions were indeed

19       prudent.

20                 In addition, my testimony clarifies that the

21       fuel adjustment process in Florida does not lend itself

22       to realtime price signals for customers because the fuel

23       factors paid by customers are levelized over the

24       calendar year, which they prefer, and are based on a

25       combination of projections and prior period cost

FLORIDA PUBLIC SERVICE COMMISSION

500

1       adjustments that ensures customers only pay for the

2       actual cost of FPL's fuel usage.

3                 Finally, Dr. Dismukes claims that FPL's base

4       rates are higher than peer utilities, with the

5       implication that recovery of FPL's nuclear investments

6       is the reason for higher base rates.  Utilities

7       constantly make tradeoffs between capital, O&M and fuel

8       costs, plus different jurisdictions as well as different

9       utilities recover their costs through a combination of

10       base rates and adjustment clauses.  Therefore, the only

11       true comparison is the utility's total bill.  FPL's

12       total bill is the lowest among all Florida utilities and

13       10 percent below the national average.  This concludes

14       my summary.  Thank you.

15                 MR. ROSS:  I tender the witness for cross.

16                 COMMISSIONER SKOP:  Thank you, Mr. Ross.

17                 Mr. McGlothlin, you're recognized.

18                 MR. McGLOTHLIN:  No questions.

19                 COMMISSIONER SKOP:  Thank you.

20                 Ms. Bradley.

21                 MS. BRADLEY:  No questions.

22                 COMMISSIONER SKOP:  Thank you.

23                 Ms. Kaufman.

24                 MS. KAUFMAN:  I'm afraid I do have one

25       question.

FLORIDA PUBLIC SERVICE COMMISSION

501

1                 COMMISSIONER SKOP:  You're recognized.

2                          CROSS EXAMINATION

3       BY MS. KAUFMAN:

4            Q.   Mr. Keith, if you turn to Page 3 of your

5       rebuttal testimony.

6            A.   Okay.

7            Q.   And beginning on Line 15 you quote from Order

8       Number 23232, and we've had some discussion about that

9       already.  Am I correct?

10            A.   That's correct.

11            Q.   Am I correct, as you said on Page 15, that the

12       outage that was at issue there occurred concurrently

13       with an outage that had already been scheduled; is that

14       correct?

15            A.   Yes.

16            Q.   And in the case that we have talked about

17       here, the outage that is at issue did not occur at the

18       same time as a planned outage, did it?

19            A.   No.  I think the difference here is that this

20       outage actually, this portion of the outage started, was

21       extended, started three days prior to when the planned

22       outage was.  So as a result, that's the portion of the

23       time that the Commission held the company responsible

24       for replacement power costs.

25            Q.   Right.  And in the situation in Order 23232

FLORIDA PUBLIC SERVICE COMMISSION

502

1       the portion of the outage after the initial three days

2       was an outage that had already been previously

3       scheduled; correct?

4            A.   Correct.

5                 MS. KAUFMAN:  Thank you.  That's all I have.

6                 COMMISSIONER SKOP:  Thank you, Ms. Kaufman.

7                 Staff.

8                 MS. BENNETT:  No questions.

9                 COMMISSIONER SKOP:  Commissioners, questions

10       from the bench?  Hearing none, that brings us to

11       redirect.

12                 Mr. Ross.

13                 MR. ROSS:  No redirect.

14                 COMMISSIONER SKOP:  Thank you.  No exhibits,

15       so, Mr. Keith, you're excused.  And staff --

16                 THE WITNESS:  Thank you.

17                 MS. BENNETT:  Just as a follow-up, I think

18       Mr. Butler and Mr. Beck were going to move all of their

19       witnesses' testimony.

20                 MR. BUTLER:  In an abundance of caution, I

21       would make an omnibus motion for entering into the

22       record any testimonies that may have inadvertently not

23       been entered into the record as though read.

24                 COMMISSIONER SKOP:  The motion is granted, and

25       the prefiled testimony of the witnesses as well as any

FLORIDA PUBLIC SERVICE COMMISSION

503

1       exhibits that have not been objected to will, are shown

2       as entered.

3                 MR. BUTLER:  Thank you.

4                 COMMISSIONER SKOP:  And, Mr. Beck, do you have

5       the same --

6                 MR. BECK:  We concur.

7                 COMMISSIONER SKOP:  All right.  Thank you.

8       Okay, staff, any other matters before we close the

9       record?

10                 MS. BENNETT:  No.

11                 COMMISSIONER SKOP:  Okay.  Hearing none, the

12       record is closed.  And if staff could briefly provide

13       the dates for the posthearing decision for the parties

14       before we conclude.

15                 MS. BENNETT:  Very good.  The transcript will

16       be available on March 29th.  Briefs will be due

17       April 19th.

18                 The staff recommendation is May 19th.  And

19       this will come back to the Commission for its Agenda

20       Conference on June 1st.

21                 COMMISSIONER SKOP:  Very well.  Any other

22       additional matters that need to be addressed before we

23       adjourn?

24                 MS. BENNETT:  Staff has none.

25                 COMMISSIONER SKOP:  Okay.  Commissioners?

FLORIDA PUBLIC SERVICE COMMISSION

504

1                 Hearing none, we stand adjourned.  Thank you.

2                 (Proceeding adjourned at 12:35 p.m.)

3

4

5

6

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

505

1       STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2       COUNTY OF LEON      )

3

4                 I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing

5       proceeding was heard at the time and place herein

stated.

6

IT IS FURTHER CERTIFIED that I

7       stenographically reported the said proceedings; that the

same has been transcribed under my direct supervision;

8       and that this transcript constitutes a true

transcription of my notes of said proceedings.

9

I FURTHER CERTIFY that I am not a relative,

10       employee, attorney or counsel of any of the parties, nor

am I a relative or employee of any of the parties'

11       attorneys or counsel connected with the action, nor am I

financially interested in the action.

12

DATED THIS _____ day of _____________________,

13       2010.

14

15                  ________________________________

LINDA BOLES, RPR, CRR

16                 FPSC Official Commission Reporter

(850) 413-6734

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION