1

1                              BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3       In the Matter of:

4       REVIEW OF 2010 ELECTRIC          DOCKET NO. 100262-EI

INFRASTRUCTURE STORM HARDENING

5       PLAN FILED PURSUANT TO RULE

25-6.0342, F.A.C., SUBMITTED

6       BY PROGRESS ENERGY FLORIDA,

INC.

7       -------------------------------

REVIEW OF 2010 ELECTRIC          DOCKET NO. 100263-EI

8       INFRASTRUCTURE STORM HARDENING

PLAN FILED PURSUANT TO RULE

9       25-6.0342, F.A.C., SUBMITTED

BY TAMPA ELECTRIC COMPANY.

10       -------------------------------

REVIEW OF 2010 ELECTRIC          DOCKET NO. 100264-EI

11       INFRASTRUCTURE STORM HARDENING

PLAN FILED PURSUANT TO RULE

12       25-6.0342, F.A.C., SUBMITTED

BY FLORIDA PUBLIC UTILITIES

13       COMPANY.

-------------------------------

14       REVIEW OF 2010 ELECTRIC          DOCKET NO. 100265-EI

INFRASTRUCTURE STORM HARDENING

15       PLAN FILED PURSUANT TO RULE

25-6.0342, F.A.C., SUBMITTED

16       BY GULF POWER COMPANY.

-------------------------------

17       REVIEW OF 2010 ELECTRIC          DOCKET NO. 100266-EI

INFRASTRUCTURE STORM HARDENING

18       PLAN FILED PURSUANT TO RULE

25-6.0342, F.A.C., SUBMITTED BY

19       FLORIDA POWER & LIGHT COMPANY.

________________________________/

20

21

22

23       PROCEEDINGS:             IOUs STORM HARDENING WORKSHOP

24

DATE:                    Thursday, June 10, 2010

25

FLORIDA PUBLIC SERVICE COMMISSION

2

1       TIME:                    Commenced at 9:30 a.m.

Concluded at 11:29 a.m.

2

3       PLACE:                   Betty Easley Conference Center

Room 148

4                                4075 Esplanade Way

Tallahassee, Florida

5

REPORTED BY:             JANE FAUROT, RPR

6                                Official FPSC Reporter

(850) 413-6732

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

3

1       PRESENTATIONS BY:                                 PAGE

2       David T. Bromley, Florida Power and Light           6

3       Eric Sachon, Progress Energy Florida, Inc.         22

4       T.J. Szelistowski, Tampa Electric Company          42

5       Ed Battaglia, Gulf Power Company                   58

6       Jorge Puentes, Florida Public Utilities Company    72

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

4

1                         P R O C E E D I N G S

2

3

4                 MS. L'AMOREAUX:  Okay.  Before we get started,

5       I'm just going to go over some housekeeping items.

6       There is a sign-in sheet and the copies of the

7       presentations to your right.  If everyone can please

8       sign in and get a copy, then we will begin.

9                 Good morning, everybody.  I'm Melissa

10       L'Amoreaux with staff.  Following the 2004/2005

11       hurricane season, the Florida Public Service Commission

12       took several steps to minimize future storm damage to

13       electric infrastructure and resulting outages to

14       customers.  In addition to requiring pole inspections,

15       vegetation management, and other actions, on

16       February 27th, 2006, the Commission directed staff to

17       begin rulemaking proceedings to require electric

18       utilities to strengthen Florida's electrical

19       transmission and distribution infrastructure to better

20       withstand severe weather events.  The Florida Public

21       Service Commission also issued an order that required

22       investor-owned utilities to file plans and estimate

23       implementation costs for the ten on-going storm

24       preparedness initiatives.

25                 On May 7th, 2007, Florida Power and Light,

FLORIDA PUBLIC SERVICE COMMISSION

5

1       Progress Energy Florida, Tampa Electric Company, and

2       Gulf Power each filed their respective 2007 electric

3       infrastructure storm hardening plan, which included

4       wooden pole inspection programs and the ten on-going

5       initiatives.  On December 28th, 2007, the Commission

6       voted to approve all four plans.

7                 Florida Public Utilities Company requested and

8       was allowed to file its storm hardening plan as part of

9       its general rate case.  Florida Public Utilities

10       Company's storm hardening plan was approved May 19th,

11       2008.  Consistent with Rule 25-6.0342, also known as the

12       Storm Hardening Rule, the Commission order approving the

13       storm hardening plans require that each plan be updated

14       and filed with the Commission every three years.

15                 The first plan updates for the IOUs were filed

16       May 3rd, 2010.  The storm hardening rule requires that

17       each plan contain a description of the IOU's

18       construction standards, policies, practices, and

19       procedures to enhance the reliability of overhead and

20       underground electrical transmission and distribution

21       facilities.

22                 We are here today pursuant to notice issued

23       May 11th, 2010.  This time and place has been set for

24       the review of the 2010 electric infrastructure storm

25       hardening plan updates filed pursuant to the storm

FLORIDA PUBLIC SERVICE COMMISSION

6

1       hardening rule.  By letter dated May 21st, 2010, staff

2       has asked each IOU to discuss five key topics at today's

3       workshop.  Those topics are briefly discuss the ten

4       on-going initiatives; compare and contrast the approved

5       plans versus the updated plans; address any budget

6       concerns and impacts of any changes to the updated

7       plans; briefly explain any struggles encountered in

8       achieving the ten on-going initiatives; and explain how

9       restoration and hardening is improving the overall

10       system.

11                 The letter also indicated that staff proposed

12       the presentations be in this order:  Florida Power and

13       Light, Progress Energy Florida, Tampa Electric Company,

14       Gulf Power, and FPUC.  With that, I'll hand it off to

15       David Bromley with Florida Power and Light.

16                 MR. BROMLEY:  Good morning.  My name is David

17       Bromley.  I'm the Manager of Regulatory Activities for

18       Distribution Business for FPL.  I'm going to try to

19       provide you an update today on our storm preparedness

20       initiatives as well as our hardening plans.

21                 The initiatives and hardening plans cover

22       various departments within FPL's distribution and

23       transmission business units.  While we haven't been able

24       -- weren't able to bring everybody associated with

25       implementing these plans, we did bring some individuals

FLORIDA PUBLIC SERVICE COMMISSION

7

1       to potentially help answer any questions you all may

2       have.  As to the extent that you have questions we can't

3       answer today, we certainly would be glad to answer them

4       subsequently.

5                 I'm planning to cover first the ten storm

6       preparedness initiatives, and then we will go into the

7       specific hardening plans.  Storm preparedness Initiative

8       No. 1 deal with our vegetation management initiative.

9       We are continuing to maintain our feeders on a

10       three-year average cycle.  Our laterals are continuing

11       to ramp up to reach a six-year average cycle by 2013,

12       and we are continuing to emphasize removing trees when

13       we can with customers in order to avoid problem trees.

14       This certainly is our most costly initiative of the ten

15       storm preparedness initiatives.  In 2010, we expect or

16       plan to spend around $61 million associated with this

17       plan.

18                 This is consistent with what was previously

19       approved by the Commission in 2007.  All of our storm

20       preparedness initiatives as well as our hardening plan

21       are really a continuation of what was approved back in

22       2007 with the exception of one, which I will get into

23       later, small tweak associated with a transmission pole

24       replacement.  Our plans are essentially the same.  We

25       are continuing the same path as what we had originally

FLORIDA PUBLIC SERVICE COMMISSION

8

1       been approved for.

2                 Joint use, Initiative No. 2, is associated

3       with two initiatives in that plan.  One is looking at

4       viewing on a five-year cycle all of the attachments to

5       FPL's facilities.  And really this is for primarily

6       billing purposes as well as assuring that the

7       attachments have been authorized to attach to FPL

8       facilities.  So every five years we complete a cycle

9       through our old system and those billings are trued up

10       and any unauthorized attachments are identified and

11       taken care of and addressed with attachers.

12                 Historically our number of unauthorized

13       attachments is very small.  We have a permitting process

14       that we use and it seems to work very well and it's not

15       a concern for FPL.  We also conduct as part of the pole

16       inspection program the same pole strength and loading

17       inspections on these joint use poles as we do all the

18       other poles throughout our system.  As you would expect,

19       we do find a little bit higher failures associated with

20       loading failures on our poles with joint facilities more

21       so than, you know, those that don't have attachments.

22       But essentially 95 percent of these, you know, these

23       poles are, you know, pass inspection.

24                 Initiative No. 3, transmission inspections.

25       All of our lines, substations, and structures are

FLORIDA PUBLIC SERVICE COMMISSION

9

1       inspected on a six-year cycle, and we're completing

2       that -- we're in the process of completing that six-year

3       cycle.  Everything is on schedule there.  As things are

4       identified for failures, they are -- you know, they are

5       identified for failure and then replaced the following

6       year, either the same year or the following year.

7                 Initiative No. 4, transmission hardening.

8       This is the one area we had a slight tweak to a

9       previously approved plan.  Initially as a result of the

10       2004 and 2005 storms, we saw in our transmission system

11       some issues associated with single pole unguyed

12       transmission structures, so we initially set out to

13       replace those.  However, a year or two later we modified

14       that, and we are now replacing all wood transmission

15       structures in our system.  Additionally, we saw some

16       failures associated with ceramic post insulators on

17       concrete poles, and we are continuing to replace those

18       throughout our system.

19                 Initiative No. 5 deals with developing and

20       maintaining a distribution GIS system.  We have

21       essentially incorporated into that all of the data

22       associated with our distribution facilities.  We have

23       now added all of the joint use information showing poles

24       that have attachments on them.  We've included the

25       hardening information associated with, you know,

FLORIDA PUBLIC SERVICE COMMISSION

10

1       projects since 2007.  All of our pole inspection data is

2       now being incorporated into that as well as our

3       streetlight data which was recently added to our

4       systems.  So we have essentially caught up with loading

5       our system and now are in the process of maintaining

6       that and updating it for new information, including

7       hardening, pole inspections, joint use, and so forth, as

8       well as day-to-day activities.

9                 Initiatives No. 6 and 7 really have to do with

10       evaluating our facilities after a storm has passed

11       through our service territory.  Fortunately, we haven't

12       had the ability to test this yet, but we do have systems

13       in place to gather -- forensics teams have been

14       identified, data collection processes have been

15       established, a database has been established.  Annually

16       when we go through our hurricane dry run we also test

17       those systems, as well.  And the same goes for, you

18       know, looking at our overhead versus underground

19       performance of those facilities, as well.

20                 Initiative No. 8, increased government

21       coordination.  Since 2004 and 2005, we have really done

22       a lot to try to improve our coordination and

23       communication with governmental agencies.  We saw as a

24       result of those storms it was important to keep them

25       informed as to what was going on, what we were doing,

FLORIDA PUBLIC SERVICE COMMISSION

11

1       what the plans were, what the activities were.  So in

2       addition to our normal process where we have, you know,

3       representatives in our external affairs departments as

4       well as our customer service people who deal with

5       governmental agencies.  We also work with EOCs in

6       staffing those accordingly.  We have EOCs throughout the

7       27 counties in our service territory.  We have a group

8       of 80 people that are assigned when storms or events

9       occur that are ready to staff those facilities and have

10       people there, you know, around the clock as necessary to

11       support them.

12                 The EOCs also help us in identifying critical

13       infrastructure facilities for us, which helps us to

14       prioritize and identify hardening projects in their

15       locales.  So, additionally, community outreach teams

16       were developed.  Last year in 2009, we had approximately

17       168 presentations done throughout our service territory

18       on various electric issues, but also including storm

19       preparedness plans and activities.  These are like the

20       homeowner associations as well as city and county

21       government meetings.

22                 We also enhanced an e-mail process and

23       established a specific governmental update website so

24       when we do have storms there are places that they can go

25       and find out specific information about our plans, where

FLORIDA PUBLIC SERVICE COMMISSION

12

1       our service locations are in their areas as the storm

2       occurs, estimated time of restoration for their

3       particular locales.  A lot of information that's

4       available to them that previous to 2004 and 2005 was not

5       available.

6                 Continue our research with PURC.  The

7       beginning of this year we signed another memorandum of

8       understanding along with the other IOUs, co-ops, and

9       munies in Florida.  There are efforts that have been

10       taking place regarding undergrounding, wind, the

11       evaluation of wind.

12                 Initiative No. 10.  Every year we update and

13       review our plans, disaster recovery plans, and those are

14       provided.  I think a copy of that is provided on file

15       for the Commission.  This includes primarily plans

16       associated with the distribution and transmission

17       facilities dealing with major weather events and fires.

18                 All of our ten preparedness initiatives we

19       believe are on target.  As I mentioned, they are

20       consistent with what was previously approved.  Our plans

21       for 2010 are consistent with what we have done in 2007

22       through 2009, with the small exception with the

23       transmission pole replacements.  I think that's it for

24       the storm prep plans.

25                 I'm going to move on to hardening.  We are

FLORIDA PUBLIC SERVICE COMMISSION

13

1       continuing our approach with hardening, our three-prong

2       approach, and that is we're going to continue to

3       strengthen our critical infrastructure facilities to

4       extreme wind loading.  We are going to apply incremental

5       hardening which strengthens specific feeders associated

6       with community projects along major thoroughfares, drug

7       stores, gas stations, pharmacies.  And incremental

8       hardening can include strengthening that feeder up to

9       and including extreme wind.  And then we're continuing

10       to apply extreme wind for all of our new overhead

11       construction, including major plan work, relocation

12       projects as well as daily work activities.

13                 We are continuing to apply over three wind

14       regions these specific wind profiles which would include

15       105, 130, 145, depending on the area within our service

16       territory.  The 105 mile per hour extreme wind loading

17       criteria is primarily in the northern central part of

18       our territory.  The 130 covers the northeastern/central

19       part of our service territory, and then the 145 covers

20       the southern part of the territory.  Again, this is

21       consistent with what we had previously approved, so we

22       are continuing with that plan.

23                 Just to give you an idea of what we've

24       accomplished to date through the first three-year cycle

25       of the hardening plan, we've hardened to extreme wind

FLORIDA PUBLIC SERVICE COMMISSION

14

1       loading for 227 feeders serving 266 critical

2       infrastructure customers.  We've hardened 103 highway

3       crossings and 192 O1 (phonetic) switches, which is

4       essentially the first pole out of a transmission

5       substation.  We have completed all of the hardening

6       associated with acute care facilities and hospitals as a

7       result -- at the end of 2009 in our service territory.

8                 In 2010, we will almost complete all of our

9       911 centers, and then in 2011 we will complete all of

10       our 911 centers as well as all the EOC facilities in our

11       service territory.

12                 We applied incremental hardening to 68 feeders

13       that are serving community needs, and we applied to all

14       new construction, major planning work and relocation our

15       extreme wind loading criteria.  Our total cost for 2007

16       to 2009 was $162 million for these activities.  That

17       relates to primarily the -- or solely the hardening

18       extreme wind loading as well as the incremental

19       hardening.  There is also some additional costs

20       associated with new construction, but we don't track

21       what it would have cost to build that, you know, under

22       our old construction standards versus what it would have

23       cost to build it under extreme wind.  So that's not

24       something that we track, so there is some additional

25       money associated with hardening that we can't

FLORIDA PUBLIC SERVICE COMMISSION

15

1       specifically incrementally track, but there is an

2       addition to that 162 million.

3                 Our plans for 2010 are to harden 39 feeders

4       serving 52 critical infrastructure customers, 16 highway

5       crossings, and 20 01 switches.  We are also going to

6       incrementally harden five feeders serving community

7       needs.  And, of course, continue to apply extreme wind

8       loading to all new construction.

9                 Our plans for 2011 and 2012 still would be to

10       develop -- we are actually starting the 2011 budget

11       process now.  Those will be firmed up subsequently, but

12       we have, you know, have a target of how much we think we

13       will be doing during 2011 and 2012, and our estimates

14       for costs for these for the next three years is in the

15       135 million to $163 million range.

16                 During the initial hardening planned workshops

17       back in 2007, and in review of those plans, there was a

18       lot of issues associated with attaching entities.  So as

19       a result of the outcome of those plans, we have worked

20       very closely with attaching entities in making sure that

21       they're kept up to date with what our plans are, what

22       our costs are, that they have inputs into the

23       development of our plans.  At the beginning of this

24       year, in March we send out 93 packages of our hardening

25       filing, a draft at that time, seeking input, if any,

FLORIDA PUBLIC SERVICE COMMISSION

16

1       from our attaching entities.  This would include cable

2       companies, telephone companies, local government, anyone

3       attached to our facilities have the opportunity to

4       review those and provide input to us.  We did receive

5       feedback from eight of those entities.  Some of them

6       range from, you know, we got your filing, thanks.  There

7       was a couple of clarifying questions.  No one expressed

8       any issues with our plans.

9                 Additionally, we're continuing to comply with

10       the process that was established as a result of the last

11       three-year cycle where in the September time frame of a

12       given year we provide preliminary plans to our attaching

13       entities of what we're planning to do the following

14       year, which includes a listing of the specific projects,

15       their locations, what our plans are.  You know, whether

16       it is extreme wind, incremental hardening.  And then

17       when our plans are finalized for the budget process,

18       generally in the December time frame, they are provided

19       those final plans, as well.

20                 Additionally, when we're constructing or

21       getting ready to construct these projects, we hold

22       meetings with our attachers.  They are invited to attend

23       prior to design as well as construction -- prior to

24       construction so that any issues are identified and

25       resolved prior to those things taking place.  And then,

FLORIDA PUBLIC SERVICE COMMISSION

17

1       of course, coordination takes place during the actual

2       construction, as well.

3                 Benefits of hardening.  As I mentioned

4       earlier, we haven't really had any storm activity since

5       2004/2005, so we are continuing to rely on that

6       information that we had available back then to continue

7       with our plans, and this includes the experience of the

8       2004/2005 storm seasons.  It includes a report that was

9       done by an outside firm, KEMA, back in the -- I'm not

10       sure of the exact date, but subsequent to the storms

11       that looked at the forensics associated with

12       particularly Wilma, but looked at also some of the '04

13       storms and really served as a basis for a lot of our

14       hardening plans and initiatives.

15                 Also, during Wilma we saw that our

16       transmission poles performed much better than the

17       distribution poles.  Of course, transmission poles are

18       already constructed at the extreme wind loading

19       criteria, and so that served as a basis for us moving

20       that to our distribution facilities.

21                 And then there was analysis done by a

22       consulting firm, Davies, that indicated that stronger

23       poles, in this case FPL's Grade B poles at the time,

24       performed better than lesser strength Grade C poles,

25       which the majority of utilities throughout the country

FLORIDA PUBLIC SERVICE COMMISSION

18

1       built to.  We believe that hardening will reduce the

2       number and the duration of outages, both on a storm as

3       well as nonstorm basis.  That restoration costs will

4       also be reduced, and an analysis that FPL performed

5       showed that we expect hardened feeders to save

6       restoration costs.

7                 We think our plan is cost-effective and that

8       it focuses on certain critical infrastructure that we

9       are dealing with initially as well as community

10       projects, and then, of course, over the long-term as we

11       build new facilities that will be built to extreme wind

12       that eventually, you know, our system will be built to

13       extreme wind.  That's the end of the presentation.

14                 MS. L'AMOREAUX:  Okay.  We have a few

15       questions for you --

16                 MR. BROMLEY:  Okay.

17                 MS. L'AMOREAUX:  -- or the people that you're

18       with.  One is how does FPL determine the amount of

19       feeder and lateral miles the company must maintain for

20       the approved years if there is an increase or decrease

21       in feeder miles within that given year?

22                 MR. BROMLEY:  Say that again.

23                 MS. L'AMOREAUX:  Okay.  If you have a feeder

24       and you have so many miles, and you increase those

25       miles, do you count those for that three-year cycle or

FLORIDA PUBLIC SERVICE COMMISSION

19

1       do you wait until the next cycle to clear them?

2                 MR. BROMLEY:  Are you talking about

3       vegetation?

4                 MS. L'AMOREAUX:  Vegetation management, yes.

5                 MR. BROMLEY:  Okay.  Our vegetation management

6       cycle, of course, is an average three-year cycle.  So

7       just to make sure we are all understanding what that

8       means, we could have some feeders on a two-year average,

9       some feeders might be on a three-year average, and some

10       feeders might be on a four-year average.  So we're

11       looking at our feeders primarily based on that.

12                 The miles is really an outcome of addressing

13       feeders when they need to be addressed on their cycles.

14       So I'm not sure -- we don't let the miles force us or

15       direct us as far as our budgeting process.  I mean, it

16       is a function of it, but we really focus on when does

17       that feeder need to be trimmed and what is the resulting

18       miles.  You know, we report resulting miles on that.

19                 As a result of the average cycle, miles can

20       change, miles trimmed can change from year to year.  It

21       is not always going to be one-third of the system.  So

22       what drives our feeder cycles or our feeder trimming is

23       really, you know, when those feeders need to be trimmed

24       and the miles is really an outcome result of what got

25       trimmed.

FLORIDA PUBLIC SERVICE COMMISSION

20

1                 MS. L'AMOREAUX:  The next question we have is

2       FPL states that neither the company nor the other

3       utilities generally have much experience with hardened

4       distribution facilities.  Based on the company's

5       experience, what difficulties does FPL encounter with

6       hardening just distribution facilities?

7                 MR. BROMLEY:  Well, certainly budget dollars

8       are always a factor in really just about anything we do,

9       so that certainly comes into play.  Most recently, we

10       have seen an increase in permitting issues that is

11       making us -- making it more difficult for us to complete

12       projects in the time lines that we would like to

13       complete them.  We are seeing a lot of permitting, new

14       permitting requirements at local and county levels that

15       didn't used to be there.  Whether it's associated with,

16       you know, revenue, additional revenue for these cities

17       and counties may be part of it, but that is something

18       that we are seeing increasingly making it more difficult

19       for us to complete -- complete our projects on a timely

20       basis.

21                 Without any storm experience, we have seen

22       that hardening is giving us some benefits.  We have seen

23       on a nonstorm basis hardened feeders showing an increase

24       reliability performance a year after they're hardened

25       versus the year before they are hardened.  So we feel

FLORIDA PUBLIC SERVICE COMMISSION

21

1       like even on a nonstorm basis we are seeing some

2       benefits associated with that.

3                 MS. L'AMOREAUX:  Well, you kind of answered my

4       third question, which was since no named hurricanes have

5       affected Florida since 2005, does FPL have any evidence

6       of its hardening efforts to enhance its service quality,

7       but I think you kind of covered that.

8                 MR. BROMLEY:  Yes.  Additionally, I know

9       within our service territory, and I am not sure if it

10       was a year -- the exact time -- but we did have a

11       tornado event come through.  And I don't know whether we

12       had any specific comparisons, forensic data that showed,

13       you know, hardened feeder versus a nonhardened feeder.

14       But I know in the specific area where there was

15       extensive damage, our hardened feeder that was in that

16       area did perform well.  There was some damage associated

17       with some of the facilities, but the poles themselves,

18       you know, were not damaged.  And all around them, you

19       know, we saw extensive damage with the trees and so

20       forth.  So there was one, you know, side event that we

21       were able to see some, you know, some of the benefits of

22       hardening.

23                 MS. L'AMOREAUX:  Well, thank you for your

24       presentation.

25                 MR. BROMLEY:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

22

1                 MS. L'AMOREAUX:  Next we will have Eric Sachon

2       from Progress Energy Florida.

3                 MR. SACHON:  Ladies and gentlemen, good

4       morning.  Before I get started, I'd like to introduce a

5       couple of colleagues of mine who have joined me here

6       today.  Charlene Rubano is the Manager of Asset

7       Performance in our transmission organization, and Nabil

8       Benwahoud is the senior engineer within our distribution

9       systems engineering organization.

10                 My name is Eric Sachon, and I am the Manager

11       of the Distribution Systems Organization.  On behalf of

12       Charlene and Nabil, we certainly appreciate the

13       opportunity to come here to speak about our storm

14       hardening plan, the ten on-going initiatives, and our

15       reliability and the hardening efforts in 2010.

16                 Before I get started, I'd like to -- okay.

17       There we go.  Thank you -- I'd like to go over the

18       outline of what we are going to present today, and that

19       is I'm going to talk a little bit about at a high level

20       what our hardening strategy is and the components that

21       make up our hardening strategy.  We will also go into

22       the ten point on-going -- or ten-point plan and the

23       on-going initiatives, and we will cover the 2010 through

24       2012 storm hardening plan and how that compares and

25       contrasts to the '07 through '09 plan, and then we'll

FLORIDA PUBLIC SERVICE COMMISSION

23

1       touch on a little bit of the reliability and hardening

2       efforts that we are employing here at Progress Energy

3       Florida.

4                 As you can see on the slide, there are three

5       main components to our hardening strategy.  The

6       ten-point plan is something we will discuss in-depth

7       today.  The wood pole inspection program is also a

8       component, and that is something we'll not really touch

9       on today.  And the third component is the storm

10       hardening plan, which we will go over in some detail as

11       well today.

12                 So let's go ahead and get started on the

13       on-going initiatives.  Just to preface a little bit, I'm

14       going to talk about the first eight initiatives, and

15       then I will hand it over to Charlene to talk about the

16       two transmission initiatives.

17                 From a vegetation management perspective, the

18       PEF integrated vegetation management program consists of

19       five sub-programs.  The five sub-programs consist of

20       production trimming, demand trimming, herbicide

21       application, vine removal, and mowing.  The objectives

22       of this plan are simply safety from both the customer as

23       well as the employee perspective and reliability from

24       the perspective of mitigating or minimizing tree-caused

25       outages.  Certainly customer satisfaction is another

FLORIDA PUBLIC SERVICE COMMISSION

24

1       component of the objective, and we want to make sure

2       that we maintain costs in a cost containment effort.

3                 We do have a vegetation management program

4       that consists of a three-year and a five-year cycle.

5       The three-year cycle is for our feeders and our backbone

6       infrastructure.  The five-year cycle is for our laterals

7       or branch line infrastructure.

8                 From a vegetation management perspective and

9       the challenges that we foresee, there are numerous

10       variables that can come into play.  Some of those can

11       include resource constraints, changes in our philosophy

12       on what we want to do for that particular year from a

13       prioritization perspective, and certainly the impact of

14       a major storm can have some play with regards to

15       vegetation management efforts.  However, I will say that

16       if we feel we have not met our obligation in any one

17       given year, that in the subsequent years we will make up

18       for that loss of not completing our expected budget

19       expenditures and meeting that cycle.

20                 The next initiative is joint use audits.

21       Progress Energy Florida has committed to auditing all of

22       our distribution and transmission poles that have joint

23       use attachments within an eight-year cycle.  There are

24       approximately 500,000 distribution poles with joint use

25       attachers and approximately 2,500 transmission poles

FLORIDA PUBLIC SERVICE COMMISSION

25

1       with joint use attachers.  At this time, we do not

2       foresee any major challenges with the joint use audits

3       other than this thing that I mentioned with regards to

4       vegetation management, and resource constraints, and

5       potential major storm implications.

6                 From a GIS upgrade perspective, that is the

7       next initiative, in 2008, Progress Energy Florida

8       completed the changeout of our GIS system.  We went from

9       a frame system to a geoelectric system.  We are

10       currently in the process of replacing our work

11       management asset management system.  The expectation is

12       by the end of this year in the fourth quarter we will

13       complete one of our four regions, the south coastal

14       region with this new work management system.  The

15       expectation is to committee the other three regions by

16       the end of 2011.  At this point from a GIS perspective,

17       we do not foresee any challenges to not meeting this

18       opportunity.

19                 The next initiative, forensic analysis.

20       Progress Energy Florida has initiated a forensic

21       analysis program within our storm plan.  The forensic

22       analysis program is a process that we employ immediately

23       following the impact of a major storm.  We have two

24       person teams that are designed to go out throughout the

25       service territory in generally the same location where

FLORIDA PUBLIC SERVICE COMMISSION

26

1       the storm has impacted our service territory and record

2       any type of pole infrastructure damages, whether that be

3       leaning or broken.  They are to collect demographic

4       information such as size, height, clearance, conductor,

5       number of conductors primary, number of joint users,

6       where the pole broke, and a host of other pieces of

7       information.

8                 The teams comprise of an engineer that is a

9       Progress Energy employee, and the intent there is to put

10       the right resource in the right place.  There is not a

11       better resource that understands how our design

12       characteristics nor our components, so they will

13       definitely understand whether the pole is actually

14       leaning or has broken and, in essence, what caused the

15       break from a perspective of attachers, tree debris, et

16       cetera.

17                 The other individual on these teams is a meter

18       reading representative.  Again, the right resource being

19       the fact that we have a representative who knows the

20       area and is very familiar with the area and can meander

21       throughout the county or the area in the event that

22       there are obstacles in the way such as a fallen tree.

23       They can find an alternate route very quickly.

24                 The areas that they will do some forensic

25       analysis or conduct a forensic analysis consists of

FLORIDA PUBLIC SERVICE COMMISSION

27

1       certainly the path of the storm, whether it's the

2       eyewall of the hurricane, or the direction and the

3       impact of a tornado and the path that the tornado took.

4       They will generally get in those areas and look for

5       downed poles and damaged poles.

6                 There is another component that these teams

7       will look at, though, and that is our storm hardening

8       projects that we have completed since 2007.  We are

9       asking these forensic analysis teams to identify these

10       particular projects, access those particular projects,

11       rather, and identify any type of performance issues with

12       regards to these projects resulting from the impact of

13       the storm.

14                 Unfortunately or fortunately, however you want

15       to look at it, we have not had a major storm impact our

16       service territory to really see how our storm hardening

17       projects have performed, and that is a good thing, I

18       guess, and we will see as time goes on if we do have

19       some storm impacts and how our projects have withstood.

20                 The next initiative -- and by the way, from a

21       challenges perspective on forensic analysis, we do not

22       see any type of issues or concerns with regard to

23       meeting this obligation and this initiative.

24                 Coordination with local governments.  Progress

25       Energy takes pride in the fact that we try to

FLORIDA PUBLIC SERVICE COMMISSION

28

1       collaborate as best we can with our local governments.

2       We have a 70-member team that is in place throughout our

3       service organization that meets with all the local

4       governments to talk about our hurricane and storm

5       preparedness prior to, during, and after the impact of a

6       major storm.  With regards to challenges with this

7       initiative, we see no issues or concerns with continuing

8       and meeting this obligation.

9                 From an overhead and underground reliability

10       initiative, Progress Energy Florida collects a

11       tremendous amount of data to review the percentage

12       impact -- or outages, rather -- I should say a

13       percentage of outages as a result of the storm impact to

14       both our underground as well as our overhead

15       distribution systems.  There are three -- basically

16       three systems that we look at.  One is our outage

17       management system that basically tells us how our

18       facilities are connected to each other; the customer

19       service system, which pretty much tells us which

20       customers are tied to which transformer.  The view

21       behind that is that our outage management system is able

22       to, when we get customer calls, identify the upstream

23       device that is most likely the device that has tripped

24       as a result of the outage or the fault.  And finally,

25       our GIS, our geographic information system is utilized

FLORIDA PUBLIC SERVICE COMMISSION

29

1       to check all the data points of our infrastructure on

2       our distribution system.  From a challenges perspective,

3       we see no challenges in continuing this initiative.

4                 The collaborative research initiative.

5       Progress Energy is continuing our efforts to work with

6       the academic community from a collaborative perspective.

7       We have sponsorship with regards to the University of

8       Florida's Public Utility Research Center, otherwise

9       known as PURC.  We have members on the team that work

10       with the initiatives.

11                 The PURC team members have looked at and

12       researched as mentioned in the previous presentation.

13       Some of those certainly include the fact that there is a

14       modeling system with regards to undergrounding that is

15       still on-going to see the benefits and the costs

16       associated with that.  There is also, as was mentioned

17       previously, a wind monitoring initiative that was

18       completed, and there is a host of wind monitors

19       throughout the state that we have access to so we can

20       identify what the wind speeds are when a major event

21       occurs, whether it's a tornado or a hurricane.  We can

22       then see how our infrastructure has withstood those

23       amounts of winds, those significant winds, which we

24       haven't had in the past.  We really had no idea what

25       wind level had some type of impact on our distribution

FLORIDA PUBLIC SERVICE COMMISSION

30

1       facilities.  Now we do.

2                 Two other issues with regard to collaborative

3       research include the forensic analysis.  We improved

4       that process and try to maintain some consistency

5       throughout the organization and other utilities.  And

6       the other is certainly vegetation management.  As far as

7       a challenge, we see no challenge with this initiative.

8       We feel very comfortable and appreciate the opportunity

9       to serve on this team.

10                 From a hurricane preparedness perspective,

11       Progress Energy prides itself in being prepared for

12       hurricanes.  We have a storm plan that's in place.  We

13       have an annual drill that occurs regularly.  This year,

14       as a matter of fact, we had the distribution drill on

15       April 22nd.  We also had a transmission storm

16       preparedness drill that occurred on May 19th.

17                 Some of the things that go into our

18       preparedness include the fact that we stage materials or

19       talk with our material vendors to make sure we have

20       materials on-site or available in the event of an impact

21       of a major storm event.  We discuss with fuel vendors to

22       make sure we have enough fuel for our fleet.  We also

23       actually during the off season meet with vendors and

24       contractors to help train them in our damage assessment

25       philosophy so that when we do have an impact that we can

FLORIDA PUBLIC SERVICE COMMISSION

31

1       leverage these individuals and they are familiar with

2       our processes on conducting the pole-to-pole patrols and

3       what devices they need to look for.

4                 From a resource perspective, we have certainly

5       engaged in the regional municipal -- I can't remember

6       what that name is.  Excuse me.  The regional mutual

7       assistance organizations where we make sure that we have

8       negotiated relationships with other organizations so

9       that if we are impacted they will send crews to our

10       service territory, and likewise in the same situation.

11       With regards to challenges with the hurricane

12       preparedness, we see no concerns and we expect to

13       continue maintaining our preparedness on the hurricane

14       initiative.

15                 For the next two initiatives, I will turn it

16       over to Charlene Rubano.

17                 MS. RUBANO:  Good morning.  Our PEF

18       transmission system is inspected every year by two

19       methods.  We have area patrols where we will patrol

20       approximately two times a year our circuits.  The other

21       method that we use is ground line inspections, and that

22       is we will patrol approximately one-third to one-fifth

23       of our transmission circuits every year by ground line

24       inspections.  These ground line inspections are looking

25       for deficiencies in the structures and the assets that

FLORIDA PUBLIC SERVICE COMMISSION

32

1       are on the structures, such as insulators.  These ground

2       line patrols will collect the data of these deficiencies

3       and categorize the amount of deficiencies into levels

4       two through five, and we will prioritize based on those

5       results to have those replaced within the year and

6       within subsequent years.

7                 Also, transmission structures are hardened

8       through a few methods.  Through our ground line

9       inspections, when we realize that poles need to be

10       replaced from those ground line inspections we will

11       replace wood poles with either steel or concrete poles,

12       and they are prioritized based on the highest need of

13       deficiency in any given year.

14                 The second method for hardening our existing

15       structures would be through customer or DOT type

16       requests where we would rebuild those lines and move

17       those lines, and we would build those structures to our

18       existing standards, which either meet or exceed the NESC

19       code.

20                 The third way that we harden our transmission

21       structures are through our planning projects, which will

22       be either rebuilds or new circuits.  And, again, those

23       will be constructed to meet or exceed our NESC

24       guidelines.  And then anytime we relocate, or we

25       rebuild, or build new, we are building to steel or

FLORIDA PUBLIC SERVICE COMMISSION

33

1       concrete structures.  So those are our two methods in

2       transmission in the ten-point plan that we are

3       existingly doing.

4                 The challenges that we -- we don't really see

5       any challenges for either of those other than any

6       resource constraints or schedule changes from the

7       customer requests, or any resource issues, we may need

8       to change our schedule based on some of those resource

9       issues.

10                 Next we will talk about some similarities and

11       some differences in our 2010 plan from our 2007 plan,

12       and I will start with the transmission hardening

13       philosophy, and then Eric will go into the rest of the

14       distribution philosophy.  The transmission hardening

15       philosophy has not changed since our 2007 plan.  We are

16       still looking to inspect our transmission structures and

17       change our wood pole structures as needed to steel or

18       concrete poles to harden that system.  We are also

19       utilizing the relocation requests, and our planning

20       projects with the rebuilds and our new projects to build

21       to our existing NESC standards, whether they meet or

22       exceed those standards, and we will utilize concrete and

23       steel structures for those philosophies.  So that

24       particular philosophy has not changed for our 2010 plan.

25                 And next I'll let Eric talk about

FLORIDA PUBLIC SERVICE COMMISSION

34

1       distribution.

2                 MR. SACHON:  With regards to our 2010 plan,

3       there are many, many similarities to the 2007 plan.  I'm

4       just going to highlight a couple of similarities.  And

5       the first one I would like to say is that we have not

6       changed or deviated from our philosophy on construction

7       standards.  They are the same as the '07 plan, so

8       nothing has changed in regard to our construction

9       philosophy.

10                 The other issue is we utilized in 2007 the

11       Davies Consulting incorporation prioritization model.

12       We will continue to utilize that prioritization model,

13       as well, in the 2010 plan.

14                 With regards to variations to the plan, three

15       main situations, three main areas that we have changed.

16       From the prioritization model that I just mentioned from

17       Davies Consulting, we actually will be utilizing that

18       prioritization model, but we have enhanced and improved

19       that utilizing or adding additional criteria to help us

20       prioritize our projects.

21                 From a geomedia perspective, we are utilizing

22       geomedia in the plan this year to help us identify where

23       our distribution areas are prone to flooding and surge.

24       This is going to help us prioritize as well as identify

25       areas for our submersible projects.  And, finally,

FLORIDA PUBLIC SERVICE COMMISSION

35

1       another hardening alternative that we have actually

2       implemented into the plan is feeder ties.  Although we

3       know that feeder ties will not mitigate outages, we do

4       know that part of outages that customers are frustrated

5       with is the duration that they are out for.  And feeder

6       ties will provide us with another opportunity to

7       reconnect some of our customers in a much more expedient

8       manner of time.  Those are the main variations of the

9       plan.

10                 MS. RUBANO:  We are next going to talk about

11       restoration and hardening efforts that are existing

12       today.  Again, I will talk about transmission briefly

13       and then Eric will finish up.  The transmission

14       hardening plan has not changed since our 2007 plan.  We

15       are continuing to prioritize based on needs and

16       deficiencies that we see in our system and also our

17       planning needs and customer requests.

18                 Our main difference that we saw in our 2007

19       plan to now is our spending has increased in our

20       hardening effort on the transmission side mainly due to

21       the number of projects and the number of requests that

22       are from the DOT projects, customer request projects,

23       and also from our planning projects.  We did not

24       anticipate that kind of increase when we filed in 2007,

25       and our actual spending in 2008 and 2009 were higher due

FLORIDA PUBLIC SERVICE COMMISSION

36

1       to that number of projects.  And next I'll let Eric

2       finish.

3                 MR. SACHON:  A continuous focus on

4       restoration.  We have implemented several changes this

5       year with regards to our efforts on restoring power and

6       changing our philosophies on how we respond and restore

7       power to our customers.  One of those situations

8       involves our trouble men (phonetic).  We recognized very

9       quickly that most of our outages are occurring during

10       the week day not the weekends.  We did have and we

11       continue to have trouble men working during the

12       weekends, but we have changed those schedules on some of

13       those trouble men to stay on more of a week-day shift

14       rather than weekend shift.  This is going to provide a

15       greater response rate to our customers that are

16       sustaining outages during the week day, which is, again,

17       where we see most of our outages occurring, as well as

18       provide the restoration needs improving the customer

19       satisfaction.

20                 The second area that we worked on or focused

21       on restoration involved our new service crews.  We

22       typically have had a crew work five eight-hour days

23       during the week.  We have changed that schedule.  Not in

24       all of our regions, but in most our regions we have

25       changed that schedule to a four ten-hour day.  This

FLORIDA PUBLIC SERVICE COMMISSION

37

1       helps with addressing appointments later on in the day

2       improving customer satisfaction and helping to reduce

3       costs.

4                 The last one deals with our call-out process,

5       our call-out procedure.  Typically, when an outage

6       occurs in the past what we have done is had the

7       distribution control center dispatcher contact our

8       trouble men to access the site, identify the issue, and

9       then if other resources were needed, call in the other

10       resources.  We recognize that in some of the larger

11       impacted outages where we had a high degree of customers

12       impacted that routinely we were calling out another unit

13       to help in the restoration efforts.  So in light of that

14       fact we decided that with high customer impact outages

15       we are not only going to dispatch the trouble men, we

16       are also going to dispatch a two-person crew to the

17       scene at the same time.  This is going to help, again,

18       with response rate as well as restoration improving

19       customer satisfaction.

20                 The other focus is a reliability engagement

21       model.  We just initiated that this year.  What that

22       involves is in the past we have had staff really review

23       outages from a system perspective to see trends and

24       issues of repairs and recommendations on how to mitigate

25       these outages.  What we have done with this reliability

FLORIDA PUBLIC SERVICE COMMISSION

38

1       engagement model is actually put more eyes on these

2       outages.  And we focused in three areas.  The first area

3       is high customer minutes of interpretation impact,

4       otherwise known as CMI impacts.  The second area

5       involved customers that were out of power for at least

6       three hours or more.  And the third one involved, again,

7       high impact customers where we had outages that had a

8       large number of customers go out at the same time.

9                 What we are doing with that now is it is not

10       just a system staff engineer perspective where they are

11       looking at it, we are having eyes from the operation

12       center personnel, DOMs, distribution operation managers.

13       We have incorporated an outage champion at each of the

14       op centers to review these.  All of these outages that I

15       mentioned in the three different areas are looked at and

16       viewed on a daily basis by all of these different

17       entities.  The intent there is more eyes on these

18       outages will help to address these concerns, issues, and

19       projects that are needed to mitigate and resolve these

20       outages.

21                 From a targeted hardening perspective, we

22       still continue to focus our hardening efforts on the

23       reliability side of the fence.  Since 2007, we have

24       completed 48 storm hardening projects.  In the 2010 plan

25       we have proposed 61 -- I should say we have identified

FLORIDA PUBLIC SERVICE COMMISSION

39

1       and proposed 61 projects then to be done over the next

2       three years from a hardening perspective, as well.

3                 That concludes our presentation, so I will

4       open it up for questions.

5                 MS. L'AMOREAUX:  Thank you very much.

6                 Just a few questions.  Can you please briefly

7       explain why PEF has not adopted extreme wind standards

8       for all distribution construction, including critical

9       infrastructure?

10                 MR. SACHON:  Yes, absolutely.  It is our

11       belief and experience from the '04 and '05 hurricanes

12       that distribution facilities generally are damaged not

13       as a result of wind, but more as a result of flying

14       debris, trees, et cetera.  The installation of extreme

15       wind loading facilities would not alleviate that

16       situation.  If a tree is going to fall on that pole,

17       that pole is coming down.  So we felt from that

18       perspective that really what we would be doing if we

19       went to that level of extreme wind loading on the

20       distribution system would be complicating our

21       restoration practice even more so from the perspective

22       of that we were having -- we would have to be now not

23       only staging material for our normal construction, but

24       we are also having to stage material for wind loading

25       facilities.  So, again, we do not feel from our

FLORIDA PUBLIC SERVICE COMMISSION

40

1       experience as well as industry experts we have contacted

2       that on the distribution system extreme wind loading is

3       of benefit to our customers.

4                 Other issues that we have seen is the

5       situation where extreme wind loading requires larger

6       sized poles, and that is going to cause some issues with

7       customers in particular in the more urban areas where

8       the span lengths are not quite as long, and so you may

9       have several poles that are very close together.  And

10       these are larger-sized poles, it becomes an aesthetic

11       problem for some customers as we have recognized in some

12       of our storm hardening efforts.  So that generally is

13       the reason why we've decided not to go to an extreme

14       wind loading philosophy on the distribution system.  We

15       do have that on the transmission system, though.

16                 MS. L'AMOREAUX:  My next question you touched

17       on it a little bit about the feeder ties, but can you

18       please discuss the use of feeder ties as a hardening

19       alternative and why PEF believes this concept is

20       beneficial and cost-effective?

21                 MR. SACHON:  A great question.  You know, we

22       know that outages are going to occur when a major storm

23       impacts our service territory.  It's a foregone

24       conclusion.  We also know that we have facilities that

25       are called radials.  Basically, they are not tied to any

FLORIDA PUBLIC SERVICE COMMISSION

41

1       other feeders.  When the radial goes out, literally that

2       feeder and those customers are out of power until we are

3       able to repair that radial.  Feeder ties gives us a

4       contingency that we did not have in the past,

5       particularly on radials, but it also provides a greater

6       contingency effort for those feeders that are looped.

7       And what I mean by that is if a feeder were to go out

8       and we have identified the fault, very quickly we can do

9       some switching and we can refeed the tail end of that

10       feeder from another feeder if we have the feeder tie.

11                 And that is why we feel -- again, we know that

12       it is not going to mitigate the outage, that is not the

13       intent, but we also know that duration is a concern of

14       our customers, and this will certainly reduce

15       considerably the duration those customers would have

16       been out had we not had the feeder ties.

17                 MS. L'AMOREAUX:  This question is kind of for

18       everybody, but since no named hurricanes have affected

19       Florida since 2005, discuss how PEF -- discuss PEF has

20       any evidence in hardening efforts and has it enhanced

21       its service quality?  Do you want me to restate?

22                 MR. SACHON:  Could you please restate.

23                 MS. L'AMOREAUX:  Sorry.  Yes.  Since no named

24       hurricanes have affected Florida since 2005, does PEF

25       have any evidence of hardening efforts and has it

FLORIDA PUBLIC SERVICE COMMISSION

42

1       enhanced its service quality?

2                 MR. SACHON:  I wish I could say that we do

3       have evidence, unfortunately we have not had situations

4       to impact our service territory to actually look at the

5       performance of our storm hardening projects since 2007.

6       So, unfortunately, I do not have an answer to give you

7       other than we're waiting on the impact of an event and

8       then we will monitor and identify the performance of

9       those projects.

10                 MS. L'AMOREAUX:  That's all the questions I

11       have.

12                 MR. SACHON:  Thank you.

13                 MS. L'AMOREAUX:  Next up is Tampa Electric,

14       T.J.  He told me not to say his last name.

15                 MR. SZELISTOWSKI:  Thank you.

16                 T.J. Szelistowski -- and T.J. works great -- I

17       am the Director of Engineering for Tampa Electric

18       Company in the Energy Delivery Department, and I'm happy

19       this morning to share with you Tampa Electric's storm

20       hardening update, our 2010 plan.

21                 As requested of the company, I'm going to

22       cover a number of things.  The status of the ten-point

23       initiatives and our on-going efforts there; our

24       three-year storm hardening plan in two parts.  I'll

25       touch on the 2007 to 2009 plan as well as the 2010 to

FLORIDA PUBLIC SERVICE COMMISSION

43

1       '12 plan and the differences between those; and then

2       touch also on the improvements to the overall system

3       based on those hardening efforts.

4                 A key part of Tampa Electric's hardening

5       effort in the ten-point plan as well as in our hardening

6       effort overall is our vegetation management.  We have

7       made a significant investment in vegetation management.

8       Tampa Electric Company has a three-year vegetation

9       management plan both on the feeders, on the main feeder

10       lines as well as on the laterals.

11                 We started in the 2007 plan.  As we put that

12       forth we said we would be transitioning to a three-year

13       plan.  This year we are on track to complete one-third

14       of our system, both feeders and laterals together, and

15       we have over 225 tree-trimming resources on site working

16       toward that end.  In addition, we have reactive trimmers

17       that when we have either customer complaints or specific

18       construction projects that require tree trimming, we

19       also apply tree trimmers to those areas, as well.

20                 We continue to work with local governments in

21       terms of vegetation management, tree planting guides,

22       address concerns from local governments in terms of

23       trees.  Tree trimming is kind of a two-edged sword.  On

24       the one hand it certainly helps with your liability, on

25       the other hand from an aesthetic standpoint in some

FLORIDA PUBLIC SERVICE COMMISSION

44

1       areas, park areas, those type of things, there's a lot

2       of customer concerns with trimming, especially getting

3       adequate tree trim clearances.  The aesthetics involved

4       with that sometimes are a challenge.  And so we continue

5       to work with our local governments to make sure that we

6       are balancing that.

7                 Another part of the ten-point initiatives

8       involves a joint use attachment audit.  We completed

9       that, our last one in 2008.  We have a commitment to do

10       that at least every eight years, and our next one will

11       be starting in 2011 or 2012, so we will be doing it

12       before the eight-year cycle, but we do have that coming

13       up in the near future.

14                 In the meantime whenever we have as part of

15       our pole inspection program as we have joint users on

16       poles, we do a comprehensive loading analysis on those

17       poles to ensure that we don't have undue stresses on the

18       poles due to joint attachers as we go through that

19       inspection process.

20                 Transmission inspections is another point of

21       the ten-point plan initiatives.  Specifically, the six

22       year inspection comprehensive inspection cycle we do

23       generally by helicopter.  We have in the past done a

24       climbing inspection, but generally by helicopter and do

25       a comprehensive inspection, one-sixth of the system

FLORIDA PUBLIC SERVICE COMMISSION

45

1       every year.  And, in addition, we, of course, have the

2       eight year ground line inspection cycle for transmission

3       and distribution.  And we also every year do two things

4       on the transmission system.  We do an infrared patrol by

5       helicopter where we identify any unnatural heating of

6       connection elements.  In addition to that we have a

7       ground patrol once a year on the entire transmission

8       system.

9                 In terms of transmission hardening, Tampa

10       Electric Company since the early 1990s has installed

11       non-wood poles for all transmission.  They are either

12       concrete or steel.  We continue to do that as part of

13       our ten-point initiatives and overall hardening.  We

14       use, again, generally concrete or steel, but either --

15       both in new construction as well as maintenance

16       change-outs we replace poles and add new poles for

17       transmission.

18                 GIS.  Tampa Electric Company accepted its GIS

19       program officially from the vendor in the fall of 2009.

20       And so we do have the GIS system implemented as was part

21       of the ten-point plan initiatives.  We continue to work

22       with that program to make sure it is as efficient and

23       user friendly as possible with our system and with our

24       designers.

25                 Post-storm data collection forensics, another

FLORIDA PUBLIC SERVICE COMMISSION

46

1       name for the same thing.  We have a contract in place.

2       We have not had to use it yet, but we have a contract in

3       place with a vendor to come in after the storm, after

4       any hurricane or large storm effects Tampa Electric's

5       service territory and do the storm data collection and

6       forensic analysis on the structures.  In addition, we

7       are set up so that we can do outage data collection for

8       overhead versus underground after a major storm event.

9                 Increased coordination with local government.

10       We have always had strong relationships with the local

11       governments.  We have continued to increase that

12       coordination since the 2004/2005 hurricanes, and we have

13       a number of events every year that we hold with local

14       governments, both storm related and nonstorm related,

15       including mock storm events, exercises, that type thing

16       to make sure that we are working closely and in

17       conjunction with the local government.

18                 Collaborative research.  PURC was mentioned

19       several times.  We have been involved with that

20       throughout the last three years and we will continue to

21       be involved, both on the underground to overhead or

22       overhead versus underground tool that was developed as

23       well as the vegetation management.

24                 And the disaster preparedness plan.  We have

25       exercised that plan this year.  Every year we revisit it

FLORIDA PUBLIC SERVICE COMMISSION

47

1       and come up with lessons learned and improve that plan

2       every year.  And we have done that and are well prepared

3       for storm season for this year.

4                 In a nutshell, we are on track in all the

5       areas with the ten-point storm initiatives.  We believe

6       that those ten points have improved our overall system

7       both for storms as well as for every day operation.

8                 I will go now into the three-year storm

9       hardening plan, 2007 plan versus the 2010 plan.  And I

10       will talk about, again, some specifics in those plans as

11       well as the status of where we are and what we have

12       coming for the 2010/2012 plan.

13                 Both plans, the plans are very similar in

14       their design.  They focus in three distinct areas,

15       construction standards, the deployment strategy, as well

16       as attachment standards and procedures, and I will talk

17       about each of those.  Under distribution design, Tampa

18       Electric Company since the early '70s has built to Grade

19       B construction, National Electric Safety Code, Grade B.

20       Generally, distribution facilities are required to be

21       built to Grade C, which is a lesser standard, or not as

22       strong a standard as Grade B.  There are certain

23       distribution facilities that do require a Grade B, but

24       Tampa Electric Company designs and constructs all of its

25       distribution to the higher standard, to Grade B

FLORIDA PUBLIC SERVICE COMMISSION

48

1       construction.

2                 In addition, we have gone to stainless steel

3       construction on our underground switched gear and

4       transformers, and that is a slight change from our 2007

5       plan.  In the 2007 plan the switchgear was stainless

6       steel as well as the outside of the transformers, but we

7       have now gone to a stainless steel tank, as well, and

8       that is something new for us.

9                 On the transmission side, I mentioned that our

10       standard is non-wood construction for all installations,

11       both replacement as well as new construction.  That

12       includes maintenance replacement as well as road

13       widenings, and then, of course, new construction.

14                 We use extreme wind for all the transmission.

15       In addition, transmission construction at Tampa Electric

16       for our 230kV, which is our backbone, we go to an even

17       higher standard.  The extreme wind in Tampa, the extreme

18       National Electrical Safety Code extreme wind would

19       require anywhere between 110 and 120-mile per hour wind

20       speed design depending on how far you are from the

21       water.  And the first point is we use the 120-mile per

22       hour wind across the entire service territory, so we

23       use -- we err on the side of the higher wind speed.  In

24       addition to that, for all of our bulk 230 transmission,

25       we design all of that at 133-mile per hour design wind

FLORIDA PUBLIC SERVICE COMMISSION

49

1       speed.

2                 Getting now into the deployment strategy a

3       little bit.  Vegetation management I mentioned.  Again,

4       we are very proud and a significant part of our

5       hardening commitment is in our vegetation management

6       with the three-year both on the laterals as well as the

7       feeders.  And, again, in 2010, we believe we are on

8       track to get to one-third of our system in terms of that

9       vegetation management.

10                 Inspection and maintenance.  Certainly we will

11       continue with that.  I mentioned the transmission

12       inspection before, and, of course, we have the eight

13       year distribution inspection cycle on the ground line

14       and we will continue that.

15                 We did 12 overhead-to-underground conversions

16       of crossings.  These are interstate crossings in the

17       Tampa area along major evacuation routes, and we have

18       completed the undergrounding of all of those, all of

19       those 12 that were in the original 2007 plan.

20                 We have several extreme wind pilot hardening

21       projects.  Tampa Electric Company identified several

22       critical facilities, one of which is St. Joseph's

23       Hospital, I'll talk about that in a minute, the Port of

24       Tampa, and then another project that we have involving

25       Tampa International Airport, and I'll go into detail

FLORIDA PUBLIC SERVICE COMMISSION

50

1       about all three of those.

2                 St. Joseph's Hospital is a Level II trauma

3       center in Tampa.  We rebuilt the feed to that to an

4       extreme wind feed.  The distribution feed to that

5       involved a number of transmission poles that we changed

6       to non-wood structures as well as quite a few

7       distribution poles, again, to bring that up to extreme

8       wind design.  We completed that in 2008.

9                 The Port of Tampa hardening was divided into

10       three phases.  The Port of Tampa is a critical port to

11       Florida.  Approximately 40 percent of the gasoline for

12       the state comes in through that facility, so it is very

13       critical to the state after a hurricane.  A lot of times

14       lack of fuel is a big hindrance in terms of restoration

15       efforts from the community standpoint.  We completed the

16       first phase in 2008, where we rebuilt some transmission

17       to non-wood where we had distribution lines underneath

18       the transmission conductors, and changed out a number of

19       distribution poles, as well.

20                 There are actually three circuits in that area

21       that serve the port, and so those were the three phases.

22       We completed the first phase in 2008 and the second

23       phase in 2009.  We replaced quite a few transmission

24       poles and distribution poles again to bring that up to

25       extreme wind.  And we are in the process now for Phase

FLORIDA PUBLIC SERVICE COMMISSION

51

1       3.  We will complete that by the end of this year.  It

2       says transmission poles.  There are also 30 or so

3       distribution poles that would be replaced, as well.  And

4       again, this project will bring the distribution that

5       feeds that Port of Tampa area up to extreme wind design.

6                 Tampa International Airport.  This was in our

7       2007 to 2009 plan, and I've got some diagrams here to go

8       through, but the original plan was to harden the source

9       to the airport.  And we've talked to the airport

10       facility and our planners and we came up with what we

11       think is a much improved plan, and that is what we have

12       embarked on, so I will talk about that a little bit.

13                 This picture, a real basic schematic of the

14       way Tampa International Airport is fed.  It's fed out of

15       a substation that is not dedicated specifically to the

16       airport.  It serves some other load in the area.  And

17       the dashed line is really -- it represents

18       six distribution circuits that feed the airport.  The

19       lines to the left on this diagram show the transmission

20       lines that are brought into that substation.  The bold

21       line is the line that in our original plan we were going

22       to rebuild with non-wood structures.  These are older

23       lines.  And as we looked at that design, while there are

24       multiple transmission feeds to that substation, we did

25       have some concern that we were feeding the airport --

FLORIDA PUBLIC SERVICE COMMISSION

52

1       continuing to feed the airport with this design out of

2       the same substation and that gave us some concern.

3                 So the next slide is actually the improved

4       design.  What we have done is we have added three

5       distribution, underground distribution feeds from a

6       second substation.  We have left the ones in from the

7       west, but, in addition -- and this was an existing

8       substation, but we have added -- we are adding a second

9       transformer at the new substation, or at the second

10       substation, and in addition are building a new line into

11       that substation.

12                 What this does for us is you can see pretty

13       plainly on the diagram is it provides us duplicate

14       service to the airport so we can feed the entire airport

15       from either direction.  A much improved design, and we

16       are in the process of finishing that now.  We have done

17       the distribution work and are in the process of doing

18       the substation transmission work before the end of this

19       year.

20                 Attachment standards and procedures, part of

21       our hardening.  We have a very good relationship with

22       our joint use attachers.  We have a good process for

23       having them make us aware of requests to attach to our

24       poles.  We have improved the relationship with those

25       folks, I believe, over the last three years.  And I know

FLORIDA PUBLIC SERVICE COMMISSION

53

1       that overlashing has been an issue after 2004 and 2005.

2       We had 1,000 instances of overlashing requests being

3       made to the company, and so we believe the communication

4       is good between the joint users and Tampa Electric

5       Company, and we continue the good relationship there.

6                 As we have requests for attachments to our

7       poles, we have an electronic means of communication back

8       and forth for the permitting process as well as the

9       communication if they want to attach additional

10       facilities on a pole.  Now, in some cases, depending on

11       the structures, they can attach without any changes.  In

12       some cases there is make ready that needs to be done.

13       Poles need to be changed out or strengthened, and that's

14       all part of our process.  And, again, that works very

15       well for us, and we are pleased with that.

16                 Joint use attachment audits.  I mentioned

17       before there is a commitment for once every eight years.

18       Our last one was in 2008.  There is something on the

19       horizon that gives a little bit of caution and concern

20       at Tampa Electric Company in terms of joint use.  The

21       FCC broadband plan you may be familiar with has a

22       potential with the rulemaking to allow what is called

23       boxing and bracketing, which is essentially putting more

24       joint use attachments in the same space on either side

25       of the pole or out on cross-arms.  And we have some

FLORIDA PUBLIC SERVICE COMMISSION

54

1       concern with that for a number of reasons, one of which

2       is storm restoration.  We are talking about hardening

3       today.  Storm restoration is you add facilities on both

4       sides of the structure; it makes replacing that

5       structure when they go down much more difficult.  We

6       have some real concerns and we will be happy to share

7       more of our concerns with the staff at a later date.

8       But, again, our relationship with our joint users is

9       very good and we continue to work with them on

10       attachments.

11                 This next chart -- the next two charts,

12       actually, show the 2007 and 2009 plan and the difference

13       between that plan and the 2010 plan.  The first one

14       shows the things that -- the one-time projects that we

15       have completed, or the status of those projects from the

16       first plan.  The 12 interstate crossings I mentioned.

17       Conversion of 4 kV system we did in the last three

18       years.  We converted the last of Tampa Electric's 4 kV

19       distribution system to 13 kV.  Our system, our

20       distribution system is 13 kV, and that allows us to have

21       backup supplies and backup material, so we no longer

22       have any 4 kV distribution on our system.

23                 St. Joseph's Hospital.  Source hardening I

24       mentioned.  That's complete.  Two of the three phases of

25       the Port of Tampa are complete.  The third one will be

FLORIDA PUBLIC SERVICE COMMISSION

55

1       complete by the end of this year.

2                 This is one thing I didn't mention.  We talked

3       about the joint research with PURC.  Now we are doing

4       some stuff on our own, as well.  We have installed 26

5       breakaway service connectors as a test.  The service

6       connector -- our service line is the line from the pole,

7       the transformer to the individual residence, and

8       sometimes after a hurricane you will have a limb or

9       something that will fall on that service connector that

10       will pull away the mast from the house.  And what

11       happens is even though we may be ready to put power back

12       to the house, because of damage to that facility the

13       customer can't receive power, and that is ultimately

14       what we are trying to do.  And so we have tested, we

15       have put in 26 of these breakaway connectors as a test

16       that will essentially -- there is a force fitting that

17       give way and pull the wire away from itself rather than

18       pull the mast away from the house.  And we are testing

19       those to see how they work under normal summer storm

20       conditions as well as if we have a hurricane to see if

21       we have those in place if that avoids that breakage of

22       that mast or that damage to the home.

23                 And the last item on here, the improved plan

24       for the Tampa International Airport, again, will be

25       completed this year.  And then the host of things that

FLORIDA PUBLIC SERVICE COMMISSION

56

1       we are going to continue on.  I have talked about the

2       Grade B construction for our distribution.  Extreme wind

3       for transmission, both for maintenance as well as new

4       construction.  The same for the above extreme wind case

5       for the 230 kV; our non-wood construction for

6       transmission and special maintenance programs; our

7       vegetation management as well as our attachment

8       standards and procedures.

9                 Overall, you all had asked what we see in

10       terms of improvements with this hardening effort, and we

11       believe that with the commitment we have made on the

12       transmission system, we have a strong transmission

13       system.  It performed very well in the hurricanes of

14       2004 and 2005; and, again, we are going to continue our

15       efforts there.  We have hardened sources to some

16       critical facilities, and while those haven't been tested

17       it really will take some wind to see if those really do

18       hold up better or if the wind-borne debris really is the

19       governing issue with the distribution.

20                 And our system in terms of tree trimming, and

21       that is one that we do see some everyday improvement to.

22       You know, before and after the trim of a circuit, we see

23       significant difference in the reliability of that

24       circuit.  So while we are spending significant dollars

25       on our tree trimming and a significant investment there,

FLORIDA PUBLIC SERVICE COMMISSION

57

1       it's not just the benefit that we see with a hurricane.

2       We also see some day-to-day benefit for our customers.

3                 In summary, we are going to continue with the

4       ten-point plan initiatives as I have outlined.  We are

5       going to implement the 2010 plan, assuming approval from

6       the Commission, and we believe that will result in

7       improved system performance not only after a storm, but

8       during normal operations.  So we ask that you consider

9       the plan for approval.

10                 With that, I'll be happy to answer any

11       questions.

12                 MS. L'AMOREAUX:  I just have one question for

13       you.  In the updated plan, TECO states that the company

14       will conduct audits on all pole attachments on an

15       eight-year cycle.  In addition, the company states that

16       it reserves the right to complete this audit on an

17       annual basis.  Under what circumstances would TECO

18       choose to do an audit on an annual basis?

19                 MR. SZELISTOWSKI:  I don't expect for us to do

20       something on an annual basis.  It's a pretty big effort,

21       and generally the attachments that go up on an annual

22       basis, if we are being communicated with well, there is

23       really not a reason to do it on an annual basis.  You do

24       an audit to find things that have been put up that

25       you -- because you are inspecting the same system,

FLORIDA PUBLIC SERVICE COMMISSION

58

1       obviously.  So if you are doing things -- you're doing

2       that to find things that have been put up without your

3       knowledge.

4                 And so to do that every year is probably too

5       much.  If we have instances where we have seen a lot of

6       attachments going up that we weren't informed about,

7       then we might move it up.  But, again, at this point we

8       feel that every four or five years is adequate.

9                 MS. L'AMOREAUX:  Thank you.

10                 MR. SZELISTOWSKI:  Sure.

11                 MS. L'AMOREAUX:  Next we have Gulf Power

12       Company, Ed Battaglia.

13                 MR. BATTAGLIA:  Good morning.  My name is Ed

14       Battaglia, and I'm the Technical Services Manager for

15       Gulf Power, and I'll be presenting Gulf's storm

16       hardening plan.  And we have brought a few added folks

17       as far as technical support to help with any questions

18       that staff may have.  And, also, please excuse me if I

19       have to clear my throat a little bit every once in

20       awhile; I'm trying to get over a little bit of a cold.

21                 Gulf Power's updated storm hardening plan

22       reflects Gulf's commitment to continuous improvement by

23       building on its experiences, by learning from data

24       collected each year of the plan's implementation, and by

25       research that addresses the potential benefits of

FLORIDA PUBLIC SERVICE COMMISSION

59

1       initiatives.  Gulf recognizes the need to address the

2       concerns expressed by both its customers and the Florida

3       Public Service Commission to find ways to storm harden

4       its system which could lead to less frequent outages and

5       improved continuity of service during major

6       storm-related events.  At the same time, Gulf is

7       obligated to balance storm hardening with the need to

8       maintain reasonable costs and still achieve the expected

9       results.

10                 In these first two slides, I will brief

11       discuss the ten on-going initiatives.  Gulf's vegetation

12       management plan consists of a three-year main feeder

13       trim cycle, a six-year lateral trim cycle, and a program

14       for removing hazard trees outside the normally trimmed

15       zone.  In addition, Gulf performs an annual pre-storm

16       season inspection and corrective action program on the

17       remaining two-thirds of mainline feeders.

18                 In respect to joint use attachment audits,

19       Gulf Power has in its current joint use contract

20       agreements to conduct a field audit of the joint use

21       poles every five years.  The last audit was in 2006 with

22       the next one scheduled for 2011.  A pole strength load

23       assessment pilot program was initiated by Gulf in 2007

24       based on the 2006 joint use field audit survey.

25                 Inspection cycle of transmission structures

FLORIDA PUBLIC SERVICE COMMISSION

60

1       and storm hardening activities for transmission

2       structures.  Gulf Power's transmission inspection plans

3       meet or exceed the approved six-year inspection cycle.

4       Gulf completed the replacement of 774 wood crossarms and

5       storm guyed 700 structures at an annual estimated cost

6       of $600,000 as part of the company's approved storm

7       hardening plan.

8                 Geographic information systems, or GIS.  Gulf

9       Power's transmission and distribution data essential for

10       its asset management programs and forensic data analysis

11       have been mapped into its GIS application as part of the

12       company's approved storm hardening plan.

13                 Post-storm data collection and forensic

14       activities.  Gulf worked with industry vendors, such as

15       OSMOSE, Incorporated, and KEMA, Incorporated, to develop

16       and establish a post-storm forensic process for the

17       company.  It has been successfully tested and refresher

18       training completed.

19                 Outage data differentiating between overhead

20       and underground systems.  Gulf Power developed a process

21       and made needed programming changes to its trouble call

22       management system to establish a means to collect this

23       added data.  We continue to collect this outage data as

24       events occur.

25                 Coordination with local governments.  Gulf

FLORIDA PUBLIC SERVICE COMMISSION

61

1       Power representatives are assigned to county Emergency

2       Operations Centers, EOCs, in northwest Florida.  They

3       assist city and county agencies and officials during

4       emergencies that warrant activation of the county EOCs.

5       Gulf Power will provide on-going communications,

6       pre-storm communications, and post-storm communications

7       through our corporate communications department.

8                 Collaborative research.  Gulf Power

9       participated in collaborative efforts to conduct

10       research and development on the effects of major

11       hurricanes on the electrical systems throughout the

12       state of Florida.

13                 Disaster preparedness and recovery plans.

14       Gulf Power uses the plans described in its storm

15       recovery plan to respond to any natural disaster that

16       may occur within its service area.  As part of its

17       annual operations, Gulf conducts yearly storm drills and

18       continues to refine its planning and preparations for

19       the possibility of a natural disaster within Gulf

20       Power's service area.  All of these ten initiatives are

21       on target.

22                 In the next few slides I compare Gulf's

23       approved plan versus the updated plan.  Whenever you see

24       any kind of red font, that indicates that initiative was

25       changed.  Gulf's current vegetation management plan

FLORIDA PUBLIC SERVICE COMMISSION

62

1       consists of a three-year main feeder trim cycle, a

2       six-year lateral trim cycle, and a program for removing

3       hazard trees outside the normally trimmed zone.

4                 Analysis of data shows that 65 percent of

5       Gulf's related mainline outages are now being caused by

6       the failure of large overhanging limbs.  Based on this

7       analysis of data, Gulf proposes placing greater emphasis

8       on overhanging limb removal on mainline feeders in

9       conjunction with a continued danger tree removal during

10       its annual mainline inspection.  Gulf will continue with

11       its three-year cycle on mainline feeders.

12                 Gulf found that establishing a trim back

13       distance, which will provide six years of clearance to

14       be extremely difficult.  Also, danger tree removal in

15       residential areas served by laterals has proven to be

16       very challenging.  Customer acceptance of these

17       practices has not been positive.  In response to this

18       data, Gulf proposes to shorten the trim cycle length on

19       lateral lines to four years and reduce emphasis on

20       lateral danger tree removal.

21                 Joint use attachment audits.  Gulf Power has

22       in its current joint use contract agreements to conduct

23       a field audit of the joint use poles every five years.

24       And, again, the last audit was in 2006 with the next one

25       scheduled for 2011.  Gulf Power recommended and received

FLORIDA PUBLIC SERVICE COMMISSION

63

1       approval from the Commission for a random sampling for

2       pole strength load assessment on five percent or

3       approximately 500 joint use poles.  Gulf initiated this

4       strength load assessment pilot program in 2007.  Again,

5       based on the analysis of data, the low failure rates,

6       and the fact that all new construction and maintenance

7       work are constructed to Grade B construction, which Gulf

8       is transitioning to, Gulf proposes to discontinue the

9       random pole strength pilot project activity for the

10       updated storm hardening plan.  This continuation of the

11       pole strength pilot project will save approximately

12       100,000 over the 2010/2012 time frame.

13                 There are no proposed changes with the next

14       three initiatives, inspection cycle of transmission

15       structures, storm hardening activities for transmission

16       structures, and with our GIS system.

17                 With these next five initiatives, again, Gulf

18       is not proposing any changes as far as data collection,

19       outage data differentiating between overhead and

20       underground, our coordination with local governments,

21       collaborative research, and the disaster preparedness

22       and recovery plans.

23                 Gulf plans to continue its pole inspection

24       program on an eight-year cycle utilizing the same

25       inspection matrix approved by the Commission in 2007

FLORIDA PUBLIC SERVICE COMMISSION

64

1       with one minor exception.  As a result of the findings

2       during the past three years, Gulf plans to discontinue

3       the one percent sample of nonexcavated CCA poles that

4       are less than 15 years old.  Gulf performed full

5       excavation and treatment on 954 CCA poles that initially

6       passed the visual inspection.  None of the excavated

7       poles were rejected, and only minor decay was noted on

8       some of these poles.  This sample clearly indicated that

9       Gulf's inspection matrix is effective in assuring that

10       no defective poles remain in service.

11                 Since this program adds costs without

12       providing additional benefits, Gulf proposes to

13       discontinue the one percent sample program for the

14       updated storm hardening plan.  This will result in an

15       estimated annual savings of approximately $7,500.  Gulf

16       will continue all other elements of the current wood

17       pole inspection program, which has been so successful

18       over the past three years.

19                 Compliance with National Electric Safety Code,

20       NESC.  Gulf Power's transmission system, substations,

21       and distribution system are designed to meet the

22       National Electric Safety Code.  In respect to

23       distribution, exceeds the NESC with Gulf's transition to

24       Grade B construction on all new construction, major

25       projects, and maintenance work.  There are no proposed

FLORIDA PUBLIC SERVICE COMMISSION

65

1       changes in this initiative.

2                 Extreme wind loading standards.  Gulf's

3       approved storm-hardening plan exceeded the National

4       Electric Safety Code by transitioning to Grade B

5       construction on distribution construction.  Gulf Power

6       plans to continue this transition to Grade B

7       construction standards on all new construction, major

8       projects, and maintenance work.

9                 As part of its approved storm hardening plan,

10       Gulf also constructed extreme wind loading pilot

11       projects for distribution facilities serving critical

12       infrastructures such as hospitals, fuel depos, sewage

13       treatment plants, and major roadway crossings.  Gulf

14       proposes to change its approach by expanding its Grade B

15       initiative to target critical pole lines with multiple

16       feeders on them and convert them to Grade B

17       construction.

18                 In addition, the existing wood poles will be

19       replaced with concrete poles from the substations to

20       strategic operational points on the feeders.  This

21       initiative is taking design concepts which we know work

22       well in the transmission and substation areas and

23       carries them to the distribution side.  Gulf has

24       budgeted approximately $2.3 million for this initiative

25       over the three-year period covered by the plan.

FLORIDA PUBLIC SERVICE COMMISSION

66

1       There are no changes to the next two initiatives,

2       mitigation of damage to underground facilities and

3       supporting T&D facilities due to flooding and storm

4       surges, and the placement of new and replacement

5       distribution facilities to facilitate access.

6                 Other key elements.  Gulf proposes no changes

7       to the feeder patrols and infrared patrols which are

8       completed annually prior to June 1st.  In respect to

9       wind monitors, Gulf completed the installation of 19

10       wind monitors as outlined in the approved storm

11       hardening plan and will maintain those wind stations as

12       part of the updated storm hardening plan.  The wind

13       speed data gathered from these monitors, along with the

14       forensic data gathered after a major storm event, will

15       help determine the effectiveness of the storm hardening

16       initiatives, such as the Grade B construction and the

17       pilot programs where we constructed facilities to the

18       extreme wind loading standards.

19                 Additional proposed storm hardening

20       initiatives, conversion of 4 kV distribution.  Gulf

21       proposes to convert its remaining three 4 kV

22       distribution feeders to its standard 12.47 kV

23       distribution voltage.  These conversions will reduce

24       potential outages and facilitate improved restoration

25       times by converting to Gulf's standard specifications

FLORIDA PUBLIC SERVICE COMMISSION

67

1       and materials which will be more readily available after

2       a major storm.  In addition, the added clearance

3       requirements and increased insulation levels for 12.47

4       kV will reduce potential outage causes.

5                 Also, any needed pole replacements as a result

6       of the conversion would be built to the stronger Grade B

7       conversion, which would help to accelerate Gulf's

8       transition to Grade B construction.  Gulf plans to

9       convert one feeder per year at an approximately average

10       cost of $300,000.

11                 Distribution automation.  Gulf proposes to

12       install reclosers or automated switches at approximately

13       the midway point on distribution feeders.  Additional

14       switches would be deployed on long or critical feeders

15       to further segment the feeder for outage restoration.

16       These devices which protect downstream from temporary

17       faults will be controlled remotely by Gulf's

18       distribution control center personnel and/or placed in

19       an automated restoration scheme.  Gulf's estimated cost

20       per year to implement this is $2 million.

21                 Strategic installation of automated fault

22       circuit indicators, or FCIs.  These are devices designed

23       to provide a visual indication of an outage if it

24       occurred beyond their location.  They will help to

25       expedite the location of outage causes and the isolation

FLORIDA PUBLIC SERVICE COMMISSION

68

1       of the problem so that service can be restored to some

2       customers while the problem is being corrected.

3       Initially, Gulf proposed to install FCIs at 20 locations

4       on its system.  The estimated annual cost is

5       approximately $20,000.

6                 Development of a distribution supervisory

7       control and data acquisition system, or DSCADA system.

8       In order to reduce storm restoration times, Gulf

9       proposes to develop and to begin implementation of the

10       systems and application that would permit the monitoring

11       and remote control of the distribution automation

12       devices that I mentioned earlier.  The estimated annual

13       cost of this activity is $217,000.

14                 This chart shows Gulf's estimated cost for the

15       updated storm hardening plan versus the estimated cost

16       for the approved plan and actual cost of the approved

17       plan.  As you can see, Gulf is proposing to increase its

18       commitment to storm hardening its system.  Gulf's

19       updated plan makes adjustments based on lessons learned

20       from the approved plan and expands the number of

21       initiatives which we feel will improve the reliability

22       of its system and increase its storm resistance.

23                 This map illustrates Gulf's service areas, and

24       I know it is a little difficult to see as far as on the

25       screen there, and it indicates locations of projects

FLORIDA PUBLIC SERVICE COMMISSION

69

1       completed in the approved plan.  And we also went ahead

2       and plotted projects proposed in the updated plan.

3       Gulf's initiatives and projects are dispersed across its

4       system so that in the event of a major storm there will

5       be opportunities to test how well the various storm

6       hardening options perform.

7                 In respect to struggles or challenges to

8       achieving the ten initiatives, the uncertainty related

9       to material and labor is one.  With most utilities

10       focusing on the same issues, the availability of the

11       needed materials and skilled labor is a concern.  And,

12       of course, in the event of a major storm, it could

13       reduce the availability of needed resources creating

14       work delays in implementing the plan.

15                 Another struggle is with city ordinances,

16       existing ones, and possibly expanded city ordinances.

17       They impact the possible effectiveness of some of the

18       initiatives and impact work schedules.  An example of

19       this would be, say, the trimming and removal of trees.

20       Power restoration and hardening is improving overall on

21       Gulf's system.  For Gulf, the initiatives such as

22       extreme wind loading and Grade B construction, those are

23       pilot projects in the sense that based on Gulf's

24       experience and knowledge over many years of storm

25       restoration activities, that what we have seen that it

FLORIDA PUBLIC SERVICE COMMISSION

70

1       predominately is not the pure wind, it's the debris

2       carried on the wind that causes the outage problems.  So

3       for Gulf in an analysis of actual storm data collected

4       over time, it is essential to try to determine their

5       benefits.  And, of course, and I'll say fortunately Gulf

6       has not experienced any major storms to test these

7       initiatives.  And this may address the question that you

8       were putting out there as far as for all utilities.

9                 In respect to Gulf's vegetation management

10       plan, Gulf is seeing reduced customer interruptions and

11       reduced customer minutes of interruption due to tree

12       outages when you focus on that one particular

13       initiative.  So, again, we feel that is an improvement.

14       And as we stated, we are looking to try to make more

15       gains by reducing our lateral trim cycle from six to

16       four years.

17                 T&D inspections.  The initiatives involving

18       T&D inspections, which that includes the patrols as far

19       as digital patrols, the infrared patrols that I

20       mentioned earlier as far as other key elements where we

21       do those before the start of storm season.  The six-year

22       transmission inspection and eight-year distribution wood

23       pole inspection, all of those contribute to possible

24       outages by being proactive in the maintenance of Gulf's

25       T&D systems, so we feel those are real positives.

FLORIDA PUBLIC SERVICE COMMISSION

71

1       And that concludes my presentation.  Are there any

2       questions?

3                 MS. L'AMOREAUX:  I have a couple of questions.

4       A couple of them you have already answered, so that is

5       kind of good.  In the updated plan, and as you spoke in

6       your presentation, you have specific changes to your

7       trim cycle.  What experience has Gulf encountered that

8       has led to these changes?

9                 MR. BATTAGLIA:  Predominately as far as our

10       experience there for changing from the six to four year

11       lateral is the dramatic increase in what we're having to

12       do in spot tickets to trim those areas, which is

13       indicating clearly to us that the current cycle is not

14       adequate.  So the number of those tickets that have

15       dramatically risen has driven us to say we need to do

16       something else there.  And then also the amount of

17       clearance, as I mentioned earlier, as far that is needed

18       on a six-year versus a four-year cycle, and the other

19       element was the removal of danger trees on laterals.  As

20       far as the amount of customer resistance to those type

21       of activities, we basically said to improve our plan we

22       needed to shorten that cycle.

23                 MS. L'AMOREAUX:  And can you briefly discuss

24       how Gulf's new storm hardening initiatives are

25       beneficial and cost-effective?

FLORIDA PUBLIC SERVICE COMMISSION

72

1                 MR. BATTAGLIA:  Well, predominately overall,

2       as I mentioned earlier on that last slide, you know, to

3       determine the actual benefits of the initiatives such at

4       Grade B construction, the extreme wind loading projects,

5       those types of initiatives that are our high cost as far

6       as needing forensic analysis of that after a major storm

7       to try to determine if there are benefits there.  But

8       there are elements of the plan, such as the inspections

9       that I mentioned, such as vegetation management, and

10       with the added elements of the plan that we're proposing

11       such as the 4 kV conversion, the distribution

12       automation, the SCADA system that we feel will achieve

13       as far as what our expectations for storm hardening,

14       expediting restoration of service, but at the same time

15       add what we feel is a better cost/benefit ratio for our

16       customers.

17                 MS. L'AMOREAUX:  That's all the questions I

18       have.  Thank you.

19                 MR. BATTAGLIA:  Thank you.

20                 MS. L'AMOREAUX:  Next up is Florida Public

21       Utilities Company, Mr. Puentes.

22                 MR. PUENTES:  Good morning, staff.  My name is

23       Jorge Puentes.  I'm the Northeast Division Electric

24       Operations Manager.  I would also like to acknowledge

25       the presence of Mark Cutshaw, who is our Northeast

FLORIDA PUBLIC SERVICE COMMISSION

73

1       General Manager, as well as Buddy Shelley, who is the

2       Northwest General Manager.

3                 We appreciate the opportunity to come and

4       participate in the workshop, but before I give you the

5       status update on our storm hardening plan and give you

6       the highlights, the differences between what was

7       approved and what has been updated, I would just like to

8       give you a brief overview of our company.

9                 We are a very small investor-owned utility.

10       As of October of 2009, we are a wholly-owned subsidiary

11       of Chesapeake Utilities.  Our electric customer base is

12       only 28,000 customers and our territory is small.  We

13       have about 15 in the northeast division, which is a

14       coastal territory, and 13,000 of them are in northwest

15       Florida, which is more of a rural territory.

16                 Now, as I pass on to provide you the status

17       update on our storm hardening initiatives, I'd like to

18       start with the vegetation management.  I'd like to also

19       note that during the 2008 rate case there was a change

20       to our original 2007 plan in this area where we agreed

21       to implement the three-year cycle of tree trimming for

22       feeders and the six-year cycle for laterals.  Initially,

23       we were planning to do this with seven crews and at the

24       end we agreed to do it with five crews.  We continue to

25       be on target with this initiative.  Since 2008 and up to

FLORIDA PUBLIC SERVICE COMMISSION

74

1       2009, we have removed about 530 danger trees, and also

2       we have trimmed in both divisions a total of 119 miles

3       of feeders and about 100, almost 200 miles of laterals.

4       And up to this year we have trimmed about 34 miles of

5       feeders and seven miles of laterals.  That's up to the

6       end of May.

7                 In terms of the joint use pole attachment

8       audit, since 2008 and 2009, we have identified our

9       contractor, working with our contractor we have

10       identified about 53 poles having third-party attachments

11       that had some loading issues.  And what we plan to do

12       with those is do further analysis by using software.  We

13       have Pole-Foreman, and after we obtain the results we

14       will then work with our current agreements and try to

15       let them know what attachments will have to be moved and

16       we will make those facilities more strengthened.

17                 In terms of the other initiative, number

18       three, of transmission inspections, we are doing this on

19       a six-year basis.  We have performed in 2008 and 2009

20       visual inspections, but the plan is to begin climbing

21       inspections from this year on.

22                 In terms of the GIS information system, in

23       2008 we were able to install that in the northwest

24       division, and in 2009 we had that implemented in the

25       northeast division.  The northwest division has a little

FLORIDA PUBLIC SERVICE COMMISSION

75

1       bit more improvement because they have SCADA

2       capabilities, and we're looking to see if we can

3       implement SCADA in the northeast division.  But it's a

4       very useful tool that we use also for outage management,

5       and we're using it to report now our yearly performance

6       indicators using that software now.

7                 In this other initiative about the

8       transmission storm hardening, I also would like to make

9       a note that during the 2000 rate case there was a change

10       from our original 2007 plan where we were proposing to

11       replace about 190 wood poles on our 69 kV system, and we

12       were planning to do this over a 15-year period.  At the

13       end, in 2008, we agreed to change that to a -- to change

14       25 of those poles on a ten-year cycle, more or less

15       going and changing about 2.5 poles per year.  We have

16       accelerated this by changing several poles.  For

17       example, in 2009 we completed a project along our

18       coastal area where we replaced 14 69 kV wood poles with

19       spun concrete.  This year we also changed another

20       additional three wood poles with concrete, spun concrete

21       poles in another project.  We did these two projects

22       using the extreme wind loading criteria, which we are

23       applying to the northeast division to be 130 miles per

24       hour, and for the northwest division we are implementing

25       120 miles per hour.

FLORIDA PUBLIC SERVICE COMMISSION

76

1                 We also applied this criteria to the

2       distribution facilities that are critical to our

3       customers.  For example, the hospitals, the highways

4       along major -- feeders along major highways, and also

5       feeders to sewer plants and other facilities.

6                 In terms of the post-storm data collection

7       forensics, we have established a procedure, and we plan

8       to use a contractor.  However, we haven't had as much --

9       as other companies have reported, we haven't had

10       experience with hurricanes since the 2005 period, but

11       once we have some information on this we will report it

12       to the Commission.

13                 Going on with our storm hardening initiatives,

14       by using our outage management system we are able to

15       also comply by providing the overhead and underground

16       system information.  We're providing that on a yearly

17       basis.

18                 We also like to coordinate very closely with

19       our EOCs.  We attend all their meetings.  We also

20       provide safety training to them.  We have a program

21       where we go and explain to them the hazards of wires

22       down and what they should do in cases like that when

23       their crews, their tree-removing crews, or construction

24       crews are close to them.  We also participate in any of

25       their events.

FLORIDA PUBLIC SERVICE COMMISSION

77

1                 We work closely with them on vegetation, and

2       we have a good understanding of what they also need from

3       us, because we also are going to provide some personnel

4       like never before in terms of when hurricanes happen

5       they will be over there located, and they will be able

6       to inform them of what's going on with our utility in

7       terms of outages.

8                 In terms of the collaborative research, we are

9       active in that area.  We attend their workshops, and we

10       support their initiatives and research.  We have been

11       active in the tree trimming, underground, and wind

12       loading areas.

13                 In terms of the disaster preparedness and

14       recovery, we have developed plans.  We update these

15       annually, and we review them with our employees, and we

16       have training with them so that everyone knows what they

17       are supposed to do in case we have an emergency.  We

18       ensure that material for storms is available and it is

19       reviewed.  We review our trucks, our radio communication

20       equipment, and we ensure the readiness of all personnel.

21                 As we contrast the approved plan versus the

22       updated plan, there is one major change that we are

23       proposing for your approval.  This has to do in terms of

24       the wood pole inspections.  Currently we are doing

25       detail -- we are doing detailed inspections about

FLORIDA PUBLIC SERVICE COMMISSION

78

1       one-eighth of them on an eight-year cycle.  We have used

2       OSMOSE as our contractor, and since then we have

3       inspected about 5,815 poles.

4                 And during this period of inspections between

5       2008 and 2009, we were able to uncover some evidence

6       that allowed us to make this proposal, and this has to

7       do with detailed inspections for CCA, less detailed

8       inspections for CCA poles.  What we found is that out of

9       nearly half, about 2,625 CCA poles that were inspected,

10       none of them had failures.  And the ages of those poles

11       inspected were between one year and 28 years, and that

12       is outlined in our plan.

13                 And we are saying that based on these new

14       facts we would like to propose to do a less detailed

15       inspection for CCA poles under 16 years of age.  And in

16       an effort to be consistent with what other IOUs are

17       doing, we would like to augment the inspections by

18       one percent of CCA poles not requiring a detailed

19       inspection.

20                 To summarize what our plan has been

21       accomplishing as we continue to implement this plan, at

22       this point we have not found any issues in achieving

23       these ten initiatives.  In terms of the budgeting or the

24       costs, we continue to monitor those costs, and at this

25       point those costs that are monitoring have been

FLORIDA PUBLIC SERVICE COMMISSION

79

1       estimated and they were included in that 2008 rate case

2       proceeding.  And in terms of some of your questions that

3       if we believe that this plan hardens the infrastructure,

4       we believe it does.  Certainly we believe that we will

5       see benefits.  Again, I can say that we haven't had any

6       storms hitting our -- major storms hitting our

7       territory, but we believe that it does create a stronger

8       system.

9                 That concludes my presentation, and I'd like

10       to ask you if you have any questions.

11                 MS. L'AMOREAUX:  I just have one question.

12                 MR. PUENTES:  Yes.

13                 MS. L'AMOREAUX:  Can you explain why there is

14       a shortage of tree trimming crews in your area?

15                 MR. PUENTES:  A shortage of tree trimming

16       crews meaning --

17                 MS. L'AMOREAUX:  In your amended updated plan

18       you said that current tree trimming crews, there was a

19       shortage of them, and if and when they become available

20       you will work to trim trees.

21                 MR. PUENTES:  I think that was mainly in the

22       first plan -- and correct me, Mark, if I'm not -- in the

23       first plan we wrote that, but I think in the updated

24       plan, or after the 2008 rate case, we came to an

25       agreement that we would do this three-year cycle on

FLORIDA PUBLIC SERVICE COMMISSION

80

1       feeders and six-year cycle on laterals with five

2       tree-trimming crews, and since then we haven't had that

3       shortage.

4                 MS. L'AMOREAUX:  I'll check into that.

5                 MR. PUENTES:  Sure.

6                 MS. L'AMOREAUX:  Do you have any questions,

7       Dave?  Lisa?

8                 All right.  Well, if there's no more

9       questions --

10                 MR. PUENTES:  Thank you.

11                 MS. L'AMOREAUX:  Oh, thank you.

12                 MR. PUENTES:  Thank you very much.

13                 MS. L'AMOREAUX:  I would first like to thank

14       everybody here today, especially the presenters for

15       giving very informative presentations.  Staff is still

16       reviewing the updated storm hardening plans, and after

17       which we will be sending maybe one or more rounds of

18       discovery.  Our target is to bring a recommendation to

19       agenda probably around August, no later than September.

20                 In addition, if the parties want to submit any

21       post-workshop comments, we ask that you submit those by

22       June 28th, 2010.  And with that, this workshop is

23       adjourned.  Thank you.

24                 (The workshop concluded at 11:29 a.m.)

25

FLORIDA PUBLIC SERVICE COMMISSION

81

1       STATE OF FLORIDA    )

2                           :    CERTIFICATE OF REPORTER

3       COUNTY OF LEON      )

4

I, JANE FAUROT, RPR, Chief, Hearing Reporter

5       Services Section, FPSC Division of Commission Clerk, do

hereby certify that the foregoing proceeding was heard

6       at the time and place herein stated.

7                 IT IS FURTHER CERTIFIED that I

stenographically reported the said proceedings; that the

8       same has been transcribed under my direct supervision;

and that this transcript constitutes a true

9       transcription of my notes of said proceedings.

10                 I FURTHER CERTIFY that I am not a relative,

employee, attorney or counsel of any of the parties, nor

11       am I a relative or employee of any of the parties'

attorney or counsel connected with the action, nor am I

12       financially interested in the action.

13                 DATED THIS 24th day of June, 2010.

14

15

___________________________________________

16                         JANE FAUROT, RPR

Official FPSC Hearings Reporter

17                          (850) 413-6732

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION