1

1                              BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3       In the Matter of:

DOCKET NO. UNDOCKETED

4

HURRICANE PREPAREDNESS.

5       ________________________/

6

7

8

9       PROCEEDINGS:    WORKSHOP

10       COMMISSIONERS

PARTICIPATING:  CHAIRMAN RONALD A. BRISÉ

11                       COMMISSIONER LISA POLAK EDGAR

COMMISSIONER ART GRAHAM

12                       COMMISSIONER EDUARDO E. BALBIS

COMMISSIONER JULIE I. BROWN

13

DATE:           Wednesday, May 9, 2012

14

TIME:           Commenced at 1:33 p.m.

15                       Concluded at 4:45 p.m.

16       PLACE:          Betty Easley Conference Center

Hearing Room 148

17                       4075 Esplanade Way

Tallahassee, Florida

18

REPORTED BY:    LINDA BOLES, RPR, CRR

19                       Official FPSC Reporter

(850) 413-6734

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

2

1       APPEARANCES:

2       SAM MOORE, Florida Power & Light

3       JASON CUTLIFFE, Progress Energy Florida

4       DAVID SWEAT, Tampa Electric Company

5       SHARON PINKERTON, Gulf Power Company

6       BILL GRANT, Florida Public Utilities Company

7       JODY FINKLEA, Florida Municipal Electric Association

8       ROB McGARRAH, City of Tallahassee

9       HERMAN DYAL, Florida Electric Cooperatives Association

10       GREG FOLLENSBEE, AT&T Florida

11       SHAUN McLAURY, Verizon Florida, LLC

12       SANDRA A. KHAZRAEE, CenturyLink

13

14       FOR THE FPSC:

15       MICHAEL LAWSON, ESQUIRE

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

3

1                         P R O C E E D I N G S

2                 CHAIRMAN BRISÉ:  Good afternoon.  We're going

3       to go ahead and convene this workshop, and we're going

4       to ask staff to read the notice.

5                 MR. LAWSON:  Pursuant to the notice issued in

6       the FAW and as issued by this Commission, notice is

7       given that this workshop will convene today, May 9th,

8       2012, 1:30 p.m. 'til 5:00 p.m. at this location.  The

9       purpose of this workshop is to provide a forum for

10       Florida electric utilities and the three major incumbent

11       local exchange carriers to brief the Commission on their

12       2012 hurricane season preparation, and for other matters

13       as properly described in said notice.

14                 CHAIRMAN BRISÉ:  Thank you.  At this time we

15       will take appearances.  Okay.

16                 MR. LAWSON:  Michael Lawson on behalf of the

17       General Counsel's Office, Public Service Commission.

18                 CHAIRMAN BRISÉ:  That's it?  All right.

19                 In 2006 the Florida Public Service Commission

20       adopted a multifaceted approach and a response to ensure

21       all utility infrastructures will be better able to

22       withstand the impact of hurricanes and implement lessons

23       learned from the 2004/2005 seasons.  We adopted ten

24       storm hardening initiatives and required investor-owned

25       utilities to form -- to file formal storm hardening

FLORIDA PUBLIC SERVICE COMMISSION

4

1       plans subject to our approval.

2                 In our July 2007 report to the Legislature we

3       cited our most critical recommendation that Florida

4       remain -- I'm sorry -- Florida maintain a high level of

5       storm preparation.  The annual hurricane season

6       preparation workshop provides utilities and local

7       exchange companies a forum to advise us of their

8       individual hurricane season preparation activities.

9                 This is the seventh year that we've conducted

10       such a workshop.  After three years with no hurricanes

11       visiting our shores, fading memories can lead to

12       complacency.  We, however, should view the hurricane

13       season of 2012 with caution and recognize that

14       preparedness is key to minimizing storm impacts.  The

15       forecasters remind us that only one hurricane making

16       landfall in our area will make it an active season for

17       all of us.

18                 We ask each of our presenters to candidly

19       address the status of their company's preparation for

20       the 2012 hurricane season.  Please include the status of

21       the work achieved to protect facilities to date, work in

22       progress, and work to be accomplished in the near

23       future.

24                 Finally, we ask that you specifically address

25       the areas of vulnerability within your service area, and

FLORIDA PUBLIC SERVICE COMMISSION

5

1       let us know if there's anything that the Public Service

2       Commission can do to assist you.

3                 It is understood that while the electric

4       utilities own the vast majority of the electric

5       transmission and distribution infrastructure in the

6       state, local exchange companies own many of the poles

7       upon which the electric utility infrastructure is

8       placed.  The ILECs, therefore, play a vital role in

9       preparation for the hurricane season as well, and we

10       welcome their participation as well.

11                 We go through this exercise and we've gone

12       through this exercise for several years, and we

13       certainly hope that the most pertinent information is

14       presented today.  And if there's information that sort

15       of goes over information that we've covered in past

16       years, that we go through that information rather

17       quickly and get to the information that is most pressing

18       and important for us to look at that is sort of new

19       information for us to, to avail ourselves of.

20                 With that, I'm going to allow, if there are

21       comments from my fellow Commissioners that they would

22       like to make at this time before we get into the order

23       of presentations and all of those things and before I

24       turn it over to staff.

25                 (No response.)

FLORIDA PUBLIC SERVICE COMMISSION

6

1                 Okay.  Seeing no comments from fellow

2       Commissioners, no comments from staff.  So the order of

3       presentation will be as such:  Florida Power & Light

4       will go first, then Progress Energy Florida, Tampa

5       Electric Company, and then Gulf Power.  After that point

6       we anticipate taking a short break.

7                 We ask, for the, for the purposes of keeping

8       it moving at a good pace that -- obviously,

9       Commissioners, you can ask a question whenever you want

10       to ask a question, but for, for the flow I would ask

11       that at the end of the presentation that we enter into

12       the questions at that point rather than entering into a

13       back and forth in terms of questioning with, with each

14       presenter.

15                 So with that, I suppose that we will call

16       Florida Power & Light, and I think it will be Sam Moore.

17                 MR. MOORE:  Yes.  Good afternoon,

18       Commissioners and staff.  My name is Sam Moore.  I am

19       the General Manager of Operations for the Miami-Dade

20       region in FPL's service territory.  Included in my

21       responsibility is being part of the team that oversees

22       FPL's storm restoration and preparedness activities.

23                 Thank you for providing us this opportunity to

24       review FPL's hurricane preparedness plans for the 2012

25       storm season.  My presentation will address activities

FLORIDA PUBLIC SERVICE COMMISSION

7

1       and results of our distribution and transmission

2       systems.

3                 Let me start off by saying FPL is well

4       prepared and we are ready to respond should our

5       communities be faced with hurricane activity this year.

6       And even though we have been fortunate in avoiding a

7       major hurricane since 2005, we have maintained our focus

8       and continued efforts to improve our system and

9       processes, as well as strengthen our infrastructure to

10       be better prepared for this and future storm seasons.

11                 About preparedness -- preparations, I'm sorry,

12       FPL's ongoing and continuous hurricane preparation

13       efforts concentrate on four key elements.

14                 First, we continue to strengthen our

15       distribution and transmission infrastructure.  This is

16       being accomplished through our hardening plans, our pole

17       inspection program, and our vegetation management

18       programs, all of which have been reviewed and approved

19       by the Commission.

20                 Second, as we do every year, we continue to

21       prepare our storm organization, ensuring that we have

22       the right people in the right roles with the necessary

23       training and knowledge so that they can respond quickly

24       and safely.

25                 Third, we continue to improve our already

FLORIDA PUBLIC SERVICE COMMISSION

8

1       well-tested restoration plan by incorporating lessons

2       learned and utilizing technology.

3                 And finally, we continue to look for ways to

4       provide more and better information to our customers.

5                 Now let's look at each of these elements in a

6       little bit more detail.  Hardening, distribution.

7       Hardening is a key component of our plan to strengthen

8       our infrastructure.  For our distribution system, FPL

9       continues to implement its three-prong approach.  We're

10       hardening our critical infrastructure facilities or

11       CIFs, these are hospitals, 911 centers, and police and

12       fire stations, hardening those circuits to the National

13       Electric Safety Code extreme wind loading criteria.

14                 We're also incrementally hardening up to and

15       including our extreme wind loading criteria what we

16       refer to as our community projects.  These are major

17       thoroughfares with key community needs like grocery

18       stores, gas stations, and pharmacies.

19                 We're utilizing our EWL design guidelines to

20       construct all new overhead facilities, major planned

21       work, and relocation projects, as well as our daily work

22       activities.

23                 For our CIFs we've now hardened all major

24       hospitals and acute care facilities and essentially all

25       911 and emergency operation centers throughout our

FLORIDA PUBLIC SERVICE COMMISSION

9

1       system.  Since 2007 we've hardened approximately

2       1,000 miles and 305 feeders serving 330 CIF customers as

3       well as other community needs.

4                 For 2012 an additional 27 CIF and 14 community

5       projects are planned.  Our hardening focus this year

6       includes water sewage treatment plants.

7                 Transmission hardening.  While FPL's

8       transmission system is already constructed to extreme

9       wind loading criteria, we continue to improve the

10       strength and resilience of the transmission system by

11       replacing all wood poles and structures with concrete

12       and replacing ceramic post insulators on concrete poles

13       with more reliable polymer post insulators.

14                 Since 2007 FPL has replaced 9,600 wood

15       transmission structures.  Additionally, we have replaced

16       ceramic post insulators on more than 3,000 structures.

17       In 2012 we're planning to replace approximately 1,000

18       additional wood structures, as well as the ceramic post

19       insulators on nearly 300 additional structures.

20                 Pole inspections, distribution.  FPL began the

21       implementation of its systemwide eight-year distribution

22       pole inspection program in May of 2006, ensuring that

23       each pole meets strength and loading requirements.

24                 At the end of 2011, FPL had inspected

25       approximately 74% of its 1.1 million poles and is on

FLORIDA PUBLIC SERVICE COMMISSION

10

1       target with its eight-year pole inspection cycle.  In

2       2012, we again plan to inspect approximately one-eighth

3       of our distribution poles.

4                 Pole inspections, transmission.  All of our

5       approximately 66,000 wood, concrete, steel transmission

6       structures are on a six-year inspection cycle.  In 2012,

7       FPL completed its first six-year inspection cycle -- in

8       2011 we completed the first six-year inspection cycle,

9       and in 2012 plans to begin a new cycle of inspections.

10                 Additionally, to complement our distribution

11       hardening and storm preparation efforts, we plan to

12       complete inspections on all 500kV lines and transmission

13       facilities serving critical infrastructure functions

14       prior to the 2012 storm season.  These inspections are

15       underway and on schedule to be completed as planned.

16                 Vegetation management, distribution.  Like

17       hardening, vegetation management is a key component of

18       our plan to strengthen the infrastructure and prepare

19       for storms.  We continue to maintain our feeders on a

20       three-year average trim cycle and on are schedule toward

21       achieving our approved six-year average trim cycle for

22       laterals by the established target of 2013.

23                 Also, consistent with our efforts over the

24       last couple of years, we're on schedule to complete the

25       trimming of all lines serving our top critical

FLORIDA PUBLIC SERVICE COMMISSION

11

1       infrastructure facilities prior to the height of the

2       2012 hurricane season.

3                 Finally, as we all know, no vegetation

4       management program can be effective without the

5       cooperation of our customers.  We continue to

6       proactively promote "Right Tree - Right Place" programs

7       with our customer community leaders to ensure that

8       future planting of trees will avoid conflicts with our

9       lines.  Also, we continue seeking their support in

10       trying to remove existing trees that are interfering

11       with our lines.

12                 Vegetation management, transmission.  The

13       vegetation management plan for FPL's transmission

14       right-of-way is very straightforward.  Twice a year we

15       inspect 100% of our transmission right-of-way and

16       perform all necessary trimming to make sure the required

17       North American Electric Reliability Council standard

18       clearances are maintained.

19                 Annual preparations.  Each year we ensure that

20       all storm roles are identified and staffed with the

21       right personnel.  We conduct extensive training,

22       including our annual company-wide hurricane dry run

23       exercise that includes our field as well as support

24       personnel.  The exercise tests our systems and processes

25       to ensure they're ready.

FLORIDA PUBLIC SERVICE COMMISSION

12

1                 This year's exercise is being held this Friday

2       and will be directed from FPL's new Category 5 rated

3       command center in Palm Beach County.  This new facility

4       will provide a secure location from which the company

5       will conduct uninterrupted command and control

6       operations from pre-landfall to post-restoration.

7                 As in the past, we invite officials from

8       certain county emergency operation centers to join us

9       during the dry run to further improve our understanding

10       of one another's storm operations.

11                 Also, FPL's storm organization includes

12       forensic teams that are responsible for observations and

13       the collection of data assigned with damaged

14       infrastructure.  We've been fortunate to have had few

15       opportunities for data collection over the past few

16       storm seasons, but ultimately this information will

17       allow us to better understand how our infrastructure

18       performed and provide valuable lessons for future

19       evaluation and actions.

20                 Our restoration plans.  Our restoration plan

21       has one clear objective, to safely restore electric

22       service for our communities' critical infrastructure

23       functions and needs along with the greatest number of

24       customers in the shortest amount of time.

25                 For the 2012 storm season all of our resource

FLORIDA PUBLIC SERVICE COMMISSION

13

1       plans are in place.  For example, we have the necessary

2       arrangements for catering, housing, water, staging sites

3       throughout our system, equipment for these sites,

4       arrangements with foreign utilities through our, through

5       our mutual assistance agreements, agreements with

6       contract crews, and increased material and fuel

7       inventories.

8                 Also, in 2012, FPL continues with its

9       implementation of the incident command system, ICS,

10       which correlates with the National Incident Management

11       System.  While FPL already adheres to many of the key

12       features of ICS, our goal is to be consistent with as

13       many ICS tenets as possible to further enhance

14       communications with external agencies in standardized

15       key roles.

16                 Communications.  Experience during the 2004

17       and 2005 storm seasons taught us that communicating with

18       our customers and communities can be just as important

19       as our restoration efforts.  As a result, we meet

20       annually with county emergency managers to identify

21       critical infrastructure locations within each

22       jurisdiction.  We also make certain that we've assigned

23       representatives to support each of the 27 county and

24       seven satellite emergency operation centers located

25       throughout our service territory.

FLORIDA PUBLIC SERVICE COMMISSION

14

1                 We have also developed a dedicated government

2       portal website that allows government officials to

3       obtain the latest media releases and information on

4       customer outages, estimated restoration times, FPL crew

5       resources, outage maps, and other information.  In

6       addition, our enhanced e-mail distribution process

7       targets key messages to governmental audiences.

8                 Further, FPL continues to actively participate

9       in the National Hurricane Conference, discussing with

10       government and community leaders how best to bring

11       communities back to normal after severe storm events as

12       we continue to participate and support the government's

13       hurricane conference.  Additionally, in 2011 FPL's

14       community outreach teams conducted 59 presentations to

15       local community-based organizations, including the topic

16       of storm readiness.

17                 Finally, in response to the most frequent

18       asked, question asked of us, "When will my power be back

19       on?", we continue to enhance our outage communication

20       system to provide even more detailed estimated times of

21       restoration.

22                 Finally, Commissioners, we were again asked to

23       address in all presentations any areas of concerns or

24       vulnerability.  Our four items to note remain the same

25       as in past years.

FLORIDA PUBLIC SERVICE COMMISSION

15

1                 The first one is that our service territory

2       may be affected by a storm or storms before we're able

3       to complete our hardening efforts.

4                 The second is being affected by multiple

5       storms over a short period of time like we experienced

6       in 2004 and 2005.

7                 The third, being impacted, impacted by

8       catastrophic storms like Hurricane Andrew or Hurricane

9       Katrina, which can destroy everything in her path.

10                 And last, experiencing a shortage of

11       sufficient resources, whether it be material, equipment,

12       and/or personnel.

13                 While some of these are beyond our control and

14       means, we will still do all we can to reasonably

15       mitigate these occurrences.

16                 In summary, FPL is confident that it's well

17       prepared for the 2012 season.  Our hardening, vegetation

18       management, and pole inspection initiatives have

19       strengthened and are strengthening our system.  Our

20       storm organization is in place, well trained, and ready.

21       We've refined our already well-tested restoration plan.

22       And, lastly, we are in a position to better communicate

23       with our customers.

24                 We, like all of you, are hoping for an

25       inactive hurricane season.  However, should hurricanes

FLORIDA PUBLIC SERVICE COMMISSION

16

1       affect our communities in 2012, FPL is ready to respond.

2       Thank you.

3                 CHAIRMAN BRISÉ:  Thank you, Mr. Moore.

4                 And, Commissioners, are there any questions or

5       comments at this time?

6                 Okay.  Commissioner Brown and then

7       Commissioner Edgar.

8                 COMMISSIONER BROWN:  Thank you, Mr. Chairman.

9       And thank you for your presentations.

10                 With this year's hurricane drill occurring on

11       Friday, are you incorporating anything different from

12       last year's experiences or lessons learned?

13                 MR. MOORE:  The one thing that is really

14       different this year is that we will be in a new

15       facility.  And, and with that, we, we also will be

16       employing new modes of communicating with our customers.

17                 The one big thing that we have noticed and a

18       lesson learned from the last dry run was that social

19       media has really, really and will be playing a really

20       big part in all of our efforts in the future, whether it

21       be Facebook, Twitter or any of them.  And so we will be

22       establishing blogs and communicating that way to

23       customers on restoration times and so forth.

24                 COMMISSIONER BROWN:  That's great.  And just

25       another question about your "Right Tree - Right Place"

FLORIDA PUBLIC SERVICE COMMISSION

17

1       program.

2                 MR. MOORE:  Yes.

3                 COMMISSIONER BROWN:  Can you elaborate a

4       little bit more about that?

5                 MR. MOORE:  Well, you know, unfortunately --

6       well, I actually should say fortunately, we all love

7       trees and so do I.  But unfortunately a lot of our

8       customers aren't exactly sure where to plant those trees

9       and sometimes those trees are planted right underneath

10       our overhead lines.  And so what we do is we communicate

11       with those customers and we try to get them to relocate

12       the trees.  But we have a program where we will actually

13       replace the tree for them, relocate it to a better

14       location and replace that tree.

15                 COMMISSIONER BROWN:  And what's the cost?

16                 MR. MOORE:  Pardon me?

17                 COMMISSIONER BROWN:  What's the cost

18       associated with that to relocate it?

19                 MR. MOORE:  I'm not -- it depends on the tree.

20       I'm not exactly sure what the cost it.

21                 COMMISSIONER BROWN:  It's okay.  I was just

22       curious.  Thank you.

23                 CHAIRMAN BRISÉ:  Commissioner Edgar.

24                 COMMISSIONER EDGAR:  Thank you, Mr. Chairman.

25                 And thank you for your comments.  Early in

FLORIDA PUBLIC SERVICE COMMISSION

18

1       your presentation you gave us some numbers on the

2       transmission hardening, and I think something around

3       9,500 wood structures having been replaced and 3,000

4       ceramic post insulators.  And you said for this year,

5       2012, probably 1,000 more of the wood structures and

6       300 of the ceramic to be replaced.

7                 So my question is where are you in the process

8       of completing what had been identified for hardening or

9       replacement in that process?

10                 MR. MOORE:  On the transmission side?

11                 COMMISSIONER EDGAR:  Yes.  Recognizing that

12       this is an ongoing effort that was begun approximately

13       six years ago.

14                 MR. CARTWRIGHT:  Yes, ma'am.  Hoss Cartwright

15       with Florida Power & Light.  I'm in the transmission

16       system.

17                 We have replaced over 9,600 poles.  We have

18       about 15,000 more wood poles.  Our goal was to replace

19       all the wood in our transmission system over the next 25

20       to 30 years, and that was presented in 2008.  So we've

21       got a little over 15,000 to go.  And we roughly do

22       between 900 and 1,000 through our inspection cycle that

23       we find that we replace every year.

24                 COMMISSIONER EDGAR:  Thank you.  Very roughly,

25       a third of the way?

FLORIDA PUBLIC SERVICE COMMISSION

19

1                 MR. CARTWRIGHT:  Yes, ma'am.

2                 COMMISSIONER EDGAR:  And the vegetation

3       management requirements that are on an ongoing cycle,

4       three years for feeders, six years for laterals, are you

5       able to keep up with that, your O&M people and

6       contractors?

7                 MR. MOORE:  Yes.  Our feeder cycle program,

8       we're on a three-year cycle.  Our lateral program, at

9       the end of 2013 we'll be there.

10                 COMMISSIONER EDGAR:  And if this is an unfair

11       question, I apologize and you can say so.  I know at the

12       time that that requirement was put in place there was

13       discussion as to what would be the right time frame, the

14       right time periods, and also cost-effectiveness from

15       recognizing that we have not had a major hurricane in

16       the past few years.  But from your people that are out

17       there, you know, in the field every day, do you have a

18       sense as to whether that now with more experience seems

19       to be a good, cost-effective timeline to keep up with

20       vegetative management in obviously a tropical area?

21                 MR. MOORE:  The growth is tremendous.  We find

22       that the three-year cycle on the feeders is probably

23       about right.  And having not quite reached the six-year

24       cycle on laterals, which we'll do at the end of next

25       year, it appears that that might be the right time also

FLORIDA PUBLIC SERVICE COMMISSION

20

1       right now.  Based on certain circumstances, we have to

2       get to some a little sooner than others.  But right now

3       it looks like that time frame might be appropriate.

4                 COMMISSIONER EDGAR:  All right.  Thank you.

5                 CHAIRMAN BRISÉ:  Commissioner Balbis.

6                 COMMISSIONER BALBIS:  Thank you, Mr. Chairman.

7                 I just have two questions for you, and thank

8       you for your presentation.  You mentioned that Florida

9       Power & Light has made, I believe it was 59

10       presentations throughout the service territory on

11       hurricane storm hardening or other efforts.

12                 MR. MOORE:  They were, they were last year 59

13       community outreach presentations, many of them on storm

14       presentations -- on storm preparations, yes.

15                 COMMISSIONER BALBIS:  Okay.  And did the

16       public that attended those presentations, did they

17       present any additional concerns, or what was really the

18       outcome of those interactions with the public?

19                 MR. MOORE:  Usually they're education based,

20       and communities will -- would request someone come out

21       and provide information on a specific topic.  The

22       majority of them happen to be in the area of storm

23       preparedness.  But I'm not sure if there were any

24       concerns at this time that were communicated back on

25       each of those.

FLORIDA PUBLIC SERVICE COMMISSION

21

1                 COMMISSIONER BALBIS:  Okay.  And one final

2       question.  I know some municipalities have amnesty

3       programs for vegetation pickup to kind of encourage

4       preparedness for the hurricane season.  I know the City

5       of West Palm Beach, for example, that had a limitation

6       on the size of the vegetation debris pile in front of

7       the house, that during the amnesty period they would

8       allow, you know, larger sizes.  Does FPL work with

9       municipalities to encourage those types of programs, are

10       they helpful, or are you not aware of that?

11                 MR. MOORE:  I'm not, I'm not aware of that.

12                 COMMISSIONER BALBIS:  Okay.  All right.

13       That's all I had.  Thank you.

14                 CHAIRMAN BRISÉ:  Thank you.  I have two

15       questions for you myself.

16                 You mentioned communications and social media.

17       I think that is fantastic.  Have you all considered

18       texting to provide information to consumers?

19                 MR. MOORE:  That's part of it also.

20                 CHAIRMAN BRISÉ:  Perfect.  This may be an

21       unfair question but I'm going to pose it anyway.  If the

22       circumstances of the 2005 storm season were to arise

23       again, considering all the changes and, and I guess

24       hardening and all those things that FPL has done, would

25       the things that occurred during that storm season in

FLORIDA PUBLIC SERVICE COMMISSION

22

1       terms of length of time that -- because I'm from Miami,

2       so my house was without for about two and a half weeks

3       or three weeks or so.  Would the length of time for the

4       restoration of power and all of that, do you think that

5       that would be reduced dramatically with, if, if it's the

6       same type of circumstance based upon the hardening that

7       has occurred?

8                 MR. MOORE:  I know what you're asking.  Yes.

9       We believe the efforts that we've put in place over the

10       last six years and lessons learned from not just '05 but

11       '04, we believe that the restoration time would be

12       shorter.

13                 CHAIRMAN BRISÉ:  Okay.  Thank you.  And that's

14       one of the things that, you know, concerns me because

15       obviously individuals who live in those areas understand

16       that these are things that need to happen and they

17       support the investment in these programs, but they want

18       to make sure that the investment is, their investment is

19       actually going to generate some benefit.  So I'm

20       thankful that you're fairly confident that --

21                 MR. MOORE:  Yes, we are.

22                 CHAIRMAN BRISÉ:  Thank you very much.  I don't

23       know if there were any other questions or comments at

24       this time.

25                 MR. MOORE:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

23

1                 CHAIRMAN BRISÉ:  Commissioner Edgar.

2                 COMMISSIONER EDGAR:  Thank you, Mr. Chairman.

3                 I would just follow up on that while we're

4       waiting for the next speaker.  As I am the only

5       Commissioner up here who served on the Commission during

6       a portion of that storm season, I started in January of

7       '05 and then was here, of course, in '06 and '07 and

8       beyond when we were working with all stakeholders and

9       interest groups, the providers, of course, and also

10       community leaders and citizen groups to try to amass

11       information as to what we had learned, what had been

12       done, what worked, and what steps we could take, working

13       all together, of course, with other state initiatives.

14       One of the things that we tried very hard to take into

15       account is a cost benefit analysis.  Certainly there can

16       be a long wish list of things that we would always like

17       to do to mitigate and be better prepared, but we wanted

18       to try to the best of our ability to make sure that the

19       ratepayers were getting a good value for the money that

20       would be directed to these efforts.

21                 And, of course, as has been pointed out, we

22       have not thankfully had an individual or series of

23       massive storm events as we did, but I do personally

24       believe it's only a matter of time.  And I am certainly

25       hopeful and believe that good, thoughtful, analysis has

FLORIDA PUBLIC SERVICE COMMISSION

24

1       gone into trying to give that good value so that we are

2       better prepared.

3                 CHAIRMAN BRISÉ:  All right.  Thank you very

4       much, Mr. Moore.

5                 MR. MOORE:  Thank you.

6                 CHAIRMAN BRISÉ:  At this time we're going to

7       move forward with Progress.  Mr. Cutliffe.

8                 MR. CUTLIFFE:  Good afternoon, Mr. Chairman,

9       Commissioners, and staff.  I am Jason Cutliffe.  I'm the

10       Director of Distribution Asset Management for Progress

11       Energy.  And I thank you for the opportunity to report

12       our status of hurricane preparation for the 2012 season.

13                 I'll review some prepared comments and then be

14       happy to take any questions at the end.  What I'm going

15       to share really boils down to the fundamentals.  It's

16       about getting our system ready, getting our organization

17       and people ready, and ensuring that we are thoroughly

18       engaged with our communities and community leaders, and

19       I suspect that'll be a theme of what you hear today.

20                 But let me begin by saying our, our T&D

21       delivery infrastructure performed well in 2004 and 2005

22       and in some more recent severe weather events.  We've

23       improved the system each year, taking additional

24       aggressive hardening measures in conjunction with the

25       Public Service Commission's initiatives, including the

FLORIDA PUBLIC SERVICE COMMISSION

25

1       ongoing ten-point preparedness plan and the wood pole

2       inspection process.

3                 Our hurricane restoration operational plan

4       which also functioned well in 2004 and 2005 has

5       undergone annual review and continuous improvement.  All

6       lessons learned from past major and midlevel storms, our

7       annual drills, and experiences from other utilities

8       across the nation are incorporated into our 2012 written

9       plan and were included in our 2012 storm drill conducted

10       the last week of April.

11                 So in summary, our organization, our T&D

12       delivery infrastructure are prepared for the 2012

13       hurricane season.  And so what I'll do now is discuss in

14       a bit more detail the key elements of our annual

15       hurricane season preparation.

16                 All right.  What I'll go through is

17       distribution and then transmission system readiness,

18       then our organizational readiness, and finally our

19       coordination with local government.

20                 On our distribution delivery system our wood

21       pole plant continues on a firm eight-year inspection

22       cycle.  We're entering year six out of eight years, and

23       our inspections and maintenance are on this eight-year

24       cycle and complies with the Commission's storm

25       preparedness initiatives.  The inspections are targeted

FLORIDA PUBLIC SERVICE COMMISSION

26

1       and prioritized based on hurricane risk.  And in 2011,

2       we inspected over 99,000 wood distribution poles.  And

3       more than 57,000 of those were treated for -- to prevent

4       decay and over 2,800 were replaced.

5                 Other system maintenance activities completed

6       in 2011 include 997 pad mount transformer replacements,

7       over 88,000 circuit feet of hardening rebuild projects,

8       and over 600,000 feet of underground cable replacement.

9                 The distribution system inspection,

10       maintenance, and replacement projects are the

11       cornerstone of our annual work plan and resource

12       planning, and the manpower and material needs are

13       identified in the prior year in order to prioritize,

14       construct efficiently, and complete all this

15       pre-hurricane season work on time.

16                 Progress Energy is on a three-year backbone,

17       five-year lateral vegetation management cycle.  In 2010

18       we completed our first lateral five-year cycle, and in

19       2011 we wrapped up our second full year, full three-year

20       backbone trimming cycle.

21                 Our 2012 plan is on schedule, and it includes

22       May completion of preseason visual patrols of all 3,600

23       backbone miles, and June completion of all follow-up

24       pruning and tree removal identified in those preseason

25       patrols.  Already in the first quarter of 2012 the VM

FLORIDA PUBLIC SERVICE COMMISSION

27

1       operations have removed over 1,100 trees, hot spot

2       trimmed another 9,800, and applied herbicide to more

3       than 600 miles of right-of-way floor.

4                 Also, Progress Energy remains fully committed

5       to the Public Service Commission's ten-point ongoing

6       preparedness plan, including the following.  A full

7       inventory of joint use attachments was completed in 2011

8       and now details each attaching company at every pole on

9       the system.  Also in 2011 we completed a rollout of a

10       Logica ARM Suite Work Management System along with a

11       Facilities Management Data System.  And these two, two

12       software packages are now fully integrated with an

13       upgraded GIS system that was rolled out in 2008.

14                 Also in 2011 a post-storm forensics process

15       was expanded to include the capability of responding not

16       just to major but to midlevel storms as well.  And as

17       mentioned earlier, annual review and update of our

18       written hurricane restoration plan was completed in

19       preparation for the 2012 season.

20                 And finally, as described in our 2010

21       three-year hardening plan filing, we continue to

22       implement a comprehensive process to identify,

23       prioritize, and assess storm hardening options within

24       our service territory.

25                 Transmission system readiness is built upon

FLORIDA PUBLIC SERVICE COMMISSION

28

1       comprehensive structure inspections and system

2       maintenance.  In 2011 inspections were completed on

3       184 transmission circuits and over 11,000 wood

4       structures, and more than 1,500 wood structures were

5       replaced with steel or concrete in accordance with NESC

6       extreme wind design.

7                 Since 2006 when this effort began, we've

8       replaced over 10,000 wood transmission structures with

9       steel or concrete, continuing this systematic hardening

10       via maintenance upgrades, DOT relocations, and other

11       line rebuilds.  Aerial patrols of the entire

12       transmission system took place in quarters two and

13       four of 2011 and are underway in 2012.  Inspections are

14       also complete inside all 481 substations, as is all

15       identified critical follow-up maintenance.

16                 The transmission vegetation management

17       projects in 2011 cleared over 1,100 miles of

18       right-of-way, and this work included 267 miles of

19       herbicide application, over 61,000 tree removals, and

20       removal of over 2,300 danger trees from outside the

21       right-of-way.

22                 2012 projects are on schedule to clear an

23       additional 274 miles of right-of-way in addition to the

24       tree work that we identified by the aerial patrols and

25       ground inspections.

FLORIDA PUBLIC SERVICE COMMISSION

29

1                 And, again, the PSC ten-point preparedness

2       plan and storm hardening rule have been implemented,

3       including enhanced GIS capability for transmission

4       facilities, post-storm forensic data collection,

5       structure inspection cycles, and, most notably,

6       hardening by way of wood pole replacement with concrete

7       or steel.

8                 Our organizational readiness can be

9       characterized as tested through our annual drill, again

10       conducted last month.  The annual storm plan review and

11       update process is complete for 2012.  A recent addition

12       to our plan is proactive communication to critical care

13       customers.  What this amounts to is that prior to

14       hurricane landfall customers identified with these

15       critical care needs receive a phone call from Progress

16       Energy, and the agent delivers a preparation message

17       including location of area shelters equipped to provide

18       critical care assistance and a reminder to check in

19       advance the working condition of their own equipment and

20       any backup life support.

21                 As I mentioned earlier, our 2012 hurricane

22       drill was completed in April, and each of our individual

23       storm organizations and leadership teams were tested on

24       their preparation efforts and ability to react to

25       changing storm conditions.  This drill and accompanying

FLORIDA PUBLIC SERVICE COMMISSION

30

1       tabletop exercises and training efforts clearly

2       demonstrated our readiness for the 2012 season.

3                 And we've also taken steps this year to ensure

4       access to critical material and fuel from multiple

5       sources.  Inventory levels of critical material has been

6       increased over normal stocking levels, and our supply

7       chain organization has again assembled 16 storm kits.

8       Each of these kits which are staged throughout our

9       territory contain enough emergency material and supplies

10       to outfit up to 400 linemen for three days.  Our

11       transmission organization also has increased its

12       inventory level of poles, insulators, and other basic

13       restoration equipment, and maintains storm kits that

14       will outfit transmission crews for three to five days.

15       And, again, we've negotiated retainer contracts with our

16       fuel vendors to ensure that fuel needs are met.  These

17       arrangements also improve our access to fuel when

18       sending Progress Energy repair crews off system in

19       support of our mutual assistance partners in Florida and

20       elsewhere.

21                 So even though we have supplier agreements in

22       place, these additional measures address risks and

23       ensure that restoration can begin as soon as the weather

24       clears and we can safely begin restoration.

25                 And lastly, external line and tree trimming

FLORIDA PUBLIC SERVICE COMMISSION

31

1       personnel are vital elements of a successful operation.

2       And we've taken steps to ensure access through

3       arrangements with contractors and relationships with

4       other utilities through regional mutual assistance

5       organizations like the EEI and the Southeastern Electric

6       Exchange.

7                 I'll comment now about our coordination with

8       local government.  Our communication and coordination

9       with local leaders has been strengthened in 2012.  We've

10       maintained a cross-functional team focused on

11       governmental engagement to ensure two-way communication

12       with local leaders.  We include EOC leaders in our

13       drills, as we did this year, and our representatives

14       participate in the EOC-run drills, including their

15       annual prioritization of critical infrastructure.

16                 By placing a Progress representative inside

17       the major county EOCs, we're able to incorporate local

18       governments' priorities in our tactical restoration

19       plan.  And Progress Energy is also equipped this year to

20       provide local governments with resource and restoration

21       information before, during, and after storm events to

22       assist them with their own local planning.  Our program

23       is now operational year-round, and we're able to provide

24       detailed outage information down to the square mile grid

25       provided on secure files to each of the EOCs.  But it's

FLORIDA PUBLIC SERVICE COMMISSION

32

1       a format that allows them to incorporate this

2       information into those that have their own emergency

3       management software.  Additionally, we're able to

4       provide these maps beginning this year for midlevel

5       storms as well.  And this information is supplemented by

6       outage maps with data that's sequenced throughout the

7       day with all of our other messaging on our external

8       website for all customers and stakeholders to see.

9                 And we continue the "Know Where You Grow"

10       program which informs the public and community

11       organizations of the most compatible tree species and

12       where to plant them in the vicinity of power lines.

13                 And, finally, we enthusiastically participate

14       in public education and community leader forums:  For

15       example, the recent Tampa Bay forum's Coastal City

16       Summit held just last week.

17                 So in conclusion, even with the best

18       preparation, Mother Nature presents risks and areas of

19       vulnerability, and they fall into two general areas.

20       The first is restoration resource limitation and the

21       second is storms that produce catastrophic damage.

22                 So with regard to the first, with restoration

23       resource limitations, anything that dilutes resources is

24       a risk.  Primarily you've heard these items before,

25       multiple storms and/or severe storms that enter the

FLORIDA PUBLIC SERVICE COMMISSION

33

1       region.  And to mitigate this we maintain robust

2       relationships with both line contractors, tree trimming

3       contractors, as well as the mutual assistance groups

4       mentioned earlier.

5                 The second area of vulnerability are

6       catastrophic weather events, intense hurricanes,

7       Categories 3, 4, and 5 or those with significant storm

8       surge have the potential for unprecedented damage.  So

9       one way we mitigate this risk is by maintaining very

10       strong relationships with community, community leaders

11       and county emergency operation centers.  And this

12       two-way communication of damage and restoration

13       priorities allows us to align as quickly as possible

14       with the priorities of local community leaders.

15                 So in conclusion, Progress Energy's

16       organization and our T&D delivery system are prepared

17       for the 2012 hurricane season.  The system that

18       performed well in previous major weather events has been

19       inspected, maintained, hardened, and improved, and our

20       internal organization has been drilled and relationships

21       strengthened with community and emergency response

22       leaders.

23                 As a seven-time Edison Electric Institute

24       Restoration Award winner, Progress Energy has a track

25       record of high performance in this area.  Our most

FLORIDA PUBLIC SERVICE COMMISSION

34

1       recent award came in 2009 for off system support to

2       Entergy Texas and CenterPoint Energy following Hurricane

3       Ike.  That was the largest off system deployment in our

4       company's history.  And these off system efforts along

5       with those of the other utilities that are represented

6       here today strengthen an already strong standing in the

7       mutual assistance community, and that's a standing that

8       will pay dividends not if but when Florida is next

9       impacted and we're calling for support from outside of

10       our state to mitigate our risks here.

11                 So, Commissioners, this concludes my prepared

12       remarks.  Thank you for your attention.  I'd be happy to

13       take any questions at this time.

14                 CHAIRMAN BRISÉ:  Thank you very much.

15                 Commissioners?  Commissioner Brown.

16                 COMMISSIONER BROWN:  Thank you.  Again, thank

17       you for your presentation.  And same question I asked

18       Florida Power & Light about anything differently that

19       you incorporated in this past year's hurricane drill

20       that you didn't do or lessons learned from the previous

21       year?

22                 MR. CUTLIFFE:  Well, one thing we added to the

23       drill, this is kind of getting into the details, but we

24       have two systems we assess damage on our system by.  One

25       is an outage management system that we use just about

FLORIDA PUBLIC SERVICE COMMISSION

35

1       every day of the year.  We have other tools for major

2       weather events that we have to drill and train on

3       because they're built for a different purpose.  So what

4       we did deliberately in our drill this year is produce

5       data that conflicted in those two systems, and we taught

6       our people to fly by instruments and not by sight.  And

7       in doing so, we identified a few gaps that we're

8       following up on.

9                 One is when you approve some documentation to

10       our frontline field leaders to give them guidance.

11       Every year turnover is a challenge, new people in roles,

12       often the same people in different roles, and it's basic

13       fundamentals.  We've got to continue to train every

14       year, not get complacent there.

15                 Another thing we identified in our drill is

16       the need for a backup system command center.  And so we

17       conducted our drill out of a new facility this year, and

18       we learned some lessons about landlines and network

19       capacity that will allow us to use that location in a

20       real event.

21                 COMMISSIONER BROWN:  Great.  Thank you.  And

22       also how would you measure your "Know Where You Grow"

23       program in terms of public awareness and success?

24                 MR. CUTLIFFE:  The -- you know, it's a great

25       way to reach out to people through Home Depot and Lowe's

FLORIDA PUBLIC SERVICE COMMISSION

36

1       and put literature in their hands.  That's an effective

2       message to keep out there.  But where it really makes a

3       difference is in working with local communities who are

4       doing streetscapes, and often times work with

5       contractors who are doing their plantings, and we're

6       able to maintain those relationships.

7                 The cheapest tree to deal with is the one that

8       gets planted 20 feet from the line in the first place.

9       And so that's, that's an investment we make every year.

10       And it, it produces benefits because we don't have to

11       come back and deal with a mature tree five, six years

12       later that is now a removal situation.

13                 COMMISSIONER BROWN:  Agreed.  Thank you very

14       much.

15                 CHAIRMAN BRISÉ:  Commissioner Edgar.

16                 COMMISSIONER EDGAR:  Thank you.  And I also

17       would pose the same two questions I did to Mr. Moore.

18       The first being with the process that you're going

19       through for replacement and/or hardening, particularly

20       of transmission related infrastructure, and recognizing

21       that that's a multiyear process, where are you in the

22       planning process and implementation towards the ultimate

23       goal for that aspect?

24                 MR. CUTLIFFE:  As I mentioned, since 2006

25       we've addressed about 10,000 structures, but a vast

FLORIDA PUBLIC SERVICE COMMISSION

37

1       majority of our transmission network is built with wood.

2       So it's a long-term systematic approach.  We are in the

3       20-to-30 year range also.  But what we are able to do is

4       take advantage of every opportunity where there is any

5       kind of construction going on, as well as target those

6       replacements that do take place to the most critical

7       circuits in the most hurricane prone areas.

8                 COMMISSIONER EDGAR:  And my understanding is

9       that with that replacement schedule that there has been

10       a prioritization that has taken place.

11                 MR. CUTLIFFE:  Yes.

12                 COMMISSIONER EDGAR:  Thank you.

13                 And then the second question was related to

14       the vegetation management program and the time period as

15       you've cycled through three years and five years,

16       recognizing that for some of your areas are more rural

17       than some of the service areas that FPL or some of the

18       other smaller providers have.

19                 From the operations and being out there on the

20       ground, did the three-year/five-year cycle seem to be

21       both effective and cost-effective?  And I ask that

22       question, recognizing that when these initiatives were

23       put in place, we fully expected that we would learn as

24       we go and maybe data would show that adjustments should

25       be made.

FLORIDA PUBLIC SERVICE COMMISSION

38

1                 MR. CUTLIFFE:  I would, I would answer this

2       way.  We've, as I mentioned, we've completed a five-year

3       lateral cycle.  So we have that, that data in our

4       records.  We just last year finished our second

5       three-year backbone cycle.  At about the same time we,

6       we invested in some software to model the vegetation

7       conditions on our rights-of-way on our system.  We now

8       pre-inspect every span that gets trimmed before our

9       contractors get there.  So when we go back to those

10       circuits in later years, we know what type of

11       trimming -- we can forecast costs and resource needs

12       much more effectively, but it also gives us a more

13       accurate profile of the vegetation conditions on our

14       right-of-way.

15                 So in more direct answer to your question,

16       we're at a point where our data is going to allow us to

17       do a much better job of assessing that question,

18       striking a balance, and that area is under active review

19       right now.

20                 COMMISSIONER EDGAR:  Great.  Thank you.

21                 CHAIRMAN BRISÉ:  Any further questions?

22                 Okay.  I'll, to be consistent, I'll ask two

23       similar questions to the ones I posed to FPL.

24                 Are you in a better position this year than

25       you were last year?  And in a better position for

FLORIDA PUBLIC SERVICE COMMISSION

39

1       response than the last time you had to deal with a major

2       storm?

3                 MR. CUTLIFFE:  For, for us, 2004 was our major

4       hurricane year, and our system performed very well in

5       2004, as did our organization.  But I can tell you

6       without reservation our performance will be better the

7       next time it happens.  You will know sooner when your

8       lights are going to come back on.  Your lights will come

9       back on sooner, and we will do a better job of aligning

10       our tactical plan with the needs of local communities.

11                 CHAIRMAN BRISÉ:  Thank you.  And the second

12       question, I heard throughout your presentation your

13       interaction and plan to communicate with local leaders

14       and government and so forth.  What is your plan to

15       communicate with actual consumers?

16                 MR. CUTLIFFE:  We, we provide information on

17       our website is the most effective way to reach out.  So

18       our direct contact is through, through the external

19       website.

20                 When we work with our emergency operation

21       center contacts, we also ask that they include our

22       messaging in their outreach communities as well because

23       we do clear a lot of our priorities through their

24       operation.  And so if there's a, if there are critical

25       lift stations that a neighborhood may have or if there

FLORIDA PUBLIC SERVICE COMMISSION

40

1       are care facilities or other locations that the

2       community deems -- schools, for example, could become a

3       high priority -- we work with the EOCs to set those.

4       And so we work through them to get the messaging out to

5       customers as well.

6                 In -- I'll add this, in actual restoration

7       situations we've also added, we've added social media to

8       our, our outage maps on our external website.  Twitter

9       is one of the means now.  So when my lights go out, I'll

10       ask my teen-ager when they're coming back on again.  But

11       we're constantly evaluating those methods and looking

12       for faster ways to reach customers.

13                 CHAIRMAN BRISÉ:  All right.  Thank you very

14       much.  Seeing no other lights, I thank you for your

15       presentation this afternoon.

16                 Tampa Electric Company, Mr. David Sweat.  I

17       just wanted to make sure.

18                 MR. SWEAT:  Good afternoon, Mr. Chairman and

19       Commissioners.  It's my pleasure to be here today.  My

20       name is David Sweat, and I am the Director of Energy

21       Deliveries, Energy Engineering and Operation Services

22       team.  And it's -- I appreciate this opportunity to

23       share with you what we have in store for our plan for

24       the hurricane season upcoming in 2012.

25                 We broke this up into three different areas:

FLORIDA PUBLIC SERVICE COMMISSION

41

1       The system infrastructure, our pre-storm prep and

2       coordination, as well as our areas of concern as well.

3                 Starting with the system infrastructure,

4       you're familiar with our wood pole inspections as well

5       as the ten-point plan initiatives.  We'll be looking at

6       the three-year storm hardening plan that we've put

7       forth.

8                 With the wood pole inspections, as with

9       everyone else, we're on a eight-year cycle for this, and

10       at this point we're doing quite well.  We have roughly

11       52,000 poles that we are anticipating getting done this

12       year, as well as last year.

13                 And our distribution poles, just for the

14       record, is Class B, so that's a little bit more than

15       what is the norm and what is required.

16                 The ground line inspection program is the

17       visual inspection that we do, as well as the sound and

18       bore and excavation as needed.  We'll also do pole

19       loading analysis and repair and reinforce or replace, if

20       it's required.

21                 The ten-point plan initiatives.  We talked

22       about the vegetation management.  We're on a three-year

23       trim cycle presently.

24                 The joint use attachers and audit.  We've

25       improved our processes for attaching entities to attach

FLORIDA PUBLIC SERVICE COMMISSION

42

1       their poles to Tampa Electric poles through the use of

2       (inaudible) and the Engine's Online Program.

3                 Comprehensive loading analysis is performed on

4       these poles as needed, and, if need be, they'll be

5       replaced.  In 2012 we'll continue to use the

6       comprehensive loading analysis where it's necessary and

7       evaluate when to initiate the next systemwide pole

8       attachment audit.

9                 Transmission inspections on the one-, six- and

10       eight-year cycles.  The ground patrol, aerial infrared

11       patrol, and substation inspections are done annually.

12       Our aboveground inspections are on a six-year cycle and

13       our ground line inspections on an eight-year cycle.

14                 Transmission hardening.  We take a systematic

15       approach to replacing our wood transmission structures

16       with non-wood structures.  In 2011 we hardened over

17       900 structures and plan to do the same for 2012.

18                 Our transmission circuits are designed for

19       extreme wind.  That's the 69kV and 138kV, and our 230kV

20       is, is strengthened to a stronger wind standard than

21       that, up to 133 miles an hour design.

22                 Our post-storm data collection, we continue

23       our relationship with an outside consultant for forensic

24       analysis to determine any root cause of the storm damage

25       after a major storm.  As far as the data collection at

FLORIDA PUBLIC SERVICE COMMISSION

43

1       this point, we're very fortunate that we did not have

2       any impacts on hurricanes in 2011, as has been mentioned

3       before.  We do know that the measures are in place that

4       will allow for post-storm data collection and any data

5       that is needed should we have a major storm come

6       through.

7                 Our coordination with local governments, I've

8       heard it said -- a lot of people around here have had a

9       lot of examples here and we'll probably be the same.  We

10       had a storm workshop with the Hillsborough County storm

11       preparedness exercises with the Hillsborough County

12       Commissioners this year.  The EOC, we are very heavily

13       involved in that as well, the City of Tampa as well as

14       Hillsborough County.

15                 We also participated in the search and rescue

16       tabletop exercise with the Hillsborough County Fire

17       Department, and we hosted a fire safety demonstration in

18       September of last year for our emergency responders.

19       That was just to name a few.

20                 Our disaster preparedness and recovery plan,

21       it's reviewed annually and we have, are ready for

22       implementation as the need arises.  And once again, all

23       of our people are very much aware of their roles and

24       assignments in this disaster preparedness and they are

25       ready at this point.

FLORIDA PUBLIC SERVICE COMMISSION

44

1                 For our three-year storm hardening, I

2       mentioned before we're at a Grade B construction for our

3       distribution, so we continue to do that.  We build for

4       extreme wind for the transmission for the 69 to 138, and

5       extreme wind plus for the 230 system.  We replace all of

6       our transmission with non-wood construction.

7                 And moving into the conversion of the overhead

8       distribution interstate crossings to underground, this

9       was something that had been identified before.  I

10       believe you've probably seen that in the past.  All 12

11       crossings that have been identified have been completed,

12       and any further crossings that are found will be

13       converted at that time as they're made known to us.

14                 Testing our network protectors.  We pressure

15       tested 18 of our network protectors in ten of our

16       low-lying areas of manholes and vaults.  We replaced the

17       gaskets as needed, and any of the other protectors were

18       replaced as was required.

19                 Underground construction of the stainless

20       steel.  We have made it -- the stainless steel

21       transformers as our new standard for underground, which

22       aligns very well with our established practice of

23       stainless steel switchgear.

24                 Extreme wind pilot project, St. Joe's Hospital

25       as well as the Port of Tampa.  Although Tampa Electric's

FLORIDA PUBLIC SERVICE COMMISSION

45

1       standard is to build to the NESC Grade B, as part of the

2       hardening initiative we chose two projects because of

3       their importance to the region as well as Florida as a

4       whole.  St. Joe's Hospital is a major trauma center and

5       the Port of Tampa delivers roughly 40% of Florida's

6       petroleum supply.  Both of these were built to extreme

7       wind requirements.

8                 For the pre-storm prep and coordination, mock

9       storm exercise -- I've heard a lot of comments on the

10       mock storm.  And last year, in 2011, we had our mock

11       storm exercise, and it was a Category 2 hurricane.  From

12       that we had anticipated tidal surge of between six to

13       ten feet coming into the Hillsborough County area in the

14       bay.  This gave us a lot of opportunities to look at our

15       system and how well we would respond to that.  We had

16       numerous action items from that and they've now been

17       addressed.  Our second -- for the one for 2012 our mock

18       storm is going to be on the 22nd of this month.

19                 Some of the lessons learned, I know -- I'll

20       probably just jump ahead to some of the questions, if I

21       could.  A couple of the things that we've noted.  We've

22       done mock storms for, for quite a few years, and we know

23       our system and we're fine-tuning it.  I think that's

24       what -- it's a struggle sometime because you want the

25       big ticket items but you don't necessarily get the big

FLORIDA PUBLIC SERVICE COMMISSION

46

1       tickets, but you fine-tune your process and that's what

2       we've done.  And we've found some things that, at least

3       a couple of things that I think are worth mentioning.

4                 Continuity of work.  We streamlined the

5       process between the handoffs between the various crews.

6       Something as small as that, very helpful so that you

7       don't have a delay in restoration for the public.  Also,

8       when we're talking about load shedding, there was

9       clarification between and coordination between some of

10       our T&D system as well as our generation, those two,

11       some handoffs there that we found were very beneficial

12       to us as well.

13                 Okay.  The incident base review.  TECO has

14       worked with our local business owners and officials to

15       verify existing incident bases were still available.

16       The company renewed existing agreements for primary

17       sites and secured backup locations as additional

18       contingencies.

19                 Team member prep.  In order to maximize our

20       team members' availability, it was very important that

21       they had an understanding of what their emergency role

22       would be.  All have been trained and they're very much

23       aware of what their assignments are.

24                 Personal preparation also is important.  They

25       can't help out the company if they have not taken care

FLORIDA PUBLIC SERVICE COMMISSION

47

1       of their own personal business, so we also want to make

2       sure that they have prepared for the storm season on

3       their own.  And we have some documentations, get ready

4       documents for them as well.

5                 Material inventory review.  Prior to the

6       hurricane season, material inventory is reviewed and

7       ensured to provide at least a four-day supply of

8       materials.  The procurement contracts are in place to

9       provide additional supplies within four days of

10       landfall.  And as has been mentioned before, restoration

11       providers such as the Southeastern Electric Exchange and

12       contractors are very crucial to our restoration efforts.

13                 Local government coordination.  We've

14       participated in several Hillsborough County led

15       initiatives focusing on joint efforts to rebuild and

16       revive the area after a storm.  We also participated in

17       joint mock exercises with Hillsborough County Emergency

18       Management personnel prior to hurricane season.  We've

19       met with various government agencies to enhance our

20       communication and coordination of the emergency

21       management.

22                 And public communication.  We provided public

23       service information at the beginning of every storm

24       season through the local news media and anything else

25       that is required in order to effectively communicate

FLORIDA PUBLIC SERVICE COMMISSION

48

1       with the public.

2                 And our areas of concern as well.  Should we

3       have the multiple storms within one season, how does

4       that impact our resource availability?  And a

5       catastrophic storm has been mentioned.  All of those

6       would have an impact on us this year if that were to

7       happen.  We hope that doesn't occur.  But any one of

8       those would limit our ability to restore power.

9       Fortunately for us too, we have such strong bonds with

10       other utilities like the SEE and the contractors would

11       be here to help us out.  We faired very well in the 2004

12       storm and I think that we would do very well in the

13       future going forward.

14                 So in summary, our system, we believe our

15       transmission and distribution systems are stronger than

16       they have been in the past.  We've hardened our sources

17       to critical facilities.  Our people have been trained

18       and are ready.  Our storm plan has been reviewed.  Our

19       external relationships and contracts, we've coordinated

20       efforts with all of our external relationships, reviewed

21       and updated our contracts, and are prepared for the 2012

22       storm season.

23                 Thank you.

24                 CHAIRMAN BRISÉ:  Thank you very much.

25                 Commissioners, are there any questions?

FLORIDA PUBLIC SERVICE COMMISSION

49

1       Commissioner Brown.

2                 COMMISSIONER BROWN:  Thank you.  And thank you

3       for your presentation and for coming to Tallahassee.

4                 Have you thought about including Tampa General

5       Hospital in your extreme wind pilot hardening project

6       because of its unique location on Davis Island and the

7       fact that it is a major statewide trauma center?

8                 MR. SWEAT:  Yes.  That has its own set of

9       issues associated with it because of its proximity to

10       the water.  There are some concerns there.  But we

11       believe we've worked with the hospital in making sure

12       that they are as hardened a system as they can be.

13                 COMMISSIONER BROWN:  It is difficult.

14                 MR. SWEAT:  Yes, it is.

15                 COMMISSIONER BROWN:  Thank you.

16                 CHAIRMAN BRISÉ:  Commissioner Edgar.

17                 COMMISSIONER EDGAR:  Thank you.  And I'll also

18       follow along with some of the same questions that I

19       asked the previous speakers.

20                 First, I appreciate your comments about, you

21       know, the first few years of taking a more comprehensive

22       look at these type of issues, that some of the, the big

23       ticket items are easier to see.  And then from that

24       point on I know you said fine-tune, I think kind of a

25       refinement of, and so I appreciate your comments and

FLORIDA PUBLIC SERVICE COMMISSION

50

1       recognize that dynamic.

2                 Recognizing that your service territory is

3       geographically smaller than that of the prior two

4       presenters, where are you in that long-term, multiyear

5       process of hardening and/or replacing primarily

6       transmission related infrastructure?

7                 MR. SWEAT:  As has been mentioned by the

8       others, any opportunity we have to change out poles on a

9       go-forward basis, we're doing that and hardening our

10       system with non-wood transmission structures.  Presently

11       we're hardening about 900 structures each year, so we're

12       probably at about a 30% at present.

13                 COMMISSIONER EDGAR:  Thank you.  And I had

14       also asked prior about the vegetation management time

15       schedule.  And with, with your area and particularly

16       with some of the concentration that you have with your

17       service territory, from the information that you have

18       now does the time period that is required seem to be

19       effective?

20                 MR. SWEAT:  We are presently on a three-year

21       cycle but we have petitioned for a four-year, and we'll

22       be talking about that, I'm sure, at length.

23                 COMMISSIONER EDGAR:  Okay.  Thank you.

24                 CHAIRMAN BRISÉ:  Thank you.  You answered one

25       of the questions which I posed to the others.  The

FLORIDA PUBLIC SERVICE COMMISSION

51

1       other, only other question I would pose for you is your

2       post-storm communication plan to actual consumers.

3                 MR. SWEAT:  Right.  And at present we also use

4       the local media.  We use our -- we have Twitter and I'm

5       sure that our corporate communications folks will be

6       actively using that as, as necessary.  Our web-based

7       communication is very critical to us as well.  So I

8       think all of those things, along with the media at

9       large, I think will be very helpful for us to

10       disseminate that information.

11                 CHAIRMAN BRISÉ:  Thank you very much.  If

12       there are no other questions from Commissioners, Mr.

13       Sweat, you --

14                 MR. SWEAT:  I did have one other comment.

15                 CHAIRMAN BRISÉ:  Sure.  Go right ahead.

16                 MR. SWEAT:  I failed to mentioned for our mock

17       storm, you might find this helpful, our mock storm is

18       going to be for, during the time of the RNC.  So it's

19       going to be a Category 3 storm coming into the bay and

20       how do we handle that with the RNC in town?  So that

21       ought to be interesting.  Just food for thought.

22                 CHAIRMAN BRISÉ:  Well, thank you, Mr. Sweat,

23       and good luck with that.

24                 MR. SWEAT:  Thank you.

25                 CHAIRMAN BRISÉ:  All right.  Moving forward to

FLORIDA PUBLIC SERVICE COMMISSION

52

1       Gulf Power.  Ms. Pinkerton.

2                 MS. PINKERTON:  Thank you.  And my name is

3       Sharon Pinkerton.  I'm the Project Services Manager at

4       Gulf Power Company, and I'll be presenting our 2012

5       preparedness briefing today.

6                 The distribution and transmission activities

7       I'm going to cover today are part of our culture of

8       preparedness.  It's a year-round process where our storm

9       readiness never stops, and it's refined every time we

10       have an on system event or whether or not we participate

11       in off system events.  Our latest experience obviously

12       on system has predominantly been with the 2004/2005

13       storms of Ivan and Dennis.

14                 Concerning our distribution activities related

15       to vegetation management, each year one-third of our

16       mainlines will be systematically pruned, while the

17       remaining two-thirds will be inspected and trimmed to

18       correct any deficiencies that could possibly pose a

19       hazard over the next 12 months.  In addition, our

20       vegetation management looks at any overhang issues, and

21       we still proactively try to remove what we consider

22       hazardous trees which are not within the right-of-way

23       but are off right-of-way on private property, and a lot

24       of that oftentimes involves getting customer permission.

25                 Each year the laterals are evaluated based on

FLORIDA PUBLIC SERVICE COMMISSION

53

1       the reliability performance, the date of the last trim,

2       and overall field conditions.  But, regardless, they are

3       systematically pruned on a four-year cycle.  So this

4       year by June 1st we will trim 240 miles of the mainline.

5       We're going to inspect and trim as needed the other

6       two-thirds, which equates to 477 miles.  And our lateral

7       trim will involve 323 miles of the roughly 1,300 miles

8       total.  We also have a distribution lockout report which

9       we look at when a breaker operates.  We determine the

10       root cause.  And at that time if we determine that the

11       root cause was a tree, we will immediately go and

12       correct that situation.

13                 Tree Gulf additionally is an e-mail address

14       internal to Gulf where our employees can e-mail a

15       location that they find on their own.  Particularly in

16       the spring this is an active address with a lot of the

17       vines.  So that's one of the ways we also use our

18       employees to help us out with any vegetation problems.

19                 Concerning our pole inspections related to our

20       distribution, we've completed in 2011 the fifth year of

21       our eight-year cycle.  We've identified a little over

22       700 poles for replacement.  Those will be completed by

23       June 1st of this year.  Additionally, late in 2011 we

24       went ahead and did the six-year inspection.  An

25       additional 638 poles were identified for replacement

FLORIDA PUBLIC SERVICE COMMISSION

54

1       there.

2                 We also look at critical pieces of equipment

3       for hot spots such as connectors, insulators

4       overheating, and lightning arrestors, and these are

5       usually on our reclosers, our regulators, our capacitor

6       banks.  And all those inspections were completed on

7       March 15th, and as of today we're 99% through with the

8       corrective measures.

9                 Specifically our storm hardening measures, we

10       just covered vegetation management and the pole

11       inspections.  Our extreme wind loading projects are

12       focusing, like others have said, on critical

13       multi-feeder poles and facilities on major

14       thoroughfares.  We're trying to beef up what I would

15       call commercial hubs that would be beneficial to have

16       strengthened in the event of a storm for the customers

17       to be able to get groceries, fuel, building supplies.

18                 We continue to use Grade B construction as our

19       normal design whether it's for new installations or

20       maintenance, such as Osmose poles are now replaced to

21       Grade B standard construction standards.

22                 In the event we do have an event on our

23       system, we're prepared to collect forensic data.  We've

24       pre-identified the areas throughout our service area

25       that we're going to look at.  They're both overhead and

FLORIDA PUBLIC SERVICE COMMISSION

55

1       underground areas we'll look at, both coastal and

2       inland.  And then we can send that data to KEMA, our

3       consulting group, to analyze it and be prepared to

4       address any concerns.  Osmose does do a refresher every

5       year.  They come down and make sure the computers are

6       working, the handheld devices they take into the field

7       are working, and our maps are current that we give them.

8                 Like you've already heard today, we have our

9       communications with the local EOCs as well.  We will

10       participate in their storm drills pretty much throughout

11       the month of May.  A lot of the ones that are to be

12       determined I think coincide with the state drill.

13       Thirteen Gulf Power employees are assigned to the county

14       EOCs, and those personnel have certifications through

15       FEMA's Emergency Management Institute, ICS, and the NIMS

16       certification.

17                 Twice a year we have two sets of meetings in

18       the first quarter and in the third quarter where we meet

19       with our third party attachers.  The first one was held

20       February 29th in Panama City and March 2nd in Pensacola

21       where we talk about the operational issues, any kind of

22       notification of what major projects we may have where

23       they may have to set poles or transfer or modify their

24       facilities.  So we try to keep that line of

25       communication open, and we do that twice a year.  The

FLORIDA PUBLIC SERVICE COMMISSION

56

1       next one is scheduled probably for about September.

2                 Our forestry services personnel are in

3       constant communication with members of the communities

4       and government officials concerning where we're going to

5       be trimming, notifying folks that we're going to be in

6       the area.  So they play a vital role in, as you've

7       heard, making sure we're keeping our customers informed

8       of where we're going to be trimming.

9                 One other thing concerning the third party

10       attacher, we do have a designated employee assigned in

11       the event of a storm situation that will help with the

12       flow of communication to our third party attachers.

13       They have his direct phone number and can call and see

14       where we are working and where facilities have been

15       restored.

16                 Moving on a little bit to the transmission

17       activities, we too are in compliance with all the NERC

18       standards.  By June 1st of this year we will have made

19       any inspections and corrections of the vegetation and

20       hazards associated with our 230kV lines.  Additionally,

21       we'll be through with year-end on both the 115kV lines

22       and the 46kV lines, and you can see that those are

23       roughly 1,000 miles with the 115 lines, a little over

24       100 for the 46kV lines.

25                 We have pole inspection programs for our

FLORIDA PUBLIC SERVICE COMMISSION

57

1       transmission poles regardless of whether they're wood,

2       concrete, or metal.  There's different inspection

3       programs that run simultaneously such that each pole is

4       visited at least every six years.  And we have the

5       groundline programs, comprehensive walking programs, and

6       we also do four aerial patrols, usually one every

7       quarter by a fixed wing aircraft.

8                 Specifically related to our storm hardening

9       measures for transmission, we are installing guys on our

10       H-frame structures.  We are in year five of the

11       five-year program.  And this year it would be completed

12       when we install 650 guy installations.

13                 Arm replacements, we will replace 200 wood

14       arms with steel arms this year, and we are in year five

15       of a ten-year program on that item.

16                 For both distribution and transmission our

17       post-storm recovery plans are built on lessons learned.

18       Like I said before, whether we're on system or off

19       system, we bring back best practices and incorporate

20       them into our storm procedures.  These plans can apply

21       to any natural disaster, whether it's a hurricane or a

22       tornado.

23                 Like others, we rely on the Southeastern

24       Electric Exchange for resources, also our Southern

25       Company affiliates, as well as contractors.  And we have

FLORIDA PUBLIC SERVICE COMMISSION

58

1       contracts, arrangements in place for logistics, whether

2       it's fuel or food or, or logistics, sleeping

3       arrangements.  And we also beef up our inventory levels

4       like everyone else.  And then during the six-month

5       hurricane season also fuel is topped out at 75% at all

6       times.

7                 Our annual drill was conducted last Tuesday,

8       and we called it a storm exercise this time rather than

9       a hurricane exercise because we didn't have a hurricane.

10       We had a tornado similar to the one that our sister

11       company, Alabama Power, experienced last April.  And

12       what we did is we tested -- let me back up.  Hurricanes

13       afford you the opportunity to know that it's coming.  A

14       tornado, you might know there's bad weather coming but

15       you don't have the luxury of having three to four days

16       to have all of your conference calls and get everyone

17       prepared.  So we took our hurricane plan and applied it

18       to a tornado restoration effort.

19                 We are going to be updating some of our plans

20       and processes.  We're training our folks still.  One

21       important part of the drill we did this year was to

22       remind our employees that they need to prepare their

23       home and families as well because they are required to

24       report for storm duty.  And we stressed that, that they

25       cannot -- it's imperative that they know their family

FLORIDA PUBLIC SERVICE COMMISSION

59

1       and their home is safe and secure.  We do try to

2       consider the worst-case scenarios, and we thought that

3       would be the example this year by having a tornado

4       instead of a hurricane.

5                 We also have our new employee orientation

6       about once a quarter.  Any of our new folks that have

7       come onboard are made aware of their storm expectations,

8       and we still provide any training, whether it's new or

9       ongoing.

10                 Like you've already heard today, we have the

11       same concerns, multiple events not necessarily on our

12       system or not necessarily even within Florida, but

13       whether it's in the Carolinas and then us and then

14       perhaps Texas, stretching the available resources very

15       thin is a concern.  And competition for qualified

16       electrical workers is always out there.

17                 Gulf Power though is fully prepared through

18       our T&D storm hardening initiatives, through our

19       communications within the communities, with our

20       government officials, and with our third party

21       attachers, and with our customers, and on our

22       experiences based on system and off system.

23                 That's the end of my prepared comments, and I

24       thank you for the opportunity.

25                 CHAIRMAN BRISÉ:  Thank you, Ms. Pinkerton.

FLORIDA PUBLIC SERVICE COMMISSION

60

1                 Any questions or comments from Commissioners?

2       All right.  It seems like you covered all the basis.

3       Thank you very much.

4                 MS. PINKERTON:  Thank you.

5                 CHAIRMAN BRISÉ:  At this time we're going to

6       take about a ten-minute break, and so that will bring us

7       back at 3:05.

8                 (Recess taken.)

9                 We will reconvene at this time, and we will

10       ask Mr. Bill Grant to come forward from Florida Public

11       Utilities Company.

12                 MR. GRANT:  Good afternoon, Commissioners,

13       staff.  I really appreciate you giving us the

14       opportunity to present the FPU 2012 hurricane

15       preparedness update.  My name is Bill Grant.  I'm the

16       Engineering Manager for the Northeast Division of

17       Florida Public Utilities.

18                 Florida Public Utilities Company is a small

19       investor-owned utility with two electric divisions.  One

20       division is located in Marianna along the Panhandle.

21       The second is along the Atlantic Coast in Fernandina

22       Beach.  The two divisions are roughly 250 miles apart.

23       We distribute electricity in Jackson, Calhoun, and

24       Liberty Counties in the northwest division, and on the

25       Amelia Island portion of Nassau County in the northeast

FLORIDA PUBLIC SERVICE COMMISSION

61

1       division.  Our customer base is approximately 28,000

2       retail customers.  Presently 100% of the electricity we

3       sell is purchased from Gulf Power Company in the

4       northwest and JEA in the northeast.

5                 The agenda for our presentation today is to

6       give an overview of facility inspections, some of the

7       recent maintenance and reliability projects that were

8       completed or that we have planned; talk about our

9       coordination efforts with other utilities, government

10       agencies, and community groups; and any recent storm

11       hardening measures that we have undertaken.  In

12       addition, I will give a brief overview of our storm

13       recovery and forensic data collection plans.  Then I

14       will express any concerns that we may have about the

15       upcoming hurricane season.  Finally, I will answer or

16       find answers to any questions that you may have.

17                 During 2011 we completed the fourth year of

18       our eight-year wood cycle -- wood pole inspection

19       program.  Inspections today account for 51% of

20       approximately 26,000 wooden poles that we have on our

21       system.  This indicates that we are on schedule with our

22       inspections.  Poles that fail inspections are

23       prioritized for replacement based upon the remaining

24       strength identified by the contractor during the

25       inspection.  It simply means that we replace the weakest

FLORIDA PUBLIC SERVICE COMMISSION

62

1       poles first in an effort to protect and be safe out

2       there to the public.

3                 In 2011 we replaced 215 poles.  So far in 2012

4       we have replaced 76 poles.  New poles are installed in

5       accordance with the recently developed storm hardening

6       requirements and procedures.

7                 To assure public safety and enhanced

8       reliability we perform periodic inspections on various

9       transmission, substation, and distribution equipment.

10       Inspection periods range from weekly to annual depending

11       upon the devices to be inspected.  In addition to poles,

12       equipment inspected includes street lights,

13       transformers, relays, breakers, reclosers, voltage

14       regulators, automatic transfer switches, substation

15       batteries, and capacitor banks.

16                 FPU has an ongoing vegetation management

17       program for a three-year trim cycle on our main

18       distribution feeders and a six-year cycle on lateral

19       feeders.  In addition to being on a three-year trim

20       cycle, our transmission lines are visually inspected

21       annually for any hot spot trimming that may be needed.

22       In the northeast division we completed the six-year

23       transmission climbing inspection and the replacement of

24       electrical and mechanical relays with microprocessor

25       relays in our substations.  And I might mention that all

FLORIDA PUBLIC SERVICE COMMISSION

63

1       our transmission poles are located in the northeast

2       division.

3                 Additionally, a distribution feeder

4       coordination study was completed for both divisions by a

5       utility engineering consultant.  The results of the

6       coordination study and the climbing inspection results

7       will be used to develop future reliability improvement

8       projects.

9                 Several residential developments in the

10       northeast division have aging direct buried underground

11       cable systems mostly with a Concentric neutral that was

12       exposed and we are now experiencing very unacceptable

13       failure rates.  We have identified the remaining

14       locations and stepped up our conduit installation and

15       cable replacement efforts to complete all cable

16       replacement projects by the end of 2013, which means

17       that by the end of 2013 we hope to have all our

18       underground cable with non-Concentric neutral but

19       isolated insulated neutral in conduit.

20                 Finally, due to the coastal corrosion related

21       failures in northeast, we have an extensive effort

22       underway to replace all porcelain insulators and coastal

23       highway insulators by the end of 2012.  That project is

24       in process and on track.

25                 We participate in activities coordinated by

FLORIDA PUBLIC SERVICE COMMISSION

64

1       the Southeastern Electric Exchange, including mutual

2       assistance.  We provided crews to assist with both storm

3       restoration efforts on three occasions during 2011.  In

4       addition to membership in SEE, we are also members of

5       the Public Utility Research Center, Southeastern

6       Reliability Corporation, the Florida Reliability

7       Coordinating Council, and the North American Electric

8       Reliability Corporation.

9                 Both electric divisions actively participate

10       in the emergency operations activities in the counties

11       we serve.  During 2011 a new Energy Management Director

12       was hired in Nassau County.  We met with him to exchange

13       ideas and to offer our commitment and full support with

14       emergency operations efforts.  We also toured the Nassau

15       County Emergency Operations Center.  As of yesterday we

16       have been trying to get together and have a meeting to

17       actually go through the, a similar presentation to this

18       within the county with the other agencies that would be

19       involved in a restoration effort, and that meeting is

20       scheduled for the 24th of May.

21                 During 2011 the Northwest Division completed a

22       wood to concrete pole conversion upgrade to the federal

23       prison and a storm hardened pond crossing.  Transmission

24       climbing inspection in the Northeast Division identified

25       31 wooden poles in need of replacement.  This represents

FLORIDA PUBLIC SERVICE COMMISSION

65

1       almost 20% of the wooden transmission poles remaining in

2       our system.  These poles will be replaced with spun

3       concrete poles.  We feel like we're ahead of schedule on

4       our, our concrete pole replacement, and this kind of

5       helps speed it up even a little bit more.  We were not

6       excited when we found out about this, so we're going to

7       put an extensive effort underway to make sure we get

8       those poles replaced.

9                 New FPU facilities are being designed using

10       recently developed storm hardening standards and

11       procedures.

12                 During storm recovery, safety of our

13       employees, contractors, and the public we serve are

14       always given a high priority, whether performing routine

15       work or post-storm recovery activities.  Well in advance

16       of the first storm we update our emergency restoration

17       plan, refresh or train FPU employees on the procedures,

18       and increase our inventory levels.  These actions

19       usually take place by the end of May of every year.  I

20       think this is pretty consistent with what you've heard

21       from all the other companies as well.

22                 When a storm develops and it appears it may

23       impact our service area, we activate our storm plan,

24       communicate with our employees, provide vital

25       instructions, and initiate our logistics plan.

FLORIDA PUBLIC SERVICE COMMISSION

66

1                 As soon as practical following a storm, a

2       preliminary assessment is made to determine the extent

3       of the damage and the manpower and material resources

4       that will be needed for the restoration effort.  If we

5       determine additional manpower is needed, a request for

6       assistance is made through the Southeastern Electric

7       Exchange and by using our utility contractor alliances.

8       Again, you've heard this before.

9                 The FPU Emergency Response Control Center is

10       activated so all damage reports and restoration activity

11       can be coordinated and dispatched from one location.

12       This minimizes confusion and duplication of effort.

13       Additionally, a member of the FPU storm restoration team

14       is sent to the EOC to make sure our restoration effort

15       is being coordinated with other restoration efforts of

16       the other companies and agencies involved.

17                 FPU employees have specific staffing

18       assignments and will be fully involved with the

19       restoration effort.  Therefore, we hire a knowledgeable

20       utility contractor to collect our forensic data.  Once a

21       determination is made that a storm will impact FPU's

22       service area, territory, excuse me, as much advance

23       notice as possible is given to internal and external

24       forensic team coordinators.  Forensic team members are

25       alerted to the potential impact of the storm and are

FLORIDA PUBLIC SERVICE COMMISSION

67

1       provided instructions regarding personnel assignments,

2       mobilization, safety procedures, and forensic data

3       reporting requirements.

4                 After the storm passes and it is determined it

5       is safe to proceed, the forensic teams will be

6       dispatched to collect all necessary data and complete

7       the PURC damage assessment forms.

8                 Our concerns pretty much mirror the concerns

9       that have been expressed by all the other companies.

10       The primary concern being that if a major storm causes

11       significant damage, we're going to have bigger issues.

12       Being a smaller company, our size limits our internal

13       resources and could impact our ability to procure

14       external resources.  Should this occur, restoration time

15       may be lengthy and result in an extended outage period

16       before power can be fully restored to all of our

17       customers.

18                 I'd like to thank the Commissioners and staff

19       once again for allowing us to present our 2012 hurricane

20       preparedness update.  At this time I will do my best to

21       answer any questions you may have.

22                 CHAIRMAN BRISÉ:  Commissioners, any questions

23       at this time?

24                 (No response.)

25                 All right.  Seeing none, thank you very much

FLORIDA PUBLIC SERVICE COMMISSION

68

1       for your presentation this afternoon.

2                 MR. GRANT:  Thank you.

3                 MR. GARL:  Mr. Chairman, staff would like to

4       note that the next presenter was scheduled to be Barry

5       Moline from the Florida Municipal Electric Association.

6       He is unable to be with us today.  In his place is

7       Mr. Jody Finklea, the Assistant General Counsel and

8       Manager of Legal Affairs for FMEA, who will give

9       Mr. Moline's presentation.

10                 CHAIRMAN BRISÉ:  Thank you very much.

11                 Mr. Finklea.

12                 MS. FINKLEA:  Finklea.  Yes, sir.  Good

13       afternoon.  I was going to say for those of you who know

14       Barry, obviously I'm not Barry.  With Fred Bryant and

15       myself, we are General Regulatory Counsel to FMEA, we

16       call ourselves FMEA spokes models.  That's our role.

17                 What I'm going to do today is first give you

18       an overview of Florida's municipal electric utilities,

19       and then I'm going to turn the presentation over to Rob

20       McGarrah, who is the General Manager of the City of

21       Tallahassee Electric Utility, your own utilities.

22                 As you can see, Florida's municipal electric

23       utilities are a significant presence in the electric

24       utility industry in Florida.  Combined, our 34 utilities

25       serve more than a million customers, or approximately

FLORIDA PUBLIC SERVICE COMMISSION

69

1       14% of the state's population.  Our largest utilities

2       are JEA, OUC, and the City of Tallahassee.  One of our

3       smallest utilities is the City of Bushnell.  Combined,

4       our utilities are the third largest electric utility in

5       the state after FPL and Progress Energy.

6                 Geographically we're very diverse; from the

7       southern most point in Key West, north to Jacksonville

8       and Jacksonville Beach, and west all the way over to

9       Calhoun County in the City of Blountstown, our utilities

10       cover the entire state.  Generally speaking, any storm

11       event will affect at least some of our utilities in the

12       peninsular Florida.

13                 Our utilities take storm preparedness very

14       seriously.  Looking at this map you may wonder, how do

15       such a bunch of small cities generate power?  Well, they

16       don't.  Most of our cities purchase their wholesale

17       power needs from other suppliers.  In fact, only 12 of

18       our 34 cities own any generation resources at all.

19       Wholesale power suppliers include the Florida Municipal

20       Power Agency who serves all of the needs of 14 of our

21       cities and part of the needs of eight more of our

22       cities.  Other suppliers include Progress, TECO, FPL,

23       Gulf Power, and Glades Electric Cooperative for one of

24       our cities.

25                 The geographic diversity of our municipal

FLORIDA PUBLIC SERVICE COMMISSION

70

1       utilities around the state actually give them an

2       advantage in mutual aid.  They have mutual aid

3       agreements and arrangements among them.  A utility in

4       South Florida can rely on a North Florida or a Panhandle

5       city to provide mutual aid and vice versa, and they have

6       mutual aid arrangements with investor-owned utilities

7       and the cooperatives of the state.

8                 Outside of Florida our utilities are also

9       mutual aid participants in the southeastern wide program

10       and the national program through APPA.  In fact, for

11       past events mutual aid has come to support our cities

12       from as far away as Maine and Wisconsin, Kansas and

13       Texas, and reciprocally our cities have sent crews

14       outward from Florida to some or most of these same

15       places.

16                 Our cities' mutual aid resources can come from

17       a few towns away or many thousands of miles away, but in

18       all of this, FMEA is a proactive and constant companion

19       to our members, who ordain all of their mutual aid needs

20       to restore service to their customers, always keeping

21       foremost in mind the needs of those customers.

22                 Our cities' mutual aid agreements are

23       memorialized in contracts through FMEA, APPA, and

24       directly between and among our utilities in the state

25       and throughout the southeast.  Procedures are in place

FLORIDA PUBLIC SERVICE COMMISSION

71

1       to quickly assess and mobilize needed assistance and to

2       place it where it can be the most help.  FMEA is a

3       strong and constant partner with our cities in planning

4       and implementing mutual aid procedures.  During events

5       FMEA is a constant presence in the state EOC center here

6       in Tallahassee, and we're in constant contact with our

7       cities, our mutual aid providers, and state and local

8       authorities.

9                 In fact, for mutual aid to work best,

10       communication is the key not only with and among

11       utilities, but importantly with state and local

12       authorities.  Here especially our municipal utilities

13       excel, being closely linked to their cities, their

14       counties, and the local emergency operation centers.

15                 Individually our cities may look small, and

16       indeed some of them are, but together they form a

17       powerful presence and a potent foe to storms and other

18       events that affect the service we provide to our

19       customers.

20                 Now particularly to address how one of our

21       cities is handling storm readiness and mutual aid, it's

22       my privilege to introduce Rob McGarrah, the General

23       Manager of the City Electric -- City of Tallahassee

24       Electric Utilities, your own utility.  Rob?

25                 MR. McGARRAH:  Mr. Chairman, Commissioners, I

FLORIDA PUBLIC SERVICE COMMISSION

72

1       appreciate the opportunity to be here today and talk

2       about our activities of preparing annually for storm

3       events.  What I'd like to do today is tell you a little

4       bit about us and our experience with storms, and then

5       run through what we do to prepare, and how we operate in

6       a storm event, and some of our emergency response

7       features.

8                 Our system is, as Jody said, serves 113,000

9       customers here in Tallahassee.  We include the

10       municipal, the corporate limits of the city, plus part

11       of the county.  We have a 221-square mile service

12       territory with 188 miles of transmission at the 115 and

13       230 level; 2,800 miles of distribution, with 1,700 of

14       that underground.  So the majority of our distribution

15       is underground.  You'll see in a later slide virtually

16       everything we build today is underground.

17                 We have 24 substations throughout our service

18       territory.  And then we are one of the municipals in the

19       state that do generate our own power.  We have three

20       power plants that we own and operate:  The Purdom plant

21       located in St. Marks, Florida; the Hopkins plant in Leon

22       County, it's in the western part of Leon County; and

23       then we operate the Corn Hydroelectric Facility that is

24       the dam that makes up Lake Talquin.  And in addition to

25       making electricity there, we do do some flood control

FLORIDA PUBLIC SERVICE COMMISSION

73

1       with that facility.

2                 Our utility has a lot of experience, both

3       direct experience and through mutual aid with storms.

4       We've had nine storms over the last few years that we've

5       dealt with directly, five where we've sent crews to

6       other systems.  I won't go through the list here, but

7       these two slides give you a list of those storms.

8       Having both the direct experience and the mutual aid

9       experience is great for our folks in keeping us prepared

10       to deal with storm events.

11                 Our preparation starts with the design and the

12       construction of our system where we're using the

13       National Electric Safety Code and the extreme wind

14       loading standards.  Our system is designed where our

15       facilities are on front lot lines, which makes it easier

16       to get to and restore.

17                 As I said earlier, virtually all of our new

18       distribution construction is underground.  And then we

19       do have a program on our transmission system; any new

20       transmission facility or scheduled replacements are done

21       with steel or concrete poles.

22                 We have an active vegetation management

23       program on our distribution side of the operation.  We

24       trim on an 18-month cycle all of our circuits.  We also

25       use a tree growth regulator to retard the regrowth.  And

FLORIDA PUBLIC SERVICE COMMISSION

74

1       on our transmission system we have a three-year minimum

2       trim cycle, and we have someone mowing the right-of-way

3       and inspecting the right-of-way at least annually.

4                 We inspect our distribution poles on an

5       eight-year cycle.  We do a three-year process every

6       eight years to inspect them.  Our transmission poles are

7       inspected annually visually, but every five years

8       there's a physical inspection which includes a climbing

9       inspection of the poles.

10                 Biannually we do an infrared inspection and

11       flying inspection of the transmission system.  And I'll

12       talk in a minute about our integration, but one of the

13       things about being part of the city is we get to work

14       collaboratively with both the rest of the city and the

15       county.  In the case of the flying inspections, we work

16       with the Leon County Sheriff's Department.  We funded

17       part of the flare (phonetic) system on their helicopter.

18       In return we get to use it for the flying inspections

19       both on a routine, you know, on a regular preventative

20       basis and when we have problems.  And then lastly we do

21       increase our material inventory in the spring so that we

22       have a ready supply of equipment should we get struck

23       with a storm.

24                 As I said, on our emergency operations side of

25       the business, we're fully integrated into the city's

FLORIDA PUBLIC SERVICE COMMISSION

75

1       emergency management organization.  We -- the city uses

2       the NIMS system and ICS system.  The city has an area

3       command center that coordinates all of the city's

4       response to storm events and other emergency events.

5       And in fact, prior to my assuming the role of General

6       Manager last year of the utility, the prior ten years I

7       served as the utility leader at the Area Operations

8       Center for any storm events for the city, coordinating

9       not just electric but all of the city's utilities'

10       response to storm events.

11                 We do coordinate our restoration through the

12       Electric Control Center, but the main communications

13       focus is through our Area Operations Center.

14                 As storms approach -- at the start of the year

15       we do crew assignments, review our plans, and update

16       them.  As storms approach, depending on the severity and

17       the location of the storm, we start mobilizing that

18       plan.  We've integrated our outage management system in

19       our GIS systems together, and you'll see in a later

20       slide our outage management system is actually displayed

21       at our Area Operation Center where all the cities'

22       operations can see where we're seeing outages.  It's

23       also -- a portion of that data, the larger outages is

24       put into a larger GIS system that can be viewed at the

25       county emergency operations system or center.  And then

FLORIDA PUBLIC SERVICE COMMISSION

76

1       we do have established restoration priorities within our

2       system.

3                 Some of the other emergency response, we work

4       with police, fire, and public works on a pre-staged road

5       clearing task force within the city where we have

6       electric utilities staffed with the task force.  There

7       are certain predetermined routes that have been

8       identified to the city to get folks from the interstate

9       into the hospitals and other critical facilities in the

10       city.  We put these teams out in the field.  After the

11       storm passes their job is to, on their own, clear a path

12       into those critical facilities and they have all the

13       resources to do that.

14                 We have assessment teams within the electric

15       utility that are available to go out and assess the

16       damage.  And then there's, as I said, there's continual

17       communications between our Area Operation Center and our

18       Control Center.

19                 As Jody talked about, we have a number of

20       mutual aid agreements through FMEA, the American Public

21       Power Association, and the Florida Electric Coordinating

22       Group that gives us access to resources to help us if

23       there's a storm event that's greater than our staff can

24       handle.  And conversely, we're available to support

25       other municipals and other utilities if they have storm

FLORIDA PUBLIC SERVICE COMMISSION

77

1       events that are greater than they can handle.

2                 We do have a backup control center and a

3       backup call center location so that if we have damage to

4       the facilities within the city, that they stay

5       operational.  As I talked earlier, the sheriff's

6       helicopter is available to us, and our key staff are

7       trained in the ICS 100, 200, 700, and 800 training.

8                 Lastly, on the logistical support, because

9       we're fully integrated into the city's emergency

10       operations program, we have that entire logistical

11       support group to help the electric utility and provide

12       the logistical support we need during a storm.  We also

13       have the public information support through the city

14       available where we use, do the standard media releases,

15       we've got the information we put on our web page, we're

16       on Facebook.

17                 But one of the things I didn't put here is we

18       started a program recently where we do instant alert, is

19       we gather the mobile phone and home phone and e-mail

20       information for our customers.  We will right now any

21       time we have a circuit level outage of over a couple

22       minute duration, we notify the customer directly that we

23       know that there's an outage at their house, and then we

24       notify them after the outage is restored so that if

25       they're not home, they know they may want to go do

FLORIDA PUBLIC SERVICE COMMISSION

78

1       something else.  If they're home, they know that we are

2       there, that we are aware of it, and we've got crews

3       coming out.  We also work with the local media on both

4       pre-storm public safety messages and during the storm

5       events.

6                 In closing, I think we're prepared.  We show

7       a -- we have a good plan and we're ready for the storm

8       event.  Obviously we're like every other utility, if we

9       get a major storm event or multiple storm events at one

10       time, our ability and the speed at which we can respond

11       would be impacted.  But we have an experienced group of

12       folks and a solid plan for meeting storm events.

13                 CHAIRMAN BRISÉ:  Thank you.  Commissioner

14       Edgar.

15                 COMMISSIONER EDGAR:  Thank you, Mr. Chairman.

16       And thank you, Mr. McGarrah, for coming.

17                 I'm a longtime Tallahassee resident, and for

18       better or for worse, maybe to your pleasure, I don't

19       know, but we have as a regulatory body very little

20       interaction actually with the City of Tallahassee

21       utilities.  So thank you for coming and spending your

22       time to share with us some of the things that you do.

23                 You know, I've asked some of the others

24       speakers about their vegetation management program and

25       you touched on that.  In your prepared slides it says an

FLORIDA PUBLIC SERVICE COMMISSION

79

1       "18-month trim cycle for distribution."  I recall a

2       number of years ago there being -- it seemed to be that

3       there were more complaints and concerns raised by

4       residents sometimes about tree trimming.  I have, and

5       this is purely anecdotal, but I don't seem to hear or

6       see as many complaints as perhaps there were some years

7       ago.

8                 So could you just speak in a little more

9       detail about some of the efforts for tree trimming and

10       vegetation management that the city has and how you

11       interact with local residents, who, of course, like

12       every other area, we love our trees.

13                 MR. McGARRAH:  Yes, ma'am.  Our tree trimming

14       program actually was born out of some citizen

15       participation.  Back in the late '90s there were a lot

16       of complaints about our tree trimming cycle.  We were on

17       a three-year cycle.  As a result of that interaction

18       with the citizens, we modified our tree trimming cycle.

19       We don't trim quite as far back as we used to but we're

20       trimming twice as often.  It still gives us the

21       clearance, the same clearance you would get in a normal

22       three-year cycle when the trees grow in.  So that's one

23       of the things we did is we responded to our customers'

24       feedback on the tree trimming program and developed a

25       program that works operationally for us and is

FLORIDA PUBLIC SERVICE COMMISSION

80

1       acceptable for our customers.

2                 The other thing we do is we do a lot of

3       communications with our customers when we're out in

4       areas starting to do tree trimming.  We'll post notices.

5       Our forester is out making presentations, meeting with

6       community groups.  We've tried to be much more

7       aggressive in our communications and interaction with

8       our customers so that they know what we're doing prior

9       to us doing it.

10                 COMMISSIONER EDGAR:  Thank you.  And I've

11       given this disclaimer publicly many times, but I will

12       point out that my residence is actually in the county

13       outside the city limits, and we, at my home and for my

14       family, receive service from Talquin.  And so that leads

15       me to the more general question, you've talked about

16       coordination with the EOC and with other city services

17       and aspects.  How, as a, as a municipal right side by

18       side with a co-op, how is the communication and

19       coordination with that local co-op, which in this

20       instance is Talquin?

21                 MR. McGARRAH:  In this type of an event it's

22       done at our control center level.  Our control center

23       operators are routinely talking to the Talquin dispatch

24       folks and back and forth.  We actually have some city

25       customers on their lines and they have some Talquin

FLORIDA PUBLIC SERVICE COMMISSION

81

1       customers on our lines.  So we -- there's routine

2       communications both on normal operations and during any

3       storm event between our respective dispatch groups.

4                 COMMISSIONER EDGAR:  And you feel like all of

5       that is, goes well?

6                 MR. McGARRAH:  That's going well.  And

7       there's -- obviously every time we have a storm event we

8       relook at what happened and do a lessons learned and

9       integrate anything we learned from the storm event in to

10       change the process.  But that is working well.

11                 COMMISSIONER EDGAR:  All right.  Thank you.

12       And thank you again for your comments.

13                 CHAIRMAN BRISÉ:  Commissioner Balbis.

14                 COMMISSIONER BALBIS:  Thank you, Mr. Chairman.

15                 Actually I have a question for the

16       representative of Florida Municipal Electric

17       Association.

18                 MS. FINKLEA:  Yes, sir.

19                 COMMISSIONER BALBIS:  Thank you for your

20       presentation.  And I also want to thank the City of

21       Tallahassee utilities, thank you for your presentation

22       as well.

23                 My question is more general to the municipal

24       utilities that, that you represent.  I recall in the

25       2004/2005 hurricane season that at least some of the

FLORIDA PUBLIC SERVICE COMMISSION

82

1       municipal utilities struggled to restore power at least

2       when compared to maybe some of the other larger

3       utilities.  The mutual aid agreements and other measures

4       that you listed, do you feel that that will at least

5       help to solve that problem so that they're more in line

6       with, with the other utilities, or is that just really

7       one, one situation that will not occur?

8                 MS. FINKLEA:  Well, 2004 and 2005 were

9       exceptionally challenging years.  I would say that since

10       then we have strengthened considerably our mutual aid

11       reach.  Prior to -- during that time we had not had

12       pre-staged agreements for food and housing and shelter

13       for crews that are working in our cities.  We've since

14       remedied that and we now have those agreements available

15       and our cities have taken advantage of them.

16                 I actually think that there were, in that, in

17       that 2004 and 2005 time frame, many instances where our

18       cities were at the same level as surrounding

19       investor-owned utilities or even restored service

20       faster, although there were some outliers in some areas.

21       I think those outliers have been handled and we have

22       better procedures, better coordination, and better

23       resources in place today.

24                 COMMISSIONER BALBIS:  Okay.  Thank you.

25                 MS. FINKLEA:  Uh-huh.

FLORIDA PUBLIC SERVICE COMMISSION

83

1                 CHAIRMAN BRISÉ:  Thank you.  If there are no

2       further questions or comments by Commissioners, thank

3       you very much for your presentation this afternoon.

4                 At this time we'll call forward Florida

5       Electric Cooperatives Association, Mr. Dyal with Clay

6       Electric Cooperative.

7                 MR. DYAL:  Good afternoon, Chairman and

8       Commission and staff.  I appreciate you letting me come

9       and present Clay Electric Cooperative's 2012 hurricane

10       preparedness program.

11                 First I'd like to tell you a little bit about

12       Clay Electric.  You may not be familiar with us.  We're

13       headquartered in Keystone Heights, Florida.  I'm sure

14       you know where that is.  But we serve in 14 North

15       Florida counties.  We're in north central.  We also

16       operate out of six district offices:  Gainesville,

17       Keystone Heights, Lake City, Orange Park, Palatka, and

18       Salt Springs.

19                 If you look here at the map, you can see we're

20       kind of in the north central part would be the large

21       green there in the middle.  We have over 10,000 miles of

22       overhead distribution line.  2,100 of that is

23       underground.  So we do have about 8,000 plus that is

24       overhead.  We do operate 213 miles of transmission, 46

25       substations, and serve 173,000 customers.

FLORIDA PUBLIC SERVICE COMMISSION

84

1                 First, in our standards of construction, we do

2       go by National Electric Safety Code compliance.  We do

3       not use extreme wind loading.  Our experience in the

4       2004 hurricanes, we just didn't feel justified in that.

5       Our damage was such in looking at it, we felt

6       comfortable by staying by the National Electric Safety

7       Code.

8                 Flooding and storm surges for Clay is not a

9       real problem.  We are not a coastal -- as you noticed,

10       we're inland both from the east and west coast.  Our

11       attachment by others, our agreements, we basically

12       require them to verify their clearance and strengthen.

13       And I apologize for the spelling there, but we do

14       require them by their contracts to sign off by a

15       professional engineer that it meets the strength and

16       clearance requirements.

17                 In our transmission, after 2007, any work we

18       do to rebuild or build, we do go to extreme wind

19       loading.  We felt that was a prudent investment.  In the

20       new lines we also use concrete poles with polymer

21       insulators.

22                 In the past year, 2011, we did replace five

23       miles of wood pole lines with concrete.  We're now

24       sitting, as you can see, about 50/50; we have about

25       100 miles of concrete and 113 miles of wood, and we will

FLORIDA PUBLIC SERVICE COMMISSION

85

1       continue to work through the wood as needed.

2                 Our facility inspections in distribution, this

3       is a core of our maintenance program, has been for

4       years, as any cooperative -- I think if you remember

5       when we did the pole inspection program originally, it

6       was built around RUS, and we were on a ten-year cycle

7       prior to 2007.  So we began to mitigate over to an

8       eight-year.  We do our inspections by sub and feeder,

9       not just by number of poles.  So it takes a mitigation

10       to change our schedule over.  But beginning in 2013 we

11       will be completely on an eight-year cycle.

12                 We have approximately 206,000 wood poles.  In

13       2011 we inspected 21,549.  Here again that falls out to

14       be a little over 10%.  But our program is on schedule;

15       we will be on the eight-year.  Some years we're going to

16       be a little low, some years we'll be a little high

17       because of the way we do our cycle.

18                 Facilities inspections in transmission.  We

19       have 1,688 wood poles, 908 concrete poles, 14 steel

20       poles.  We do a groundline inspection every eight years.

21       Our next inspection, that is scheduled for 2014.  During

22       the course of the year we do helicopter inspections

23       three times annually.  Typically they'll fall in March

24       before hurricane season, we'll do it during the storm

25       season, and then as a follow-up.  So typically three

FLORIDA PUBLIC SERVICE COMMISSION

86

1       times a year is on average for us.

2                 Our ground visual patrol we do every two

3       years.  Our last was in 2010.  We're scheduled to do one

4       this year.  Climbing inspection is every four years; the

5       last 2008, and we'll do one in 2012, this year.  So when

6       we do a climbing, we kind of roll those two together.

7       And as you can see, they'll hit.  But here again, we're

8       on schedule.  All things will be inspected.  We're very

9       comfortable where we're at in our transmission.

10                 Our vegetation management, both in our

11       transmission and distribution we do feeder cycling.  We

12       don't separate main line from laterals.  We, here again

13       we tend to work by feeder.  So we will classify our

14       foresters, we'll classify them as we go out on a three-,

15       four-, or five-year based on the right-of-way width,

16       whether it's rural, just what the conditions are.  We do

17       that on a GIS system.  We do have a software system that

18       maintains that.  Our foresters will look at it every

19       year, they'll look at it as cut and then make a

20       determination of what that cycle should be next time

21       based on how much they were able to clear and what they

22       feel the growth is.

23                 Right now, as you can see, three years or 25%

24       of our feeders; four years, 40; five years, 35; average

25       about 3.9.  And we do include when we do go through a

FLORIDA PUBLIC SERVICE COMMISSION

87

1       cycle, there's parts of the feeders we trim, there's

2       parts we mow, and we do do chemical.  And that program,

3       I'm happy to say, is on schedule, has been.  It's pretty

4       much like the pole treating; we've done it for years.

5       All we see through the years is it tends to creep down.

6       Where we maybe used to have 45% to 50% in five years,

7       we're now down to 35 that tend to, tend to cut the cycle

8       by.

9                 We do do a lot of education.  Clay educates

10       their consumers.  We have two types of brochures.  One

11       is "Keep the Lines Clear," which is basically where we

12       try to educate them into why we clear them, how we clear

13       them, how we're going to cut them, what our cycle is.

14       And then we have one that is "Landscape Planning" where

15       we try to teach them what to plant, what type of

16       species, where to plant, those type things.  And we

17       constantly work with our counties and our zonings to try

18       and here again hopefully we'll get these planted in the

19       right place.

20                 Annual activities in storm preparedness.  Our

21       emergency plan is reviewed and revised annually.  We'll

22       sit down and starting in the February time frame we'll

23       go through, look at our personnel assignments, we'll

24       look at our, all of our internal resources, we'll assign

25       them, we'll identify outside contractors, we'll set up

FLORIDA PUBLIC SERVICE COMMISSION

88

1       our agreements, we'll work with statewide Florida

2       Electric Cooperative on our mutual aids, we'll get

3       everything updated and everything so all of our

4       agreements are in place.

5                 Communications has become a huge issue

6       obviously.  One of the first things we'll do, every year

7       we establish communications.  Like I say, we work in 14

8       counties, so we're working with 14 different EOCs and we

9       have 14 different working arrangements.  Each one is a

10       little different, their needs are different, and we try

11       to match with them.  We do not staff each one during

12       hurricanes simply because of the numbers.  When you take

13       14 employees out of your mix, it gets pretty tough.  But

14       what we do do is we set up an EOC response team at our

15       office and they have a direct line in.  That line

16       doesn't handle anything else but EOC traffic and they

17       solve EOC problems.  So it's worked well for us.

18       Obviously there's hiccups, but right now that's what

19       we'll continue to work with.

20                 We establish communication lines for all of

21       our local law enforcement in our control center.  That

22       operates a different communication line.  But we make

23       sure that we have a place to respond to their needs and

24       they're not waiting in line with some other customer

25       need or EOC need.  Obviously we do daily updates on

FLORIDA PUBLIC SERVICE COMMISSION

89

1       storm restoration progress in our work areas, not only

2       where we restore them but where we're going to be

3       working.  We work with state EOC, local EOC, local

4       media, cooperative websites.  We have a web-based

5       graphical outage map.  We are working in Facebook and

6       other opportunities to communicate every way we can as

7       to what our restoration progress is and where we're

8       working and what we think restoration times will be to

9       try and give all of our customers as much access as we

10       can.

11                 In summary, our transmission distribution

12       system we think is inspected and maintained according to

13       standards.  Our storm plan is reviewed and revised, is

14       current.  Our communication plans, probably the most

15       thing, continuously reviewed and revised as we go and

16       opportunities arise.

17                 Areas of vulnerability that y'all have asked

18       us to address on.  Obviously for us, due to our size and

19       the area we serve, we serve urban areas, we also serve

20       extremely rural areas.  Heavy right-of-way, large amount

21       of distribution in rural wooded areas.  We serve Alachua

22       County.  They really love their trees and it's a

23       challenge for us working in there.  So we always get

24       concerned that you get overwhelmed.  So we'll -- we

25       worry about that.

FLORIDA PUBLIC SERVICE COMMISSION

90

1                 Insufficient outside crews.  While it is

2       fortunate that we're in North Central Florida and we

3       don't get the brunt of the others, that also means that

4       we're last in line usually to get crews.  So we end up

5       maybe sometimes getting a few days out before we can

6       amass crews.  So we're constantly worried.  A lot of

7       times, I think as he alluded to earlier, we have to

8       reach outside.  We'll get crews from Mexico.  In '04 we

9       had crews from Mexico, Minnesota.  You have to reach

10       where the crews are to get them in.  So that concerns

11       us.  And then obviously, like anybody else, multiple

12       storms is tough.  That would be a thing to deal with.

13       Any questions?

14                 CHAIRMAN BRISÉ:  Thank you very much, Mr.

15       Dyal.  Are there any questions from Commissioners?

16                 (No response.)

17                 All right.  Seeing none, thank you very much

18       for your presentation.

19                 At this time we're moving to a presentation

20       from AT&T.  Mr. Follensbee.  Hopefully I'm pronouncing

21       that right.

22                 MR. FOLLENSBEE:  You did.  Mr. Chairman,

23       Commissioners, AT&T thanks you for the opportunity for

24       us to come here today to talk about how AT&T is prepared

25       for both natural disasters and manmade disasters.  In a

FLORIDA PUBLIC SERVICE COMMISSION

91

1       nutshell, AT&T is prepared.

2                 Since 1992 we have actually had to deploy our

3       natural disaster recovery teams every year to some site

4       in the United States.  So it isn't a case that we're

5       preparing for storms or natural disasters.  We're

6       actually involved with them someplace in one of our 50

7       states.  Because of the fact we're offering both

8       wireline and wireless, we're not just in wireline states

9       where we have 22 operations.  We actually are in 50

10       states.  Also have it in Puerto Rico, the Virgin

11       Islands, and we also have some natural disaster recovery

12       capabilities in some of our foreign countries as well.

13       So for AT&T it's not just an endeavor, it's actually

14       ingrained as part of our business.

15                 So today what I'm going to talk about is how

16       we are prepared, what we do to try to restore both the

17       wireline and wireless, talk just a little bit about our

18       inventory of generators because power continues to be

19       the long pole in the tent for us to make sure we can

20       restore service, and then a little bit about how we are

21       operating to do this, particularly since some of the

22       Commissioners haven't heard this since this is kind

23       of the -- we've kind of organized this the same way and

24       have been for several years.

25                 All right.  Our greatest asset is our people.

FLORIDA PUBLIC SERVICE COMMISSION

92

1       And so basically what we will do every year is we

2       prepare and support the employees so they can

3       concentrate on restoring service to our customers.  We

4       are constantly holding employee awareness meetings to

5       prepare for them.  We take great pride and try to make

6       sure our employees are safe, we try to take great pride

7       in trying to make sure the employees' families are safe.

8       Because if the families are safe, then the employees

9       don't have to worry about that particular event if their

10       families are in an area that's been hit by a disaster.

11       For instance, in a couple of weeks all of the employees

12       will have to call in to report to work to basically say

13       I reported to work today.  It's kind of a check that we

14       do of our system so we can check on are the employees

15       actually at work or were they not able to work because

16       they're harmed, hurt, or something that we'll try to

17       take care of them.

18                 We hold annual preparedness meetings annually

19       with each of the business units involved.  I mean, that

20       includes the unit I'm involved, which mainly is in

21       public policy.  We hold periodic exercises to make sure

22       we're, you know, test for emergency plans, and we

23       participate with state and local authorities as well as

24       other utilities just about everywhere in the nation

25       where one is held.

FLORIDA PUBLIC SERVICE COMMISSION

93

1                 For instance, since we operate in all 67

2       counties in Florida, if a county is holding a

3       preparedness initiative, we will participate in that.

4       Part of it may just be because of our wireless

5       facilities.  The other part will be because of our

6       wireline and wireless facilities.

7                 One of the things I want to highlight here is

8       that AT&T is proud to announce that we are the first

9       private sector company in the United States to be

10       certified under the Department of Homeland Security's

11       standards for disaster preparedness.  This is a program

12       that they actually started after the September 11th,

13       2001, disaster.  They actually put it in place in 2010.

14       You go through a program to be certified under this

15       program.  AT&T has spent a lot of effort to become

16       certified, and we are proud to announce we are the first

17       one that the Department of Homeland Security has

18       certified that we are prepared to meet any natural or

19       manmade disaster that may face the United States.  The

20       program pretty much is, is oriented just to the United

21       States, including Puerto Rico and the Virgin Islands,

22       but it's something we're quite proud of.  We've spent

23       over $600 million on natural disaster recovery programs.

24       Now this does not include the money we spend to harden

25       our plants or get our facilities in place.  This is

FLORIDA PUBLIC SERVICE COMMISSION

94

1       actually other money we're spending in training people

2       and buying the necessary equipment.

3                 As it shows here, we've got over 320

4       technology and equipment trailers throughout the nation

5       that are prepared to be deployed anywhere we need to to

6       face the disaster that we're dealing with.

7                 We have five natural disaster recovery

8       warehouses in the United States.  Two are in the

9       southeast.  One of those is in Florida.  So Florida is

10       definitely well positioned to deal with any kind of

11       disaster we'll face this year.

12                 Let me talk about the fact that because in

13       natural disasters you don't know what you're going to be

14       facing, we have deployed new emergency communication

15       vehicles, we've upgraded some of those.  For instance,

16       our Cell Tower on Wheels used to be 2G compatible, then

17       3G compatible.  Most of them now these days are 4G

18       compatible.  All that means is we're continuing to

19       replace or upgrade those trucks to make sure they have

20       available the latest technology you need for

21       communications.

22                 As part of the program we've also got 12

23       members that have gone through the hazmat training in

24       the University of North Carolina at Chapel Hill.  Again,

25       depending on what kind of disaster you're dealing with,

FLORIDA PUBLIC SERVICE COMMISSION

95

1       you may be dealing with a hazardous spill of some

2       nature, you know, God forbid, a manmade disaster.  And

3       so these people are equipped to deal with that

4       environment if that's what they need to do to help deal

5       with our plant restoration and protecting it.

6                 We continue to enhance our network redundancy

7       in hurricane prone areas, installing more backup and

8       permanent generators, and I'll get into that a little

9       bit more in a couple of slides up ahead.

10                 Basically we're prepared to mobilize anywhere

11       we need to in the nation, including Florida.  We -- our

12       supply management, chain management group has secured

13       and continues to change out as necessary suppliers to

14       ensure supplies and equipment are needed, not just for

15       our plant but we also have suppliers to deal with

16       housing our employees, if needed, or their families in

17       case they're displaced.

18                 We have staging areas that I'll get into in a

19       second for Florida, but we have staging areas across the

20       nation.  If we know a storm is coming, we will start to

21       bring more and more supplies closer to where we think

22       the storm is going to hit to make sure we're prepared

23       after it lands so we can quickly get to restoration.

24                 Once the storm hits, we'll have sweep teams

25       that will be dispatched as quickly as we can once we

FLORIDA PUBLIC SERVICE COMMISSION

96

1       know it's safe to enter the area to identify what kind

2       of restoration requirements we're going to need.  As

3       I've said, we've got businesses that'll help house it.

4       We've also got suppliers for fuel.  To the extent that

5       we're relying on generators to supply backup power to

6       our cell towers, our switches, our remote terminals, we

7       want to make sure we've got a ready supply of fuel.  In

8       addition, we want to make sure we've got a ready supply

9       of fuel for our trucks that need to be dispatched.

10                 To talk a little bit about it, the way we've

11       got our hierarchy set up is in Florida we've got two

12       local response centers.  They are usually the first

13       point of where we go to look for preparing for, for a

14       disaster.  We've got one in Miami, one in Jacksonville.

15       The one in Miami pretty much covers from Key West up to

16       the south area I think up to Indian River, and then the

17       one in Jacksonville covers the rest of the state.  Those

18       two centers are staffed up, you know, 24 by 7, 365 days

19       a year, to be prepared to start to deploy what we need

20       to depending where the disasters hit.  To the extent

21       they need assistance, they will go to Atlanta, which

22       also has a backup center in Birmingham.  Again, what

23       you're doing there is if you can't get what you need

24       from the state where we stocked up supplies, we'll go

25       first to Atlanta to the regional center.  And then, if

FLORIDA PUBLIC SERVICE COMMISSION

97

1       necessary, we'll go to the local network operation

2       center which is actually located in Bedminster, New

3       Jersey.  I think I've got a picture of that we'll show

4       in a minute.

5                 What we have in place is several strike teams.

6       We basically have determined that you're going to need

7       specialized strike teams to deal with certain things

8       rather than be generalist in nature.  So we basically

9       have a team that deals with tracking storms.  We've

10       actually had to augment that tracking to deal a lot more

11       with tornadoes, which is something we didn't use to face

12       as much in the past, but we're now in a pattern of quite

13       deadly tornadoes that are coming particularly in the

14       southeast and the midwest, and we've augmented that team

15       to basically start to do the best they can to track

16       tornadoes.  We've also got the, a safety strike team, a

17       generator strike team, cell site, E911, damage

18       prevention strike team.  Basically these are specialized

19       teams that deal with just that area.  So, for instance,

20       the team dealing with 911, they're going to do

21       everything they've got to do, for instance, to restore

22       piece apps if they're out of services and you can't make

23       911 calls.  So it's a team that's just dedicated to

24       dealing with 911 service is that part of the network.

25                 This is a picture, and it's hard to see, this

FLORIDA PUBLIC SERVICE COMMISSION

98

1       is a picture of a world-class state of the art center

2       that we've got in Bedminster that basically tracks our

3       network anywhere in the nation.  It also does some

4       tracking of networks globally.  So basically they also

5       are a way that if they see something has happened to a

6       major fiber cut or something, they can deploy teams to

7       restore that service as quick as possible.

8                 Okay.  I think I've already kind of gone

9       through this, but the one thing I want to mention is

10       this year the national exercise we held was actually in

11       Hallandale Beach, Florida, in March and April.  We will

12       rotate that natural -- the team, the exercise we do to

13       some state in the nation.  This year we felt it was

14       necessary to do one in Florida.  We, we, you know, we

15       hope it doesn't happen, but because we haven't had a

16       major storm hit Florida in the coastal area for many

17       years, we felt we really needed to stress hurricane

18       preparedness this year.  In past years we've done

19       blizzards, tornadoes.  So it kind of depends what you're

20       dealing with.  This year we felt it was necessary to

21       really stress hurricanes, not that we think one's going

22       to hit, but we just thought the odds are starting to get

23       greater that we may see something since we haven't had a

24       major one, I think, since 2005.

25                 Now, interestingly enough, we experienced

FLORIDA PUBLIC SERVICE COMMISSION

99

1       hurricanes last year.  We actually had to deploy a team

2       to Connecticut.  You know, the hurricane that completely

3       skirted the whole east coast didn't -- it ended up going

4       into the New England states.  We have operations in

5       Connecticut, and we learned some things there that were

6       different.  Because hurricane -- I don't -- Connecticut

7       hadn't experienced a hurricane in I can't remember how

8       many years.  So it was very unique to them, but we could

9       draw on our experience in Florida, for instance, to

10       deploy up there to help them out.

11                 Part of our preparedness is what we call Cells

12       on Wheels or Cells on Light Trucks.  Most of what we've

13       gone to now are Cells on Wheels.  We not only use these

14       for actual disasters, we'll use these for special

15       events.  For instance, we've got a set of these that are

16       going to be deployed in August in Tampa for the

17       Republican National Convention.  You know, we want to

18       make sure we have the best service we can.  But these

19       trucks basically allow us to go in where a cell tower

20       has come down that they can't be repaired, and we

21       instantly are able to put up a cell tower and get

22       service in that area very quickly.

23                 We have 2,500 cell sites in Florida.  It's

24       growing every day.  50% of them have permanent

25       generators on-site.  What that means is they have

FLORIDA PUBLIC SERVICE COMMISSION

100

1       standby power that we can rely on.  For those that

2       don't, we will deploy temporary generators.  Basically

3       we have 170 portable generators in Lakeland, Florida.

4       We have an additional 300 that are in other states in

5       the southeast.  So if we need to deploy a generator to a

6       cell tower, we have the ability to do that very quickly

7       for those that don't have standup backup.

8                 Let me go through the emergency restoration.

9       We've got quite a bit -- we've got a generator pool also

10       in Jacksonville and Hialeah to deal with our wireline.

11       Because we are replacing more and more of our copper

12       with fiberoptics and electronics for IP digital

13       services, we're actually finding we're needing, you

14       know, more reliable service for power there.  Therefore,

15       we're seeing that we need more generators deployed to

16       make sure we can power up those systems.  Some of them

17       will have standby power, new batteries that we've put in

18       place, some of them will have propane gas or another

19       type of natural gas as a backup.  But in a lot of cases

20       our best backup is just to take a truck, a truck of

21       generators and just stick them out in the field and

22       power up the particular remote terminal for a first

23       site.

24                 As you can see, we've got 2,028 of our digital

25       loop carrier sites, which is a site that basically is

FLORIDA PUBLIC SERVICE COMMISSION

101

1       needed with our fiberoptics to do the digital service

2       that have permanent generators in the south, of which

3       1,400 are here.  And we've got nationwide 10,000

4       portable generators.  I don't think we're ever going to

5       need to deploy 10,000 generators at one site.  Let's,

6       let's hope not.  But basically we're well served in

7       Florida in case we need, in case we have a hurricane

8       come up.

9                 As you can see, we have seasonal pools we'll

10       do as well.  Like I said, we've got one in Hialeah,

11       we've got one in Margate, one in Jacksonville, and we'll

12       stage more, if necessary.  For instance, if we see a

13       storm that's getting ready to hit the Panhandle, we'll

14       stage generators as close as we can to that area to be

15       prepared in case they're needed.

16                 In a nutshell, AT&T is prepared.  As I said,

17       we go through a natural disaster someplace in the United

18       States every year, and so for us it's actually

19       implementing what we've learned, not so much preparing

20       for what may be coming.  And with that, I conclude.

21                 CHAIRMAN BRISÉ:  Thank you very much.

22                 Commissioner Brown.

23                 COMMISSIONER BROWN:  Thank you.  I'm quite

24       impressed with your presentation and what AT&T is doing

25       with regard to natural disaster preparation.  It's very

FLORIDA PUBLIC SERVICE COMMISSION

102

1       apparent that your company is very prepared, and I

2       appreciate you coming down and talking with us and

3       relaying what you all are doing.  And thank you again.

4                 MR. FOLLENSBEE:  You're welcome.

5                 CHAIRMAN BRISÉ:  Commissioner Edgar.

6                 COMMISSIONER EDGAR:  Thank you.

7                 Very briefly.  As I recall, after the storms

8       here in Florida approximately eight years ago, one of

9       the issues had to do with third party attachments, and

10       some -- at the time, maybe this is not the right word,

11       but at the time some confusion in some areas as to

12       ownership and responsibility and overlapping authority

13       and other things.  And I know a lot of work has been

14       done on that issue since then, some of our early

15       presenters mentioned.  So I was just wondering if you

16       could touch on that.  And from your company's

17       perspective, has that, at that time a little bit of

18       confusion, been cleared up sufficiently?

19                 MR. FOLLENSBEE:  A couple of points on that.

20       Number one, we have.  I mean, we're very clear now who

21       owns the pole, who doesn't own the pole, and what needs

22       to be done with it.

23                 One of the biggest benefits from what the

24       electrics have done also benefits us.  We attach on more

25       poles than we own.  And to the extent that the electric

FLORIDA PUBLIC SERVICE COMMISSION

103

1       industry has done a great job in hardening their

2       facilities, that means our facilities are protected as

3       well.  But on the other hand, with our facilities

4       ourselves we have continued our pole inspection program,

5       we haven't discontinued it.  We still find it to be

6       beneficial.  And so every time we do that we clearly

7       identify who owns the pole in case there's a question of

8       it.  But we're attaching to any poles that we don't have

9       ourselves, which includes the co-ops, the municipalities

10       and all that.  I haven't heard of any issues we've had

11       in recent years on that.  So I think we're in good shape

12       to know that when we need to go in and deal with a pole,

13       you know, what needs to be done.  And a lot depends on

14       what's been damaged.  I mean, if it's not the electric,

15       it's the lower part of the pole, you know, that's

16       normally us because usually the telephone cable is on

17       the bottom part of the pole and electric is on the top

18       part.

19                 COMMISSIONER EDGAR:  Thank you.  And just to

20       point out -- and I thank you, and to all of those, as I

21       mentioned, I know a lot of work has gone into that to

22       clear up some of the uncertainties and some of the maybe

23       blurred areas of responsibility and cost allocation, and

24       it's something that we haven't really had come up to my

25       knowledge as an issue here for us, and I think that

FLORIDA PUBLIC SERVICE COMMISSION

104

1       attests to, you know, the good work and cooperation that

2       has been done.  So thank you.

3                 CHAIRMAN BRISÉ:  Thank you.  And thank you for

4       your presentation this afternoon.

5                 MR. FOLLENSBEE:  Thank you.

6                 CHAIRMAN BRISÉ:  At this time we will hear

7       from Verizon Florida, Shaun McLaury.  Mr. McLaury.

8                 MR. McLAURY:  Commission and staff, thank you

9       very much for inviting Verizon here today to participate

10       in your workshop.  We always gain something out of

11       these.  It's great to hear what other companies are

12       doing, and sometimes we have those aha moments, you

13       know, and can go back and say that's something we want

14       to also do.

15                 Verizon -- basically we'll cover our Florida

16       overview today, we'll cover our emergency operation

17       structure, and then we'll talk about our 2012 strategy.

18       And a lot of what we're going to focus on today is just

19       simply what's new.  We have a lot of things we covered

20       last year, you know, with our generators and things, and

21       we won't go into that detail this year.  So it'll only

22       be what's new since last year.

23                 CHAIRMAN BRISÉ:  Thank you.  We appreciate

24       that.

25                 MR. McLAURY:  Basically we have our networks

FLORIDA PUBLIC SERVICE COMMISSION

105

1       that provide data, video, and voice service in West

2       Central Florida, so primarily six counties around the

3       Tampa Bay area.  We have over 1,700 fleet vehicles.

4       That's not much change since last year.  And a presence

5       in over 300 buildings, which is down just a few from

6       what we've had in previous years.  Most of what we've

7       taken out of the, the equation now is some

8       administrative buildings, and then a few of our work

9       centers have been consolidated into larger units.

10                 Basically our operation structure, we have a

11       region control center.  That's our local folks that

12       handle any emergency.  We have a centralized point for

13       information.  We coordinate personnel and resources.  We

14       develop our service restoration plan there, and then we

15       compile all of our travel reports and volumes.  So

16       everything is just funneled through our, our local -- we

17       used to call it emergency operations center, but now we

18       have two or three of those nationally, so it's the

19       region control center now.  But they're very dependent

20       upon us to be the first point of contact for Florida and

21       to make sure that we accurately capture and are in

22       charge of any event that's happening.

23                 We have our damage assessment group out there.

24       These are the folks that actually go in and take a look

25       at the damage.  They relay the information back to us,

FLORIDA PUBLIC SERVICE COMMISSION

106

1       help us prioritize what needs to be done.  They usually

2       follow the first responders in.  We also have teams of

3       first responders that are primarily line crew type

4       individuals.  They actually camp out with the county

5       EOCs during the storm, and then go in with their road

6       clearing crews and with their emergency responders so

7       that we can try to protect our facilities, keep them

8       from being damaged further, maybe lay them on the ground

9       to where you could drive over them, anything that we can

10       do to help facilitate entry into an area but yet keep

11       our facilities intact too.  Everyone depends on

12       communication after a storm, so we do all that we can to

13       make sure we protect it.

14                 We have our National Emergency Coordinating

15       Center.  Basically that's overall management at a

16       corporate level.  We have two different locations, one

17       is in Texas, one is in New Jersey, so we always have a

18       backup.  They basically take the information that we

19       provide, report it to our executives, and then also try

20       to deploy any resources that we may need.  Since we are

21       a large company, our primary focus on resources is

22       internally from other regions, and they're very quick to

23       offer those resources and to get them in place, as well

24       as we also send our resources to other areas.  During

25       last year it was Hurricane Irene that hit in the

FLORIDA PUBLIC SERVICE COMMISSION

107

1       northeast and we had to go up there primarily because of

2       flooding that was in the area.  We've sent crews to

3       California for wildfires, Texas for ice storms.  So

4       we're well versed in those things as well as hurricanes.

5                 Our 2012 strategy storm hardening, we also

6       have continued our pole inspection program.  We're

7       really getting toward the tail end of it.  When we

8       started our program, we concentrated heavily on our

9       coastal counties, meaning Pinellas, Pasco, Sarasota, and

10       Manatee Counties.  Those were wiped out pretty quickly.

11       Then we moved inland.  Right now we're probably more

12       than 70% complete in all of our inspections, and right

13       now of the poles that we have inspected, there's only --

14       there's 1,207 that haven't been replaced yet.  All of

15       those are in work order status and are actually in the

16       field being replaced as we speak.

17                 We actually funded our pole replacement

18       program a little bit heavier this year in anticipation

19       of moving into easier work.  When we're working with

20       power companies and doing transfers, multiple transfers

21       and things, it kind of slows things down.  It's just

22       more complicated.  Now as we move into our inland

23       counties where we've got 25 and 30 foot poles, it's

24       primarily we're the only attacher.  It moves a lot

25       faster when we find those.  So we wanted to make sure

FLORIDA PUBLIC SERVICE COMMISSION

108

1       that we were funded to replace those quickly this year.

2       And, in fact, from the time they find the pole, to go

3       through engineering, drafting, and back out to the field

4       is about ten days now on those smaller poles.

5                 We have a decreasing dependency on aerial

6       facilities.  All of our FiOS network, probably 98% of it

7       or a little bit higher percentage is all underground,

8       including the service drops as well as the terminals and

9       the mainline cables.

10                 We looked at our copper facilities out there.

11       Everything that we can take down right now we're taking

12       down, number one, to get it out of the way for storms,

13       but also, you know, we have a lot of theft with copper

14       right now, so it's just get it down, get it out of the

15       way.

16                 The real advantage to us when it comes to

17       storm restoral is if you don't have dead cables or dead

18       drops hanging in the area, you don't have to worry about

19       those.  You can get on to the customers that really need

20       the service.  So it just helps clean things up.

21                 The other thing that we're doing a lot of is

22       removing digital loop carrier units.  Back when we had

23       high field counts on cables the digital loop carrier was

24       what we had to use to help augment service for people

25       and as well as to extend the reach of our, our DSL

FLORIDA PUBLIC SERVICE COMMISSION

109

1       service.  Now then as we've lowered our field counts and

2       our cables and we've moved people over into our fiber

3       we're able to take out a number of those units and we've

4       continued a very aggressive program in removing those

5       units.

6                 The other thing we did for our carrier units

7       at the end of last year that, that have to stay in place

8       is we did a major battery replacement on those.  So when

9       you put the new batteries in, it comes with a minimum

10       five-year warranty on those batteries.  So normally they

11       last anywhere between seven and ten years before they

12       need extra work.  So we feel like that the remaining

13       DLCs are very well prepared now for the storm season as

14       far as batteries.

15                 Material, it's the same as in previous years.

16       We keep a fairly high stockpile locally.  We also have

17       all of our other Verizon facilities in other states that

18       can immediately route material to us, if needed.  And

19       then as far as poles, we have a contract with our vendor

20       to where when we've got a named storm and we forecast it

21       to hit our area, they immediately stage trucks just out

22       of state to bring into our area.  The only reason we

23       don't go ahead and bring them in is we want them

24       delivered right to the site that we need them.  So we,

25       we kind of wait until after a storm.  Then we bring the

FLORIDA PUBLIC SERVICE COMMISSION

110

1       trucks in and we drop them off and we don't have to

2       handle the material twice.

3                 Our all fiber network eliminates many of the

4       storm related issues that we have with our copper.  The

5       majority of it, of course, 98% is underground.  All of

6       our service drops are buried.  And in the past the

7       optical cable is not affected by moisture.  That's a big

8       one for us.  It's also much, much easier to restore

9       fiber cable if it is damaged versus the large pair count

10       copper cable, especially, you know, we still have a few

11       of our old paper cables.  Those can be very

12       time-consuming to restore; whereas, the fiber cable is

13       very, very quick for us, so.

14                 Another strategy for 2012, and this is kind of

15       one of the aha moments, you know, that we took away.

16       When we looked back at 2004, that was the last time that

17       our Tampa Bay area was impacted, and we were impacted by

18       three hurricanes that year.  And we took a look at our

19       damage assessment teams and how they relayed information

20       back to our region control center, how that information

21       was entered into the system, how we tracked it to make

22       sure it was dealt with, and then how we completed

23       everything out, and then how we tried to look at it

24       after the storm to see what we did right, what we did

25       wrong.  And it was, it was more of a paper process back

FLORIDA PUBLIC SERVICE COMMISSION

111

1       then, but we noticed we really hadn't done anything to

2       improve it.  So at the end of last year we embarked on a

3       program to really move us into modern day.  Part of

4       that, we put all of our technicians in the field on

5       BlackBerries.  It's kind of an interim step.  Later this

6       year we're going to start moving them onto tablets with

7       the 4G network.  This allows them a lot better access to

8       the records, but it also gives us much quicker feedback

9       from them in the field.

10                 They now have a, basically a real short form

11       that they fill out when they go out to do a damage

12       assessment that feeds back into an internal system

13       that's laid over a geographical map.  It's also now on a

14       10K grid, just like the county emergency responders use.

15       That was something that we had neglected to do in years

16       past.  So now when we talk to the counties and they tell

17       us that they're in the LL78 grid, we know exactly where

18       they're at and they'll know exactly where we are.  So

19       it's a common language for us.

20                 This, this new damage program, really excited

21       about it because it allows realtime tracking for us.

22       The moment that the technician enters the damage report,

23       it pops up on the screen in our region control center.

24       We're able to then go back in, extract reports out to

25       route it to either engineering or route it to our

FLORIDA PUBLIC SERVICE COMMISSION

112

1       dispatch for immediate dispatch.

2                 Part of our strategy also is we know that when

3       you have multiple storms hit you can kind of burn your

4       people out, especially that are in your region control

5       centers.  So on May 2nd we did an exercise with all of

6       our region control centers around the country, and that

7       whole exercise was focused on backing each other up.  In

8       other words, how can you come in and take over for them?

9       And we were recognized, Florida was recognized because

10       of our work and moving onto this platform.  I think the

11       rest of the country is going to move onto it very

12       quickly because any other region control center could go

13       in, look at our data, it's already been entered, and

14       they could status any ticket for any customer calling

15       in.

16                 The other thing we did was go onto a common

17       platform for our IPACD.  That's an integrated --

18       internet protocol automatic call distributor system.

19       Because Verizon was put together by a number of

20       companies, we have different systems in different areas.

21       Now we're all on one common platform where calls can be

22       routed very, very easily between different areas and

23       different sites.  Also since that works through

24       basically a computer, your call goes through the

25       computer as well as your data connection.  We can pick

FLORIDA PUBLIC SERVICE COMMISSION

113

1       up our computers if we think an office is in jeopardy

2       and move it to a different location, a person can plug

3       right back in and be up and running.

4                 So it was kind of a really good one for us

5       this year.  Hopefully we'll never have to use that, but

6       it's there for us.

7                 We conducted our annual emergency exercise.

8       Like I said, May 2nd was when we did our region -- our

9       national one.  We're going to do a local one in late

10       May.  It'll be right around Memorial Day.  And what we

11       want to do during the Memorial Day exercise, every

12       employee that enters damage assessment will be entering

13       fictitious reports into our system at that time.

14       Basically we're going to try to crash our system.  But

15       we want to see how it all works in a, in a non-realtime

16       environment.  But just to see how it works, how the

17       tickets are routed, whether somebody off-site in New

18       Jersey or somewhere else can status the ticket for a

19       customer calling in.  So we'll really process it all the

20       way through.

21                 We've really rebuilt our partnerships with our

22       county emergency management teams.  And, you know,

23       it's -- the longer you go without having a disaster, the

24       easier it is to find something else to do rather than

25       going to those county EOC meetings.  So those last

FLORIDA PUBLIC SERVICE COMMISSION

114

1       couple of years we've really worked hard on getting our

2       manpower staff back into the EOCs, talking to them about

3       their concerns, and then about our concerns too.

4                 Probably our biggest concern, or one of the

5       things that we learned after the 2004 hurricanes was how

6       severely we were impacted by the damage removal teams.

7       You know, when you've got the debris removal teams going

8       in and picking up everything out there, they tend to

9       bring in heavy equipment and damage whatever we have

10       alongside the road also.  So now we've developed plans

11       with all the EOCs in how we can limit that damage and

12       identify our facilities there even if it has debris

13       piled over the top of it.

14                 We also have a MERIT team that's a major

15       emergency response incident team.  This basically was a

16       team that was formed in 1993, and we had kind of a

17       nasty, I think it was an asbestos event in one of our

18       offices.  And the office went down but it was a hazmat

19       area and we couldn't get back in to work in that office.

20       So a team was formed of folks that were trained in

21       hazmat type entry.  It's -- basically it has a number of

22       members on the team from just about every specialty we

23       have, whether it be a cable splicer, a central office

24       tech, building maintenance tech, you name it, there are

25       electricians, power specialists.  Anybody that we have,

FLORIDA PUBLIC SERVICE COMMISSION

115

1       we have a special person on that team.

2                 So if we go into an area where a hazmat area

3       has been declared, they have the ability to suit up, go

4       in, and take care of our equipment, restore our network,

5       get it back online, or to keep it running during this

6       event.

7                 The one thing we noticed with this hazmat team

8       is local fire responders and hazardous materials teams

9       didn't know the capabilities of this team, they didn't

10       know the training of this team, they didn't know

11       anything about them.  And so, of course, they're going

12       to be suspicious if they come to town.  You know, do we

13       have to go in and drag this people out or what do we

14       have to do?

15                 So this year we conducted an exercise in

16       Temple Terrace in March and we invited all the different

17       county hazmat teams in to do a co-exercise with them.

18       It was just kind of interesting to see them all climbing

19       over each other's equipment, you know, and looking at

20       the stuff.  But we have a very high level of

21       communication now.  I think they're very comfortable

22       working together.  Part of that was just simply in

23       preparation for the RNC later this year.  We've got some

24       things downtown that we want to make sure are well

25       protected.

FLORIDA PUBLIC SERVICE COMMISSION

116

1                 But also when we ran our hurricane exercise

2       last year, we did a scenario kind of like what someone

3       else described where we had a significant storm surge in

4       Tampa Bay that basically crippled some of our downtown

5       buildings.  And part of what we recognized then was

6       we're kind of on the north side of the Port of Tampa and

7       we could have oil or other things that are in the

8       lobbies of our buildings now when we need access.  So

9       not only, you know, when this team came to town, we not

10       only did the exercise, we took them downtown, took them

11       through all our buildings, made sure they were well

12       versed in what needed to be worked on there should we

13       need their help.

14                 Just some pictures in the deck of this hazmat

15       team.  I always like new stuff that's out there.

16       They're very well prepared, they're very self-contained

17       with all kinds of specialized vehicles, hazmat

18       protective gear.  They have all the certifications.  All

19       of their equipment can be shipped by air.  Their intent

20       is to be anywhere they're needed within 24 hours.

21                 As you can see, they all ran their -- they all

22       use specialized suits.  I think those suits are about

23       $1,700 apiece, and they're a single-use suit, and they

24       also have a 12-month expiration date on them.  So it's

25       very costly to keep them suited up, but it's definitely

FLORIDA PUBLIC SERVICE COMMISSION

117

1       a cost that we bear willingly in order to have them

2       available.

3                 So in summary, we're continuing to invest in

4       our pole replacements.  We're nearing the end of our

5       pole replacement program.  We're now down to the part of

6       our program where it's mostly our own poles, mostly in

7       rural areas smaller poles.  The poles that we are

8       replacing, we don't go anything less than a Class 5 or

9       larger diameter pole.  In previous years, you know,

10       before 2006 we had Class 6 and Class 7 poles, so we made

11       a change to the stronger poles.

12                 We're lessening our dependency on aerial

13       facilities.  And, in fact, one of our programs this year

14       is to remove over 60,000 attachments off of poles.  So

15       that's a combination of being able to remove some of our

16       own poles as well as removing attachments off other

17       poles.

18                 We're lessening our dependency on digital loop

19       carrier.  We want to try to get as much of that out of

20       our network as possible so that we don't have to worry

21       about power for those during storms.

22                 We're implementing better damage assessment

23       communication methods.  We're very proud of our new

24       system there.  Looking forward to seeing how it works.

25       We kept our old system in place just in case we needed a

FLORIDA PUBLIC SERVICE COMMISSION

118

1       backup, but we're very, very excited to be going into

2       this system with our new damage assessment.

3                 And we're also practicing quick network

4       restoration and recovery methods.  So we've always

5       practiced that.  We probably have more emphasis on it

6       now than we've ever had.  You just, you can't be slow in

7       keeping communication flowing, especially when others

8       are depending on us.

9                 So that's what I have today.  If there's any

10       questions that I can answer for you.

11                 CHAIRMAN BRISÉ:  Thank you very much,

12       Mr. McLaury.

13                 Commissioner Brown.

14                 COMMISSIONER BROWN:  Thank you for a great

15       presentation.  We appreciate it.  I lived in the Tampa

16       Bay area in 2004, and I'm going to steal a question from

17       what our Chairman asked some of the utilities earlier.

18       If the, if the 2004 hurricane season occurred today, it

19       sounds as if Verizon is much better off today than it

20       was back in 2004.

21                 MR. McLAURY:  Absolutely.

22                 COMMISSIONER BROWN:  Okay.  Well, we

23       appreciate your presentation.  Thank you so much.

24                 MR. McLAURY:  Thank you.

25                 CHAIRMAN BRISÉ:  Any further questions or

FLORIDA PUBLIC SERVICE COMMISSION

119

1       comments.

2                 (No response.)

3                 Thank you very much for your presentation this

4       afternoon.

5                 MR. McLAURY:  Thank you.

6                 CHAIRMAN BRISÉ:  Okay.  At his time we're

7       going to hear from CenturyLink, Sandra Khazraee.

8                 MS. KHAZRAEE:  Hey, you did pretty good.

9                 CHAIRMAN BRISÉ:  All right.  Thank you.

10                 MS. KHAZRAEE:  You know, during the break I

11       got excited when I realized that this year I was not

12       going to be standing between a room full of people and

13       lunch.  I'm not sure this is any better, but maybe I got

14       excited a little too early.

15                 CHAIRMAN BRISÉ:  You're standing between us

16       and the rain, so it's okay.

17                 MS. KHAZRAEE:  That's good.  It came at a

18       perfect time.

19                 Good afternoon.  I am Sandy Khazraee on behalf

20       of CenturyLink.  And in previous years my presentation

21       has focused specifically on Florida preparation for

22       hurricane season, so this year I'm not doing that.  But

23       at the end if you have any questions of me about what

24       we've done specifically in Florida, please ask.

25                 What I want to show this year is the bigger

FLORIDA PUBLIC SERVICE COMMISSION

120

1       picture.  I want to kind of take the camera further back

2       and get a picture from 30,000 feet of our crisis

3       management.  We've designed our plans -- whoops, I went

4       the wrong way -- we've designed our plans to ensure that

5       we continue providing service to our customers in the

6       event of any significant business disruption.

7                 So, first all, a quick overview of

8       CenturyLink.  We are the third largest

9       telecommunications company in the United States, and we

10       provide broadband, voice, wireless, managed services to

11       consumers and businesses.  We are actually in 37 states.

12       And because of a recent purchase of Savvis, which is a

13       cloud infrastructure and hosted IT solutions company, we

14       have presence internationally as well.

15                 Why do we plan for disasters?  And the answer

16       is because bad things happen and we have to be prepared.

17       In this picture, I think you'll recognize at least two

18       of these.  The top left-hand side is, of course, the

19       Super Dome after Katrina, the damage that was done to

20       the roof there.  On the right-hand side is the World

21       Trade Center.  That picture was taken about three weeks

22       after 9/11, and it is a New York firefighter standing

23       there at the site.  The bottom left picture is actually

24       in our service territory in Colorado, and it was a

25       wildfire.  That's actually a picture of the air tanker

FLORIDA PUBLIC SERVICE COMMISSION

121

1       trying to put that fire out.  And we had facilities that

2       were not right there but could have been encroached on

3       by that fire.

4                 We have several plans designed to minimize the

5       opportunity of disruption to CenturyLink services and

6       they address critical internal business functions that,

7       if disrupted, would lead to service outages.

8                 So what makes a successful plan?  Well, we

9       look at threat assessment and business impact analysis

10       as we do business continuity planning.  So for hurricane

11       preparedness, that means, for instance, we keep up with

12       the forecasts, we watch the weather in realtime.  We

13       learn from history.  We are vigilant in our design and

14       construction in areas that are prone to damage from

15       hurricanes.

16                 Geographic diversity of recovery resources,

17       that's very important.  But not only are we talking

18       about geographic diversity of our actual network

19       facilities, but also of ways to get relief supplies in

20       and multiple facility routes to reroute traffic if one

21       area gets hit.

22                 Number three is multiple business resumption

23       options for each critical function.  We actually have a

24       mobile option to get critical circuits back up and

25       working.  If we lose a network operations center, we

FLORIDA PUBLIC SERVICE COMMISSION

122

1       have other network operations centers that we can

2       transfer control over to to take care of specific areas.

3       If you've got a subdivision that's been hard hit, we can

4       bring in at least a bank of payphones or bring in, you

5       know, some kind of Cells on Wheels in order to give

6       people some immediate service while we're restoring.

7                 And then routine plan reviews, updating, and

8       testing.  And we are currently updating our plans that

9       are specific to Florida.  We began that about three

10       weeks ago, and at the end of this month we will have the

11       big conference call with all the regions in Florida to

12       go through the preparedness plans and make sure that we

13       are all ready for what may come this season.

14                 Okay.  Threat assessment.  Understanding the

15       business impact.  We need to understand if one

16       particular area gets hit what might occur, what might

17       happen to our customers, what might happen to our

18       facilities.  And we have to identify what our customers

19       expect, the service level requirements they have.  We

20       have to prioritize critical functions and applications.

21       We may have customers that need their telecommunications

22       facility because they're part of the Department of

23       Homeland Security, they're hospitals, they are the EOCs,

24       any type of group that may need to respond to the, the

25       disaster at hand.  And then we focus on the risk and we

FLORIDA PUBLIC SERVICE COMMISSION

123

1       mitigate.

2                 And these pictures at the bottom are just

3       examples of how we focused on a risk and we mitigated.

4       The bottom two on the left were pictures in Colorado

5       Springs.  There was a Cottonwood Creek where severe

6       erosion was occurring, and on the left top of the

7       picture you can see a building there and that was

8       actually our central office building.  And if erosion

9       had continued to occur, it would have put our central

10       office building in danger.  So we installed some

11       portable sump pumps, we put some barriers around the

12       central office, we added some additional fuel tanks, we

13       diversified our fiber runs out of that building.

14                 Another example is on the right, and that was

15       an area where there was a dam that might possibly --

16       well, it had a leak.  And so because of that the water

17       level was not allowed to be as high behind the dam as it

18       had been previously, which meant flooding could occur

19       downstream.  We were downstream.  That was our office.

20       And that's, you can't tell it, but that black thing in

21       front is a six-foot barrier wall that we had to install.

22                 An example in Florida where we've done that is

23       in, for instance, in Shell Point.  After the '05,

24       '04/'05 hurricanes we installed a digital loop carrier

25       on a platform 20 feet up because we learned the hard way

FLORIDA PUBLIC SERVICE COMMISSION

124

1       that storm surge would take out the equipment that we

2       had that was closer to ground level.  We also knew that

3       when you put something 20 feet up and you've got a

4       hurricane coming in, you have the possibility of wind

5       damage.  So we had to find a low profile cabinet to keep

6       it as short as we could while having it 20 feet up in

7       the ground [sic].  And that's the type of thing that we

8       do as we assess and then mitigate.

9                 Geographic diversity.  This slide just shows

10       you some of the main routes that we have for carrying

11       calls, data through our network.  That even includes

12       Europe and Asia Pacific.  But one point I want to make

13       on this slide is that it's not just geographic

14       diversity.  There are other types of diversity, and

15       those include having mutual support agreements with

16       other companies, having remote work arrangements, having

17       third party agreements with other companies to help us

18       carry traffic or to provide people or equipment to us in

19       time of need.

20                 Business resumption.  Just briefly, these two

21       pictures, the one on the top right is our Savvis center

22       in Tokyo, Japan, just shortly after the earthquake and

23       tsunami last year.  And because we didn't sustain

24       anything but minor damage, we were able to be up and

25       online fairly quickly after that event and continue to

FLORIDA PUBLIC SERVICE COMMISSION

125

1       handle traffic internationally.

2                 The lower left is a building in Des Moines,

3       Iowa.  And on Saturday, January 22nd, of last year there

4       was a fire on the 4th floor of that building at 3:22 in

5       the morning.  Because it was a Saturday, early morning,

6       there were only eight people in the building.  They got

7       out with no, no damage, no injury.  They were evacuated

8       safely.  But the third and fourth floors were left

9       uninhabitable.  We had 260 employees on those two floors

10       who handled critical circuits for our critical circuit

11       orders for our customers.  By Monday morning at 9:00 we

12       had those 260 employees in a building a couple of blocks

13       away set up and taking orders from customers.

14                 Other resources.  We have a lot of resources

15       full-time in the company.  We also have part-time

16       resources.  And then we get resources from all sorts of

17       outside agencies.  You can see a lot of them on this

18       slide.  I'm not going to cover all of that.  But just to

19       tell you we have mutual aid agreements with two major

20       telecom carriers to provide mutual support in the event

21       of a disaster.  We have both provided and received

22       support as a result.

23                 We have disaster recovery trailers that I

24       mentioned, and that's a picture of one in the upper

25       right-hand corner.  We own several -- seven mobile

FLORIDA PUBLIC SERVICE COMMISSION

126

1       switching trailers that can be rapidly deployed.  We

2       have both commercial power and onboard general -- diesel

3       generator on that.

4                 Plan reviews, updating, and testing.  And what

5       I want to say on here, on this slide is that we've got a

6       disaster preparedness staff that is full-time.  They

7       oversee and they support all elements of our corporate

8       program of disaster preparedness.  That staff holds

9       certifications, graduate degrees, they have experience

10       in telecom operations and IT operations, so they're

11       highly qualified.

12                 Under them we have six regional teams.

13       They're led by a regional director.  They have

14       representation from all of our critical business and

15       support units at the local level.  Those teams are

16       activated whenever there's an event that has the

17       potential to affect one or more business units.  Under

18       that we have crisis management teams and our, all of our

19       business units are represented on those teams.  And

20       those are the teams that would send out the damage

21       assessment and rapid response teams at the end of a

22       hurricane in Florida.

23                 We have command centers that operate 24 hours

24       a day, seven days a week, 365 days a year.  This is a

25       picture of one that we have in the central part of the

FLORIDA PUBLIC SERVICE COMMISSION

127

1       country.

2                 We have a number of them.  And as I mentioned

3       earlier, if one is unable to control, we can transfer

4       control to another one.

5                 Service restoration priorities.  I alluded to

6       this earlier that we have critical customers who need

7       their service restored first following a disaster.  We

8       also participate in the national communications system

9       of the federal government, which has actually priority

10       levels for restoration.  And customers who need it can

11       sign up for that service and then they are given the

12       priorities you see on this chart to be restored in that

13       order.

14                 That is my planned presentation.  And if you

15       have any questions, I'd be happy to address them.

16                 CHAIRMAN BRISÉ:  Commissioners, any further

17       questions?

18                 (No response.)

19                 Thank you very much for your presentation this

20       afternoon.

21                 I don't know if Commissioners have any

22       comments they would like to make before we close this

23       afternoon.

24                 (No response.)

25                 Well, I want to thank all of the presenters

FLORIDA PUBLIC SERVICE COMMISSION

128

1       this afternoon.  I think that this workshop has been

2       quite helpful and informational.  I feel fairly

3       confident that every Floridian, regardless of where you

4       live in the state, that we are better prepared this year

5       than we were last year, and much better prepared than

6       the last named storm that we had in the state, both from

7       the electric sector and the telecommunications sector.

8       And I trust that if we all work together, that if, God

9       forbid, that we do have a storm this year, that we will

10       fare better this year than we have fared in the past.

11                 Staff, is there anything else that we need to

12       handle at this time?

13                 (No response.)

14                 Seeing that that is the case, if there's

15       nothing else, with that we adjourn.  Thank you very much

16       for your participation this afternoon.

17                 (Proceeding adjourned at 4:45 p.m.)

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

129

1       STATE OF FLORIDA   )

:     CERTIFICATE OF REPORTER

2       COUNTY OF LEON     )

3

4             I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing

5       proceeding was heard at the time and place herein

stated.

6

IT IS FURTHER CERTIFIED that I stenographically

7       reported the said proceedings; that the same has been

transcribed under my direct supervision; and that this

8       transcript constitutes a true transcription of my notes

of said proceedings.

9

I FURTHER CERTIFY that I am not a relative,

10       employee, attorney or counsel of any of the parties, nor

am I a relative or employee of any of the parties'

11       attorneys or counsel connected with the action, nor am I

financially interested in the action.

12

DATED THIS _____ day of _____________________,

13       2012.

14

15                   ________________________________

LINDA BOLES, RPR, CRR

16                  FPSC Official Commission Reporter

(850) 413-6734

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION