240

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

DOCKET NO. 010503-WU

3

In the Matter of:

4

APPLICATION FOR INCREASE IN WATER

5   RATES FOR SEVEN SPRINGS SYSTEM IN

PASCO COUNTY BY ALOHA UTILITIES, INC.

6   _____________________________________/

7

ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

8                 A CONVENIENCE COPY ONLY AND ARE NOT

THE OFFICIAL TRANSCRIPT OF THE HEARING,

9            THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

10                              VOLUME 3

11                        Pages 240 through 369

12

PROCEEDINGS:        HEARING

13

BEFORE:             CHAIRMAN BRAULIO L. BAEZ

14                       COMMISSIONER J. TERRY DEASON

COMMISSIONER RUDOLPH "RUDY" BRADLEY

15                       COMMISSIONER CHARLES M. DAVIDSON

COMMISSIONER LISA P. EDGAR

16

17   DATE:               Tuesday, March 8, 2005

18

TIME:               Commenced at 9:30 a.m.

19                       Concluded at 6:25 p.m.

20

PLACE:              Betty Easley Conference Center

21                         Hearing Room 148

4075 Esplanade Way

22                       Tallahassee, Florida

23   REPORTED BY:        JANE FAUROT, RPR

Official FPSC Reporter

24                       (850) 413-6732

25   APPEARANCES:        (As heretofore noted.)

FLORIDA PUBLIC SERVICE COMMISSION

241

1                              I N D E X

2                              WITNESSES

3

NAME:                                             PAGE NO.

4

JOHN R. SOWERBY

5

Direct Examination by Mr. Jaeger               243

6        Prefiled Direct Testimony Inserted             245

Cross Examination by Mr. Wharton               255

7        Redirect Examination by Mr. Jaeger             263

Cross Examination by Mr. Wood                  263

8

9   V. ABRAHAM KURIEN

10        Continued Cross Examination by Mr. Jaeger      270

11

DAVID W. PORTER, P.E.

12

Direct Examination by Mr. Deterding            282

13        Prefiled Direct Testimony Inserted             284

Cross Examination by Mr. Beck                  307

14        Cross Examination by Mr. Wood                  313

Cross Examination by Mr. Jaeger                       319

15        Redirect Examination by Mr. Deterding                 330

Recross Examination by Mr. Jaeger                     333

16

17   V. ABRAHAM KURIEN

18        Prefiled Rebuttal Testimony Inserted                  337

19

DAVID W. PORTER, P.E.

20

Prefiled Rebuttal Testimony Inserted                  361

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

242

1                              EXHIBITS

2   NUMBER:                                      ID.    ADMTD.

3

1-19                                                 289

4

23        VAK 19 through 27                  336     336

5

6

7

8

9

10

11

CERTIFICATE OF REPORTER                           369

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

243

1                         P R O C E E D I N G S

2             (Transcript follows in sequence from Volume 2.)

3             CHAIRMAN BAEZ:  We'll go back on the record.  We have

4   Witness Sowerby.

5             Mr. Sowerby, will you stand up and raise your right

6   hand.

7             (Witness sworn.)

8             CHAIRMAN BAEZ:  Mr. Jaeger.

9                        JOHN R. SOWERBY, P.E.

10   was called as a witness on behalf of the Commission Staff, and

11   having been duly sworn, testified as follows:

12                         DIRECT EXAMINATION

13   BY MR. JAEGER:

14        Q    Mr. Sowerby, please state your name and business

15   address for the record.

16        A    John Sowerby, Florida Department of Environmental

17   Protection, 2600 Blair Stone Road, Tallahassee, Florida.

18        Q    And in what capacity are you employed by DEP?

19        A    I'm a professional engineer in the drinking water

20   program.

21        Q    Have you prefiled direct testimony in this docket

22   consisting of six pages?

23        A    Yes, I have.

24        Q    Do you have any changes or corrections to your

25   testimony?

FLORIDA PUBLIC SERVICE COMMISSION

244

1        A    No.

2        Q    No?

3        A    No.

4        Q    If I asked the same questions today, would your

5   answers remain the same?

6        A    Yes.

7             MR. JAEGER:  Chairman, may we have Mr. Sowerby's

8   testimony inserted into the record as though read.

9             CHAIRMAN BAEZ:  Without objection show the testimony,

10   that will be the direct testimony of John Sowerby, entered into

11   the record as though read.

12             MR. JAEGER:  And there were no exhibits.

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

251

1             MR. JAEGER:  I tender Mr. Sowerby for cross.

2             CHAIRMAN BAEZ:  Thank you, Mr. Jaeger.

3             And I'm not quite sure how to do this one, but we can

4   start with Mr. Beck.

5             MR. BECK:  Thank you, Mr. Chairman.

6                          CROSS EXAMINATION

7   BY MR. BECK:

8        Q    Good afternoon, Mr. Sowerby.

9        A    Good afternoon.

10        Q    I would like to ask you a few questions to begin with

11   on Rule 62-555.315(5) that you refer to in your testimony.  At

12   Page 3 of your testimony between Lines 12 and 15 you state that

13   the Department has a fairly new rule, and give the rule number,

14   requiring that applicants for a construction permit to connect

15   a new or altered well to a community water system provide

16   appropriate treatment as necessary to reduce total sulfide in

17   the water from the new or altered well to less than .3

18   milligrams per liter, is that right?

19        A    That's right.

20        Q    You also at Page 5 of your testimony, Lines 6 through

21   8, you state that the rule requires that appropriate treatment

22   be provided to reduce total sulfide in the water from a new or

23   altered well if the total sulfide in the raw water from the

24   well equals or exceeds .3 milligrams per liter, is that right?

25        A    That's right.

FLORIDA PUBLIC SERVICE COMMISSION

252

1        Q    I passed out an exhibit, a cross-examination exhibit

2   that is a copy of the rule.  Do you have that there?

3        A    Yes, I do.

4        Q    Could you turn to Subpart 5 of the rule?

5        A    All right.

6        Q    First of all, this rule only applies to new wells

7   after August 28th, 2003, is that right?

8        A    New or altered wells, yes, sir.

9        Q    So it doesn't apply to the wells that Aloha is

10   currently using, is that right?

11        A    Assuming that they existed prior to that date no, it

12   would not apply.

13             COMMISSIONER BRADLEY:  Excuse me.

14             CHAIRMAN BAEZ:  Hold on, Mr. Sowerby.  I want to

15   clear up something in my mind.  Would you define what an

16   altered well is?  Mr. Beck, I'm sorry, I want to --

17             THE WITNESS:  We would consider an altered well as

18   one that is changing the depth, changing the location where the

19   water was being withdrawn which could, therefore, change the

20   quality of the water.

21             COMMISSIONER BRADLEY:  Okay.  Thank you.

22             CHAIRMAN BAEZ:  Go ahead, Mr. Beck.

23   BY MR. BECK:

24        Q    And the rule requires them to measure, among other

25   things, sulfide, or take a sample in the new or altered well,

FLORIDA PUBLIC SERVICE COMMISSION

253

1   does it not?

2        A    Yes, sir.

3        Q    And if the total sulfide equals or exceeds .3

4   milligrams per liter in the raw water, it requires certain

5   items, does it not?

6        A    That's correct.

7        Q    And what it does, it requires the removal of the

8   total sulfide as necessary, is that right?

9        A    That's correct.

10        Q    And it also says that direct chlorination shall not

11   be used to remove, i.e., oxidize .3 milligrams per liter or

12   more of total sulfide unless the elemental sulfur formed during

13   chlorination is removed, is that right?

14        A    That's correct.

15        Q    What is the concern of the rule that requires removal

16   of the sulfur?

17        A    Let me start by mentioning this.  This rule is a

18   product of an interagency copper pipe corrosion project which I

19   was not a direct part of.  So I cannot say for certainty what

20   all the thought process was in that project.  But elemental

21   sulfur, the concern is that that can be converted back to

22   hydrogen sulfide, or reduced back to hydrogen sulfide leading

23   to potential problems in black water.

24        Q    So the rule doesn't require or doesn't prohibit

25   chlorination, it just requires removal of the sulfur if it

FLORIDA PUBLIC SERVICE COMMISSION

254

1   exceeds certain levels in the raw water, is that right?

2        A    That's correct.

3        Q    With respect to Aloha, have you read the transcripts

4   from this case, for example, the customer proceedings in this

5   case?

6        A    No, I have not.

7        Q    Have you reviewed customer complaints about Aloha to

8   the Public Service Commission?

9        A    No, I have not.

10        Q    Have you seen any of the black water that customers

11   have reported?

12        A    No, I have not.

13        Q    Do you have any specific knowledge related to Aloha

14   Utilities as opposed to just general knowledge about the rules?

15        A    No, I do not.

16        Q    With respect to Aloha's compliance with DEP rules,

17   did you look at any of the source materials regarding their

18   compliance with DEP rules?

19        A    No, I did not look directly at the data.  I asked our

20   district office about the compliance status and was given

21   information from that office.

22        Q    You simply asked them are they in compliance, and

23   they told you that they were?

24        A    That's correct.

25             MR. BECK:  That's all I have.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

255

1             CHAIRMAN BAEZ:  Mr. Wharton, do you have questions?

2                          CROSS EXAMINATION

3   BY MR. WHARTON:

4        Q    Good afternoon, Mr. Sowerby.

5        A    Good afternoon.

6        Q    With regard to the questions that Mr. Beck was just

7   asking you about determining that Aloha is in compliance with

8   DEP's rules, is that what you would normally do if you were

9   trying to learn that kind of information, contact your people

10   in the field?

11        A    Yes, it is.

12        Q    Or the field offices?

13        A    Yes, it is, Tallahassee district -- well, our

14   day-to-day compliance, enforcement, data-keeping, data-entry is

15   all done at our district offices, or in the case of ten

16   counties, it is the county health department.

17        Q    Sir, you say in your testimony that DEP does not have

18   a rule on hydrogen sulfide, other than the one you have been

19   describing for new or altered wells, correct?

20        A    That's correct.

21        Q    Are you aware that one of the issues in this case is

22   whether the Commission should establish an MCL for Aloha on

23   hydrogen sulfide?

24        A    I'm vaguely aware from just having been sitting in

25   here this afternoon.

FLORIDA PUBLIC SERVICE COMMISSION

256

1        Q    Isn't it true that you have been intimately involved

2   over the course of your career with the implementation of new

3   rules at DEP or the changing of existing rules?

4        A    Yes, I have.

5        Q    Now, you have been with the department 12 years and

6   in your time DEP has never chosen to establish an MCL without

7   it coming from EPA first, correct?

8        A    I have been with the department for about 20 years.

9   I have been with the drinking water program for over 12.  And

10   while with the drinking water program, that is correct, we have

11   not ever attempted to promulgate an MCL that did not originate

12   from EPA.

13        Q    EPA goes through a very involved process before it

14   determines that a particular MCL should be established, doesn't

15   it?

16        A    Yes, it does.

17        Q    Isn't it true that they look at the contaminants on

18   the unregulated list, and they move it to their monitoring

19   list, they do health studies, they look at laboratory tests,

20   and that they also consider cost/benefits?

21        A    Yes, sir, particularly with regard to the primary

22   drinking water standards, yes, sir.

23        Q    Can it take years from its initiation at EPA until a

24   particular MCL is put into place?

25        A    Yes, it can.

FLORIDA PUBLIC SERVICE COMMISSION

257

1        Q    Just so the record is clear, Mr. Sowerby, do you

2   agree that there is no DEP rule which would require Aloha in

3   any way, shape, or form to meet a goal, action level, MCL, or

4   anything else of 0.1 mg/L of hydrogen sulfide in their water?

5        A    That's correct.

6        Q    There is no DEP rule which requires Aloha to meet any

7   particular level of hydrogen sulfide at any point in their

8   system, correct?

9        A    That is correct.

10        Q    Do you have any idea how many water wells in the

11   State of Florida were grandfathered under the rule that Mr.

12   Beck talked to you about?

13        A    No, I do not.

14        Q    Do you think it is over 10,000?

15        A    I couldn't say.

16        Q    Do you think thousands would be a safe bet?

17        A    I couldn't say.  I have no idea what that number is.

18        Q    Let's try this.  Do you have any idea how many

19   drinking water wells are in the State of Florida?

20        A    I believe it's -- public water system wells, I

21   believe it is somewhere in the neighborhood of 10,000.

22        Q    And all of those wells that either existed before the

23   date you talked about in 2003 or have not been altered since

24   that date are not covered under that rule, correct?

25        A    That's correct.  The rule applies only to community

FLORIDA PUBLIC SERVICE COMMISSION

258

1   water system wells.  And the number I gave you is total public

2   water system wells.  So there is about 10,000 public water

3   system wells out there.  As far as how many are community water

4   system wells, I really don't even have a guess.

5        Q    What is the difference between those two?

6        A    A public water system is a water system that serves

7   water to the public, 25 or more people 60 days or more out of

8   the year.  Public water systems are then divided up into three

9   subsets.  There is community water systems which serves 25 or

10   more year-round residents, or 15 or more service connections to

11   year-round residents.  And those are the typical water systems

12   that most people think of when they hear the word utility.

13   There are also, though, noncommunity water systems which then

14   are divided into two categories, nontransient noncommunity and

15   transient noncommunity water systems.  I don't know if you want

16   me to go into an explanation of those here.

17        Q    No.

18        A    Thank you.

19        Q    Sir, you agree, don't you, that the primary drinking

20   water standards are designed to protect public health?

21        A    Yes, sir.

22        Q    And the secondary drinking water standards are geared

23   toward aesthetic qualities in providing water that is

24   aesthetically acceptable?

25        A    Yes, sir.

FLORIDA PUBLIC SERVICE COMMISSION

259

1        Q    Isn't it true that it is your opinion that the

2   primary and secondary drinking water standards that apply to

3   utilities in Florida are adequate to safeguard the health of

4   water consumers?

5        A    Yes.

6        Q    And it is also your opinion, isn't it, that if DEP

7   felt there was some inadequacy in a current primary or

8   secondary drinking water standard, they would be trying to do

9   something about that?

10        A    That's correct.

11        Q    And you are not aware, are you, of DEP currently

12   contemplating imposing or establishing any standard with regard

13   to hydrogen sulfide?

14        A    No, we are not.

15        Q    And to your knowledge neither is EPA, correct?

16        A    Not to my knowledge.

17        Q    Sir, it is your testimony that Aloha does

18   consistently maintain the chlorine residual to the level

19   required by DEP, correct?

20        A    Yes, based on information I've gotten from the

21   district office.

22        Q    Now, hydrogen sulfide cannot exist in the presence of

23   free chlorine, can it?

24        A    Not to my understanding, no.

25        Q    So if free chlorine is present at any particular

FLORIDA PUBLIC SERVICE COMMISSION

260

1   point in the system, there cannot be hydrogen sulfide at that

2   particular test point, correct?

3        A    That would be my understanding, yes, sir.

4        Q    And part of the testing for free chlorine that DEP

5   requires is testing at remote points in the system, correct?

6        A    We require that systems serving more than 3,300 test

7   five days a week at a remote point in the system.  It is a

8   single point.

9        Q    Do you know how many points Aloha tests at?

10        A    No, I do not.

11        Q    Aloha is also in compliance with DEP's secondary

12   standards for odor, correct?

13        A    Again, based on my information from the district

14   office.

15        Q    Isn't it true, sir, that the majority of sampling

16   points for contaminants regulated by DEP are tested at the

17   entry points to a water system's distribution system?

18        A    The majority of them are tested at the entry point.

19   There are some that are tested in the distribution system.

20        Q    There were several questions in your prefiled

21   testimony to the effect of would DEP have an objection if Aloha

22   did a certain thing.  Do you recall those lines of questions?

23        A    I believe you're talking about the questions relating

24   to sample frequency and so forth, and that's correct, DEP would

25   have no objections to a utility sampling above and beyond the

FLORIDA PUBLIC SERVICE COMMISSION

261

1   minimum requirements in our rules.

2        Q    Isn't it true, sir, so that so long as a given

3   utility is meeting DEP's rules for the testing of contaminants,

4   DEP would never be concerned if a utility was taking more tests

5   than were required, or was taking those tests in a greater

6   number of locations than was required, or was testing for

7   contaminants that they weren't required to test for, DEP would

8   have no objection in those cases?

9        A    That is correct, we would have no objection.

10        Q    In fact, DEP doesn't have any jurisdiction to tell a

11   utility not to do those things, does it?

12        A    That is correct.

13        Q    Sir, isn't it true that you believe that the odor and

14   color tests which are part of the secondary standards are used

15   as an indirect measure of the level of hydrogen sulfide in the

16   water?

17        A    Yes.  Especially the odor test, yes.

18        Q    And those tests are required at the entry point from

19   the water plant into the distribution system, correct?

20        A    That's where all tests for secondary standards are

21   taken, yes.  The samples, yes.

22        Q    To your knowledge, sir, isn't it true that DEP has

23   performed chlorine residual tests in Aloha's water in the past,

24   and all of those tests have shown Aloha to be in compliance?

25        A    I'm sure that our inspectors have done testing of

FLORIDA PUBLIC SERVICE COMMISSION

262

1   chlorine residual in that system in the past.  I cannot say

2   with 100 percent certainty that they all showed compliance.  I

3   haven't reviewed that data.

4        Q    But you are not aware of any that were out of

5   compliance?

6        A    No, I'm not.

7        Q    And, isn't it true, sir, you have no knowledge that

8   Aloha has failed to properly perform the tests that DEP

9   requires Aloha to engage in?

10        A    That is correct.

11             MR. WHARTON:  That's all we have, Mr. Chairman.

12             CHAIRMAN BAEZ:  Commissioners, do you have any

13   questions at this point?

14             COMMISSIONER BRADLEY:  I have one question.

15             CHAIRMAN BAEZ:  Go ahead, Commissioner.

16             COMMISSIONER BRADLEY:  What would the rationale be

17   for DEP testing some water at the well and some within the

18   transmission system, why is that?  Why is it that you do

19   some -- why is there a difference?  Why do you have two

20   methods?

21             THE WITNESS:  I believe you are asking why do we

22   sample sometimes at the entry point to the distribution system

23   versus in the distribution system, is that correct?

24             COMMISSIONER BRADLEY:  Exactly.

25             THE WITNESS:  In general, we require testing for

FLORIDA PUBLIC SERVICE COMMISSION

263

1   chlorine residual, disinfection by-products, and coliform

2   bacteria in the distribution system.  Those things tend to or

3   may change throughout a distribution system versus most of the

4   other water quality parameters.  There would be, in most cases,

5   no reason to believe that they would change, so that's why they

6   are sampled at the entry point only.  Have I answered your

7   question?

8             COMMISSIONER BRADLEY:  Yes.

9             CHAIRMAN BAEZ:  Mr. Jaeger, redirect.

10             MR. JAEGER:  I just have one redirect question.

11                        REDIRECT EXAMINATION

12   BY MR. JAEGER:

13        Q    Aloha is going to chloramines and hydrogen peroxide

14   possibly.  Would that place them under this new rule?

15        A    New rule meaning 62-555.315(5)?

16        Q    Right.  New wells or altered wells.

17        A    No, it would not.

18             MR. JAEGER:  Thank you.  That's all I have.

19             MR. WOOD:  Mr. Chairman, I have some questions.

20             CHAIRMAN BAEZ:  Mr. Wood, I'm sorry if I skipped over

21   you at the time.  You go ahead and ask your questions, sir.

22                          CROSS EXAMINATION

23   BY MR. WOOD:

24        Q    Mr. Sowerby, on your testimony on Page 2, 12 through

25   22, you talk about Aloha being in compliance in the lead and

FLORIDA PUBLIC SERVICE COMMISSION

264

1   copper rule.  If the water coming out of the taps of a goodly

2   number of consumers in the Aloha district is as black as the

3   top of the coffee pot there in front of you, how can they be in

4   compliance with the copper rule?

5             MR. WHARTON:  Objection, the question is leading.

6             MR. BECK:  Leading questions are allowed.

7             MR. WHARTON:  Well, maybe it is a hypothetical about

8   the water being as black as a --

9             MR. WOOD:  If I can excused, Mr. Chairman, I will go

10   out to the car --

11             CHAIRMAN BAEZ:  I'm going to allow the question, Mr.

12   Wharton.  Do you want to restate it?  Mr. Sowerby, do you need

13   Mr. Wood to restate it?

14             MR. WOOD:  If you want, I can go out to the car and I

15   can get a bottle of the black water and bring it in here.

16             CHAIRMAN BAEZ:  That is not going to be necessary.  I

17   think if you allow Mr. Sowerby to have a crack at the question,

18   we may get what we need.

19             THE WITNESS:  Well, I'm not sure I have any way to

20   answer that.  To me it is a hypothetical question.  Based on

21   the samples that we are requiring, they meet the action level.

22   I don't know how to answer that.

23   BY MR. WOOD:

24        Q    In the testing for lead and copper, why are so many

25   houses excluded?

FLORIDA PUBLIC SERVICE COMMISSION

265

1        A    There are specific criteria that have to be met for

2   sampling sites.  The lead and copper rule is not my area of

3   expertise, but there are a number of criteria that have to be

4   met as far as when the house was constructed, whether or not it

5   has point-of-entry point-of-use devices.  Point-of-entry

6   devices will exclude the site from being an acceptable site and

7   so forth.

8        Q    In what has brought this here, and we talked earlier

9   about the exclusion of certain territories under Aloha, under

10   another docket, based on what I look at there has never been a

11   house in those areas that has been tested.  Why would that be?

12        A    You're asking me to guess about things that are not

13   within my knowledge base.  I have not looked at their sampling

14   plans.  I'm not familiar with the service area.  I cannot

15   answer that question.

16        Q    But shouldn't the DEP rules take into consideration

17   what is going on in current houses so that things like the lead

18   and copper rule -- we say that there is no health problem,

19   supposedly the copper is a lead problem or a health problem.

20   Why aren't we doing something about it?

21        A    Again, my understanding is they are meeting the lead

22   and copper rule.

23        Q    But if they are not testing, and that is where you

24   have the copper, are they meeting the rule or is the rule so

25   loose that anybody can skip through it?

FLORIDA PUBLIC SERVICE COMMISSION

266

1        A    My understanding is they are testing at sampling

2   locations that have been identified in a sampling plan prepared

3   in accordance with our rules.

4        Q    Well, up through 2001, and then they got a three-year

5   extension, if you look at all the Xs that I have on this map,

6   and you look at this area down here with no Xs, this area down

7   here with no Xs is what has petitioned to be let go from Aloha.

8             MR. WHARTON:  Mr. Chairman, I object.  We are getting

9   into testimony and evidence now.

10             CHAIRMAN BAEZ:  Hang on.  Mr. Wood, first of all I

11   need to know what it is you are pointing at, first of all.  Do

12   you want to tell me?

13             MR. WOOD:  Tell you, yes.

14             CHAIRMAN BAEZ:  Well, let's tell everybody.

15             MR. WOOD:  Okay, everybody.  I have a map here of

16   where the tests were conducted.

17             CHAIRMAN BAEZ:  And where did you find that map?

18             MR. WOOD:  I got this information from the Southwest

19   Water District down in Tampa.  I didn't get the map.  I got all

20   the information, and I made up the map from the information

21   that was supplied from the Southwest Water District of the

22   tests that were turned in by Aloha.

23             CHAIRMAN BAEZ:  Oh, Mr. Wood.

24             MR. WHARTON:  All I would ask, Mr. Chairman, is that

25   if he is going to lay this as a hypothetical, maybe he can do

FLORIDA PUBLIC SERVICE COMMISSION

267

1   it.  He is assuming facts not in evidence.

2             CHAIRMAN BAEZ:  Here is the problem.  Here is the

3   problem I have is that you are referring to something that

4   hasn't been verified and it hasn't been admitted as evidence.

5   I have my doubts as to whether it could be honestly, Mr. Wood.

6   But if you want to try to pose your questions in a manner that

7   doesn't involve whatever facts you believe you know about

8   Aloha, then maybe you can get some answers that we can use.

9   BY MR. WOOD:

10        Q    The big answer that I'm looking -- the big answer

11   that I am looking for is if certain houses that have the

12   problem are not being tested, why are the requirements of such

13   that those houses are not being tested?  And statistically,

14   what is the relationship or the correlation between what is

15   being tested and what is actually happening?

16        A    I do not understand the question.

17             CHAIRMAN BAEZ:  Can I try and --

18             MR. WOOD:  Okay.

19             CHAIRMAN BAEZ:  There seems to be a question as to

20   whether the fact that you only sample -- I mean, your tests are

21   not of all the houses, all the homes in a particular area.  I

22   mean, it couldn't be.

23             THE WITNESS:  That's correct.

24             CHAIRMAN BAEZ:  For so many reasons.  I think Mr.

25   Wood is trying to ascertain whether any of the houses that at

FLORIDA PUBLIC SERVICE COMMISSION

268

1   least purportedly have the problem don't seem to be in the

2   sample that you test. I honestly don't know if there is an

3   answer to that, frankly, but --

4             THE WITNESS:  There may be, but I'm not privy to all

5   of those details.  I do not know the details of the system.  I

6   have not seen their sampling plan.  I have not seen their

7   results.  So it is difficult.  But the only thing I can tell

8   you is there are certain criteria that you have to meet to be

9   an eligible tier one sampling site.  And perhaps none of these

10   houses meet the criteria.  I do not know.

11             CHAIRMAN BAEZ:  And just for the record, you have

12   referred a couple of times to sampling plans.  The assumption

13   is, or is it your knowledge that whatever sampling plans have

14   been submitted to DEP have been approved, are in accordance

15   with your rules?

16             THE WITNESS:  That is correct.

17             CHAIRMAN BAEZ:  Whatever the result of those are, but

18   the sampling plans have to get approved beforehand?

19             THE WITNESS:  Right.  They have to submit a sampling

20   plan.  And, again, that is all reviewed and evaluated at our

21   district level.

22             CHAIRMAN BAEZ:  All right.  Mr. Wood, do you have any

23   other questions?

24             MR. WOOD:  That's all.

25             CHAIRMAN BAEZ:  Thank you, sir.

FLORIDA PUBLIC SERVICE COMMISSION

269

1             Mr. Jaeger, you had already had redirect.

2             MR. JAEGER:  That's the only one I had.  I had the

3   one question.

4             CHAIRMAN BAEZ:  All right.  Then let's handle some

5   exhibits if we have any.

6             MR. JAEGER:  Mr. Beck, did you identify that Rule

7   62.555 as the next exhibit.

8             CHAIRMAN BAEZ:  I don't know that we need that.

9             MR. BECK:  I didn't ask that it be marked.

10             CHAIRMAN BAEZ:  And I don't think that we need to.

11             Mr. Jaeger, I have Exhibit 19 that hasn't.  I don't

12   know if you ever moved that.

13             MR. JAEGER:  No, I was right in the middle of

14   starting Dr. Kurien, I was going to get him to identify it, to

15   confirm it, and I got cut off in the middle of Dr. Kurien.

16             CHAIRMAN BAEZ:  Mr. Sowerby doesn't have any

17   exhibits, correct?

18             MR. JAEGER:  No.

19             CHAIRMAN BAEZ:  Mr. Sowerby, thank you for waiting.

20   You are excused.

21             THE WITNESS:  Thank you.

22             CHAIRMAN BAEZ:  Are we ready for Dr. Kurien again?

23   All right.

24             Doctor Kurien, you are still under oath, and I think

25   we were at a point where Mr. Jaeger was going to cross.

FLORIDA PUBLIC SERVICE COMMISSION

270

1             MR. JAEGER:  That's correct.

2                          V. ABRAHAM KURIEN

3   resumed the stand as a witness on behalf of OPC/Customers, and,

4   having been previously sworn, testified as follows:

5                     CONTINUED CROSS EXAMINATION

6   BY MR. JAEGER:

7        Q    Dr. Kurien, I think I started to ask you about that

8   map I had provided.  Have you had a chance to look at that?

9        A    Yes.

10        Q    The map of the Seven Springs Subdivision showing the

11   wells and the water treatment plant at Mitchell Road?

12        A    That is correct.

13        Q    In your opinion, does that map accurately reflect

14   Aloha's service territory?

15        A    I don't know the location of all the wells.  I know

16   Wells 8 and 9 quite well.  But, in general, the map is correct.

17        Q    Dr. Kurien, it is my understanding that when hydrogen

18   sulfide is oxidized that it can form either elemental sulfur or

19   sulfate, is that correct?

20        A    That's correct.

21        Q    And it is your opinion that sulfate is not a real

22   problem, is that also correct?

23        A    No.  Sulfate can be a problem if there is bacteria

24   that can convert it back to hydrogen sulfide.

25        Q    But sulfur is a bigger problem?

FLORIDA PUBLIC SERVICE COMMISSION

271

1        A    Sulfur can cause problems for two reasons.  One

2   because being another sulfur compound it can be reduced to

3   hydrogen sulfide, just like sulfate.  Also, sulfur being

4   colloid, that is it floats around in the solution, can act as

5   what is called a nidus, a hiding place for bacteria.  And this

6   has been referred to by Mr. Porter and Doctor Levine in their

7   writings.

8        Q    Under what conditions will sulfate form when you are

9   using chlorination as opposed to sulfur?  Could you just

10   explain that process real quickly.

11        A    The oxidation of hydrogen sulfide occurs in two

12   steps.  Depending upon the amount of chlorination that is

13   available, it can go to step number one, which is the

14   production of elemental sulfur.  And then if there is adequate

15   amount of chlorination, it can go to sulfate.  But in most

16   underground water there are other substances that undergo

17   oxidation when chlorine is added.  So in reality, you can never

18   reduce 100 percent sulfate.  There will always be elemental

19   sulfur when chlorination is used.

20        Q    And what is this role of sulfur reducing bacteria?

21   You say it can hide in the sulfur, or is that something else?

22        A    Yes, it can hide in any floating matter within the

23   liquid medium of water.

24        Q    I believe in your testimony you talk about Well

25   Number 9, and I'm referring to its chlorinator.  You seem to

FLORIDA PUBLIC SERVICE COMMISSION

272

1   indicate that at high levels of hydrogen sulfide the

2   chlorinator is somehow overwhelmed.  And instead of reducing

3   hydrogen sulfide to sulfate, that larger quantities are reduced

4   only to sulfur, is that correct?

5        A    That is correct.  Doctor Levine showed in her audit

6   report that the chlorinator at Well 9 can convert only 2.6

7   milligrams of hydrogen sulfide to sulfate.  We had levels of up

8   to 6.71 reported in that well.  Therefore, when hydrogen

9   sulfide levels in Well 9 are above 2.6, there will differently

10   be elemental sulfur formed.  And when it is as high as 6.71

11   milligrams, up to 3 milligrams of elemental sulfur can be

12   formed.

13        Q    Well, can't Aloha just pump up the amount of

14   chlorine?

15        A    Because if you put in a lot of chlorine, it still

16   does not guarantee that it will go 100 percent to sulfate.

17   Aloha could have done it better than the 25 milligrams that is

18   available there.  When the well was brought on line in 1995 or

19   '96, it was known that the amount of hydrogen sulfide in that

20   well was 4.3, and yet the chlorinator has the capacity of only

21   25 milligrams.  So effectively that well is under-engineered.

22   And I would have thought that Aloha would have detected that

23   since they claim that they have experts working for them.

24   Therefore, from the time that Well 9 was brought on, there was

25   evidence to suggest that that well was capable of producing

FLORIDA PUBLIC SERVICE COMMISSION

273

1   elemental sulfur.

2        Q    Is there also a top level on the chlorine due to

3   trihalomethanes or haloacetic acid?

4        A    No, the extent to which trihalomethanes and

5   haloacetic acid is formed is proportional to the residual

6   amount of chlorine.  In fact, FDEP used to allow 5 milligrams

7   of chlorine as the residual, now they have lowered it to 4

8   milligrams because of concern about increased production of

9   trihalomethanes and haloacetic acid.

10        Q    I think you also referred once to hydrogen peroxide

11   as an untried or unproven method for oxidizing hydrogen

12   sulfide, is that correct?

13        A    Peroxide oxidizing hydrogen sulfide in drinking

14   water.  It has been used for wastewater treatment.

15        Q    But you aren't aware of where it has been used for

16   water oxidation?

17        A    For drinking water it has not been used anywhere as a

18   running project in the whole United States.  Doctor Levine used

19   it in Hillsborough County to remove sulfur.  Because if you add

20   small amounts of hydrogen peroxide to water it will immediately

21   precipitate out all the sulfur, and you can filter that sulfur

22   off.  So when hydrogen peroxide is used, it is still possible

23   to remove sulfur.  We had a discussion earlier whether it was

24   possible or not.  It is still possible.

25             But the method that Doctor Levine has suggested for

FLORIDA PUBLIC SERVICE COMMISSION

274

1   Aloha does not include the use of filtration.  So, there will

2   always be elemental sulfur produced in that system also, just

3   like it is being produced with chlorination alone.  And that is

4   the customers' concern.  And that is why we have wanted a

5   standard for elemental sulfur.

6             Customers have not objected to the use of hydrogen

7   peroxide, and I think that is a false statement that has been

8   made here.  We have said that if Aloha is going to use its

9   freedom to use whichever method it wants to, then it should

10   also take into account the possibility of elemental sulfur

11   being produced.  And since there is a well-known association

12   between elemental sulfur and black water, there should be a

13   standard created for it.

14             All standards are created to prevent problems.  And

15   since Aloha has claimed that hydrogen sulfide formation in the

16   plumbing of customers is responsible for the formation of

17   copper sulfide, and we know from literature and from Doctor

18   Levine's admission that elemental sulfur can also cause reduced

19   disinfection capability, it is very important to have

20   standards.  If you choose a method, you must choose the

21   standards appropriate to that method.

22        Q    But does the hydrogen peroxide method have a greater

23   capacity than chlorination?  Is it better?

24        A    It can do slightly better.  Because chlorination

25   produces only one atom of hydrogen per molecule of chlorine,

FLORIDA PUBLIC SERVICE COMMISSION

275

1   whereas hydrogen peroxide produces two atoms.  Therefore, there

2   will be a little bit more oxygen in hydrogen peroxide.  But

3   consider the fact that for hydrogen peroxide to work

4   efficiently, you have to change the pH of water.  And when it

5   gets to the higher pHs, there is a risk that calcium will get

6   precipitated out of water.  And that is one of the concerns of

7   other water experts who have indicated that they are not very

8   comfortable with the use of hydrogen peroxide for treating

9   drinking water.  That it is a very pH sensitive method.  And if

10   the pH is not extremely well controlled, you will have what is

11   called white water, because of the precipitation of calcium,

12   rather than black water.  And that is no solution.

13        Q    Now, I believe it has been the testimony today, and I

14   think it is also your testimony that there is no hydrogen

15   sulfide in the presence of free chlorine residuals, is that

16   correct?

17        A    It is correct almost, or often enough, but it is not

18   completely correct.  Because as Doctor Levine said earlier, you

19   are taking probably 30 CCs, 30 milliliters of water to do the

20   test.  You can have water that is outside that realm,

21   especially water that is very close to the periphery of a tube

22   which may not conform to that particular observation.

23        Q    So you are saying that a chlorine test alone would

24   not be sufficient to determine -- I'm sorry.  Strike that.

25             That a chlorine test would not be sufficient, and a

FLORIDA PUBLIC SERVICE COMMISSION

276

1   test for hydrogen sulfide or sulfite would still be necessary?

2        A    Yes.  The reason for this is basically because the

3   presence of residual chlorine neither excludes the possibility

4   of hydrogen sulfide nor does it exclude the possibility of

5   elemental sulfur.  You can demonstrate both in this, even

6   though it is not normally found.  And that is because of where

7   you test the sample.

8        Q    Now, I believe you said Doctor Levine used a scanning

9   electron micrograph to determine if sulfur was present in

10   Aloha's water, is that correct?

11        A    That's correct.

12        Q    Is there any simple test other than scanning with an

13   electron micrograph to determine if sulfur is there?

14        A    Measurement of turbidity has been suggested as a

15   method for detecting suspended material in water.  It is not

16   specific to elemental sulfur.  But if you test the turbidity of

17   water before it is processed and test it after it is processed,

18   you can use the difference between the two turbidity

19   measurements as an indicative measure of elemental sulfur.

20        Q    Turn to Page 13, Line 17, I think that's where I have

21   a question.

22        A    Page 13?

23        Q    Yes.  Starting on Line 17.  It is Page 13, Line 17,

24   while I understand.

25        A    Of my direct testimony?

FLORIDA PUBLIC SERVICE COMMISSION

277

1        Q    This is of your testimony, direct.  And you state,

2   "While I understand that efforts will be made to convert all

3   hydrogen sulfide to sulfate by pH adjustment more towards

4   alkalinity, the likelihood that elemental sulfur will be formed

5   in the presence of variable levels of hydrogen sulfide from the

6   wells remains a real concern."  Do you see that statement?

7        A    Yes.

8        Q    Where did you get that understanding?

9        A    That understanding is based on the fact that there

10   is -- if you inject or if you add a certain amount of hydrogen

11   peroxide to water, then it can neutralize only so much of

12   hydrogen sulfide.  Because we know that the levels of hydrogen

13   sulfide fluctuates, unless it is continuously monitored, it is

14   difficult to dose the hydrogen peroxide correctly.  Therefore,

15   there is always that risk.  And that is, again, one reason for

16   trying to find a method, and I have suggested the use of

17   turbidity differences between the raw water and the processed

18   water as a way of indicating whether there is elemental sulfur.

19        Q    Going on to the next page, Page 14, at the top, you

20   use the word "stoichometrically"?

21        A    Yes.

22        Q    Can you tell me what that means, and specifically

23   about the ratios of CL2 to H2S to get sulfate verse sulfur?

24        A    Stoichometrically means the amount -- proportion of

25   the amounts of two reacting substances.  As far as chlorination

FLORIDA PUBLIC SERVICE COMMISSION

278

1   is concerned, when there is one molecule of chlorine for each

2   molecule of hydrogen sulfide, you will still get hydrogen

3   sulfide present as a gas or as an ion in water.  If you raise

4   the ratio to two-to-one, you can get rid of hydrogen sulfide,

5   but still elemental sulfur will form.  You have to get it up to

6   4-to-1 to reach the theoretical dose for chlorine.  And in a

7   lot of Aloha's wells.  You never reach that 4-to-1 level, and

8   that is why we come to the conclusion that elemental sulfur is

9   being formed.

10        Q    I want to make sure I understand your position on

11   Issue 3, that is the number, frequency, and location of

12   hydrogen sulfide tests.  How many per month are you

13   recommending total hydrogen sulfide tests for Aloha?

14        A    I have suggested that they do two tests per month

15   from each well site or distribution site of each well, so that

16   is 16 tests.  And you have to do tests in duplicate to know

17   that a single measurement is not a false positive.  So you are

18   talking about 32 tests.  And I'm suggesting that as an initial

19   number, once process control is established you obviously will

20   reduce the number of tests.

21        Q    Looking at that map, how do you know when you are --

22   how far out do you go from the wells before you are getting

23   next -- like 8 and 9 are in the bottom, and I think 3 and 4 are

24   in the middle, and 1 and 2 are way off to the east, and 6 and 7

25   are way to the north.  How do you know when you are testing for

FLORIDA PUBLIC SERVICE COMMISSION

279

1   Wells 8 and 9 as opposed to 3 and 4, where does that break off?

2        A    One has to be able to use a little bit of common

3   sense about it.  Because most of the water from 8 to 9 go to

4   the areas around it.  Because even though Aloha maintains that

5   they have an interconnected loop, most of the water from the

6   well goes to areas nearest the well.

7        Q    Your testimony about the 30 bacteriological testing

8   sites --

9        A    I have given no testimony about it.  I know that they

10   do exist.

11        Q    But would testing at those sites --

12        A    Testing at those sites would be satisfactory.  But

13   you can also test at sites where there is black water.

14        Q    And is it your bottom line that if there is either

15   hydrogen sulfide or sulfur which is easily converted to

16   hydrogen sulfide and a source of copper, say a customer's

17   pipes, then you will have the problem of copper sulfide, what

18   we call black water being formed, is that correct?

19        A    It is not my opinion that it will be solved that way.

20   What I'm saying, basically, is that there are now two

21   hypotheses about why copper corrosion occurs.  One is that it

22   is due to the presence of hydrogen sulfide in the water,

23   whether because it is not adequately eliminated or whether

24   because it reforms.  And therefore it seems appropriate to test

25   for hydrogen sulfide.

FLORIDA PUBLIC SERVICE COMMISSION

280

1             And since we have provided evidence today showing

2   that Aloha's distribution system often has discolored water, we

3   feel that it is not enough to test it at the well site.  We

4   need to test it in the periphery.  Because, otherwise, this

5   kind of report that is from Aloha's own records should not

6   occur, and that was associated also with low levels of

7   chlorine.  Sometimes absolutely no chlorine.  You also need to

8   test for elemental sulfur for the same reason.  Because there

9   is a hypothesis that says that elemental sulfur is associated

10   with black water.  In fact, that recommendation was made in

11   1991, and it is almost 14 years.

12        Q    But didn't you say there is no simple test for

13   elemental sulfur?

14        A    Yes, I said that.  That is why I said that you can

15   use turbidity differences between processed water and raw water

16   as an indirect measure.  And you need to do it only in areas

17   where there are black water problems.  You don't need to do it

18   in areas where there is no black water problem, because you are

19   just wasting money doing that test.

20        Q    Looking at that map, that is Exhibit 19, is it the

21   southern half of the Seven Springs territory that seems to have

22   the most problem?

23        A    That is what I'm most familiar with.  Others may have

24   problems, but I have not explored that to find out.

25        Q    Trinity, Wyndtree, Wyndgate, Chelsea, Riviera, those

FLORIDA PUBLIC SERVICE COMMISSION

281

1   are on the south side.  Those are the ones that seems to be

2   having the most problem?

3             MR. WHARTON:  I object.  Are we laying the ground for

4   the deletion case?  Doctor Kurien hasn't testified about what

5   neighborhoods have the worse problems.  These three issues are

6   system-wide.  He just said he hadn't quantified it, and Mr.

7   Jaeger is pushing him on the issue.

8             CHAIRMAN BAEZ:  Mr. Jaeger, can you get the

9   information some other way or rephrase your question.

10             MR. JAEGER:  I will withdraw the question.

11             CHAIRMAN BAEZ:  All right.  Thank you.

12             MR. JAEGER:  That's all I have, Chairman.  That was

13   my last question.

14             CHAIRMAN BAEZ:  Commissioners, any questions of Dr.

15   Kurien?

16             Mr. Beck.

17             MR. BECK:  No redirect.

18             CHAIRMAN BAEZ:  No redirect.  Let's take Dr. Kurien's

19   exhibits.

20             MR. BECK:  I would move Exhibits 1 through 18.

21             CHAIRMAN BAEZ:  Show Exhibits 1 through 18 moved into

22   the record without objection.

23             MR. WHARTON:  Just subject to our earlier discussion

24   about the fact that some of them are hearsay.

25             MR. JAEGER:  Staff would move Exhibit 19.

FLORIDA PUBLIC SERVICE COMMISSION

282

1             CHAIRMAN BAEZ:  Without objection show Exhibit 19

2   moved into the record.

3             (Exhibit 1 through 19 admitted into the record.)

4             CHAIRMAN BAEZ:  Thank you, Dr. Kurien.  And thank you

5   again for your patience and letting us move witnesses around.

6             Commissioners, would you like a five-minute break,

7   ten-minute break to get squared away?  And our next witness is

8   Witness Porter.  Does he have stuff to set up?

9             MR. WHARTON:  He does have a demonstrative he can put

10   on an easel.

11             CHAIRMAN BAEZ:  All right.  Well, we will take ten

12   minutes and let him set up his maps.

13             (Recess.)

14             CHAIRMAN BAEZ:  Go back on the record.  Mr. Porter, I

15   don't think I swore you yet, so if you will stand.

16             (Witness sworn.)

17             CHAIRMAN BAEZ:  Mr. Deterding.

18                        DAVID W. PORTER, P.E.

19   was called as a witness on behalf of Aloha Utilities, and

20   having been duly sworn, testified as follows:

21                         DIRECT EXAMINATION

22   BY MR. DETERDING:

23        Q    Mr. Porter, please state your name and employment

24   address for the record.

25        A    David W. Porter, P.E., 3197 Ryans, R-Y-A-N-S, Court,

FLORIDA PUBLIC SERVICE COMMISSION

283

1   Green Cove Springs, Florida 32043.

2        Q    Have you been retained by Aloha Utilities to provide

3   testimony and expert opinions in this proceeding?

4        A    I have.

5        Q    Did you prepare in conjunction with my office a

6   document referred to as prefiled direct testimony of David

7   Porter, P.E., consisting of 13 pages?

8        A    I did.

9        Q    If I asked you those same questions here today, would

10   your answers be the same?

11        A    They would.

12        Q    Do you have any corrections to make to that

13   testimony?

14        A    I do not.

15             MR. DETERDING:  I request that Mr. Porter's testimony

16   be inserted in the record as though read.

17             CHAIRMAN BAEZ:  Without objection show the direct

18   testimony of David Porter inserted into the record as though

19   read.

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

297

1   BY MR. DETERDING:

2        Q    And, Mr. Porter, do you have a summary of that direct

3   testimony?

4        A    I do.

5             MR. BECK:  Mr. Chairman, if I may, before Mr. Porter

6   gets started, he apparently is going to use a document that I

7   have never seen before until he stepped up to the stand here in

8   his summary.  It has never been provided to us before.  It

9   looks like an attempt to bolster his direct testimony, and I

10   object to his use of that document.

11             MR. DETERDING:  Commissioners, it is not going to be

12   requested to be admitted into the record.  It is not evidence.

13   It is simply a demonstrative to help him explain what is in his

14   testimony, to give you points of reference on a map, to show

15   you the connection point between Aloha and Tampa Bay Water, or

16   the county, the connection point between Aloha's treatment

17   facilities and its distribution system.  It is merely a

18   schematic that illustrates what he said in his testimony.

19             CHAIRMAN BAEZ:  Mr. Beck, you were going to say

20   something?

21             MR. BECK:  Commissioners, first of all, this is a

22   summary of his testimony that is in it.  He could have easily

23   provided this schematic in his testimony ahead of time.  We

24   could have looked at it, we could have critiqued it, we could

25   have deposed him about it.  It is brought in at the last

FLORIDA PUBLIC SERVICE COMMISSION

298

1   second, nobody else has seen it before.

2             CHAIRMAN BAEZ:  Mr. Beck, I am going to allow his use

3   of the schematic.  And that said, I'm going to tell you how

4   busy it is, and how much I can't even see what all is -- I

5   mean, I don't know how much it's going to be, but that is your

6   choice to use it.

7             MR. DETERDING:  And we have small ones.  But the

8   point is we are not asking that this be admitted into evidence.

9             CHAIRMAN BAEZ:  I understand that, and that is

10   precisely why it is okay to use it is a demonstrative device.

11   BY MR. DETERDING:

12        Q    Go ahead and give us your summary, Mr. Porter.

13        A    Okay.  First of all, I would like to say the standard

14   as ordered by the Commission previously in this docket set a

15   very high level for compliance for Aloha and should not be

16   changed.  Aloha's finished water meets all the FDEP and EPA

17   standards as we sit here today.  And unlike what you may have

18   heard here or heard inferred previously, the water as it is

19   delivered to the customers is always clean, clear, and odor

20   free.  The problems that have been discussed previously are

21   those which occur inside the homes.  They are not those which

22   occur in the distribution system themselves or at the point

23   where the water is provided to the customer.  I know there has

24   been some conjecture about that, but that is just not the case.

25             One of the issues that we have talked about here is

FLORIDA PUBLIC SERVICE COMMISSION

299

1   the point at which the hydrogen sulfide standard should be

2   monitored or it should be measured.  The Tampa Bay Water

3   standard as it has become known in this case requires that the

4   hydrogen sulfide level be monitored at the point of connection

5   of the Tampa Bay Water system with its member governments.  The

6   important thing to understand is that Tampa Bay Water and its

7   member governments are one in the same.  The member governments

8   make up Tampa Bay Water and they in turn have an ability to

9   financially and managerially control Tampa Bay Water.  They

10   have a vote.  So, therefore, they are really one in the same.

11             So when Tampa Bay Water provides water to its member

12   government, it is essentially no different than if a member

13   government had its own well system in addition to the wells or

14   other treatment systems it has to that point.  And that is the

15   purpose of the demonstrative.  Would you like for me to bring

16   it closer?

17             There are two different ones.  The first one please

18   look at, simplified TBW member government water system

19   schematic.  It is important to understand the concept of the

20   connection point as required in the Tampa Bay Water standard.

21   I have three different colors outlined here.  One is just a

22   schematic of the Tampa Bay Water system itself.  The other, the

23   green is one of the member governments, and the blue would be

24   the member governments' distribution system itself.  The

25   differences are the Tampa Bay Water system and the pipelines in

FLORIDA PUBLIC SERVICE COMMISSION

300

1   it essentially operate as treatment systems and transport

2   systems, to get the water from the Tampa Bay Water sources and

3   treatment systems into the member governments one way or the

4   other.

5             Depending upon the member government, it can occur in

6   two different ways.  One way is that raw water in some cases

7   from the wells of Tampa Bay Water can be sent to a treatment

8   plant in a member government system and be treated along with

9   or in addition to the water that the member government itself

10   treats.  So it is not retreating the water, it is treating it

11   for the first time as raw water.  The second one is that the

12   water is treated by Tampa Bay Water, it comes through a

13   pipeline and then enters into the distribution system of a

14   member government.

15             MR. BECK:  Commissioners, I am going to renew my

16   objection.  He is going beyond the description contained in his

17   direct testimony.  This is nothing but an attempt to bolster

18   his direct testimony with surprise schematics and a summary

19   that exceeds what he has in his direct testimony.

20             CHAIRMAN BAEZ:  Mr. Porter, the day is getting late.

21   I mean, if you can find somewhere to -- brevity is key.

22             THE WITNESS:  I will speed it up.

23             CHAIRMAN BAEZ:  Thank you.

24             THE WITNESS:  I think it is important to understand

25   then that the water supplied by Tampa Bay Water to its member

FLORIDA PUBLIC SERVICE COMMISSION

301

1   government into a distribution system, the point at which it

2   tests the water is the point at which the member government

3   connects to the Tampa Bay Water system.  So it is not in the

4   distribution system of the member government anywhere, it is at

5   the point at which the water connects to the member government.

6   That would be the same as if it was another member government

7   well like we see here.  It is exactly the same.

8             In Aloha's case and what has been proposed here --

9             COMMISSIONER BRADLEY:  Excuse me.  So H28 test point,

10   is that what you just referred to?

11             THE WITNESS:  Yes, H2S, Commissioner.

12             COMMISSIONER BRADLEY:  Okay, H2S.

13             THE WITNESS:  And that is to indicate the water just

14   as it leaves the pipeline in the Tampa Bay Water pipeline going

15   into the distribution system.  So it is just before it gets to

16   the distribution system.  In Aloha's case it is exactly the

17   same.  If we look at green here, that is the Aloha system.  The

18   red in Aloha's case would be Pasco County's system

19   interconnecting with Aloha.  The green is Aloha's own wells and

20   its own treatment plants.  And the blue, again, is Aloha's

21   distribution system.  What is being proposed is exactly the

22   same.

23             The water that leaves the treatment system and

24   travels in the pipeline, it connects to the distribution

25   system.  It would be tested just before it goes into the

FLORIDA PUBLIC SERVICE COMMISSION

302

1   distribution system.  The same is true on each one of Aloha's

2   different treatment plants.  So what is being proposed or what

3   has been proposed and what is in the order is exactly the same

4   in both cases.

5             I do not believe that monitoring of H2S at the

6   customers' meters themselves as proposed by Dr. Kurien in his

7   protest is of any value because of a number of reasons.  Number

8   one, as Doctor Levine said earlier, there is no benefit to the

9   operation of Aloha's treatment systems by measuring it at that

10   point.

11             MR. BECK:  Commissioners, now the witness is

12   referring to the testimony given by another witness and this is

13   supposed to be a summary of his prefiled direct testimony.  I

14   object.

15             MR. DETERDING:  Commissioners, I will instruct Mr.

16   Porter, don't refer to other people's testimony, you are here

17   to summarize your own.

18             THE WITNESS:  Summarize my own.  Okay.  I do not

19   believe there is any value to it.  And as I said in my

20   testimony, it has been looked at a number of times, and it has

21   always ended up being zero or nondetect at those points.  So to

22   do so is just to add another level of complexity and cost that

23   doesn't have any bearing on operating the system.

24             An MCL versus a goal.  The existing Tampa Bay

25   standard specifies a goal.  An MCL is a different animal.  An

FLORIDA PUBLIC SERVICE COMMISSION

303

1   MCL is something that is of a maximum level, not an ongoing

2   monitoring point.  An MCL is very carefully determined or

3   developed within the EPA and the FDEP.  And to develop an MCL

4   for hydrogen sulfide has never been done by any other agency

5   that I am aware of anywhere.  It would set a new standard far

6   beyond anything that has ever been done.

7             The test method used to monitor hydrogen sulfide in

8   the field where these tests are being proposed to be done in

9   the protest, the test method itself is only accurate down to a

10   minimum of 0.1 milligrams per liter.  So what we have said so

11   far is that the .1 milligram per liter is what we are willing

12   to, or Aloha is willing to accept.  So, therefore, it is

13   already at the lowest level that can be detected in the test

14   method.  So there is no value in doing an MCL anyway.

15             To have chlorine, another indicator of whether H2S is

16   in the system, or in the distribution system, or is not, or is

17   reforming or not is the fact that if there is free chlorine

18   available in the system, then by definition hydrogen sulfide

19   doesn't exist.  And, again, that has been borne out in a number

20   of, many other tests that have been done by others other than

21   myself and Aloha and been put into testimony in many cases

22   here.

23             It has never been determined, or shown, or even

24   inferred that sulfide reformation in Aloha's distribution

25   system has ever occurred.  There was some discussion in Dr.

FLORIDA PUBLIC SERVICE COMMISSION

304

1   Kurien's direct testimony that I talked about in mine where he

2   claimed that Doctor Levine had shown there was a 0.12 milligram

3   per liter concentration of hydrogen sulfide in the water in

4   Aloha's distribution system.  That is not the case.  Where that

5   point was, or where that sample was taken was in a pretreatment

6   line, not in a line going to the final water treatment line or

7   any water that was entering the distribution system at all.  It

8   was in a line between two treatment plants, or actually three

9   different treatment plants.  It is a line that conveyed water

10   from one plant to another.  It is not indicative of what is

11   going on in the distribution system.

12             Regarding the turbidity issues, number one, there is

13   a number -- or the elemental sulfur issues, there is a number

14   of ways to determine whether you think hydrogen sulfide is

15   being converted to sulfate or some other intermediate form,

16   including and possibly elemental sulfur.  There is no direct

17   method to test for elemental sulfur.  Therefore, you have to

18   use an indicator of some sort.  Turbidity is one.  In all of

19   the years that I have seen turbidity analysis coming out of the

20   water treatment plants from Aloha, I have never seen excessive

21   turbidity.  And that has just not been the case.

22             There are other indicators as well, though, and that

23   is the bacteriological quality of the water itself in the

24   distribution system.  That has been looked at repeatedly every

25   month for the last ten years we have been talking about this,

FLORIDA PUBLIC SERVICE COMMISSION

305

1   and there has not been any indication in the bacterial quality

2   of the water that there is a problem with turbidity in that

3   system.  You know, one of the biggest problems recognized in

4   the industry with turbidity is that it lowers the ability of

5   the water to be disinfected by the chlorine that is added to do

6   the disinfection, to accomplish the disinfection.  If you had a

7   serious turbidity problem, or if there were some other issues

8   with turbidity, you would expect to see the biological

9   characteristics of the water to be such that it wouldn't meet

10   the requirements of the DEP, which this water does.

11             Also, recently, as I mentioned in my testimony, Aloha

12   has done another more intensive level of screening for

13   bacteriological quality called heterotrophic plate counts in

14   preparation for chloramination switchover, and those numbers

15   were extremely low.  Very, very low.  As a matter of fact, in

16   most cases out of the 30 that were tested they were nondetect.

17   So, all indications are, at least from a bacteriological

18   standpoint, that this water is of high quality and, therefore,

19   if you were to hazard a guess as to whether you thought there

20   was turbidity issues in the water or not, you would guess that

21   there were not.

22             Regarding significant consumption of chlorine in the

23   system, that is not the case, either.  Aloha's data that you

24   have seen put into the record by others indicates there is

25   chlorine throughout the system.  The DEP mandated 0.2

FLORIDA PUBLIC SERVICE COMMISSION

306

1   milligrams per liter of free chlorine through the system has

2   been met and continues to be met.  And, therefore, that isn't a

3   significant uptick of chlorine.

4             Regarding the conversion versus removal process or

5   issues, removal is going to be extremely costly.  You know,

6   over $10 million.  Exactly how far over 10 million depends on

7   how the system is finally configured, but it is going to be

8   very expensive and the ratepayers will have to bear the cost.

9   What Doctor Levine is proposing in the way of hydrogen peroxide

10   treatment will be much less expensive, and as you hear from --

11   well, I won't say that.  If Doctor Levine's process proves out

12   to be what she believes it is and what she has represented it

13   to be, then it will be a far better solution for the customers

14   from a monetary standpoint.

15             There has been a quite a bit of discussion about

16   sulfides or sulfate generation versus elemental sulfur

17   generation and the effect of that.  The reality is that

18   sulfates are those which convert very easily in hot water

19   systems in homes.  There is a tremendous amount of data out

20   there on sulfate conversion back to sulfides, and virtually

21   none on elemental sulfur.  Dr. Kurien has talked about one

22   paper generated back in 1992.  That paper only says that the

23   potential for black water problems exists when there is

24   elemental sulfur.

25             MR. BECK:  Commissioner, the witness is going beyond

FLORIDA PUBLIC SERVICE COMMISSION

307

1   his direct testimony and has been going about ten minutes.

2             CHAIRMAN BAEZ:  You know, whether that is true or

3   not, Mr. Porter, I have just about had it with the

4   twenty-minute summaries.  We are just going to get into the

5   questions.  I think -- you know, I think I have afforded you

6   plenty of time to finish up.

7             THE WITNESS:  Those issues were in my direct

8   testimony, but --

9             CHAIRMAN BAEZ:  That's fair enough.  I'm sure they

10   will all get crossed.

11             THE WITNESS:  Okay.

12             CHAIRMAN BAEZ:  Thank you.

13             MR. DETERDING:  I tender the witness for cross.

14             CHAIRMAN BAEZ:  Thank you.  Mr. Beck.

15             MR. BECK:  Thank you, Mr. Chairman.

16                          CROSS EXAMINATION

17   BY MR. BECK:

18        Q    Mr. Porter, could you turn to Page 10 of your

19   testimony, please.

20        A    Certainly.

21        Q    Lines 14 through 18.

22        A    Yes.

23        Q    You say Dr. Kurien is mistaken --

24        A    Yes.

25        Q    -- in his statements about Tampa Bay Water requiring

FLORIDA PUBLIC SERVICE COMMISSION

308

1   their water be tested at least four times annually instead of

2   once a year, is that right?

3        A    That's my understanding, that is correct.

4        Q    I would like to hand you a copy of Dr. Kurien's

5   rebuttal testimony.

6        A    Uh-huh.  Thank you.

7        Q    And ask you if you would please turn to Exhibit

8   BAK-26, Page 3 of 3.

9        A    Yes.  The one that is titled proposed compliance and

10   action levels?

11        Q    Yes.  Exhibit D, supplemental.

12        A    Right.  The one that says proposed, correct?

13        Q    Is that not the actual compliance levels that are in

14   effect?

15        A    I wouldn't know.  It says proposed here.

16        Q    Did you look to check?

17        A    Actually what I referenced my testimony on was the

18   comment at the very beginning of supplemental quality

19   parameters, Exhibit D, that says water supplied by the

20   authority system shall be sampled annually at a minimum at the

21   point of connection of the following parameters.  And the

22   parameter that is specifically specified is sulfides at .1

23   milligrams per liter for a goal.

24        Q    And you focused on that without looking at the Table

25   3?

FLORIDA PUBLIC SERVICE COMMISSION

309

1        A    Well, the Table 3 that you have here and the one that

2   I have seen also says proposed.

3        Q    Okay.  Could you turn to BAK-27, Page 3 of 3?

4        A    Certainly.

5        Q    This is a letter in response to a staff data request

6   by Aloha Utilities, is it not?

7        A    I'm sorry, repeat that again, please.

8        Q    This is a letter that -- is this part of a letter

9   that Aloha sent to the staff in response to a data request of

10   theirs?

11        A    Yes.

12        Q    Did you have any -- were you involved in preparing

13   the utility's response to this, or in preparing this response?

14        A    I would say I did.

15        Q    Let me ask you about the statement by Aloha that is

16   underlined.  Do you see the underlined section on Page 3 of 3?

17        A    The underlined section on page what?

18        Q    3 of 3.

19        A    Yes.

20        Q    Page 3 or 3 of BAK-27.

21        A    Uh-huh.

22        Q    And in there it says the average concentration of

23   hydrogen sulfide is no more than .1 milligram per liter based

24   on an annual average of four quarterly samples collected at the

25   point of entry to the distribution system.  Do you see that?

FLORIDA PUBLIC SERVICE COMMISSION

310

1        A    Yes.

2        Q    Would you agree then it is Aloha's position that

3   there are four annual samples taken?

4        A    I don't think it ended up this way.  I think what

5   happened was at the beginning when this letter was written, and

6   it was quite a long time ago, March 29th, this was February

7   20th, 2004, that it was really unclear as to whether it was one

8   or four or what it was.

9        Q    Well, would you agree that this statement doesn't

10   state there is anything unclear about whether it is one or

11   four?  It states four quarterly samples, isn't that right?

12        A    That is what it says.

13        Q    Has Aloha now changed its position so that it doesn't

14   agree with that now?

15        A    I believe after this was written and in between the

16   time that the final proposal went in it was brought to our

17   attention when we had Schedule D in our possession that it said

18   that the water supply for the authority system shall be sampled

19   annually at a minimum.  This was based, if I remember

20   correctly, there was based on some conversations that were had

21   in general with some other folks, and I don't remember exactly

22   how it came into being.  But that was back in February of 2004.

23        Q    So have you done any investigation to see whether

24   that is no longer effective?  And what have you done to check

25   on this?

FLORIDA PUBLIC SERVICE COMMISSION

311

1        A    Nothing other than look at Schedule D.  I think it is

2   important also, though, to go back to the table that you talked

3   about that I called proposed compliance and action levels.

4   There are really two different things you are talking about on

5   this table.  I think you need to look at both.  Under total

6   sulfide, you will notice on the action level, see Note 2, there

7   they are talking about a single sample, okay.  And on the other

8   one they are talking about a max average.  That one there is

9   the only one that references the four a year.  So it is not

10   clear.  In three different places in this Schedule D it says

11   three different things.

12        Q    Okay.  On that exhibit, total sulfide is listed under

13   the column parameter, is that right?

14        A    That is correct.

15        Q    That is one of the exhibits.  And then when you go to

16   compliance level next to it, it says .1 milligram per liter

17   (max-average), right?

18        A    Correct.

19        Q    And then in the compliance notes on the bottom it

20   refers to max-average, does it not?

21        A    Correct.

22        Q    And so wouldn't you think that the compliance notes

23   about max-average apply to what it says about total sulfides?

24        A    I think you need to look at the column next to it,

25   too, that talks about an action level.  And it says that it

FLORIDA PUBLIC SERVICE COMMISSION

312

1   will be a max value, and a max value is a value that is one

2   time not exceeded.  So there is three different places in this

3   document that describes the sampling parameters; two of them

4   talk about once, one of them talks about four times.

5             But it is even more important, I think, to realize

6   that what they are talking about here on a running annual

7   average, or an annual average, that you are still talking about

8   one compliance.  You take it four times in that case, but you

9   only report it once.

10        Q    But there is four samples, right?

11        A    There may be four samples, which is one report, and

12   that is one place in a document with three references to it.

13        Q    Okay.  Now, let me ask you, the place where it says

14   .1 milligram per liter on the table, that is under the column

15   compliance level, is it not?

16        A    Yes.

17        Q    And it says, "See Note 1," under compliance level?

18        A    Yes.

19        Q    Then action level is the last column, which is

20   completely different.  It says, "See Note 2," is that right?

21        A    That is correct.

22        Q    And so would you agree that when it refers to

23   compliance level, it is referring to compliance notes, which is

24   1?

25        A    Yes.

FLORIDA PUBLIC SERVICE COMMISSION

313

1        Q    And that is where it states four quarterly sample

2   average, right?

3        A    Yes.

4        Q    Isn't it referring, the four quarterly samples

5   referring to the .1 milligram per liter?

6        A    On that proposed document, yes.  But, again, next

7   door to it in the action level, and you can guess which one is

8   which, it also talks there about a max, which is a one sample.

9   And then in the beginning of the document it specifically says

10   water supplied from the authority system shall be sampled

11   annually, at a minimum, at the point of connection for the

12   following parameters.  So, you know, I can't speak for Aloha,

13   but whether it is one or it is four, at the point of connection

14   to the system, I don't think it makes much differences.  Open

15   to interpretation, I guess.

16             MR. BECK:  I have no other questions.

17             CHAIRMAN BAEZ:  Mr. Wood.

18                          CROSS EXAMINATION

19   BY MR. WOOD:

20        Q    In your chart, Mr. Porter, you hook up to the

21   distribution center in several places?

22        A    You need to tell me which chart to look at.

23        Q    I'm looking at the simplified water system.

24        A    Yes, sir.

25        Q    You hook up at three different places on your chart

FLORIDA PUBLIC SERVICE COMMISSION

314

1   here.

2        A    Yes, sir.

3        Q    How do I know that there is a correlation from what

4   you sample at that point and what enters into the home?

5        A    Well, again, I think it is important to understand

6   that what we are talking about is setting a standard.  And what

7   Aloha agreed to was a standard that was established by another

8   agency that is more strict than any other standard ever

9   generated.

10        Q    Mr. Porter, that is not the question.  The question

11   is how do you know there is a correlation between where it is

12   tested and after it is ready to leave the distribution center?

13        A    Okay.  I will answer that.  That is going to take

14   some time, and the reason for that is this:  It is important to

15   understand that the water does enter the distribution system in

16   many different places.  In this case I showed three.  In

17   reality there is going to be eight, and nine with the Tampa Bay

18   Water or Pasco County connection.  I think what you have to

19   understand is what your goal is when you measure the hydrogen

20   sulfide here is to be able to control the processes of these

21   treatment plants in order to obtain the level of .01 milligrams

22   per liter.

23             If you were to measure, let's say here, the furthest

24   point from that plant, and you were to get a number, whatever

25   that number is, there is no way to correlate that number with

FLORIDA PUBLIC SERVICE COMMISSION

315

1   anything that goes on at any one of these treatments plants

2   because the water is an intermix of all of those different

3   systems.  There is no value to it.  It can't tell you whether

4   you should adjust the plant here, should you adjust the process

5   here, should you adjust the process here.  There is no value to

6   that.

7             If, however, you measure here, or here, or here, that

8   will tell you without a doubt what the effect of the operation

9   of that plant is on the water entering the distribution system.

10   That has value.  That allows you then to control the process.

11   So the fact that the system is totally interconnected, the fact

12   that all the water mixes, the fact that Pasco County mixes --

13   I'm going too fast, sorry.  The fact that all the water

14   intermixes means that to test anywhere other than the points of

15   connection won't tell you anything.  It won't tell you whether

16   you should adjust the process or not, or whether you are

17   meeting a requirement to it.

18        Q    You haven't answered the question yet.  I asked you

19   how do you know that there is a correlation between testing it

20   into the customer's home versus where it is entering the

21   distribution center?

22        A    I think I just told you there is no direct

23   correlation between what that plant is doing and what happens

24   out here at a customer's home if you were to measure it there.

25        Q    Shouldn't you from the testing point know that there

FLORIDA PUBLIC SERVICE COMMISSION

316

1   is a correlation in the product that you deliver?

2        A    Again, I think you have to understand that if you

3   measure it at this location, let's say at a customer's home in

4   the distribution system itself, there is no correlation

5   between -- direct correlation between that and anything that

6   happens at the treatment plant because the water is intermixed.

7        Q    Doesn't that tell you you have a problem?

8        A    No, not at all.  It tells you have an intermix of

9   waters.

10        Q    It tells you you have a problem.

11        A    No, I didn't say you would have a problem.  Mr. Wood,

12   conversely --

13        Q    If you deliver --

14             CHAIRMAN BAEZ:  Hold on.  Hold on, Mr. Wood.  Okay.

15   What I'm going to need you to do is to let Mr. Porter answer

16   the question.  And, Mr. Porter, you are going to have to watch

17   out for when he starts asking his next one, and maybe we can

18   meet somewhere in the middle, shall we?

19             THE WITNESS:  Okay.  Very good.  I think it is

20   important to understand that conversely if you were to measure

21   it here at the customer's home and you had 0.1 milligrams per

22   liter of hydrogen sulfide, the opposite is also true.  That

23   doesn't tell you that at each one of your plants that they are

24   operating properly, because there is a time of travel through

25   the system.  I mean, I could be measuring water here today and

FLORIDA PUBLIC SERVICE COMMISSION

317

1   that is reflecting water that was made two or three or four

2   days ago back here.  So by the time I measure it here, and it

3   shows a problem with the hydrogen sulfide level, it is too

4   late.  I have got a whole distribution system full of water now

5   that doesn't meet the standard.

6             Where I need to be measuring the standard in order to

7   be able to adjust the process and meet the goal has got to be

8   at a point where I can do something about it.  If I measure it

9   here, I could have a whole distribution system full of water

10   that doesn't meet the standard.  That doesn't help anybody.  So

11   both is true.  You could find water that meets the standard

12   here that really doesn't at that day coming in.

13   BY MR. WOOD:

14        Q    Is what you are telling me then, Mr. Porter, that the

15   water is not stable?

16        A    No, not at all.  What I'm telling you is what you are

17   trying to measure here is the effect of the treatment plant

18   operation on the water quality that enters the system.  If I

19   was to measure again -- to pick this location right here -- if

20   I was going to measure the hydrogen sulfide level there rather

21   than at the point at which it comes in from the plants, two

22   things could happen.  A, I could find that the water meets the

23   standard.  Well, that is all well and good except that water

24   essentially could be as much as two and three days old.  It

25   doesn't tell me anything about when it is entering the system

FLORIDA PUBLIC SERVICE COMMISSION

318

1   today from any one of these systems.  It is only telling me

2   what is happening back where the water originated.  The other

3   problem is it may not meet the standard.  That doesn't tell me

4   anything about where the problem is, it only tells me there is

5   a problem.  Now I have got to go find it.

6             The reality is the way to have an effective system

7   that actually measures hydrogen sulfide is to do it at the

8   point where the water enters the distribution system so that

9   one can then determine if the plants are functioning and

10   whether they meet the goal.

11        Q    Okay.  You have determined that all the plants are

12   functioning from what you are saying.  If the final product is

13   not of an acceptable quality, then the plants aren't

14   functioning, is that not correct?

15        A    I'm not sure if I understand your question.

16        Q    If you can't deliver a product that meets the

17   standard, then you haven't delivered a quality product, have

18   you?

19        A    The water as it leaves the treatment system and

20   enters the distribution system, if that is where the standard

21   is being met, then it has met the standard.

22        Q    If you went to the grocery store and you bought a

23   pound of butter and you got it at home and it was moldy, has

24   the grocery store met the standard?

25        A    Well, that is not a true analogy, because the butter

FLORIDA PUBLIC SERVICE COMMISSION

319

1   had to be moldy when it left the store.  What I'm saying to you

2   here is this is a test to determine whether the butter met the

3   requirement as it left the store.  Therefore, when you got it

4   home, it should have met the standard.

5        Q    And when it gets here in the system in the blue, even

6   if it has met the standard there, it hasn't met the standard

7   there.  And you have to find a way, don't you, why it is doing

8   that?  You can't just wash your hands of the whole thing and

9   not take any responsibility, can you?

10             CHAIRMAN BAEZ:  Mr. Wood, I hate to do this, but I

11   think we have crossed the line into questions that aren't --

12   that is, in fact, what we are here to answer, okay?

13             MR. WOOD:  Okay.

14             CHAIRMAN BAEZ:  So if you have got another line of

15   questions, try and find it.  If you are not, we will --

16             MR. WOOD:  We'll let it go at that.

17             CHAIRMAN BAEZ:  Thank you, sir.  Where was I?  Staff,

18   do you have questions?

19             MR. JAEGER:  Yes, Mr. Chairman.

20                          CROSS EXAMINATION

21   BY MR. JAEGER:

22        Q    Mr. Porter, please look on Page 4, Lines 9 through 15

23   of your direct testimony.  That's is Page 4, Lines 9 through

24   15.  You state that in negotiations Pasco County refused to

25   extend the Tampa Bay Water hydrogen sulfide goal for the water

FLORIDA PUBLIC SERVICE COMMISSION

320

1   Pasco County supplies Aloha, is that correct?

2        A    That's correct.

3        Q    And how was that put to them?

4        A    We were in negotiations on the bulk water agreement.

5   I was sitting in the room.  The question was asked will you

6   agree to put a clause in this agreement that extends the Tampa

7   Bay Water standard to the point of connection with Aloha.  The

8   answer was no.

9        Q    Was there anything in writing?

10        A    I don't know.  There wasn't anything on that

11   particular day in writing.

12        Q    Who was in the meeting for the county, do you

13   remember?

14        A    You know, again, it was either Doug Bramblett and/or

15   Bruce Kennedy.  And I think on that day it was also the county

16   administrator, but I would have to go back and check that.

17        Q    And Doug Bramblett, was he the utilities director?

18        A    That's correct.

19        Q    And is he now retired?

20        A    He is.

21        Q    Did the county give a reason for its refusal?

22        A    No, other than they said that they couldn't guarantee

23   it.

24        Q    And can Aloha obtain water directly from Tampa Bay

25   Water?

FLORIDA PUBLIC SERVICE COMMISSION

321

1        A    No.  I have been told not.

2        Q    And that is even if you put a pipeline right up to

3   one of their lines, that they only give water to member

4   organizations?

5        A    That's correct, member governments only.

6        Q    You keep talking about optimizing the water treatment

7   process at the plant, and that you need to test as it comes

8   right out of the plant.  I think what Mr. Wood was getting at,

9   you want to test the water as it leaves the plant, that is to

10   optimize it.  What if you want to evaluate the process itself

11   for continued effectiveness out in the system, why wouldn't you

12   test out in the system?

13        A    What we are talking about here is setting a standard

14   for hydrogen sulfide.  Aloha agreed to a standard that Tampa

15   Bay Water agrees to.  And the standard that they have specifies

16   where and how often and when the testing will be done.  And

17   that testing, according to Tampa Bay Water, which is probably

18   the strictest standard in the United States that I'm aware of,

19   says it will be done at the point of connection.  And there is

20   a number of reasons for that.

21             There is no way for Tampa Bay Water to know what

22   happens to the water once it leaves their facility, and that is

23   true with Aloha or anyone else.  When there is intermix of

24   waters like in the case of Aloha with Pasco County's water,

25   there is no way for Aloha to be held responsible for the water

FLORIDA PUBLIC SERVICE COMMISSION

322

1   that is intermixed afterward.  There is nothing Aloha could do

2   about it.  One of the things, Ralph, that has been talked about

3   here in that vein is what would you do if you found a number

4   that didn't meet it after the water is intermixed.  And someone

5   has said, well, maybe it ought to be treated.  The problem is

6   the water can't be treated.  It has already been chloraminated.

7   So there is no way good way to retreat the water.  It is a

8   technical problem.

9        Q    Please turn to Page 7, Lines 20 to 25.

10        A    Yes.

11        Q    You say something to the effect that if Aloha were

12   ordered to meet an MCL, it would have to provide its own

13   treatment for Pasco's already treated water to ensure that

14   water provided at its customers' meters met the MCL.  This

15   would be very expensive to accomplish and would serve no useful

16   purpose, is that correct?

17        A    That's right.  And the reason it would be very

18   expensive is I'm not even sure how you would do it.

19        Q    Did you prepare a 2002 water facilities upgrade

20   report for Aloha Utilities?

21        A    I did.

22        Q    As part of that report, did you prepare a section

23   which estimated the cost for building packed tower aeration

24   facilities in the Aloha service area?

25        A    I did.

FLORIDA PUBLIC SERVICE COMMISSION

323

1        Q    Did your study conclude that to provide packed

2   tower -- or, I'm sorry, packed tower aeration for all of

3   Aloha's well sources, it would be necessary to build three

4   centralized water treatment plants?

5        A    Yes, I did.

6        Q    And was one of these centralized water treatment

7   plants designed to tie in only Wells 8 and 9?

8        A    That's correct.

9        Q    And is this referred to as the new Wyndtree water

10   treatment plant?

11        A    That is correct.

12        Q    What was your estimated total capital cost of

13   building packed tower aeration for Aloha?

14        A    You're going to have to give me a minute to look for

15   it.

16        Q    Turn to Page 30, I think you will find it there.

17        A    I was going to say, I believe it was $14,950,000.

18        Q    And 918?

19        A    And 718.

20        Q    What was your estimated capital cost for building the

21   Wyndtree water treatment plant only?  I think that's on Page

22   32.

23        A    About $3.5 million.  Wait a minute, that's not true,

24   because you still have to have the piping modifications.

25        Q    I'll ask that question.

FLORIDA PUBLIC SERVICE COMMISSION

324

1        A    You're going to help me?

2        Q    Yes.  Would there also be additional piping required

3   of 120,000 to get the water delivered to the appropriate

4   location in the distribution system?

5        A    Yes, and there may be more.  I realize that the Line

6   Item Number 6, I think that you are talking about --

7        Q    That's Page 35.

8        A    Yes, 6 and 7.  There's others that would need to be

9   done, too, Ralph, and off the top of my head, without looking,

10   I couldn't tell you which ones.

11        Q    Would Aloha have to buy additional land for this

12   packed tower aeration?

13        A    Well, at 8 and 9 they have some land available at

14   this time.  Whether it is suitable or the right size is yet to

15   be determined, but it is not at the existing well sites.  So it

16   may be that there is more land required.

17        Q    Would there be other costs such as engineering survey

18   fees that would have to be added in to get to a total cost for

19   the Wyndtree water treatment plant?

20        A    Yes.

21        Q    And I believe somewhere you estimated that would be

22   approximately 12 percent of the final total?

23        A    Well, back in those days, yes.  Those numbers have

24   risen over the last three or four years.

25        Q    What would it be?

FLORIDA PUBLIC SERVICE COMMISSION

325

1        A    I couldn't tell you off the top of my head.

2   Permitting requirements have gone up, and the amount of effort

3   that goes into permitting has also gone up.

4        Q    Did you also estimate the annual O&M budget for all

5   three water treatment plant facilities?

6        A    I did.

7        Q    And that was on Page 34.  What did you estimate that

8   cost to be?

9        A    About $4 million.

10        Q    Can you estimate what the annual cost would be to

11   operate the Wyndtree water treatment plant only?  I think

12   that's on Page 34.

13        A    Well, close.  I mean, some of the personnel and

14   administrative costs would still have be attributed to it, but

15   slightly over a million dollars.

16        Q    I'm going to go to an annual report.  I have

17   Marshall -- let's see if you know this subject.  In the annual

18   report it shows annual revenues for the Seven Springs water

19   system of $1,663,692.  Subject to check, would you agree that's

20   the annual revenues for the Seven Springs water system?

21        A    Subject to check, sure.

22        Q    Would you have any idea what percentage increase in

23   revenue it would take to provide only packed tower aeration for

24   the new Wyndtree water treatment plant for Wells 8 and 9?

25        A    I have got to be honest, I do not.

FLORIDA PUBLIC SERVICE COMMISSION

326

1        Q    Would it be probably over 100 percent increase?

2        A    Oh, I think that is probably a safe bet.

3        Q    Can you tell me if Aloha has converted all of its

4   water treatment plant currently from chlorination to

5   chloramines?

6        A    It is in the process of doing so.

7        Q    How many wells have been converted?

8        A    None of them have been totally converted because they

9   all have to be done at once.  All of them are in construction,

10   and all of them are far along in the process.

11        Q    How soon do you think that will be done, the

12   chloramines?

13        A    If you asked me this question after Thursday I could

14   tell you, there is a progress meeting.  I really don't know off

15   the top of my head at this point.  Soon.

16        Q    Are you still filing those progress reports?

17        A    Yes.

18        Q    Has Aloha constructed any facilities for the hydrogen

19   peroxide process that Doctor Levine is proposing?

20        A    Well, no.  The hydrogen peroxide process, no, because

21   Doctor Levine's work is still underway.

22        Q    So that is still in the pilot project process?

23        A    Uh-huh.

24        Q    And is the utility going to construct any of these

25   facilities for the injection of hydrogen peroxide?

FLORIDA PUBLIC SERVICE COMMISSION

327

1        A    That is the intent once Doctor Levine's work is done

2   and proves to be correct.

3        Q    I think right now there is only one interconnect with

4   the county, is that correct?

5        A    There is only one interconnect that is provided for

6   in the agreement with the county, that's correct.

7        Q    And that is up by Little Road and State Road 54?

8        A    That's correct.

9        Q    Is there any room there to build any treatment

10   facilities?

11        A    None.

12        Q    And you don't know of any other planned

13   interconnects?

14        A    No.  At this point in time, that is the only one that

15   has been identified.

16        Q    Now, can Aloha buy untreated water from the county?

17        A    No.

18        Q    And what is the catalyst for Aloha having to buy the

19   water from the county?

20        A    The fact that the water management district would not

21   allow Aloha to develop any new wells or pump its existing wells

22   at a greater rate than it does in the permit.

23        Q    So they are at the limit of their CUP or WUP or

24   whatever they call it?

25        A    The WUP.  The water use permit, that's correct.

FLORIDA PUBLIC SERVICE COMMISSION

328

1        Q    Now, Aloha's system consists of eight wells and they

2   are all interconnected, right?

3        A    That's correct.

4        Q    And so when a customer gets his water, he can't be

5   sure what well he got it from?

6        A    That's correct.  It depends on the demand and a

7   number of other issues.

8        Q    Wouldn't common sense tell you that if you are having

9   trouble in the south, and that when Wells 8 and 9 went on line

10   they started having the black water, that Wells 8 and 9 are in

11   the south, that possibly the problem might be with Wells 8 and

12   9?

13        A    Well, it depends on -- Ralph, you listen to the

14   customer testimony I have heard in the various cases we have

15   had, some people say that the problems began before those wells

16   were put on line.  Others say it happened after.

17        Q    I thought somewhere in your testimony you said

18   something about in late '95 or early '96 these problems -- that

19   you became aware of these problems?

20        A    That's when Aloha became aware of them in mass

21   numbers or in larger numbers.

22        Q    But can you tell me where most of the complaints

23   about black water are coming from?

24        A    I think it is that section of the service area.

25        Q    So all of those subdivisions are in the south of

FLORIDA PUBLIC SERVICE COMMISSION

329

1   Aloha's territory?

2        A    Pretty much so, yes, the majority.

3        Q    And, again, that's where Wells 8 and 9 are?

4        A    That's correct.

5        Q    And weren't Wells 8 and 9 put in in the fall of 1995?

6        A    I didn't put them in, but I think that's correct.

7   Subject to check, I believe that is correct.

8        Q    If you could take Wells 8 and 9 off line, if the

9   water management district would let you, and they would let you

10   drill two new wells in another area that might not have the

11   problem, what would be that cost?

12        A    I don't have those numbers.

13        Q    Do you have any estimate whatsoever?

14        A    No.

15        Q    You don't know how much it cost to drill Wells 8 and

16   9?

17        A    To be perfectly honest, I'm not sure.

18        Q    Is there any way we could get that in a late-filed

19   exhibit?  How long would it take you to calculate that number?

20             MR. DETERDING:  Commissioner, this is way beyond

21   anything in his direct testimony.

22             MR. JAEGER:  He talked about cost and expense, and we

23   are trying to figure out --

24             CHAIRMAN BAEZ:  Hold on.

25             MR. DETERDING:  He talked about costs and expense

FLORIDA PUBLIC SERVICE COMMISSION

330

1   related to the issues in this docket, not in relation to moving

2   treatment facilities.

3             CHAIRMAN BAEZ:  Mr. Jaeger, exactly what is your

4   point in trying to get this information.  Because I'm --

5             MR. JAEGER:  We are trying --

6             CHAIRMAN BAEZ:  Is it a matter of identifying

7   alternatives of some sort?

8             MR. JAEGER:  Alternatives, cheaper alternatives.

9             MR. DETERDING:  Again, I don't see -- I believe this

10   is far outside the scope of his direct testimony.  And,

11   frankly, I think it is outside the scope of the issues in this

12   proceeding.

13             CHAIRMAN BAEZ:  Well --

14             MR. DETERDING:  Chairman, if we were dealing with --

15             CHAIRMAN BAEZ:  Exactly what is it that you are

16   requesting?  I'm sorry, I want to be clear.

17             MR. JAEGER:  Chairman, staff tells me that we don't

18   need that information and that we can withdraw the question.

19             CHAIRMAN BAEZ:  Very well.

20             MR. JAEGER:  And I have no further questions.

21             CHAIRMAN BAEZ:  No further questions.

22             Commissioners, do you have any questions of Witness

23   Porter at this point?  Redirect.

24             MR. DETERDING:  I have a few redirect.

25                        REDIRECT EXAMINATION

FLORIDA PUBLIC SERVICE COMMISSION

331

1   BY MR. DETERDING:

2        Q    You mentioned the people in attendance from the

3   county at meetings at which they refused to commit to providing

4   water in conformance with the Tampa Bay Water standard.  You

5   mentioned a Mr. Bramblett and Mr. Kennedy?

6        A    One or the other, or perhaps both.  I don't remember

7   who was there, to be honest.

8        Q    And Mr. Bramblett, I believe you said in response to

9   the questions from staff counsel was the utility director for

10   the county at that time?

11        A    Yes.

12        Q    And is now retired?

13        A    Yes.

14        Q    And who is his replacement?

15        A    Bruce Kennedy.

16        Q    What is the effect of the Tampa Bay Water standard?

17   What happens if Tampa Bay doesn't meet it?

18        A    Well, if Tampa Bay Water does not meet the standard,

19   then there are monetary issues that kick in.  In other words,

20   they must meet the standard.  If they do not, they either

21   provide the water -- my understanding is they provide the water

22   at a cheaper rate to the member government, if the member

23   government is willing to retreat the water or do something

24   along those lines.  And I'm not aware of any governments who

25   are willing to do that.  I think they have all put it back on

FLORIDA PUBLIC SERVICE COMMISSION

332

1   Tampa Bay Water, to the best of my knowledge.

2        Q    But it doesn't impose on Tampa Bay Water an

3   obligation to do something to come into conformance?

4        A    Not that I am aware of, no.

5        Q    Are you aware of whether Tampa Bay Water has always

6   met that standard?

7        A    No.  As a matter of fact, I think my understanding is

8   that they have had trouble meeting that standard from time to

9   time.  And the also time I was aware of it was at a seminar

10   that I attended where I believe there was some handout

11   information that showed that they hadn't met it in many cases.

12        Q    You were asked about your report that you prepared

13   sometime ago?

14        A    Yes.

15        Q    What is the date of that report?

16        A    October 2002.

17        Q    Have prices changed since that time?

18        A    Oh, dramatically, especially for construction

19   materials.

20        Q    Specifically as to construction materials?

21        A    Yes, specifically.  I mean, steel prices have gone up

22   considerably and so have, in many cases, concrete and some

23   other materials.

24        Q    Now, you were asked about the relationship, I think

25   staff was asking you about the relationship between Wells 8 and

FLORIDA PUBLIC SERVICE COMMISSION

333

1   9 going on-line and the complaints.  Didn't Aloha start a rate

2   proceeding at the exact same time that those complaints

3   started?

4        A    Not only a rate proceeding, but the largest one ever

5   asked for by Aloha.  And the first one that had been done and

6   asked for, I believe, in 20-some-odd years, as far as not a

7   pass-through.  I mean, an honest to God rate case.  So, yes, it

8   was.

9             MR. DETERDING:  That's all I have.  Thank you.

10             MR. JAEGER:  Chairman Baez, I would like just a

11   couple of questions on that last question.

12             CHAIRMAN BAEZ:  Can you come on over, because I don't

13   think Jane can hear what you are saying and neither can I.

14             MR. JAEGER:  That last question Marty asked, I just

15   wanted to ask a couple of questions on that.

16             CHAIRMAN BAEZ:  Go ahead, Ralph.

17                         RECROSS EXAMINATION

18   BY MR. JAEGER:

19        Q    There was a rate proceeding that was filed in '95,

20   and they had a customer meeting in August of '95.  Were you

21   there for that?

22        A    If it was '95, no, I don't think so.  You know, I

23   don't know.  A customer meeting in --

24        Q    It's Docket Number 950615, and it was filed in '95

25   and the customer meeting was in August.  Were you there?

FLORIDA PUBLIC SERVICE COMMISSION

334

1        A    I don't remember, to be honest with you.  I would

2   have to look at something.  Can you stand by a minute?  What

3   was the docket number again, Ralph?

4        Q    950615.  And it was combined with 960545 was the

5   combination.

6        A    Yes, I was.

7        Q    Do you remember there being the first complaint about

8   black water in August of '95?  I mean, there was complaints

9   about discolored yellow or green, but was there the first

10   complaint at that customer meeting about black water?

11        A    You know, Ralph, I'm going to be honest with you, I'm

12   not sure I was at that customer meeting.  I was at the hearings

13   later.  Was this the reuse case that you are talking about?

14        Q    It started out as a reuse case, yes, and then the

15   customers piggybacked their complaint about the black water

16   problem.

17        A    You know, I've got to be honest, I don't know if I

18   was at that customer meeting or not.  I don't remember.

19        Q    Would you, subject to check, be surprised if you

20   listened to the tape of that meeting that there was not the

21   first black water complaint at that meeting?

22             MR. DETERDING:  Commissioners, we don't even know if

23   he was there, so why are we asking him about what when on

24   there?

25             MR. JAEGER:  You asked about he was involved in the

FLORIDA PUBLIC SERVICE COMMISSION

335

1   largest rate deal and about when these black water complaints

2   started in earnest.  And I just wanted to see if he was there.

3             CHAIRMAN BAEZ:  Mr. Jaeger, hold on.  Let me short

4   circuit this.  I think the question was merely one of timing.

5   And I don't remember his involvement being -- I don't know,

6   Jane, you can correct me -- but I don't remember his

7   involvement being questioned whatsoever.  I will let the

8   question go.  Up until now he has answered it, he doesn't

9   remember being in it, and I don't know that we can go any

10   farther than that.  Do you have any other questions?

11             MR. JAEGER:  No further questions, Commissioners.

12             CHAIRMAN BAEZ:  Mr. Deterding, do you have any other

13   redirect?

14             MR. DETERDING:  No.

15             CHAIRMAN BAEZ:  Commissioners, do you have any

16   questions at this point?  No.

17             Mr. Porter, thank you.

18             THE WITNESS:  Thank you.

19             CHAIRMAN BAEZ:  We are on to rebuttal.  Dr. Kurien,

20   rebuttal witness.

21             MR. WHARTON:  You know, Mr. Chairman, I discussed

22   with Mr. Jaeger that he doesn't have any cross questions and

23   neither do I.  Maybe we could stip Dr. Kurien's rebuttal.

24             CHAIRMAN BAEZ:  Well, with all the cross-examining

25   out of the way, is there any reason we can't stip?

FLORIDA PUBLIC SERVICE COMMISSION

336

1             MR. BECK:  Unless the Commissioners have questions.

2             CHAIRMAN BAEZ:  Commissioners, do you have questions

3   of Dr. Kurien on rebuttal?  No questions?  All right.  We will

4   stipulate Dr. Kurien's rebuttal testimony into the record.

5             Does he have exhibits?

6             MR. BECK:  Yes, VAK-19 through 27.

7             CHAIRMAN BAEZ:  VAK-19 through 27, correct.

8             MR. WHARTON:  And my objections to those exhibits

9   would only be as before, that I believe some are hearsay in the

10   purest sense.

11             CHAIRMAN BAEZ:  You can reserve those on brief.  And

12   that would be VAK.  Any objection to a composite exhibit at

13   this point?  We didn't do it the first time, but since you have

14   the same objections reserving --

15             MR. WHARTON:  Correct.

16             CHAIRMAN BAEZ:  -- we will do Composite 23 will be

17   Dr. Kurien's rebuttal Exhibits VAK-19 through 27.  And with Mr.

18   Wharton's exceptions noted, we will admit them into the record.

19             (Exhibit 23 marked for identification and admitted

20   into the record.)

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

360

1             MR. WHARTON:  We might be able to handle Mr. Porter's

2   rebuttal the same way, Mr. Chairman, but I haven't talked to

3   Mr. Beck.

4             CHAIRMAN BAEZ:  Well, we will have to take a poll on

5   that.

6             Dr. Kurien, you are excused.  Thank you, sir.

7             And, Mr. Beck.

8             MR. BECK:  I'm all in favor, let's stipulate Mr.

9   Porter's rebuttal and Mr. Sowerby.

10             CHAIRMAN BAEZ:  I'm sorry?

11             MR. BECK:  I would agree to stipulate Mr. Porter's

12   testimony, the rebuttal testimony.

13             CHAIRMAN BAEZ:  Very well.  Mr. Jaeger, do you

14   have --

15             MR. JAEGER:  No cross for Mr. Porter.

16             CHAIRMAN BAEZ:  No cross for Mr. Porter.

17             Commissioners, did have you any questions of Mr.

18   Porter on rebuttal?  No.  I think we can stipulate Mr.

19   Porter's -- and I am trying to look, I don't see any exhibits

20   for Mr. Porter on rebuttal, or do I?

21             MR. DETERDING:  No.

22             CHAIRMAN BAEZ:  He has no exhibits.  So without

23   objection, we will stipulate Mr. Porter's rebuttal testimony

24   into the record as though read, as well.

25

FLORIDA PUBLIC SERVICE COMMISSION

366

1             CHAIRMAN BAEZ:  Where does that leave us, Ralph?

2             MR. JAEGER:  I believe that it is now just what do we

3   do about post-hearing.

4             CHAIRMAN BAEZ:  That does it?  Okay.  So then why

5   don't run down -- we are done with the witnesses, why don't we

6   run down some post-hearing scheduling.

7             MR. JAEGER:  Right now the transcripts are scheduled

8   for March 24th, 2005.  But I do note that that was when this

9   was a three-day hearing, and so all the dates were set giving

10   them a little bit more time.  And briefs by April 7th, with a

11   staff recommendation scheduled for May 19th for the May 31st

12   agenda.

13             CHAIRMAN BAEZ:  Can you say those again, because I

14   couldn't hear you?

15             MR. JAEGER:  March 24th is the dates for transcripts.

16             CHAIRMAN BAEZ:  The briefs?

17             MR. JAEGER:  And we have briefs scheduled for

18   April 7th, 2005.

19             COMMISSIONER BRADLEY:  And the rec?

20             MR. JAEGER:  May 19th, 2005.

21             CHAIRMAN BAEZ:  To file, right?

22             MR. JAEGER:  For the May 31st, 2005 agenda.

23             CHAIRMAN BAEZ:  Any questions or objections on the

24   schedule?

25             MR. WHARTON:  I do think two weeks for briefs is a

FLORIDA PUBLIC SERVICE COMMISSION

367

1   little tight.

2             MR. JAEGER:  Chairman Baez, I talked to Mrs.  Faurot,

3   I think she could address this, but she said she could get the

4   transcripts out probably a lot sooner than March 24th.  And I

5   think she said that say she could probably much say the 15th

6   might be hard, or 16th, but she could probably have the

7   transcripts out by the 16th.

8             CHAIRMAN BAEZ:  Maybe we can wrap your concern into

9   this, and so I'm only -- I would like to keep the outside dates

10   intact so that whatever days you are picking up, whatever days

11   you are picking on briefing, it sounds considerable, you will

12   pick it up off whatever Mrs. Faurot can do on the transcripts.

13             Jane, what I would ask is that you get together with

14   staff counsel and -- on the 15th?  On the 15th.  Now you are

15   picking up ten days, nine or ten days by my --

16             MR. WHARTON:  Thank you very much.

17             CHAIRMAN BAEZ:  Well, it is all Jane's fault.  I had

18   nothing to do with it.  So thank her.  Very well.  So we will

19   have transcripts on close of business on the 15th, briefs on

20   the 7th of April, recommendation to be filed on the 19th, and

21   agenda on the 31st.

22             Is there anything else we need to take up?

23             MR. JAEGER:  None that I know of, Mr. Chairman.

24             CHAIRMAN BAEZ:  Mr. Beck, anything?

25             MR. BECK:  No, sir.

FLORIDA PUBLIC SERVICE COMMISSION

368

1             MR. WHARTON:  Not from us.

2             CHAIRMAN BAEZ:  Not from you.  All right.  Very well.

3   Thank you very much.  Thank you for staying late.

4             MR. JAEGER:  Thank you, Commissioners.

5             CHAIRMAN BAEZ:  We are adjourned.

6             (The hearing concluded at 6:25 p.m.)

7

8

9

10

11

12

13

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

369

1   STATE OF FLORIDA    )

2                       :              CERTIFICATE OF REPORTER

3   COUNTY OF LEON      )

4

I, JANE FAUROT, RPR, Chief, Office of Hearing

5   Reporter Services, FPSC Division of Commission Clerk and

Administrative Services, do hereby certify that the foregoing

6   proceeding was heard at the time and place herein stated.

7             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

8   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

9   proceedings.

10             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

11   or employee of any of the parties' attorney or counsel

connected with the action, nor am I financially interested in

12   the action.

13             DATED THIS 15th day of March, 2005.

14

15             ___________________________________________

JANE FAUROT, RPR

16             Chief, Office of Hearing Reporter Services

FPSC Division of Commission Clerk and

17                       Administrative Services

(850) 413-6732

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION