Cost Impact to Tampa Electric of Proposed Changes to

Rule 25-6.034 Standard of Construction

Revised May 26, 2006

(5)(a)New Overhead construction cost impact for a 120 mph wind zone

Assumptions:

50% of the poles have equipment (i.e., transformers, capacitors etc)

150 foot spans or 35 poles per mile (50% more poles)

Two joint users

Hardening pole replacements

45H2 wood poles w/equipment

45H1 wood poles w/o equipment

Impacts:

The incremental new 3 phase wood pole construction to annually build 19 miles to extreme wind-loading criteria is estimated to be $354,445.

(b) Expansion, rebuild, or relocation of existing facilities for a 120 mph wind zone

Assumptions:

75% of the poles have equipment (i.e., transformers, capacitors etc)

150 foot spans or 35 poles per mile (50% more poles)

Two joint users

Hardening pole replacements

45H2 wood poles w/equipment

45H1 wood poles w/o equipment

Includes Additional poles + incremental stronger pole cost + road widening

Impacts:

Annual cost to build to extreme wind for expansion, rebuild and relocation including road widenings of 3 phase wood pole lines is estimated to be $5,334,313.

- Targeted critical infrastructure facilities and major thoroughfares1

Hillsborough Co	521 miles

Polk Co		127 miles

Pasco		  48 miles

Total		696 miles

Assumptions:

Assume a ten year hardening plan @ approximately 70 miles/year

75% of the poles have equipment (i.e., transformers, capacitors etc)

150 foot spans or 35 poles per mile

Two joint users

Hardening pole replacements

45H2 wood poles w/equipment

45H1 wood poles w/o equipment

Impacts:

The annual cost to build targeted critical infrastructure facilities and major thoroughfares to extreme wind  is $6,396,950. A ten year plans is unrealistic but is used here for normalization and comparison purposes.

1From “FDOT’s Public Road mileage and Miles Traveled, 2004” report using Other Principle Arterials and Minor Arterials Categories. Further assumptions were made pertaining to partial service territories in counties.

(6)(a)(b)&(c) New construction cost impact for Cat 3 Flood Zone

Assumption:

Based on 2005 UG New Construction     		$ 30,407,527

25% of $ is in Cat 3 Surge Zone                      	$   7,601,881

Annual 30% adder to harden the UG facilities3            $  2,280,564

Impacts:

The annual minimum incremental new UG construction cost to build in Cat 3 Surge Zone is estimated to be $2,280,584. This high level estimate was based on dollars spent with an assumed hardening adder.  The company is unable to provide an accurate estimate for parts b and c of the proposed rule.  The extent and characteristics of facilities located in the Cat 3 Flood Zone is unknown at this time.

(8) Expansion, rebuild, relocation & OH to UG conversions to front edge of property

OH to OH conversions to front edge of property

Expansion, rebuild, relocation

Assumptions

10% of OH system is rear lot = 700 miles

Single phase OH line

40% of the poles have equipment (i.e., transformers, capacitors, etc.)

150 foot spans or 35 poles per mile

Two joint users

Hardening pole replacements

45H2 wood poles w/equipment

45H1 wood poles w/o equipment

2.5 difficulty factor is included for rear lot work

Impacts:

The annual relocation cost of an overhead single phase wood pole line from a rear lot location to the front of property using 70 miles per year is estimated to be $6,274,800.

OH to UG conversions to front edge of property

Assumptions

Davis Islands conversion cost was used in the cost per mile average of $571,428.

1% of the rear lot communities request underground facilities to be placed to the front of the property = 70 miles

10 year plan to complete = 7 miles per year

Impacts:

The annual relocation cost of an overhead single phase wood pole line from a rear lot location to

relocate and underground to the front of property is $5,250,000.

Combined conversion annual cost is $11,524,800.

3 Hardening of the Underground facilities consist of water proof switchgear (Vistagear), strand-filled cable and submersible secondary TX connectors). All equipment will be bolted to pad.