1

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

In the Matter of:

3

PROPOSED RULES GOVERNING PLACEMENT      DOCKET NO. 060172-EU

4   OF NEW ELECTRIC DISTRIBUTION

FACILITIES UNDERGROUND, AND CONVERSION

5   OF EXISTING OVERHEAD DISTRIBUTION

FACILITIES TO UNDERGROUND FACILITIES,

6   ADDRESS EFFECTS OF EXTREME WEATHER

EVENTS.

7   _______________________________________/

8   PROPOSED AMENDMENTS TO RULES            DOCKET NO. 060173-EU

REGARDING OVERHEAD ELECTRIC

9   FACILITIES TO ALLOW MORE STRINGENT

CONSTRUCTION STANDARDS THAN REQUIRED

10   BY NATIONAL ELECTRIC SAFETY CODE.

11   _______________________________________/

12             ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

A CONVENIENCE COPY ONLY AND ARE NOT

13               THE OFFICIAL TRANSCRIPT OF THE HEARING,

THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

14

PROCEEDINGS:        HEARING

15

BEFORE:             CHAIRMAN LISA POLAK EDGAR

16                       COMMISSIONER J. TERRY DEASON

COMMISSIONER ISILIO ARRIAGA

17                       COMMISSIONER MATTHEW M. CARTER, II

COMMISSIONER KATRINA J. TEW

18

DATE:               Thursday, August 31, 2006

19

TIME:               Commenced at 9:30 a.m.

20                       Concluded at 4:05 p.m.

21   PLACE:              Betty Easley Conference Center

Room 148

22                       4075 Esplanade Way

Tallahassee, Florida

23

REPORTED BY:        LINDA BOLES, RPR, CRR

24                       JANE FAUROT, RPR

Official FPSC Reporters

25                       (850)413-6734 and (850)413-6732

FLORIDA PUBLIC SERVICE COMMISSION

2

1   PARTICIPATING:

2             JAMES MEZA III, ESQUIRE, c/o Ms. Nancy H. Sims, 150

3   South Monroe Street, Suite 400, Tallahassee, Florida

4   32301-1556, and KIRK SMITH, appearing on behalf of BellSouth

5   Telecommunications, Inc.

6             DULANEY L. O'ROARK III, Six Concourse Parkway, Suite

7   600, Atlanta, Georgia 30328, and DR. LAWRENCE M. SLAVIN,

8   appearing on behalf of Verizon Florida, Inc.

9             SUSAN MASTERTON, ESQUIRE, 1313 Blair Stone Road,

10   Tallahassee, Florida 32301, GEORGE FINN and KENT DICKERSON,

11   appearing on behalf of Embarq Florida, Inc.

12             JOHN BUTLER, ESQUIRE, and NATALIE SMITH, ESQUIRE, 700

13   Universe Boulevard, Juno Beach, Florida 33408-0420, appearing

14   on behalf of Florida Power & Light Company.

15             MICHAEL A. GROSS, ESQUIRE, 246 East 6th Avenue, Suite

16   100, Tallahassee, Florida 32303, and MICHAEL T. HARRELSON,

17   appearing on behalf of Florida Cable Telecommunications

18   Association, Inc.

19             JOHN T. BURNETT, ESQUIRE, c/o Progress Energy Service

20   Company, Post Office Box 14042, St. Petersburg, Florida

21   33733-4042, appearing on behalf of Progress Energy Service

22   Company.

23             LEE L. WILLIS, ESQUIRE, c/o Ausley Law Firm, Post

24   Office Box 391, Tallahassee, Florida 32302, and KRISTINA

25   ANGIULLI, appearing on behalf of Tampa Electric Company.

FLORIDA PUBLIC SERVICE COMMISSION

3

1   APPEARANCES CONTINUED:

2             R. SCHEFFEL WRIGHT, ESQUIRE, Young Law Firm, 225

3   South Adams Street, Suite 200, Tallahassee, Florida 32301,

4   appearing on behalf of the Town of Jupiter Island, Florida, and

5   the Town of Palm Beach, Florida.

6             GREG STEWART, appearing on behalf of the City of

7   North Miami.

8             HOWARD E. (GENE) ADAMS, ESQUIRE, c/o Pennington Law

9   Firm, Post Office Box 10095, Tallahassee, 32302-2095, and

10   CAROLYN MAREK, appearing on behalf of Time Warner Telecom of

11   Florida, L.P.

12             RUSSELL A. BADDERS, ESQUIRE, c/o Beggs & Lane Law

13   Firm, Post Office Box 12950, Pensacola, Florida, 32576-2950,

14   and ERIC LANGLEY, appearing on behalf of Gulf Power Company.

15             LINDA COX, appearing on behalf of the City of Ft.

16   Lauderdale.

17             LAWRENCE D. HARRIS, ESQUIRE, and CHRISTINA T. MOORE,

18   ESQUIRE, 2540 Shumard Oak Boulevard, Tallahassee, Florida

19   32399-0850, appearing on behalf of the Florida Public Service

20   Commission Staff.

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

4

1                              I N D E X

2   PRESENTATIONS BY:                                 PAGE NO.:

3   JIM BREMAN                                            12

4   CONNIE KUMMER                                         17

5   CRAIG HEWITT                                          18

6   JAMES MEZA, III                                       21

7   KIRK SMITH                                            24

8   DULANEY L. O'ROARK, III                               35

9   DR. LAWRENCE M. SLAVIN                                36

10   GEORGE FINN                                           70

11   KENT DICKERSON (Via Telephone)                        74

12   SUSAN MASTERTON                                       75

13   MICHAEL A. GROSS                                      84

14   MICHAEL T. HARRELSON                                  97

15   GENE ADAMS                                           114

16   ROBERT SCHEFFEL WRIGHT                               117

17   GREG STEWART                                         132

18   LEE WILLIS                                           134

19   ERIC LANGLEY                                         137

20   NATALIE SMITH                                        141

21   KRIS ANGIULLI                                        145

22   LEE WILLIS                                           150

23   JOHN BUTLER                                          152

24   JOHN BURNETT                                         159

25   CERTIFICATE OF REPORTERS                             189

FLORIDA PUBLIC SERVICE COMMISSION

5

1                              EXHIBITS

2   NUMBER:                                           ID.  ADMTD.

3   1    Staff Composite Exhibit 1                    11     11

4   2    Revised Statement of Estimated Regulatory

Costs                                        12     12

5

3    BellSouth's Presentation                     20     20

6

4    Verizon's Presentation                       36     36

7

5    Embarq's Presentation                        70     70

8

6    Memorandum of Law in Support of the FCTA's

9        Suggested Rule Changes                       85     85

10   7    Comments by Michael T. Harrelson on

behalf of the FCTA                           86     86

11

8    Description of Photos by

12        Michael T. Harrelson on behalf of

the FCTA                                     86     86

13

9    Example of Overlashing                      173    173

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

6

1                         P R O C E E D I N G S

2             CHAIRMAN EDGAR:  Good morning.  Before we begin our

3   business today, I'd like to take a moment to make a comment and

4   to recognize that approximately ten weeks ago this Commission

5   had the honor of naming this hearing room after former

6   Commissioner Joe Cresse who passed away earlier this week.  And

7   I'd like to turn to Commissioner Carter to lead us in a moment

8   of silence in his honor.

9             COMMISSIONER CARTER:  As we approach this moment, we

10   offer words of comfort to the Cresse family.  We offer words of

11   comfort to the PSC family.  For we've not lost anything with

12   Joe Cresse; what we've done is gained a giant, a gentle giant

13   who had a lifetime of public service.  Even though he was a

14   gentle giant and walked through the palaces with presidents,

15   potentates, kings and governors, he still had the common man

16   touch.  And in this hallowed hall that we dedicated just ten

17   weeks ago, we come again to recognize the legacy, the

18   leadership and the character of this person Joe Cresse.  So as

19   we prepare for this moment of silence, on behalf of my fellow

20   Commissioners, we wish you God speed, Joe Cresse.  Let us pray.

21             (Moment of silence observed.)

22             COMMISSIONER CARTER:  Amen.

23             CHAIRMAN EDGAR:  Thank you, Commissioner Carter.

24             Okay.  We will move into our scheduled business for

25   the day, and I'm going to start with asking our counsel to read

FLORIDA PUBLIC SERVICE COMMISSION

7

1   the notice.  Mr. Harris.

2             MR. HARRIS:  Yes, ma'am.  Pursuant to notice issued

3   July 30th, 2006, this time and place has been set for a rule

4   hearing in Dockets Number 060172, 060173.  The purpose of the

5   hearing is as set forth in the notice.

6             CHAIRMAN EDGAR:  Thank you, Mr. Harris.

7             I'd like to go ahead and take appearances from all of

8   those that are here, and I believe we may have some

9   participating by phone as well, so that we know who is planning

10   to speak today and also whom you are representing.

11             Mr. Meza.

12             MR. MEZA:  Thank you, Madam Chair.  My name is Jim

13   Meza on behalf of BellSouth, and with me today is our primary

14   witness Mr. Kirk Smith.

15             CHAIRMAN EDGAR:  Thank you.

16             MR. O'ROARK:  Madam Chairman, I'm De O'Roark

17   representing Verizon Florida, Inc., and our principal witness

18   today will be Dr. Larry Slavin.

19             CHAIRMAN EDGAR:  Thank you.

20             MS. MASTERTON:  Madam Chairman, Susan Masterton on

21   behalf of Embarq Florida, Inc.  And also speaking on behalf of

22   Embarq today will be George Finn and Kent Dickerson.

23             CHAIRMAN EDGAR:  Thank you.

24             MS. MASTERTON:  And Mr. Dickerson will be on the

25   phone.

FLORIDA PUBLIC SERVICE COMMISSION

8

1             CHAIRMAN EDGAR:  Okay.  Thank you.

2             MR. BUTLER:  John Butler and Natalie Smith on behalf

3   of Florida Power & Light Company.

4             CHAIRMAN EDGAR:  Welcome back, Mr. Butler.

5             MR. BUTLER:  Thank you.  It's good to be here in

6   person.

7             MR. GROSS:  Good morning, Madam Chair.  I'm Michael

8   Gross here on behalf of the Florida Cable Telecommunications

9   Association, and with me sitting to my left is Michael T.

10   Harrelson, who will be our primary expert witness in this

11   matter.  Thank you.

12             CHAIRMAN EDGAR:  Thank you.

13             MR. BURNETT:  Good morning, Commissioners.  John

14   Burnett on behalf of Progress Energy Florida.

15             MR. WILLIS:  I'm Lee Willis on behalf of Tampa

16   Electric Company.  With me today is Kris Angiulli, it's K-R-I-S

17   A-N-G-I-U-L-L-I, who will make a presentation.

18             CHAIRMAN EDGAR:  Thank you.  You may have to repeat

19   that spelling for me again later.  Okay.  And who else?  Thank

20   you.  That's okay, Mr. Wright.

21             MR. WRIGHT:  Madam Chairman, thank you,

22   Commissioners.  Robert Scheffel Wright appearing on behalf of

23   the Town of Palm Beach, Florida, and the Town of Jupiter

24   Island, Florida.

25             CHAIRMAN EDGAR:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

9

1             MR. STEWART:  Greg Stewart on behalf of the City of

2   North Miami.

3             CHAIRMAN EDGAR:  City of North Miami.  Thank you.

4             Mr. Adams.

5             MR. ADAMS:  Thank you, Madam Chairman.  Gene Adams on

6   behalf of Time Warner Telephone.  And also we have Ms. Carolyn

7   Marek for Time Warner Telephone here today.

8             CHAIRMAN EDGAR:  Thank you.

9             MR. BADDERS:  Good morning, Commissioners.  Russell

10   Badders and Eric Langley on behalf of Gulf Power Company.

11             CHAIRMAN EDGAR:  Thank you.  Is there anybody that

12   I've missed that's here that would like to speak during the

13   presentation and comment time today?

14             MS. COX:  Thank you.  I'm Linda Cox here representing

15   the City of Ft. Lauderdale.  Thank you.

16             CHAIRMAN EDGAR:  Thank you.  Is there anybody else?

17   None at this time.

18             Is there anybody joining us by phone to speak?  Not

19   at this time.  Okay.  Thank you very much.

20             This hearing will be conducted according to the

21   rulemaking provisions of Section 120.54, Florida Statutes, and

22   Rule 28-103.004, Florida Administrative Code.  The purpose of

23   this hearing is to allow the Commission to inform itself on

24   matters bearing upon the proposed rules and rule amendments by

25   giving affected persons and other interested persons an

FLORIDA PUBLIC SERVICE COMMISSION

10

1   opportunity to present comments and proposed alternate

2   language, and the opportunity for Commissioners to ask

3   questions.  This will be a little more informal than an

4   evidentiary hearing would be.  We will not be swearing

5   witnesses.  There is the opportunity to present documents that

6   we will enter in as evidence.  And if you have exhibits that

7   you would like to share with the Commission and have become a

8   part of the record of this hearing, I will ask you to give us a

9   title so that we all know what document we are referring to as

10   the record is put together and we will number them in

11   chronological order.

12             I do understand that there have been discussions and

13   that we have pretty much an agreement as to the order of

14   presentations and some time frames.  We have a lot of material

15   to cover, so I will ask that each of you be cognizant of the

16   time frames that have been discussed.  I will, of course, give

17   the opportunity for Commissioners to ask questions at any time

18   during the comments.  And if there are clarifying questions

19   from any of the others who are here today that they need to

20   pose to one of the presenters, I will give the opportunity for

21   that.  However, again, keep in mind that that question

22   opportunity is for clarification purposes.

23             Okay.  We will start in a moment with our Commission

24   staff giving us a brief overview.  But before we do that, let's

25   go ahead and take up the exhibits that we have.

FLORIDA PUBLIC SERVICE COMMISSION

11

1             We have Staff Composite Exhibit 1, Mr. Harris?

2             MR. HARRIS:  Yes, ma'am.  Staff Composite Exhibit 1

3   is the rulemaking record to this point.  I did email out to

4   persons we knew are going to participate an index to it, and

5   I've today provided one copy of that exhibit to each of the

6   principals for the people we knew were going to speak.  It

7   contains all of the materials that are relevant to this

8   proceeding today.  They all came off of the Commission's

9   website in Dockets 060172 and 060173.  So for anyone who needs

10   to pull any document we're speaking about today, they can pull

11   those off of our website or staff can make a copy of them.  But

12   we didn't, due to the size, make a copy for every person in the

13   room.  That would be Exhibit 1.

14             (Exhibit 1 marked for identification and admitted

15   into the record.)

16             CHAIRMAN EDGAR:  And then we have an Exhibit Number 2

17   that we'll be entering into the hearing record, and that is the

18   Revised Statement of Estimated Regulatory Costs.

19             Mr. Harris.

20             MR. HARRIS:  Yes, ma'am.  This was a revised

21   statement.  We got -- we filed it either yesterday evening late

22   or this morning in the docket file.  We do have a number of

23   extra copies of those for persons who haven't had a chance to

24   get one.  It is revised based on the information received after

25   the last staff workshop.  And Mr. Hewitt is here to provide a

FLORIDA PUBLIC SERVICE COMMISSION

12

1   brief overview of that with the staff rule presentation, but we

2   do have some extra copies.

3             (Exhibit 2 marked for identification and admitted

4   into the record.)

5             CHAIRMAN EDGAR:  Thank you.  Are there any other

6   exhibits at this time?

7             MR. HARRIS:  I believe a number of the parties have

8   exhibits that they're prepared to either list now, introduce

9   now or as part of their presentation, depending on your

10   preference.

11             CHAIRMAN EDGAR:  Okay.  Then I think my preference is

12   to go ahead and do that in order at the time of the

13   presentation, and we'll move through it in that manner.

14             Any other matters before we go into the overview?

15             MR. HARRIS:  If I may enter an appearance for staff.

16   Lawrence D. Harris on behalf of the Commission.  With me is

17   Christina T. Moore on behalf of the Commission.

18             CHAIRMAN EDGAR:  Thank you, Mr. Harris.

19             MR. HARRIS:  Thank you.

20             CHAIRMAN EDGAR:  Okay.  And then I will look to staff

21   now to give us an overview of the proposed rules.

22             MR. HARRIS:  Thank you.  Mr. Breman is going to lead

23   off, I believe.

24             MR. BREMAN:  Commissioners, my name is Jim Breman.

25   Due to recent hurricane activities, the level of damage to

FLORIDA PUBLIC SERVICE COMMISSION

13

1   electric infrastructure, customer outages, high restoration

2   costs and an expectation that the frequency of storms may

3   increase, this Commission initiated a multifaceted effort

4   directed at hardening, weather hardening Florida's electric

5   infrastructure.  It began on January 23rd with an open

6   workshop.  It was open to public entities, industry experts and

7   governmental representatives to report their experiences and

8   suggest options.

9             The information was presented to you at an Internal

10   Affairs of February 27th where the Commission codified its

11   multifaceted effort into a program that had both short-term and

12   long-term actions.  The short-term actions required electric

13   utilities to brief the Commission on storm readiness status on

14   the June 5th Internal Affairs meeting.

15             The long-term action has two parts.  One part

16   consists of requiring the investor-owned electric utilities to

17   provide plans to implement ten storm hardening initiatives

18   which the Commission identified.  The second long-term action

19   was to modify the Commission rules to facilitate and encourage

20   storm hardening activities.

21             With respect to the ten storm hardening initiatives,

22   the Commission did not dictate how the utilities were to

23   achieve or implement each initiative.  Rather, the utilities

24   were required to respond to the policies and goals established

25   by the Commission.

FLORIDA PUBLIC SERVICE COMMISSION

14

1             The proposed rules today that are under review at

2   this hearing similarly do not dictate to the electric utilities

3   how they are to achieve or implement storm hardening.  Rather,

4   the electric utilities must prudently respond to the expressed

5   Commission policy.

6             The rule requires that all actions and interactions

7   of the electric utilities will be thoroughly reviewed and

8   subject to safeguards such as Commission complaint process.

9             With respect to construction of electric

10   infrastructure, there are four proposed rules expressing

11   Commission policy.  Rule 25-6.03 is titled "Construction

12   Standards."  6.0341 is titled "Location of Utility Electric

13   Distribution Facilities."  6.0342 is titled "Third-Party

14   Attachment Standards and Procedures."  And Rule 6.0345 is

15   titled "Safety Standards for Construction of New Transmission

16   and Distribution Facilities."

17             Commissioners, if you want me to briefly go into each

18   rule, I will.  It's, it's up to you.

19             CHAIRMAN EDGAR:  Let's do that briefly.  I think that

20   will be helpful.

21             MR. BREMAN:  Thank you.  The construction standard

22   rule clarifies that under emergency conditions and to the

23   extent reasonably practical, feasible and cost-effective

24   utilities are to include extreme wind loading criteria as

25   specified by the National Electric Safety Code, and flooding

FLORIDA PUBLIC SERVICE COMMISSION

15

1   and storm surge level matters.  The standards of construction

2   are to include guidelines and procedures establishing the

3   criteria governing the applicability and use of such extreme

4   wind load standards to enhance reliability and reduce service

5   restoration costs and outage times for three types of

6   construction:  New construction, major or planned work,

7   rebuilding, relocation projects, that's all one group, and also

8   for targeted or critical infrastructure.

9             Consequently, utilities shall at a minimum comply

10   with the National Electric Safety Code.  The standards of

11   construction are to be developed with consideration of input

12   from entities with existing shared use agreements.  And the

13   standards of construction must be completed and be available

14   for review 180 days after the effective date of the rule.  The

15   rule specifically includes that any dispute or challenge to the

16   construction standards will be resolved by the Commission.

17             Rule 6.0341, the location of electric utility

18   distribution facilities, expresses a preference for electric

19   facilities being placed in a readily accessible location and

20   provides several examples such as use of public roadways and

21   frontage of property, again, to the extent that it is

22   reasonable, feasible and cost-effective.

23             The rule also requires explicitly that electric

24   utilities seek input from and coordinate construction with the

25   third parties that are affected by the projects on the existing

FLORIDA PUBLIC SERVICE COMMISSION

16

1   distribution facilities that are subject to change.

2             Rule 6.0342, third-party attachment standards and

3   procedures, addresses a requirement for the electric utilities

4   to have standards and procedures that prudent utilities should

5   have with respect to assuring that their facilities are

6   reliable and perform well.  The standards and procedures are to

7   be developed with consideration of input for the entities with

8   existing shared use agreements.  Again, any disputes are

9   challenged and subject to the Commission's dispute resolution

10   oversight.

11             And Rule 6.0345, safety standards for construction of

12   new transmission and distribution rule, is a rule that's been

13   around for a while.  This rule states what the electric safety

14   standards are for the State of Florida.  The only substantive

15   change to the safety standard rule is the inclusion of the

16   phrase "at a minimum," and that's in (1) of the rule.

17             This new sentence reads, "Each investor-owned

18   electric utility, rural electric cooperative and municipal

19   electric system shall, at a minimum, comply with the standards

20   in these provisions."  The phrase "at a minimum" is included

21   because Senate Bill 888 included the phrase, and to avoid

22   appearance of tension between Commission policy, Commission

23   rules and the Florida Statutes.  All other proposed changes to

24   the safety standard rule are simply cleanup and editorial in

25   nature.

FLORIDA PUBLIC SERVICE COMMISSION

17

1             Thank you, Commissioners.

2             CHAIRMAN EDGAR:  Thank you, Mr. Breman.

3             Go ahead.

4             MS. KUMMER:  Connie Kummer, Commission staff.  The

5   last three rules address how the cost of the construction

6   Mr. Breman talked about is recovered from the customers.

7             Rule 25-6.064 is the general catchall of

8   contribution-in-aid-of-construction rule.  A lot of the changes

9   in there are simply cleanup and clarification.  The main

10   changes are to expand the rule to cover upgrades as well as

11   line extensions.  It also provides for a true-up of the

12   estimates used to calculate the CIAC, and it requires a

13   proration of the CIAC when more than one customer is going to

14   benefit from the construction.

15             Rules 25-6.078 and 25-6.115 both deal with the

16   construction of underground facilities.  6.078 deals only with

17   the installation of underground facilities in new subdivisions.

18   6.115 addresses the conversion of over -- existing overhead

19   facilities to underground.  And there are two primary changes

20   in philosophy or approach that we made to those rules.

21             The first is that the CIAC estimates must include the

22   net present value of life cycle costs, and that is to capture

23   the, not only the initial installation cost difference, but

24   also the ongoing differences in operations and maintenance

25   costs and also storm restoration costs.

FLORIDA PUBLIC SERVICE COMMISSION

18

1             The other major change allows the waiver of a CIAC if

2   the utility can demonstrate that the general body of ratepayers

3   will benefit from the construction.  Thank you.

4             MR. HARRIS:  And, Chairman, if I might, one

5   additional comment.  Except for 25-6.0345, none of the rules

6   here today are addressing the municipals and co-ops.  As you

7   recall, we broke out a separate docket for them.  That will be

8   going to hearing on October 4th currently.  So I wanted to make

9   it clear that although I think we have some cities and towns

10   here to speak, really the rules we're dealing with today,

11   except for .0345, are addressed at the investor-owned

12   utilities, the IOUs.

13             And now I think Mr. Hewitt is going to give a brief

14   presentation on the revised statement of estimated regulatory

15   costs.

16             MR. HEWITT:  Commissioners, Craig Hewitt, Commission

17   staff.  Previously we estimated -- or the companies -- IOUs --

18   the four major IOUs estimated that their hardening costs for

19   the capital improvements would be between $63 million and

20   $193 million.  The other affected parties subsequently

21   requested a revised SERC, which we did, and they also submitted

22   additional data.  These parties, they feel that they will face

23   with these rules some combination of higher pole rates, a cost

24   to move the pole locations along with electrics, and the cost

25   if they go underground, and possible increases in the cost to

FLORIDA PUBLIC SERVICE COMMISSION

19

1   maintain abandoned poles in case electrics moved and left them

2   behind.

3             These pole attachers have some substantial estimates

4   of increased costs if they had to do -- follow these changes in

5   the rules.  A major telecom estimated it could cost

6   $500 million if they changed out 10 percent of their

7   facilities.  And depending on which type of change occurred,

8   they had estimates ranging across the board.

9             Another telecom estimated it would cost between

10   $110,000 and $170,000 per mile to change overhead-to-overhead

11   locations.

12             Another estimate was to go underground would be

13   between $90,000 and $120,000 per mile.  Another telecom

14   estimated it would cost for a 10 percent change in the

15   locations $20 million.

16             Another study did a -- another company did a study on

17   undergrounding, and it estimated it would cost $4,000 per

18   household to go underground, if that was the choice.

19             And, finally, the cable association estimated that it

20   would cost approximately $20,000 per mile for overhead

21   movements, and $125 to $150 per service drop.  And to go

22   underground would cost between $35,000 and $40,000 per mile.

23             And, additionally, if they had to change in a

24   built-out subdivision, they estimated it would cost between

25   $100,000 and $150,000 per mile because they had to do

FLORIDA PUBLIC SERVICE COMMISSION

20

1   underground boring or under obstacles.  That's it.  Thank you.

2             CHAIRMAN EDGAR:  Thank you.

3             Mr. Harris.

4             MR. HARRIS:  Thank you, Chairman.  That concludes the

5   staff's presentation and summary of the rule.  We're now

6   available to answer your questions and any questions from

7   parties, if that's your pleasure.

8             CHAIRMAN EDGAR:  Okay.  Commissioners, before we move

9   into presentations, are there any questions of our staff at

10   this time?  No.

11             Okay.  Then I think we will move into presentations.

12   And, Mr. Meza, you are up.

13             MR. MEZA:  Thank you, Madam Chair.  We have a

14   presentation that we would like to present and have marked as

15   the next exhibit.

16             CHAIRMAN EDGAR:  Mr. Meza, do you want to describe or

17   title your exhibit for me?

18             MR. MEZA:  Yes, ma'am.  It's BellSouth's

19   presentation.

20             (Exhibit 3 marked for identification and admitted

21   into the record.)

22             MR. MEZA:  Thank you.  Good morning.  My name is Jim

23   Meza.  I represent BellSouth.  And with me today is Kirk Smith,

24   our subject matter expert on this issue.  I'm going to provide

25   a few introductory comments, and Mr. Smith is going to walk

FLORIDA PUBLIC SERVICE COMMISSION

21

1   through the presentation with you within the time frames

2   established by the Commission.

3             CHAIRMAN EDGAR:  Thank you.

4             MR. MEZA:  First, I want to thank you for the

5   opportunity to present evidence and argument regarding the

6   proposed electric hardening rules today.  This proceeding is of

7   great importance to BellSouth.  It is important because we

8   understand the desire and need to attempt to decrease power

9   outages following a hurricane.  But it's also important because

10   complying with these rules could cost, pursuant to BellSouth's

11   estimate, up to $4 billion plus solely because it attaches to

12   poles owned by electric companies.  This cost will ultimately

13   have to be passed on to Florida end users because no company

14   can absorb a cost of that magnitude, and will be in addition to

15   any costs that the electric utilities will impose upon their

16   end users for actually replacing poles.

17             And while $4 billion is staggering in and of itself,

18   there could be more costs that BellSouth just cannot estimate

19   today because of the uncertainty surrounding what exact

20   standards we will be facing.  Mr. Smith will go over a few of

21   these costs that we know will occur but just cannot quantify in

22   his presentation, but I'd like to talk to you about one

23   briefly.  And that is there is a chance that the electric

24   companies will attempt to use your rules to manipulate current

25   pre-existing language in our joint use agreements to force or

FLORIDA PUBLIC SERVICE COMMISSION

22

1   to claim that attaching entities have a responsibility pursuant

2   to that agreement to pay for a percentage of the poles.  This

3   cost would be in addition to the $4 billion that we estimate in

4   just complying with the rule as an attacher.

5             And how would they make this argument?  They will

6   argue that you are the cost causer, that your rules are causing

7   them to incur cost to replace their poles.  And as such, we

8   believe that they will try to attempt to use pre-existing

9   language that was never intended to be used in such a manner to

10   force additional costs upon BellSouth.  So at the end of the

11   day, there is a possibility that we will incur substantial

12   costs as an attacher in the range of $4 billion simply to

13   comply with the rules, and then have to face a contractual

14   claim based upon additional costs to actually pay for a

15   percentage of the electric company's cost in replacing the

16   pole.  So they get recovered from their end users their costs,

17   they're going to try to get recovery from our costs, from us

18   for the pole, and then we have additional costs.  Of course, we

19   vehemently disagree with any such interpretation of the joint

20   use agreement and deny that this claim is valid, but the risk

21   is still there.  And we raised this in our comments, and

22   tellingly, probably unintentional, they did not refute that

23   this is what they intend to do.

24             Given these costs, BellSouth believes that there

25   needs to be a serious review of a cost-benefit analysis.  And I

FLORIDA PUBLIC SERVICE COMMISSION

23

1   think that after doing such a review, you would find that maybe

2   these rules will not have the desired effect.  And our

3   rationale for that is simple:  If you look at Hurricane Wilma

4   and the statements of the utilities that followed, the

5   widespread lengthy power outages that resulted from that storm

6   were not because of distribution facilities for the most part,

7   it was because of the failures of substations and transmission

8   lines.  And these rules will not change the fact that

9   substations failed during Wilma.

10             And if you go forward five to ten years from now

11   after these companies have spent a considerable amount of money

12   in complying with the rules and a storm like Wilma comes again,

13   it is highly likely that the same type of power outages that

14   were experienced by Florida consumers last year would occur

15   again.  And that's because the substations that failed in Wilma

16   because of flying debris are not impacted by this rule.

17   Mr. Smith will expound upon that in his presentation.

18             In addition to these cost concerns, this proceeding

19   is also important because the rules result, we believe, in the

20   Commission likely exceeding its jurisdiction over pole

21   attachments.

22             The Florida Supreme Court in the case of

23   Teleprompter v. Hawkins has determined that this Commission

24   does not have the ability to certify to the Federal

25   Communications Commission under the Pole Attachment Act that

FLORIDA PUBLIC SERVICE COMMISSION

24

1   you can regulate the rates, terms and conditions for pole

2   attachments.  We believe that that law is still valid today and

3   is still binding upon you.

4             In addition, in a decision issued by the FCC in March

5   of this year, the FCC has determined that it still has

6   jurisdiction over pole agreements, even when the engineering

7   standards at issue are implemented pursuant to safety and

8   reliability concerns pursuant to state law.  So we believe that

9   these rules, to the extent they result in the regulation of

10   rates, terms and conditions associated with pole attachments,

11   exceed your jurisdiction.  Mr. Gross will expound upon our

12   jurisdictional arguments in his presentation, and we're trying

13   our best today not to duplicate arguments, so I will defer to

14   him.  And with that, I'd like to turn it over to Mr. Smith.

15   Thank you.

16             MR. SMITH:  Thank you, and good morning.  To begin

17   with, we'd like to lay out the summary of how we see the impact

18   of these proposed rules.  As you see, our interpretation is

19   very consistent from what we heard from the Commission staff in

20   that the major points of the rules that we'll be addressing are

21   each electric company will ultimately develop its own

22   construction standards that meet or exceed 2002 NESC

23   guidelines.  Each electric company will develop construction

24   standards that will incorporate, if applicable, extreme wind

25   load conditions for new build construction, major planned work,

FLORIDA PUBLIC SERVICE COMMISSION

25

1   targeted critical infrastructure and major thoroughfares.  Each

2   electric company will develop construction standards that will

3   deter damage resulting from flooding and storm surge.  Each

4   electric company shall seek input, but not be required to

5   accept input from other entities regarding the development of

6   these standards.

7             We start with statements of financial impact.  We

8   looked at several different likely scenarios that would from an

9   operational standpoint occur from the revision of these

10   standards or the, the hardening efforts of an electric company.

11   One very likely scenario is that an electric company would

12   abandon rear lot construction and replace facilities with new

13   street side aerial or buried facilities.

14             As BellSouth, an attacher to an electric

15   company-owned pole, we would have an option at that point in

16   time.  If the pole were abandoned by the electric company, we

17   have an option via our joint use agreement to purchase that

18   pole.  The purchase cost of the pole would range between $250

19   to $300 based on historical information and data that we've

20   been able to assess.

21             There is a chance that as the electric company may

22   abandon that particular route, depending upon the terms and

23   conditions of the acquisition of the easement to place the

24   poles to begin with, that easement may or may not be

25   transferrable.  We could be in a position of having to acquire

FLORIDA PUBLIC SERVICE COMMISSION

26

1   or negotiate for an additional easement.  As we would accept

2   the ownership of poles that would be abandoned by the power

3   company, our pole inspection costs would obviously increase

4   beyond what we have forecasted would be our inventory.  We have

5   not in essence forecasted the, the purchase of used poles.

6             There is also an administration of records change

7   that we would implement based on each situation where we would

8   assume the ownership of those poles and have those poles

9   incorporated into our ongoing database.  If we were to assume

10   that this were to happen to 10 percent of the poles that we are

11   attached to across the State of Florida, the low range impact

12   financially would be $18,900,000.  If we see that happening to

13   40 percent of the poles that we are attached to, the high end

14   cost for that particular scenario would be $90,720,000.

15             Given the same scenario, if an electric company

16   decides to abandon a rear lot line construction and we choose

17   as an option to follow that with the replacement of a new

18   facility, our estimated cost of replacing a new aerial or

19   buried facility on a front lot line would likely be in the $25

20   to $50 a foot range.

21             We would anticipate that the financial impact to

22   BellSouth following the power company route to the new front

23   lot line to be between $472,500,000 to $3,780,000,000,

24   anticipating, again, that this would impact on a range between

25   10 percent to 40 percent of our current attachments.

FLORIDA PUBLIC SERVICE COMMISSION

27

1             To bring these numbers into somewhat of a

2   perspective, we would like to state that we are as a company

3   attached to 756,000 electric company-owned poles throughout the

4   State of Florida.

5             Should the work operation from an electric company

6   simply be to change out a pole or to replace a pole to a new

7   stronger or taller pole, all attachers would have to transfer

8   their facilities from the old pole to the new pole.  Depending

9   on the complexity of the transfer, and it could range anything

10   from a simple unbolting an existing attachment to drilling a

11   hole and bolting it to the new pole to actually severing the

12   cable and splicing in new cable, we would have to transfer,

13   again, our facilities from the old pole to the new pole.  The

14   range of anticipated cost, again, looking at the number of

15   attachments we have, the 756,000 across the state, would range

16   potentially between $7,182,000 to $142,128,000.  The likelihood

17   is that as network hardening progresses, you would not see one

18   of these scenarios, you would see a blend of these scenarios.

19             In the conversion of these facilities, taking all

20   these things into account, we would range -- we would

21   anticipate that the range of expense to BellSouth could very

22   well be between $500 million to $4 billion to follow and to

23   accommodate the changes that we see the electric companies

24   potentially making.

25             There are additional costs that are associated with

FLORIDA PUBLIC SERVICE COMMISSION

28

1   these changes.  We see the potential, a real potential of

2   increase in pole rental fees.  In is most simplistic terms, the

3   agreements between an electric company and telecom company

4   often assume the historical pole costs and carrying costs

5   associated with, with pole inventory.  As we see a shift of

6   older poles to newer poles, smaller poles to larger poles, we

7   see those historical pole costs and we see the carrying costs

8   that influence the pole rental rates changing.  We simply at

9   this point in time because of the vague nature of the

10   definition of the standards and how often they would apply,

11   where they would apply, we simply cannot apply a price tag to

12   that particular item at this point.

13             There is another item that causes us great concern.

14   As we have seen in many cases, our facilities or anybody's

15   facilities, be they water, be they gas, be they cable, that are

16   in a front lot type situation are exposed to damage to a great

17   degree when a facility or when excavation occurs in the front

18   lot line.  We have data that supports that 75 percent of the

19   buried cable damages that we incur in the State of Florida

20   incur in just such an environment, a front lot line

21   environment.

22             As we move to identify large excavation projects, our

23   damage prevention costs increase.  We often dispatch personnel

24   that will actually patrol and monitor the excavation activity

25   working as an aide to the excavators to prevent the damage.  We

FLORIDA PUBLIC SERVICE COMMISSION

29

1   see a definite increase in this type of activity.  As I'm sure

2   most are aware, if someone is excavating, they are required by

3   law to call and request the facilities, the various utilities

4   to be located.  We see an increase in those costs as well.

5             There is a high likelihood that by virtue of the fact

6   that, that an electric company would be abandoning a pole line,

7   moving to a new location, if we assume the ownership of the

8   abandoned poles, we would be in a position of renegotiating

9   various joint use agreements, license agreements with cable TV

10   attachers and CLECs as well.  They could feasibly be attached

11   and likely are attached to the poles that we would be assuming

12   the ownership for.  This would not be in our current license

13   agreements with these, with these entities.  We would incur

14   costs to try to fold in this new arrangement.

15             We see costs that are associated with updates or

16   changes to whatever these standards may be.  As these standards

17   change, we have seen no language in the rule that in essence

18   gets any type of time line parameters for attachers that would

19   indicate something simply as to say if there are a change in

20   the rules, you would have a year to comply, six months to

21   comply.  We simply don't know.  But we do know that with the

22   possibility for the standards continually changing, we would

23   incur costs to comply.

24             There is no question in our minds that additional

25   manpower requirements would be necessary to comply with what we

FLORIDA PUBLIC SERVICE COMMISSION

30

1   see as a substantial increase in our workload.  Again, with not

2   knowing the, the nature of what these upgrades may be, the

3   extent, the time lines, we can't assess what that would be.  We

4   simply know that increased workload would bring a necessity for

5   additional manpower.

6             Use of nonwood poles is a concern of ours.

7   Historically, BellSouth has dealt in the wood pole environment.

8   As we see a transition to more use of nonwood poles, be they

9   concrete, be they fiberglass, be they steel, our attachment

10   operations have to change.  Those are an increased cost to us:

11   We estimate at a point of some $55 to $60 per pole, depending

12   on the type of material and the manner in which you have to

13   attach to a nonwood pole.

14             From a pure business case perspective there is a

15   great concern that we have that if we have recently placed a

16   facility that is a good, serviceable facility, we may be given

17   very few options to look at to, to actually say that we would

18   be replacing a facility that has recently been placed and is

19   very serviceable and has an extended lifetime that otherwise we

20   would not be replacing.

21             We do have questions on our pole inspection process.

22   Quite frankly, we are encouraged with what we're seeing from

23   the pole inspection process that we have undertaken jointly

24   with several major power companies over the last, last several

25   months.  We feel that there is a potential that this pole

FLORIDA PUBLIC SERVICE COMMISSION

31

1   inspection process could be invalidated.  From a very

2   simplistic operational standpoint, if we're inspecting poles on

3   Highway 1 today and an electric company comes by with the

4   implementation of these rules and changes the nature of those

5   facilities, we've actually wasted time and resources to inspect

6   those poles.

7             We see that there is a cost inherent to training on

8   standards.  There are 40 plus electric companies that we deal

9   with in the State of Florida.  Based on the variations of

10   construction standards that each of these companies may imply,

11   may implore, we have the arduous task of trying to communicate

12   to our technicians potentially 40 different sets of standards

13   as we perform our attachment work.  That is cumbersome and it

14   is quite a concern of us in being able to comply potentially

15   with 40 different sets of standards.

16             We believe that the, that the rules as they stand

17   today are premature and overreaching.  We are building a high

18   degree of confidence in our pole inspection program.  We

19   believe that that is a good tool to provide data analysis that

20   can support this level of expense.

21             I would draw your attention to some of the issues or

22   some of the items that we are required to comply with in terms

23   of our reporting back to the Public Service Commission.  The

24   number of poles that fail inspection, the number of poles

25   requiring minor follow-up, the number of poles that were

FLORIDA PUBLIC SERVICE COMMISSION

32

1   overloaded, the number of poles with an estimated pole life of

2   less than ten years, this is the type of empirical data I think

3   collectively the industry needs to make the decisions when this

4   type of price tag is potentially associated.

5             The definition of the construction standards

6   themselves could invalidate this inspection process, as I've

7   previously, previously mentioned.  The inspection process

8   itself is not inexpensive, and I would hate to see that we were

9   doing any type of inspections that, in fact, could be

10   invalidated by a change of standards yet to be defined.

11             Again, to the point of being somewhat premature, the

12   rulemaking uses the 2002 version of the NESC as a baseline.

13   Only yesterday I personally saw the first version of the 2007

14   code.  We think it would be prudent to look at what the 2007

15   code brings to the table before these rules are implemented or

16   addressed.

17             The proposed rulemaking also indicates that the

18   revised construction standards would be applicable to new

19   builds, conversions, critical infrastructures and major

20   thoroughfares.  We have great concern that there is, there is

21   no definition around these categories.  These are subject to 40

22   separate definitions, and they have a major impact on what the

23   price tag would be.

24             Some of the information that we observed from Wilma

25   such as poles that snapped were made of concrete as well as

FLORIDA PUBLIC SERVICE COMMISSION

33

1   various strengths of wood and some were new.  Damage to

2   substations contributed significantly to extended, widespread

3   power outages, and distribution poles damaged or destroyed

4   represented a miniscule portion of the overall network damaged

5   by Wilma.  These give us cause for concern and to ask that, and

6   state that it leads us to our conclusion that this rulemaking

7   is premature.

8             So in summary, these are the questions I feel we must

9   ask:  Are the right resources being directed to the right

10   remedy, and is the price worth the potential benefit?  Have we

11   collectively analyzed the problem to address the right things,

12   and are there alternatives that can positively impact the

13   problem and thus drive the desired consumer benefit faster and

14   in a less costly manner?  Our position is that, yes, we do

15   suggest that there are more efficient solutions that may result

16   in an even more favorable outcome, and we propose a three-step

17   collaborative approach.

18             We propose that establishing an Infrastructure

19   Advisory Committee that is a multi-industry committee that is

20   dedicated simply to the evaluation and application of overall

21   network hardening is a first step and something we collectively

22   feel very strongly we could accomplish within a 30-day period.

23   We would establish the priority issues to address which would

24   be the evaluation of existing and proposed construction and

25   attachment standards; increasing the efficiency of hurricane

FLORIDA PUBLIC SERVICE COMMISSION

34

1   restoration efforts, which we feel is a very critical

2   component; identification of specific geographic areas to

3   assess all critical infrastructures and necessary hardening

4   efforts.  With a collaborative approach with every participant

5   across the industry I think we can accomplish these things.

6             As we refine the Infrastructure Advisory Committee,

7   as a Step 2 within a 60-day period, we feel we could provide a

8   complete, comprehensive, industry-wide evaluation of target

9   areas; not just electric infrastructure, but telecom and cable

10   as well.  We propose that we use the coordination of pole

11   inspections as a first-strike data gathering process to

12   evaluate these target areas.  We feel very strongly that

13   communication of hardening projects to provide for a

14   consolidated industry coordination is critical, and to address

15   how to coordinate longer term hardening efforts.

16             Within the same 180 days, as is suggested in the

17   proposed rulemaking, we would suggest that the Infrastructure

18   Advisory Committee could accomplish developing construction

19   standards with all industry participants, develop attachment

20   standards with all industry participants, develop joint trench

21   standards for all new construction in a buried facility

22   environment, and provide continuous monitoring of pole

23   inspection data to determine what the next best things to do

24   would be.  And that concludes my presentation.

25             CHAIRMAN EDGAR:  Mr. Meza, any further comments at

FLORIDA PUBLIC SERVICE COMMISSION

35

1   this point?

2             MR. MEZA:  No, ma'am.  Thank you.

3             CHAIRMAN EDGAR:  All right.  Commissioners, any

4   questions for the BellSouth presenters at this time?  No?

5             Okay.  Then let's move on.  You're recognized.

6             MR. O'ROARK:  Again, good morning, Madam Chairman and

7   Commissioners.  I'm De O'Roark representing Verizon.  First of

8   all, Verizon agrees with BellSouth with respect to its concerns

9   about cost.  Verizon also has addressed those concerns in its

10   comments and in the affidavit of Steve Lindsey.  We agree with

11   BellSouth concerning the jurisdictional issue, and we also

12   fully support the infrastructure hardening proposal that was

13   just presented.

14             In an effort to avoid simply duplicating the points

15   that BellSouth has made, what we're going to do this morning is

16   focus exclusively on the extreme wind loading issue.  And

17   Verizon's presentation on extreme wind loading will be made by

18   Dr. Larry Slavin.  Dr. Slavin has worked in the

19   telecommunications field for 45 years:  28 years with Bell

20   Labs, another 12 years with Telecordia.  Dr. Slavin has been an

21   active member of the NESC, that is the National Electrical

22   Safety Code, subcommittee that deals with extreme wind loading.

23   He's been involved with that subcommittee since 1998.  He was

24   involved in developing the 2002 and 2007 versions of the NESC.

25   And he has prepared a PowerPoint presentation that we would

FLORIDA PUBLIC SERVICE COMMISSION

36

1   like to have admitted as an exhibit next in order.  And, Madam

2   Chairman, we would suggest that perhaps be named Verizon's

3   Presentation.

4             CHAIRMAN EDGAR:  Okay.  And that will be Exhibit 4.

5             (Exhibit 4 marked for identification and admitted

6   into the record.)

7             DR. SLAVIN:  I'd like to thank the Commissioners for

8   the opportunity to speak to you this morning.  I'll try not to

9   abuse the privilege.  You have a handout with lots of slides; I

10   think over 60.  I'll only address about half of them, unless

11   you want me to go into some of those others in detail.  There's

12   a slide number in the lower right-hand corner, so I'll try to

13   keep you up-to-date on which slide I'm referring to at the

14   moment.

15             I'll be talking about the National Electrical Safety

16   Code and what it says about extreme wind loads, and in

17   particular how it relates to distribution poles.

18             Slide 2.  Your public service proposed Rule

19   6.034(5) deals with extreme wind loading.

20             Slide 3.  Right upfront I'm going to tell you that if

21   you do adopt those rules as written, you'll probably make your

22   situation worse.  You'll delay restoration because you'll have

23   more downed poles following typical storms.  There will be

24   errors in implementation.

25             From another safety perspective, you'll probably have

FLORIDA PUBLIC SERVICE COMMISSION

37

1   more automobile accidents because of the additional or more

2   massive poles.  And there's probably going to be some other

3   unknown consequences which I haven't thought about at this

4   point.

5             Slide 4.  The most obvious effect is going to be

6   increased costs.  Typical joint usage poles will be required to

7   be one and a half to four times your present required strength.

8   That's three to eight pole class sizes, and I'll describe what

9   pole class means in a few slides from now.  That is very major.

10   The alternative to stronger poles is to have more poles by just

11   decreasing your span lengths.  In that case, you'll have one

12   and a half to four times more poles.

13             Now I want to point out -- I'm on Slide 5.  I want to

14   point out that in the last edition, the 2007 Edition just

15   issued -- it was just issued this month as we speak, all right,

16   so it's already essentially effective.  It has to be effective

17   by February, but it can be effective at any time.  We did

18   consider a change proposal, a very specific one, Change

19   Proposal 2766.  It was rejected.  But what the purpose of this

20   was was to extend extreme wind loading to structures less than

21   60 feet.  That means distribution poles.  It was a much less

22   radical change than what's in your proposed rule, much less

23   radical.

24             One of the limitations in this rule was that it would

25   limit the wind pressures or the wind speeds that had to be

FLORIDA PUBLIC SERVICE COMMISSION

38

1   considered to a level above which you would have flying debris

2   basically taking down your poles anyway.  All right?  So it

3   recognized there was a limit, a practical limit to the wind

4   speeds we should be dealing with.

5             Slide 6.  Nonetheless, it was rejected by a vote of

6   17 to 7.  And I'm not going to read through the formal comment.

7   Underneath you see the formal comment of the Subcommittee 5.

8   And just to paraphrase it briefly, what it said is distribution

9   structures, meaning under 60 feet, they're damaged during

10   extreme wind by trees, tree limbs, flying debris.  If you

11   design those structures for extreme wind, you'll increase the

12   pole strengths, you'll have a large increase in cost, design

13   complexity, and you're not going to have a commensurate

14   increase in safety.  Okay.  Slide 6.

15             Now the rest of the talk -- I'm on Slide 10 now.  The

16   rest of the talk will be divided into four parts basically to

17   support the conclusions and the comments that I just made.

18             The first talk, I'll briefly review what 2002 says.

19   That's the edition of the NESC that's explicitly cited in your

20   change proposal -- in your proposed rule.  I'll tell you a

21   little bit about 2007 which was just issued because there's

22   one or two things that relate to, you know, what we're talking

23   about today.  I'll tell you how it impacts -- how it's impacted

24   and how it relates with your proposed Rule 6.034(5), and I'll

25   give you my own recommendations.

FLORIDA PUBLIC SERVICE COMMISSION

39

1             Okay.  Slide 11 and 12.  I'm talking about the 2002

2   Edition now.  There are two sections of the NESC that

3   explicitly deal with this issue.  There's Section 25 or Chapter

4   25, the title of which is "Loadings for Grades B and C."  Now

5   I'm -- I highlighted the Grades B and C part, but that's, but

6   that's a direct exact description of that chapter.  In other

7   words, those loadings which are specified in Section 25 do not

8   apply to all grades of construction.  It applies to two of the

9   popular grades, especially Grade C, but not all grades.  And

10   there are two rules explicitly listed in Section 25, two storms

11   that are explicitly listed:  There is Rule 250B and 250C.  Now

12   just to avoid confusion, the 250B and 250C, that B and C has

13   nothing to do with Grades B and C.  That's just, you know,

14   that's not -- you know, there's no connection there.

15             Rule 250B is basically a winter storm.  It's a

16   combined ice and wind loading that we expect the poles to

17   withstand.  That applies to all transmission and distribution

18   structures as long as they're Grades B and C.

19             Rule 250C, which I highlighted in red, is the rule

20   that's in question now.  Rule 250C is the extreme wind loading

21   that's been proposed to be applied to all distribution poles.

22   Right now it is not applicable to distribution poles.

23             Section 26 of the NESC entitled "Strength

24   Requirements" has two main rules -- actually has one main rule.

25   Main Rule 261 is entitled "Grades B and C Construction."  And

FLORIDA PUBLIC SERVICE COMMISSION

40

1   what it does is it tells you how to select or design poles so

2   that they can withstand the loadings that are described in

3   Section 25 above.

4             Now there is a Rule 263, it's a very minor rule, that

5   refers to another grade of construction, the remaining grade,

6   Grade N construction.  You can picture "N" standing for no

7   rule.  That's not what it stands for, but you can imagine it

8   that way.  It talks about this other third -- this other grade

9   of construction which I'll briefly describe.

10             All right.  Next, next slide.  I'm talking about the

11   winter storm now.  This map, this loading districts map that

12   you see in front of you, I'm sure many of you have seen this,

13   it's been around about 100 years, it's been modified slightly.

14   It divides the United States for the purposes of winter storm

15   into three regions, into three districts:  Heavy in the

16   northeast, medium and light.  And you can see that Florida is

17   in the light area.

18             The next slide is 14.  This winter storm, Rule 250B,

19   is as follows:  It specifies, for example, in the heavy portion

20   of the country, in the northeast, that the conductors shall be

21   able to accumulate 1/2 inch radial ice.  Radial means that you

22   have 1/2 inch on top, on the bottom and on the side.  So you're

23   actually adding an inch of ice to a conductor if you imagine

24   that.  And we apply to that ice-laden conductor a transversed

25   wind load corresponding to 40 miles an hour.  Actually it's

FLORIDA PUBLIC SERVICE COMMISSION

41

1   specified four pounds per square foot.  That corresponds to a

2   40-mile-an-hour wind.  So we apply this four pounds per square

3   foot to the projected area, the bigger area of the conductor

4   surrounded by ice.

5             In the medium portion of the country, in the

6   midsection, we have the same four-pounds-per-square-foot wind

7   pressure with only 1/4 inch radial ice.

8             Now at the bottom of this slide, of course, is the

9   one we're interested in.  I have it in red.  In the light

10   section of the country -- oh, and a conductor, I might add, is

11   a wire, it's a cable, it's a telephone cable, it's a power

12   cable, it's any of the cables that you see stretched, you know,

13   spanning between the poles when you walk down the street.  It

14   could be cable TV, it could be power, it could be telephone.

15   Okay.  We use them interchangeably in the code and we're not

16   always explicitly clear about it.  Okay?  Conductors, wires,

17   cables, all the same thing.

18             All right.  Now in Florida, you see it's in red and

19   it's considered light.  Okay.  Well, "light" I put in quotes.

20   That is a total misnomer.  We're getting away from that

21   terminology to some extent.  We did a little bit in the 2007

22   Edition.  The reason that we say it's light is because it's

23   light on ice.  There's no ice in Florida, for example.  But we

24   apply a 60-mile-an-hour wind.  That 60-mile-an-hour wind

25   corresponds to nine-pounds-per-square-foot wind pressure, more

FLORIDA PUBLIC SERVICE COMMISSION

42

1   than twice as much as in the rest of the country.  And even

2   though it's on a conductor without ice, in many cases that can

3   be a much more significant load.  So the term "light" is really

4   a misnomer.

5             And as you'll see later on, we take these wind

6   pressures for this winter storm -- and this winter storm,

7   remember, does apply now to all transmission and all

8   distribution structures.  In fact, it becomes the basic design

9   rule for distribution across the country.  We apply a safety

10   factor to those numbers to make them even more severe.  Okay?

11             Slide 15.  So now let's get over to the, to the

12   extreme wind load, Rule 250C.  This is the one we're talking

13   about extending the structure to distribution structures.  If

14   you -- there's a contour map that's in the National Electrical

15   Safety Code.  I'll show you a more detailed one on the next

16   slide.  But if you look at the bottom of this slide, this wind

17   load is not required for structures less than or equal to

18   60 feet in height, meaning it exempts distribution structures,

19   distribution poles.  That's the point of it.

20             Slide 16 shows a particular figure, it's 250-2(d),

21   and this is explicitly referenced in your, you know, your PSC

22   proposal, and because it, you know, highlights what's happening

23   in Florida.  And you can see that the wind speeds that are

24   talked about are as high as 150 miles an hour and down to a

25   little bit under 100, let's say 95 miles an hour in the

FLORIDA PUBLIC SERVICE COMMISSION

43

1   northern tip over there just for, you know, purposes of, of the

2   discussion.  I also assumed that in some of the calculations

3   I'm going to show you.  So we have something between 95 and

4   150 miles an hour for Florida.

5             Now jump ahead to Slide 21, okay, flip ahead a few

6   pages.  All right.  There's stuff in between you can ask me

7   about afterwards, if you're so inclined.

8             All right.  This wind from either the hurricanes

9   under the extreme wind loading which we're talking about today

10   or from the 60-mile-an-hour winds that we talk about in the

11   winter, this wind puts a horizontal load on the conductors or

12   the wires or the cables as you see in red on that figure.

13   Okay?  And it also blows on the pole, as you can see.  That

14   tends to be the dominant design criteria for poles.  The weight

15   of the ice, the weight of the pole, the weight of the

16   conductors, minor, minor effect.  This may not be intuitive to

17   you, but it's not.  It's the lateral horizontal force that's

18   applied to the conductors or the wires on the pole which is

19   generally the design criteria for the poles.  Okay?

20             That is why, if you go ahead to Slide 22 -- or

21   actually let's go to 22 and let's go to 23.  What I'm going to

22   do is I'm going to tell you what wood pole class means in case

23   you're not familiar with it.  Okay?

24             Slide 23.  It shows -- this is right out of the

25   ANSI-05 Wood Pole Standard.  I serve on the ANSI-05 also.  But

FLORIDA PUBLIC SERVICE COMMISSION

44

1   it's a very, you know, common standard that people in the

2   industry are familiar with, both power industry and

3   communications.

4             All right.  We define the strength of poles, of wood

5   poles.  But let me tell you, the nonwood poles have to match up

6   to this because everybody's familiar with the wood poles since

7   it's the standard.  So the nonwood poles we'll also talk

8   equivalent classes.  All right?  There's some issues with that,

9   but basically they'll say this is an equivalent Class 4 pole

10   even if it's made out of something that's not wood.  And the

11   way we define the strength of these, of our poles, wood or

12   otherwise, is you put a lateral load near the top of the pole,

13   and you can see a load two feet from the top of the pole.  And

14   this is how the tests are done actually.  Okay?  It's not done

15   on poles on the ground.  You know, we do it a little

16   differently.  But basically you put a load two feet from the

17   tip of the pole and you classify the pole by how much that load

18   can be.

19             So if you look in this table to the right, you'll see

20   I highlighted Class 4s.  You see the four in red and the

21   2,400 pounds next to it.  That is a typical, you know,

22   distribution pole, Class 4.  That can take 2,400 pounds applied

23   near the tip of the pole.  And then we have a whole spectrum of

24   strengths starting with Class Size 10, which is very small.

25   The higher number classes are actually weak.  It's sort of like

FLORIDA PUBLIC SERVICE COMMISSION

45

1   wire gauge; a higher number wire gauge is a thin wire.  A

2   smaller wire gauge is a thick wire.  Spaghetti pasta is

3   classified that way also.  All right?  The higher numbers are,

4   you know, generally smaller and thinner.

5             So you start from the Class 10, which is a very small

6   pole, can take a few hundred pounds, and you go down to a

7   Class 1 which is really big for distribution, which is 4,500

8   pounds, and then you can get into the H Class size, all right,

9   you know, which are, you know, hardly ever used for

10   distribution, and you go H1, H2, H3, H4, H5 and H6.  And in

11   this case the strength goes up with the H number.  So this is

12   how we classify the poles.  All right?  Remember, Class 4 is

13   pretty typical.  You might see Class 5s out there a lot, Class

14   3s out there a lot.  That's a typical distribution pole.

15             All right.  Let's move ahead to Slide 25.  Now how do

16   we pick the strength of the pole to match the storm loads?  We

17   do not simply take the strength from that chart that I just

18   showed you and say, well, that has to be at least as big as the

19   load that's applied by the wind blowing.  Now that's -- and you

20   have to check whatever wind is appropriate, whether it's the

21   extreme wind which is not for distribution but it is for

22   transmission, okay, or whether it's the winter storm load.  And

23   you multiply that load, those pressures -- remember, I

24   mentioned nine pounds per square foot, you should remember.  We

25   multiply that by a design or a safety factor.  It's an

FLORIDA PUBLIC SERVICE COMMISSION

46

1   amplification factor, it's a safety factor.  So in the case of

2   Grade C construction which I'm going to talk about, the design

3   factor is two.  In the case of Grade B, it's four.  So it's a

4   healthy design factor, a safety factor that's applied to those

5   winter storms.  All right.

6             Next slide, 27.  The magnitude of that safety factor

7   depends on the grade of construction.  Grade B is the highest

8   grade of construction.  It's the one that's supposed to be the

9   most reliable.  It will have the highest safety factor,

10   possibly four to one.  It will be four to one for the winter

11   storm.  It's very rarely required.  It's required at crossings,

12   railroad crossings, limited access highways, so it's not a very

13   common -- it's not commonly required.

14             The one that is commonly required is Grade C.  Grade

15   C, and I highlighted it in red, is typical distribution

16   designed for joint usage applications.  It will apply when you

17   have primary power on the pole, meaning you have thousands of

18   volts at the top of the pole.  Okay?  And you might have a

19   transformer which steps down those thousands of volts to, say,

20   hundreds of volts which you would use in your home:  120 volts,

21   240 volts.  And then a few feet below that you would have your

22   communications cables, telephone cable, TV or whatever.  That's

23   typical Grade C construction.  That is the most common one and

24   that's the one we should be thinking about primarily in terms

25   of my discussion here.  Although I will refer to the others

FLORIDA PUBLIC SERVICE COMMISSION

47

1   too, Grade C is the one to worry about.

2             Okay.  But what is Grade N?  Grade N is the lowest

3   grade of construction.  I'm not sure how much of it is that's

4   out there.  It's not unusual.  This applies when you don't have

5   thousands of volts at the top of the pole, which means you have

6   secondary power.  You don't have the transformers on these

7   poles.  A typical example would be when you have

8   telecommunications-only poles.  Now we're not talking about

9   that today.  I mean, there could be a lot of

10   telecommunications-only poles in that category.

11             But in terms of the joint use poles where you have

12   power-owned poles, it would apply, you know, to when you had

13   secondary power on the pole.  There are no detailed

14   requirements on this in the NESC.  The most we say about this

15   in Rule 263 is it doesn't have to be as good as Grade C.  Okay?

16   I put the quotes there for the exact words.  But as I say, it

17   doesn't have to be as good as Grade C.  We're not telling you

18   what it is.  But we're also saying that initially it should be

19   able to withstand expected loads without telling you what those

20   expected loads are.  Because, remember, those storm loads come

21   out of the chapter that refers to Grade B and Grade C.  All

22   right?  So it's very vague and you have to -- you know,

23   reasonable people can make reasonable judgments of how to, you

24   know, apply this, and I did something like this in one of the

25   slides I'm going to show you, but there's nothing really

FLORIDA PUBLIC SERVICE COMMISSION

48

1   specific in the code about this whole category of structures.

2             So let me tell you about -- go to Slide 30.  I'm

3   going to tell you a little bit about what happened in 2007.

4   2007 was just issued this month as we speak.  Okay?  It's

5   applicable any time between now and February of 2007.  Okay.

6   It's 2007 because of the February date.  Okay?

7             Go to Slide 31.  We had several changes in the code,

8   but the one that's immediately relevant to this is the fact

9   that we actually reduced the design or the safety factor for

10   the extreme wind load where it's applicable.  Where is it

11   applicable?  It's applicable for transmission for the tall

12   structures.  For those structures for Grade C, and this is Rule

13   250C, okay, we actually reduced the safety factor by a certain

14   amount.  Okay?  So we're going the other direction.  All right?

15             Now go to Slide 36.  We did talk a whole lot about

16   extending this Rule 250C to distribution poles.  It was

17   rejected.  This discussion comes up every code cycle.  It came

18   up last code cycle for 2002, it came up this code cycle and

19   it's going to come up next code cycle.  I can promise you that.

20   All right?

21             Let's go to Slide 37.  What is there about this

22   change proposal?  It's Change Proposal 2766.  This was

23   developed internally to Subcommittee 5.  Change proposals can

24   in theory come from outside the subcommittee, from the public,

25   and we get many, or they can come from within the subcommittee.

FLORIDA PUBLIC SERVICE COMMISSION

49

1   The most important ones come from within the subcommittee.  We

2   know it's important, we have to address these things, and we're

3   going to be doing it again next code cycle.  All right?

4             But in any case, in the preprint, the preliminary

5   version of the 2007 code where we try to announce to the public

6   a few years early what we're considering, this change proposal

7   was put in as recommended.  Now recommended doesn't mean, hey,

8   we're going to run in and adopt it.  What it means is please

9   take a look at this very carefully.  We're very seriously

10   considering this and we want your public comments on this.  All

11   right?  It's an important item here.  And what it does is it

12   would extend this extreme wind loading, this Rule 250C, to

13   structures less than 60 feet, the distribution structures.  All

14   right?

15             But there's a very critical mitigating factor in this

16   change proposal.  It would limit the wind pressures for Grade C

17   structures, for example.  It also limits it for Grade B, but

18   I'm talking Grade C here is the most common.  It limits the

19   wind pressure for Grade C structures that are less than 60 feet

20   tall to 15 pounds per square foot, because at that pressure

21   level you're having winds that are basically going to blow

22   around debris and branches and take it down for other reasons

23   that you're not designing for.  Okay?  Now these are very rough

24   numbers.  It's hard to pick out these numbers when debris and

25   branches start flying around.  But this is the number that

FLORIDA PUBLIC SERVICE COMMISSION

50

1   approximately we're talking about.

2             You know what?  If this rule is passed, which it

3   wasn't, it would have no significant impact in Florida because

4   basically we're already designing for pressures that are at

5   least that high.  Because, remember I told you, remember that

6   nine-pounds-per-square-foot pressure for Florida for wind?

7   There's a safety factor of two applied to that.  Nine times two

8   is 18.  We're already designing for within those pressure

9   limits.  Okay?  Meaning above that pressure you're going to get

10   flying debris.  Okay?

11             Now let's go to Slide 38.  Okay.  This change

12   proposal, as moderate as it is, okay, nothing compared to, you

13   know, the one that's in your change, in your proposed rule,

14   received the most comments of all change proposals submitted by

15   Subcommittee 5.  And that's a challenge because we have a lot

16   of controversial issues.  All right.  Subcommittee 5 deals with

17   a lot of these controversial subjects.  More than 10 percent of

18   the comments that came in regarding -- were addressing this

19   particular change proposal.  An overwhelming number of those

20   comments, 90 percent of them, had strong objections.  The

21   minority, the 10 percent, said, look, we can live with this as

22   a lesser of evils because we have those pressure limits in

23   there.  All right?  And, by the way, the next three runner-up

24   change proposals for comments also related to this rule.  And

25   the typical response from the industry across the country --

FLORIDA PUBLIC SERVICE COMMISSION

51

1   and, remember, most of the industry that's commenting on this

2   is the power industry.  Okay?  Telecommunications comments, you

3   know, were involved, but really the NESC and all the comments

4   are pretty much dominated by the power industry.  When I give

5   presentations at panel sessions, it's to the power industry.

6   All right?  So, anyway, that's Slide 38.

7             Let's go to Slide 39.  It was rejected, and I showed

8   this one before, by a vote of 17 to 7.  And the reason, you

9   know, I highlighted in red again is because, look, you're going

10   to increase pole strengths and cost and complexity.  You're not

11   going to get any significant increase in safety.

12             All right.  Now I will tell you that different

13   circumstances -- this vote 17 to 7 was one-sided but it's not

14   unanimous by any means.  Different circumstances might have

15   affected that vote.  But if you go back a minute to two slides

16   before that, Slide 37, remember what they were voting on.  They

17   were voting on a very moderate change proposal that would have

18   limited the wind pressure for such structures to 15 pounds per

19   square foot.  All right?  If that limitation was not in it,

20   first of all, it would not have been recommended in the first

21   place in the preprint.  Maybe it never would have gotten in.

22   Who am I to say not recommended?  Right?  The public can still

23   look at it and make their comments.  You know, sometimes we

24   reverse things.  But it would not have been recommended.

25             Going to the next slide, 38.  Instead of 90 percent

FLORIDA PUBLIC SERVICE COMMISSION

52

1   strong objections, you can figure it would be 99 percent strong

2   objections, maybe 100.  All right?  And if you go to Slide 39,

3   it would not have been rejected by a vote of 17 to 7.  It would

4   have been a much more one-sided vote.  Okay?  So there was no

5   way that there was any possibility that the proposal such as

6   you're proposing in, you know, in your Rule 6.034 would have

7   been, you know, consistent with anything we would do in the

8   NESC.

9             Okay.  Now a general comment that I want to make, and

10   this is true in general for the NESC but in particular for

11   this, we believe the NESC, we ourselves, you know, believe the

12   NESC is a well-respected document.  We believe it's served the

13   industry well.  I base this on the comments that we, that we

14   get from the industry, the interest when we give presentations

15   and, you know, any other input that we've gotten.  We,

16   therefore, are very reluctant to make significant, dramatic

17   changes because we don't want to disturb it too much, so we'll

18   introduce gradual changes.  And these gradual changes will

19   minimize the potential impact and unintended consequences that

20   may happen with a dramatic change.  You have a dramatic change

21   and I'm going to go into that a little bit.

22             Okay.  Slide 41 is the proposed, proposed rule.

23             Slide 42.  You're going to have three different

24   effects or three different categories as I listed here.  There

25   will be a delay in restoration after a storm, there will be

FLORIDA PUBLIC SERVICE COMMISSION

53

1   other consequences and, of course, you have the direct effect.

2             Let me quantify this.  Go to Slide 44.  Okay?  All

3   right.  This is a chart here, but I think it's understandable.

4   What I've shown here is what the relative strengths would be

5   based on the present rules, the present rules which are

6   basically the winter storm that's applied to, you know, all

7   structures, both distribution and transmission.  And what would

8   happen if we actually adopted this rule the way it's written

9   now?  On the left side of the dotted line, this vertical dotted

10   line, it shows the present rules.  On the right side it shows

11   proposed rules by PSC, by Florida PSC.  All right?  Now let's

12   look at the left side.  I've got these three colored bars.  The

13   red one is the main one we should be thinking of.  That's the

14   typical Grade C construction.  I show that at 100 percent, you

15   know, just for relative magnitude.  That has a two-to-one

16   safety factor built into that nine-pounds-per-square-foot

17   pressure I mentioned.  The blue bar, which is Grade B, is twice

18   as strong because it has a four-to-one safety factor

19   approximately.  Okay?  The green bar, which is, I said,

20   Grade N, well, there is no rule for Grade N.  But what I said

21   is, look, let's assume a safety factor of one-to-one for Grade

22   N.  That's a reasonable assumption, reasonable people might

23   assume that, but there's no requirement in any way, as I

24   indicated, for Grade N.

25             But let's look at the Grade C.  That's at a

FLORIDA PUBLIC SERVICE COMMISSION

54

1   100 percent level.  Now let's look to the right of the dotted

2   line.  For 95 miles an hour, which is at least what you're

3   going to have in Florida at the very tip there, down to

4   150 miles an hour, that shows the magnitude of what's going to

5   be required for the pole strength.  That means that Grade C

6   pole will now be at least one and a half times to possibly as

7   much as four times the present required strength.  Okay?

8   That's Slide 44.

9             Slide 45 shows what it means in terms of pole

10   classes, which I introduced to you before.  People in the power

11   and, you know, the distribution industry, the utilities and in

12   telecommunications are familiar with class sizes, possibly more

13   than you are.  But what it would show is that this class -- a

14   typical Class 4 pole for Grade C which is shown in red, okay,

15   you've got this four next to the red bar there, that's a

16   typical size for distribution poles.  Now you'd be jumping up a

17   minimum of three class sizes to as much as eight class sizes up

18   to H5 poles.  This is really horrendous.  Okay?  So you're

19   going to have an enormous increase in pole classes, okay, which

20   corresponds to the required increase in strength.  Okay?

21             Go to Slide 46.  This is going to put in words in

22   front of you what I just described informally.  What's going to

23   happen is this.  You can have whatever increased costs are

24   associated with the following:  The Grade C applications will

25   be one and a half to four times the present required strength,

FLORIDA PUBLIC SERVICE COMMISSION

55

1   three to eight pole classes, or the alternative is to just

2   shorten your spans.  Okay?  You can accomplish it that way.

3   All you'll need is one and a half to four times more poles.

4   Now Grade B is affected less but still significantly affected.

5   The Grade N applications, if it's applied to that too, and I

6   saw nothing in the code that excluded anything like this, you

7   will have three to eight times present required strength or

8   six to 11 class, pole class sizes.  Enormous.  And there will

9   also be more extensive use of nonwood poles.

10             Now I'm not personally against nonwood poles.  I

11   wrote the change proposals for some of these.  All right.  I've

12   been involved in trying to -- I think they're good ideas in

13   general, they have their place in the utility industry, and I

14   think they should have access to it.  But the combination of

15   extensive use of nonconventional poles with more poles,

16   stronger poles is going to have, going to have some other

17   unintended consequences, other consequences.  For one thing,

18   when the typical storm comes along and knocks them down anyway

19   because of the flying debris, you're going to have more poles

20   to replace, more massive poles to replace, more nonconventional

21   poles to replace.  That is going to slow down your restoration.

22   All right?

23             In addition, there's going to be a lot of confusion

24   in areas in implementation.  This rule, this extreme wind

25   loading rule is complicated to use.  The transmission engineers

FLORIDA PUBLIC SERVICE COMMISSION

56

1   complain when you put this into the code.  The transmission

2   engineers are very experienced.  I mean, they're dealing with

3   these tall structures, they deal with these type of issues.

4   But they complain when we start putting this in.  It's getting

5   too complicated.  Not that they're not doing it, but it's

6   getting too close to what they're doing and they're getting a

7   little nervous.  Some of them are not so comfortable with this

8   to the extent that they suggested change proposals to make

9   these rules a little bit easier for them to use.  Distribution

10   people don't even come close to this.  All right?  They're

11   going to make errors, there's going to be delays.  And what the

12   errors will do, I have no idea.  We can only guess.  All right.

13   That's going to happen.

14             All right.  And in the bottom there, the last one is

15   there's going to be a significant increase in fatalities and

16   injuries that are vehicular accidents.  We're going the wrong

17   direction of what the U.S. Department of Transportation wants

18   and I believe the Florida Department of Transportation based on

19   what I've seen recently.  The U.S. Department of Transportation

20   wants less poles.  They don't want car accidents to the same

21   extent.  They're encouraging, you know, less poles.  Here we

22   are giving them more poles or more massive poles.  All right?

23   So there's going to be this other factor here which also

24   relates to safety.

25             So what are my recommendations?  Jump ahead to 55.

FLORIDA PUBLIC SERVICE COMMISSION

57

1   There are a whole lot of other slides in between.  Some of them

2   are complicated.  The intention was to give you a headache if

3   you want to get into it because I wanted to show you how

4   complicated these rules would be.  All right?

5             Let's go to Slide 56.  Okay.  And I'll step down this

6   slide.  These are my recommendations.  I have basically -- my

7   primary recommendation means if I had my druthers, you know, I

8   mean, if I really had that, I would say, look, enforce your

9   present rules.  The present rules do give you a certain basic

10   robustness, okay, as I've described during the talk.  All

11   right?  I don't know to what extent this may have been, you

12   know, a factor in the problems that you've had, but they should

13   be enforced.  And what does that mean?  Make sure your

14   design -- that your poles are within the capacity as defined by

15   those winter storms, you know, with those safety factors.  Pole

16   inspection, I understand, you know, you're actively

17   introducing.  That's good.  That's consistent with the NESC.

18   It says you have to maintain strengths of your poles, and for

19   Grades B and C it even tells you how strong they have to be.

20   So those are good.  That, to me, is the primary thing that you

21   should do.  All right.

22             I would not, therefore, adopt this other rule for

23   extreme wind for all the reasons I've given you, not in its

24   present form certainly.  And I would encourage you to get

25   active in the next issue.

FLORIDA PUBLIC SERVICE COMMISSION

58

1             Now we just had a 2007 issue, and it sounds like the

2   2012 issue is six years off.  It is not.  It is not.  Outsiders

3   and guests comment all the time, our meetings are open, and

4   they give presentations and they express their concerns.  And

5   we also have people who are active members of our subcommittee

6   from Florida, from the utilities.  All right?  They're very

7   outspoken and they're very vocal.  And this 2012 Edition, work

8   will start on that next year because the stuff that we do in

9   Subcommittee 5, unlike the other subcommittees, we can't wait

10   until 2010 which is when the code has to be finalized.  We

11   start right away.  All right.

12             So 2007 we're going to start putting change proposals

13   together.  You're going to be sure there's going to be

14   something addressing this issue.  There's no doubt about it.

15   It comes up every time.  It's important.  You know, we

16   understand what you're going through.  We wrestle with it all

17   the time.  It has to be finalized by 2010.  So in this period

18   between next year and a few years after that you're going to

19   know what's happening and you can have a lot of input into

20   that.  In fact, your input could be very direct.  NARUC, the

21   National Association of Regulatory Utility Commissioners, has a

22   representative on Subcommittee 5.  All right.  That can be

23   very -- that -- they're voting members, all right, they're

24   voting members.  They have been since I gave a presentation in

25   San Francisco to the commissioners there following ice storms

FLORIDA PUBLIC SERVICE COMMISSION

59

1   and other problems that were in the northeast in '98.  Okay?

2   So you have a direct input, okay, to Subcommittee 5.

3             Now what's my alternative recommendation?  I told you

4   what I would do, you know, if I had my druthers.  What would

5   the alternative be?  57.  Please limit the scope of this.  At

6   least exclude -- if you're going to go through with it, okay,

7   exclude explicitly -- okay, be explicit about some of these

8   things.  Explicitly exclude Grade N applications.  All right?

9   They're not even covered in some of the -- in most of the rules

10   that we're reciting here.

11             All right.  Two, explicitly cite the 2007 Edition.

12   The 2007 Edition, as I indicated, reduced the overload factors

13   for Grade C when it applies, which is transmission only, of

14   course.  But if you're going to extend it down to distribution,

15   at least use what's in 2007.  It reduces the overload factors

16   by -- it says 13 to 25 percent for Florida.  It will be

17   basically 25 percent for most of the state.  That helps.  It

18   helps.  You know, not as much as it should, but it helps.  All

19   right?

20             And, finally, I would really encourage you to do this

21   as a pilot study because of all the problems that I described.

22   Limit it to a specific area, a defined period.  It would be

23   very useful to have that information, you know, and I think it

24   would prevent you from having widespread problems as I

25   described.  And that is it.

FLORIDA PUBLIC SERVICE COMMISSION

60

1             CHAIRMAN EDGAR:  Thank you.

2             Commissioners, any questions for Dr. Slavin at this

3   time?

4             Commissioner Arriaga.

5             COMMISSIONER ARRIAGA:  It's a question for staff.

6   Staff, thank you.  Mr. Breman, let's go to Slide 57, please.

7             MR. BREMAN:  Excuse me.  Which slide?

8             COMMISSIONER ARRIAGA:  57.

9             MR. BREMAN:  Yes, sir.

10             COMMISSIONER ARRIAGA:  Explicitly exclude, and there

11   are two proposals there.  How does that affect the proposed

12   rule?

13             MR. BREMAN:  I think what you're talking about in

14   this slide is implementation of your policy, Commissioners.  We

15   haven't seen what the utilities propose in response to your

16   policy to harden facilities and assets.  So what you're seeing

17   here is simply an implementation.

18             COMMISSIONER ARRIAGA:  I don't understand.  I'm

19   sorry.  I just want to know how does this recommendation affect

20   the proposed rule; does it change, does it vary?  Because I

21   understood the Legislature explicitly said at a minimum NESC

22   standards.  So I'm wondering if by excluding these things, we

23   are under the "at a minimum" suggestion or mandate from the

24   Legislature.  I may be confused.  I don't know.

25             MR. BREMAN:  Well, there's two ways to read the word

FLORIDA PUBLIC SERVICE COMMISSION

61

1   "exclude" here, and perhaps we need some clarification from the

2   witness.  Does exclude mean not to address at all or to require

3   utilities to use it or --

4             DR. SLAVIN:  No.  No.  What I mean is you should

5   discourage the utilities from applying this rule to Grade N

6   applications.

7             MR. BREMAN:  Okay.  We'll just go bullet by bullet

8   then.

9             COMMISSIONER ARRIAGA:  Excuse me?

10             MR. BREMAN:  I'll go bullet by bullet.

11             Grade N applications, Commissioners, as you may or

12   may not recall -- and we can clarify this with the FPL when

13   they come forward during the Hurricane Wilma review that we

14   did.  A Grade N pole is not really used for distribution

15   facilities for Grade C and B construction.  They're light

16   poles.  One of the other slides showed that they don't really

17   hold a lot of weight.  Sometimes you see them as being meter

18   poles and service drops and that kind of infrastructure for

19   electric utilities.

20             With respect to the NESC 2007 Edition, that just came

21   out.  And those documents, when they come out, and they're

22   published every five years, the Commission staff reviews them

23   and then makes a recommendation to you whether or not it should

24   be accepted in total or what other things should or shouldn't

25   be accepted with respect to safety.  So -- and I'm working off

FLORIDA PUBLIC SERVICE COMMISSION

62

1   of memory right now, but I do recall one recommendation where

2   something in the NESC was not recommended for your acceptance

3   and you did deviate from an NESC requirement when you, when you

4   set the rule change.

5             The pilot study that is being recommended here, this

6   really is implementation or a variance of that, of the rule

7   where we say targeted infrastructure, identifying critical

8   infrastructure and hardening those assets.  That's the policy

9   guidance in the rule.  You're not telling the utility or

10   anybody how to achieve that hardening.  The utility simply

11   needs to be prudent in the process.  So I don't think these

12   points on this slide really affect the rules.  But it might be

13   something that the utility considers in its review, in its

14   decisions in implementation.

15             COMMISSIONER ARRIAGA:  Thank you.

16             CHAIRMAN EDGAR:  I've got some glare.  Let's see,

17   11:00.  Let's take a short recess.  We will come back at 11:15

18   by the clock on the wall.

19             MR. WRIGHT:  Madam Chairman.

20             CHAIRMAN EDGAR:  Mr. Wright.

21             MR. WRIGHT:  I would like to ask two kind of factual

22   clarifying questions about Dr. Slavin's slides, if I might.

23             CHAIRMAN EDGAR:  Can they be brief?

24             MR. WRIGHT:  They are brief.

25             CHAIRMAN EDGAR:  Okay.

FLORIDA PUBLIC SERVICE COMMISSION

63

1             MR. WRIGHT:  Dr. Slavin, I'm just trying to

2   understand some of the meaning of what you've presented.  If

3   you would look at your Slide 44, there are references in some

4   of your slides to the points at which poles would be knocked

5   down anyway.  And my question -- the question about this is at

6   what wind speed does the flying debris, as you've discussed in

7   your presentation, knock down poles anyway?

8             DR. SLAVIN:  It's approximately the -- it would be in

9   the mid 80s, mid 70s, the mid 80s.

10             MR. WRIGHT:  That's three-second gusts or sustained?

11             DR. SLAVIN:  Okay.  That's the, that's the

12   uncertainty.  When I said before it's hard to pick out the

13   exact number -- because it could be as much as a 20 percent

14   difference between one minute sustained speeds and three-second

15   gusts.  That is why when they picked this rule, they realized

16   there was, look, there's a range here, and also it's kind of

17   calibrated to the Saffir-Simpson hurricane definition of, you

18   know, of category storms and is very vague.  But they picked

19   the 15 as being a round number that's about right.  You can

20   argue with that number.  It might be 20 pounds per square foot,

21   it might be 15, but it's in the range of, say, 75 miles an hour

22   to maybe 85 miles an hour, that kind of range for three-second

23   gusts.

24             MR. WRIGHT:  Okay.  And then the other question is in

25   several of your slides you referred to a typical case in which

FLORIDA PUBLIC SERVICE COMMISSION

64

1   poles will be down regardless of extreme wind.

2             DR. SLAVIN:  Right.  What I mean by that is --

3             MR. WRIGHT:  Did that correspond to what you just

4   said, that basically something in a low Cat 1, 75 to 85 miles

5   an hour, is what you would consider a typical case?

6             DR. SLAVIN:  No.  That's not what I was referring to

7   actually, although that might be correct.

8             MR. WRIGHT:  Okay.

9             DR. SLAVIN:  What I was referring to is the fact that

10   we get an overwhelming number of comments from the industry,

11   okay, saying, look, the poles are coming down because of debris

12   and you're not going to do anything about it.  And that to me

13   is what the typical hurricanes are where that's happening.  If

14   you have a situation where something else happened and that was

15   not the source of the problem, then to me that was an atypical

16   situation.  So I did not mean in terms of wind speeds.  What I

17   meant was in terms of the response and the experiences of the

18   industry.

19             MR. WRIGHT:  Thank you.  Thank you.

20             CHAIRMAN EDGAR:  Thank you, Mr. Wright.  Thank you,

21   Dr. Slavin.

22             Okay.  We'll go ahead and maybe be a little more

23   realistic and I'll say 11:20 we will start again.  We are on a

24   short break.

25             (Recess taken.)

FLORIDA PUBLIC SERVICE COMMISSION

65

1             CHAIRMAN EDGAR:  Okay.  Thank you all.  We will begin

2   again.  And before we do, I want to make sure that we do have a

3   phone connection made.  So, Mr. Dickerson, are you with us?

4             MR. DICKERSON:  Yes, I am.

5             CHAIRMAN EDGAR:  Okay.  We are going to begin now

6   with some questions on the previous presentation, and then we

7   will move to the Embarq presentation after that.  And so I do

8   believe that we've got some questions from staff for Dr.

9   Slavin.

10             MR. BREMAN:  Before we begin that, there is a point

11   of clarification with Commissioner Arriaga that I would like to

12   follow up on, if that's okay.

13             CHAIRMAN EDGAR:  Uh-huh.

14             MR. BREMAN:  Commissioner, you asked with respect to

15   the alternative recommendation being provided to exclude

16   Grade N poles to explicitly cite NESC 2007 overloading factors

17   and to apply a pilot study initially limited to geographic

18   areas and defined periods; for example, one to two years.

19             The proposed rule, and if you turn to 25-6.0345, it

20   states, "For the construction of distribution facilities, each

21   utility shall, to the extent reasonably practical, feasible and

22   cost-effective, be guided by the extreme wind loading standards

23   specified by Figures 250-2(d) of the 2002 Edition of the NESC.

24   As part of its construction standards, each utility shall

25   establish guidelines and procedures governing the applicability

FLORIDA PUBLIC SERVICE COMMISSION

66

1   and use of the extreme wind loading standards to enhance

2   reliability and reduce restoration costs and outage times for

3   each of the following types of construction."  Then it

4   enumerates the types of constructions.  So that's the rule.  To

5   me that's very clear.  You're setting a policy and setting the

6   guidance.

7             COMMISSIONER ARRIAGA:  I want to thank you so much

8   for the clarification because that's exactly what I was getting

9   at.  Being that we're not imposing any specific thing to

10   anybody, it is moot to explicitly exclude it because it's not

11   being imposed.  That's what I was trying to get at.

12             MR. BREMAN:  Yes, sir.

13             COMMISSIONER ARRIAGA:  All right.  Thank you.

14             MR. HARRIS:  Thank you, Chairman.

15             Dr. Slavin, my name is Larry Harris.  I'm staff

16   counsel at the Commission here.

17             On Slide 39 of your presentation you had spoke about

18   the NESC subcommittee's decision to reject a change.  I want to

19   clarify in my mind if I'm understanding what you're saying.

20   The National Electric Safety Code is a safety code; is that

21   correct?

22             DR. SLAVIN:  Yes.

23             MR. HARRIS:  Okay.  And so the last sentence of that

24   slide says, "The safety of employees and the public is provided

25   using the current NESC loading requirements."  Is it the intent

FLORIDA PUBLIC SERVICE COMMISSION

67

1   of your presentation today to stress that the NESC is for the

2   safety of the public and workers?

3             DR. SLAVIN:  I believe that's in the scope of the

4   NESC as stated in the front of the document.

5             MR. HARRIS:  So would your presentation today be

6   directly applicable to the reliability of the electrical

7   infrastructure in the State of Florida?

8             DR. SLAVIN:  We tend to use -- we tend to think that

9   they're related.  I'm not sure they're synonymous.  I can

10   picture probably cases where you have something that's reliable

11   -- or not reliability but not safety related because it depends

12   what the consequences are if something comes down.  Okay?  So

13   the -- you know, so I don't think they're synonymous, but I

14   think they are related.

15             MR. HARRIS:  So would it be fair to say that when the

16   committee was voting on whether to accept these changes, they

17   were looking from a safety perspective and not necessarily a

18   reliability perspective?

19             DR. SLAVIN:  Well, no, I think that's too strict an

20   interpretation.  I think we do tend to -- they are related.  I

21   said they're not synonymous, but they are related.  That's why

22   we have grades of construction which do deal with reliability,

23   and we put safety factors in accordingly.  So I think the

24   answer you want is, yes, they are related.  Okay.  I don't want

25   to use the word synonymous though because I can picture where

FLORIDA PUBLIC SERVICE COMMISSION

68

1   they may not be exactly identical.

2             MR. HARRIS:  Thank you, Doctor.  On your Slide 37 you

3   used -- the last bullet point, "No significant impact in

4   Florida versus present Rule 250B."

5             DR. SLAVIN:  Uh-huh.

6             MR. HARRIS:  Could you define for me what you mean by

7   "significant impact"?

8             DR. SLAVIN:  What I mean is that if you're going to

9   limit the wind pressures to 15 pounds per square foot or

10   thereabouts, because it is an approximation and I think I was

11   trying to make that, and you're already designing -- say it was

12   15 to 20, I think that's merely a range that I could figure

13   out.  I didn't want to get the slide too confusing.  I didn't

14   want to, you know, get into that kind of detail.  But if you

15   picture the range being 15 to 20 pounds per square foot as

16   being the range above which you start to get the flying debris,

17   and Florida is already designing to 18, all right, you're

18   not going to -- you're already designing to the level at which

19   the wind pressure -- you're already designing to the level

20   below which the flying debris is not an issue.  If you design

21   to higher than the 18, the flying debris is going to take over

22   and be the dominant effect.  Okay?  So there may -- so it

23   may -- I'm not saying there's a zero impact, but it's not going

24   to be much of an impact.  Okay?

25             MR. HARRIS:  Thank you.  And the last question that I

FLORIDA PUBLIC SERVICE COMMISSION

69

1   have is is the National Electric Safety Code designed for sort

2   of the day-to-day safety of the public and employees or

3   designed for emergency situations or both?

4             DR. SLAVIN:  I would say it's more the first.  But

5   there are some statements about emergency conditions, okay,

6   where some of the rules might be able to be bent a little bit,

7   so to speak.  I forget the exact wording.  If you look in some

8   of the, in some of the sections there, they say on an emergency

9   basis you might be able to, you know -- like in clearance

10   issues, for example, you might be able to -- I don't want to

11   use -- effectively bend the rules a little bit temporarily, and

12   that might be open to interpretation where you can do it.  I

13   would say it's more in day-to-day -- it's for operation, it's

14   for maintenance and it's for storms.  It is for storms.

15             MR. HARRIS:  All right.  Thank you.  Thank you,

16   Chairman.

17             DR. SLAVIN:  My pleasure.

18             CHAIRMAN EDGAR:  Okay.  Any additional questions for

19   Dr. Slavin or for Verizon?  Anybody else?  No?  No.

20             Okay.  All right.  Then thank you very much, and we

21   will move on to the next presenter.  Ms. Masterton.

22             MS. MASTERTON:  Yes, Madam Chairman.  And Embarq does

23   have a PowerPoint presentation that we would also like to move

24   as an exhibit into the record.  And for consistency's sake,

25   label it Embarq's Presentation, and I think the number would be

FLORIDA PUBLIC SERVICE COMMISSION

70

1   Exhibit 5.

2             CHAIRMAN EDGAR:  Yes.  Thank you.

3             (Exhibit 5 marked for identification and admitted

4   into the record.)

5             MS. MASTERTON:  And the way we've structured our

6   presentation, George Finn is going to discuss some operational

7   concerns that we have with the rules as proposed; Kent

8   Dickerson, who's on the phone, will discuss some cost concerns;

9   and then I'm going to conclude with some concerns regarding the

10   validity of the proposed rules.  So with that, I'll turn it

11   over to Mr. Finn.

12             MR. FINN:  Good morning, and thank you for the

13   opportunity to address you today.

14             As Susan mentioned, my name is George Finn, and I'm

15   currently the Director of National Policy for Embarq's Network

16   Services Organization.  Among other things, my team is

17   responsible for the policies, methods and procedures related to

18   outside plant construction, engineering, including pole

19   attachments.

20             Prior to assuming this role in October 2005, I served

21   as the Director of Customer Service Operations here in Florida

22   where I was responsible for service operations in Central

23   Florida from Yeehaw Junction up through Ocala, and have direct

24   experience with the power and devastation of these storms as

25   well as the lengthy recovery processes.

FLORIDA PUBLIC SERVICE COMMISSION

71

1             As you know, Embarq is both a pole owner and a pole

2   attacher here in Florida and in the 17 other states in which we

3   operate.  As such, our policies, methods and procedures for the

4   engineering and construction of outside plant facilities and

5   pole attachments adhere to NESC, ANSI and Telcordia and

6   Bellcore standards.  These industry standards have been widely

7   adopted and recognized as safe and appropriate.  And based on

8   our experience in 2004 and 2005 with our distribution plant,

9   these standards proved to be sufficient.

10             While we certainly had poles damaged during the

11   storms, we did not experience any massive pole failures.  We

12   found that the damage to our distribution facilities was caused

13   by many factors:  Airborne debris, falling trees, falling tree

14   limbs, flooding, storm surge, sand, as well as wind.

15             I am unaware of any data from Florida or any of the

16   other states in which we operate that suggests that the

17   existing standards are inadequate, nor am I aware of any

18   documented evidence that suggests that exceeding the current

19   standards would provide any additional protection from these

20   violent storms.  As I mentioned, much of the damage came from

21   falling trees, falling tree limbs, flying debris, storm surge.

22   Just making stronger poles doesn't necessarily ensure that

23   outages will not be had.

24             It is our opinion that any construction or pole

25   attachment requirements that extend beyond the industry

FLORIDA PUBLIC SERVICE COMMISSION

72

1   standards should reflect the collective and agreed upon impact

2   from all impacted parties.  The electric, telecommunication and

3   cable industries have historically worked cooperatively to set

4   the standards for the joint use of poles, joint placement of

5   facilities underground.  We rely on each other to provide

6   service to our customers and have proven the ability to work

7   together successfully over time.  We believe that adopting a

8   model that gives one industry full discretion over these

9   standards is undesirable.

10             In the area of underground construction, accepted

11   industry standards have long been used to guide electric

12   utilities and ILECS in the construction and use of common

13   trenches.  We work together on these standards every day, and

14   Embarq remains supportive of joint trust use and new

15   construction.

16             On Slide 3, just a few comments on cost-benefit

17   analysis.  Given the ambiguity surrounding what any new

18   construction and attachment standard might be makes it

19   extremely difficult to perform any meaningful cost-benefit

20   analysis.  Until the standards are clearly articulated, the

21   size and scope of the changes laid out, no one can predict with

22   any absolute certainty what those costs may be.  And the

23   ultimate cost of these rules will be both route and cite

24   specific depending on the variables in each project:  Whether

25   we're talking about rock and sand, whether we're boring under

FLORIDA PUBLIC SERVICE COMMISSION

73

1   roads, driveways and streets, whether we're moving aerial

2   cable, whether we're burying cable, whether we're in a

3   greenfield environment or relocating existing plant.  Until

4   these unknowns are decided, it is difficult to make cost

5   assumptions due to the inherent variability of this type of

6   work.

7             And lastly on Slide 4, I just want to take a

8   pragmatic approach to make sure we don't underestimate the

9   level of disruption that could occur as existing rear lot line

10   facilities are moved to front lot line facilities.  It's not a

11   simple matter of moving the cable from the rear of the lot to

12   the front of the lot.  It will require the placement of new

13   poles, new cables, new terminals, require the removal of such

14   from the rear facilities.

15             If the front line facilities are built underground,

16   it will require new trenches, easements, rights-of-way, as well

17   as dealing with the existing facilities, water, power -- or

18   water, sewer, gas that are currently built underground.

19             In addition, it will also likely require

20   premise-mounted equipment such as NIDs and drops to be

21   relocated on the consumer's home to now be served from the new

22   poling (phonetic).  All of this activity results in torn up

23   lawns, sidewalks and fences and makes for an inconvenience for

24   Florida customers, and we think that that shouldn't be

25   overlooked.

FLORIDA PUBLIC SERVICE COMMISSION

74

1             That concludes my portion of the remarks, and I'll

2   turn it over to Kent Dickerson, our Director of Cost Support.

3             MR. DICKERSON:  Thank you, George.

4             I'd like to thank the Commission for the efficiency

5   of allowing me to make some very brief remarks via the

6   telephone.

7             The first point would be that the electric companies

8   have proposed a plan for cost recovery, and they've proposed a

9   possible combination of funding from the local municipalities

10   or cities that have requested a change in their plant, perhaps

11   aerial going underground, and that they also would be able to

12   make up portions of those costs that would not be potentially

13   funded by that local entity through their normal ability to

14   request rate increases from the Commission.

15             And so a point from a telephone industry perspective

16   that would fall from that is that as attachers to poles that

17   potentially have either had an increased cost from one loading

18   or have been moved from back lot to front lot and/or were on a

19   pole before and have moved underground potentially, that the

20   costs that are incurred to do that construction to the extent

21   the electric companies have already recovered those costs or

22   have the ability to recover those costs through entity funding

23   and rate increases, that they not, you know, be able to mix and

24   include those costs in their attachment rates to, to cable and

25   telephone companies.

FLORIDA PUBLIC SERVICE COMMISSION

75

1             And then second following that would be that the

2   telephony attachers have no similar rate increase mechanism to

3   recover their costs, and, therefore, it would be all the more

4   important that any actions or activities be justified with

5   sound cost-benefit analyses.  And that was all the remarks I

6   had.  I'll turn it back to Susan Masterton at this point if

7   there's no questions.

8             MS. MASTERTON:  Thank you.  And my remarks are really

9   just another facet of the same theme that you've heard from

10   Mr. Finn and Mr. Dickerson, and that is Embarq's belief that

11   the rules just leave an unacceptable amount of discretion with

12   the electric companies.  The rules require that electric

13   companies unilaterally adopt construction and attachment

14   standards that may exceed the National Electric Safety Code and

15   that appear to us to be without limitation.  These new

16   standards will substantially affect parties who attach to the

17   electric utility poles.

18             Florida law prohibits an administrative agency from

19   delegating its rulemaking authority to private entities, and

20   I've included some cases that I think are relevant to that

21   point of law.  The first case, the Amara case, essentially

22   stands for the proposition that a governmental entity cannot

23   delegate its governmental powers to a private entity.

24             Then the second case or the second legal authority is

25   an Attorney General opinion that this Commission requested, and

FLORIDA PUBLIC SERVICE COMMISSION

76

1   it was in relation to its regulation of motor carriers.  It had

2   set up private ratemaking entities to develop rates for the

3   motor carriers, and then those entities were going to recommend

4   those rates to the Commission.  And the Commission was asking

5   the Attorney General to say is that an improper delegation of

6   our authority to a private entity?  In that case, the Attorney

7   General, after researching the relevant case law, determined

8   that that situation was not an unlawful delegation, and this is

9   what the opinion says about that.  "The crucial factor in

10   reaching this conclusion is the administrative agency's

11   retention and exercise of ultimate authority to determine

12   rates."  And these rules don't do that.  I mean, these are

13   alleged to be guidelines but to us appear to be too ambiguous

14   to, to adequately guide the electric companies in determining

15   what standards might exceed the National Electrical Safety

16   Code.  And there's no approval authority for the Commission.

17   In fact, the guidelines are never -- the standards are not

18   required to be filed with the Commission or even required to be

19   reviewed by the Commission.

20             Now some have argued that the provision that says

21   that disputes can be brought to the Commission cures that

22   invalidity.  But the third case that I've cited, the Florida

23   Nutrition Counselors Association case, refutes that decision,

24   and it says that an enforcement action cannot validate an

25   invalid delegation of rulemaking authority.

FLORIDA PUBLIC SERVICE COMMISSION

77

1             One of the primary reasons for requiring that

2   administrative agencies adopt rules that will substantially

3   affect other parties rather than private entities is that it

4   ensures that the procedural protections of the Administrative

5   Procedures Act as well as the provisions of the open records

6   and open meetings laws are followed in adopting the standards.

7             In the case I've cited here, the News and

8   Sun-Sentinel case, addresses an issue of public records that I

9   think is relevant here because, as I understand it, one of the

10   primary reasons that the electric companies do not want to file

11   their standards with the Commission for approval is that

12   they're proprietary and they don't want them to become public

13   records.  So I think that's a relevant case.  But in addition,

14   this delegation, Embarq believes, prevents the Commission from

15   adequately fulfilling the SERC requirements of the

16   Administrative Procedures Act.  Because the rules, because the

17   rules would result in standards that are unknowable at this

18   time and at the time of adoption, the Commission is unable to

19   ensure that it adopts the lesser cost alternatives that would

20   achieve its regulatory objective.  And the staff's revised

21   SERC, I think, just points that out in a couple of places.

22             On Page 3 in the provisions about electric utility

23   costs, the staff states, "Other rule changes would have

24   additional cost, but estimates are not available at this time."

25   And then on Page 4, the staff acknowledges Embarq's comments

FLORIDA PUBLIC SERVICE COMMISSION

78

1   that the Commission cannot know what the standards will

2   ultimately be and, therefore, cannot know the added value of

3   the additional cost any new standards exceeding the NESC may

4   engender.

5             In addition, the staff -- although they discussed

6   generally benefits from the rules, those are not quantified.

7   They're just stated in generic terms that the entities and

8   their customers would also substantially, benefit substantially

9   from fewer and shorter outages from downed poles and lines.

10   But there's no dollar value placed to that benefit to enable

11   the companies to do some kind of -- or the Commission and the

12   parties to adequately weigh the benefits versus the costs, the

13   substantial costs that the other parties here today have

14   indicated would be borne by the attachers, but also costs that

15   the electric companies would incur.

16             So basically what Embarq is saying is that we support

17   the proposal that BellSouth has put forth of the industry

18   getting together to work out standards that would apply.  And

19   in the alternative of that, we're saying that the NESC is

20   sufficient.  Mr. Finn addressed that.  We have no evidence --

21   we don't believe the evidence contained -- the record contains

22   any evidence that it was the inadequacy of the NESC standards

23   that caused the damages in the storms.  But if there are going

24   to be any standards imposed in excess of the NESC, we're saying

25   that to be valid they must be imposed by the Commission, not

FLORIDA PUBLIC SERVICE COMMISSION

79

1   unilaterally by the electric companies.  And we've also

2   suggested that the rules relating to the location of facilities

3   should apply only to new construction because we believe that

4   the cost and the disruption of moving existing facilities

5   exceeds the benefits that doing that would impart.  And that

6   concludes my remarks.  Thank you.

7             CHAIRMAN EDGAR:  Thank you.

8             Commissioner Arriaga.

9             COMMISSIONER ARRIAGA:  Ms. Masterton, you raise a

10   very important point, which is the issue of delegation.  And I

11   confess to you that during the briefings that I've had with

12   staff that issue has come to my mind also, and I've been trying

13   to read and understand the pros and the cons and the different

14   arguments that were placed forward.

15             If the PSC, the Commission changed the proposed rule

16   as it is right now to require that any standards developed

17   under these rules prior to all the negotiations and

18   conversations you wish to have be brought back to us for our

19   approval, does that remove any subdelegation concerns that you

20   have?

21             MS. MASTERTON:  I think that that would go a long way

22   just from the way you've described it, yes, of addressing the

23   subdelegation concerns.  Because when you do that, that would,

24   at the time that you approved them, that would give, ensure

25   that the protections of the Administrative Procedures Act and

FLORIDA PUBLIC SERVICE COMMISSION

80

1   the ability for parties to have input would be assured.

2             COMMISSIONER ARRIAGA:  Thank you.

3             May I follow up with staff?  Mr. Harris, if that were

4   the case, does staff have any specific issue with bringing

5   those standards for approval to the Commission so they don't

6   become a specific utility dictating mandates to anybody else

7   and our authority or delegation of authority is no question?

8   Does that raise any concerns to you?

9             MR. HARRIS:  None whatsoever.

10             COMMISSIONER ARRIAGA:  So you would be okay with a

11   proposal like this?

12             MR. HARRIS:  Yes, sir.  And, in fact, I believe the

13   original draft of the rule that we proposed for the first

14   workshop did include some language that the standards would be

15   approved by the Commission.

16             COMMISSIONER ARRIAGA:  But it isn't like that right

17   now.

18             MR. HARRIS:  It was removed due to the workshopping

19   process.  There was a number of concerns brought up by some of

20   the participants in the workshops that led us to believe that

21   could be removed.  We still believe there's no subdelegation.

22   However, in order to strengthen the rule, we are not opposed to

23   including language requiring them, the standards to be approved

24   by you.

25             COMMISSIONER ARRIAGA:  Okay.  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

81

1             MS. MASTERTON:  Commissioner, I -- Madam Chairman, if

2   I may.  I just wanted to note that some of the other parties

3   have addressed some concerns about the jurisdiction of the

4   Commission which I did not readdress here, and I'm not sure

5   that this was -- in fact, I would say those parties would say

6   that that mechanism would not address those concerns but it

7   would address the concerns related to subdelegation.

8             COMMISSIONER ARRIAGA:  And I do have some comments

9   over jurisdiction, but I'll leave that for a little later.  I

10   want to hear the cable companies, et cetera, before I do that.

11   Okay.  Thank you.

12             CHAIRMAN EDGAR:  Commissioner Tew.

13             COMMISSIONER TEW:  I have a follow-up question for

14   Mr. Harris.  You said that you believe there would be no

15   subdelegation issue.  Can you elaborate on how you came to that

16   conclusion?

17             MR. HARRIS:  Yes, ma'am.  My, my interpretation of

18   the case law regarding delegation requires that the Commission

19   make the ultimate decision, and you cannot delegate the

20   ultimate decision to someone else, a private entity.

21             I believe in this case the rules were very carefully

22   drafted to, A, establish your policy, which is one of the

23   things that are allowed under the case law, that you can set a

24   policy and then say here's our policy, here's what we want

25   done, now you go do it.  And then on the back end there needs

FLORIDA PUBLIC SERVICE COMMISSION

82

1   to be some ultimate review authority on your part.  You can't

2   just say go do it and you all enforce it, we wash our hands of

3   it.  You have to retain responsibility, for lack of a better

4   word.  I think the rules were drafted to allow you to retain

5   that through staff audits, through your ability to ask

6   questions, through the staff's ability to bring it back before

7   you, and, most importantly, to the ability of any person, not

8   just an attacher, but any person out there to bring back a

9   complaint and say we have a problem with this standard or that

10   standard or all of the standards.  And it doesn't have to be

11   when they're developed; it can be at any time.  So a year from

12   now, two years from now, five years from now you will be the

13   ultimate decision-maker as to whether that standard is

14   appropriate or not, and I think that removes the subdelegation

15   argument.

16             COMMISSIONER TEW:  I guess one follow-up to that.

17   The case that Ms. Masterton mentioned about Florida Nutrition

18   Counselors Association v. DBPR, and I know you may not have had

19   a chance to look at it, but I think she was saying that an

20   enforcement action cannot validate the delegation of authority.

21   So, I mean, it sounds like to me that your answer is saying

22   that because we have the enforcement action on the back end,

23   that it does in a sense cure any sense of a delegation of

24   authority.

25             MR. HARRIS:  I have not read the case and I certainly

FLORIDA PUBLIC SERVICE COMMISSION

83

1   will.  However, I'm not sure what the term "enforcement action"

2   means.  If that means that the delegated entity has the

3   enforcement mechanism, that's a problem.  If that means that

4   the PSC would go to enforce that standard without having

5   reviewed it, that would be a delegation problem.  If, however,

6   once the PSC reviews the standard and approves it and then

7   seeks to enforce it, I think you remove subdelegation because

8   you have been the ultimate decision-maker.  So I would want to

9   read it carefully for the distinction between what an

10   enforcement action is:  Are you telling the IOUS to go do it

11   without you having any review or, if there's a problem, would

12   you then make the ultimate decision and then you would enforce

13   it?  But I haven't read the case.

14             CHAIRMAN EDGAR:  Commissioner Deason.

15             COMMISSIONER DEASON:  Ms. Masterton, I believe you

16   said that you -- that Embarq endorses the concept of a

17   voluntary infrastructure advisory committee; is that correct?

18             MS. MASTERTON:  That's correct.

19             COMMISSIONER DEASON:  Okay.  Now how does -- if such

20   a committee were to be created, according to your

21   understanding, how would that committee not violate your

22   concerns about unlawful delegation?

23             MS. MASTERTON:  I mean, this hasn't been entirely

24   fleshed out with the industry, but in my -- the way I

25   understand that proposal, the rule would not address the

FLORIDA PUBLIC SERVICE COMMISSION

84

1   standards in excess of the National Electrical Safety Code.  It

2   would require compliance with the National Electrical Safety

3   Code as a minimum compliance to meet the rule.  And I think

4   that leaves then the industry to agree to additional standards

5   that there's no rulemaking involved.  It becomes just an

6   agreement of the industry.

7             But to the extent that the Commission would feel that

8   it, that it had a role or wanted to, you know, embrace that

9   through the rule, then I think having approval authority for

10   the Commission as the final determination would cure any

11   delegation problems, just as the questions that Commissioner

12   Arriaga asked about the current rule.

13             CHAIRMAN EDGAR:  Were there any additional questions

14   from staff?

15             MR. HARRIS:  No, ma'am.  Thank you.

16             CHAIRMAN EDGAR:  None at this time.  Any questions

17   from anybody else regarding the Embarq presentation?  No?

18             Okay.  Then we will move on to the next presenter,

19   and, Mr. Gross, that is you.

20             MR. GROSS:  Just checked to see if I could still say

21   good morning.  I think I can.

22             Madam Chair, Commissioners, Michael Gross for the

23   FCTA.  And I thank you very much for giving us an opportunity

24   to make a presentation today.  And we also want to express our

25   appreciation of previous opportunities we've had to make

FLORIDA PUBLIC SERVICE COMMISSION

85

1   presentations at expanded workshop opportunities and to make

2   filings and to have our viewpoint heard and become part of the

3   record.  Thank you very much for that.

4             I have some handouts, and I would like to kind of

5   take care of that first.  I think that's being taken care of.

6   Thank you.  But what we propose to do today is I myself will

7   make a brief presentation addressing some legal issues that

8   seem to have come to the forefront in this matter, and then

9   Michael T. Harrelson, our expert witness, will talk about some

10   of the technical issues in the case.  And we're going to try

11   not to duplicate what's already been said, but we may

12   supplement or complement some of the things that have been

13   previously stated.

14             CHAIRMAN EDGAR:  Mr. Gross, before we move right into

15   that, let's go ahead and take up the documents that you've

16   passed out.  We'll have them be exhibits as part of the record

17   of this hearing, and so go ahead and label them and we'll

18   number them.

19             MR. GROSS:  Yes.  Okay.  One document is Memorandum

20   of Law in Support of the FCTA's Suggested Rule Changes.

21             CHAIRMAN EDGAR:  Okay.  And that will be Exhibit 6.

22             (Exhibit 6 marked for identification and admitted

23   into the record.)

24             MR. GROSS:  The next will be Comments by

25   Michael T. Harrelson on behalf of the FCTA.

FLORIDA PUBLIC SERVICE COMMISSION

86

1             CHAIRMAN EDGAR:  Okay.  And we will number that as 7.

2   Thank you.

3             (Exhibit 7 marked for identification and admitted

4   into the record.)

5             MR. GROSS:  Thank you.  And a third exhibit, the

6   final exhibit is a Description of Photos by Michael T.

7   Harrelson on behalf of the FCTA.

8             CHAIRMAN EDGAR:  Okay.  That will be Number 8.  And I

9   think we're ready to jump into it.

10             (Exhibit 8 marked for identification and admitted

11   into the record.)

12             MR. GROSS:  Okay.  Thank you.  The FCTA does not

13   dispute that Florida Statutes confer jurisdiction on the

14   Florida Public Service Commission to prescribe and enforce fair

15   and reasonable construction standards for electric transmission

16   and distribution facilities, even those that exceed the NESC

17   when doing so is necessary to ensure the reliable provision of

18   electric service.  And that comes right out of the authority

19   set forth in Section 366.04(6) and Section 366.05(1).

20             In fact, as the FCTA has stated throughout this

21   proceeding, the FCTA applauds the Commission and the Florida

22   Legislature for taking these positive steps to address the

23   storm damage and protracted power outages that were experienced

24   during the recent storms.  Cable operators, which are now

25   providing telephone and broadband services in addition to

FLORIDA PUBLIC SERVICE COMMISSION

87

1   video, and, more importantly, their customers which number more

2   than 5 million in the State of Florida have a genuine interest

3   in assuring the integrity of the electric pole plant.

4             Furthermore, the FCC has acknowledged that utilities

5   can rely on the NESC in prescribing standards as well as other

6   industry codes that are widely accepted objective guides for

7   the installation and maintenance of electrical and

8   communications facilities.

9             The FCC also has said that a state requirement that

10   is more restrictive than the corresponding NESC standard may

11   still apply.  However, in that same order which is cited in our

12   memorandum of law, and I'm going to -- the reason we handed

13   that out was to conserve time, and I'm not going to go into

14   great depth as far as what's in that memorandum of law other

15   than to highlight some of the main points of it.

16             But in the order cited in that memo, the FCC has said

17   that a state requirement can be preempted if it is inconsistent

18   with FCC rules and policies, and significantly that a utility

19   may not be the final arbiter of denials based on capacity,

20   safety, reliability or engineering, nor should the pole owner's

21   determinations be presumed reasonable.  Indeed, the law is

22   clear that both the pole owner and a would-be attacher must

23   agree that a pole lacks capacity before a utility may deny

24   access on such grounds.

25             Specifically, the FCC's rule on access was challenged

FLORIDA PUBLIC SERVICE COMMISSION

88

1   by a group of electric utilities in Southern Company v. FCC.

2   And in that case, the 11th Circuit Court of Appeals held that

3   the FCC's regulations requiring utilities to expand capacity

4   were overbroad in light of the statutory language in Section

5   224(f) of the act and vacated the rule, just for some

6   background.  But the key point that we're citing that case for

7   is the court also found that utilities may not make a

8   unilateral determination that capacity is insufficient for

9   third-party attachers.  Specifically, the court explained that

10   electric utilities do not have unfettered discretion to

11   determine insufficient capacity because that could only be

12   found as to a particular pole when it is agreed that capacity

13   is insufficient.  Thus, only where a third-party attacher

14   agrees that a taller pole, rearrangement or make-ready is not

15   feasible could capacity be deemed insufficient to justify a

16   denial of access.

17             The reason I cite these pronouncements by the FCC and

18   by the federal courts is because we have suggested language in

19   our suggested rule changes that we think would address the

20   problem by requiring standards to be jointly developed with all

21   attaching entities and approved by the Commission.  And I'll

22   get to that subdelegation issue momentarily.  So we didn't just

23   make this up out of a vacuum that agreement among the parties

24   would be more in line with the FCC decisions, you know, in this

25   area.  We're combining the holding on the capacity issue by the

FLORIDA PUBLIC SERVICE COMMISSION

89

1   11th Circuit that the parties must agree on whether there's

2   sufficient capacity or not before access can be denied.  And

3   certainly if there's a dispute, that would be brought to the

4   FCC if the parties can't agree on that.  But also the

5   Commission has made it clear that with respect to safety,

6   reliability and engineering standards as grounds for denial of

7   access, that the utilities don't have unfettered discretion or

8   presumption of correctness and they cannot act unilaterally.

9   So we feel that there is some legal support for the suggested

10   rule change that we've put forth there.

11             Now as we've stated, the Commission may prescribe

12   fair and reasonable construction standards including NESC or

13   standards that exceed the NESC for the prescribed purposes of

14   ensuring reliable provision of service.  That's right out of

15   your statutory authority.  But in our view, the rules as

16   presently crafted fall short of this fair and reasonable

17   standard to the extent that they give an inappropriate amount

18   of discretion to the utilities, which are in this case private

19   entities which have an interest in the stake -- with a stake in

20   the interest of the outcome of this proceeding; in fact, a

21   pecuniary interest.  And the rule doesn't provide adequate

22   representation to other entities attached to the poles.  The

23   FCTA's proposed amendments address this problem by requiring

24   that the rules be jointly developed.

25             Now the next point regarding the subdelegation issue,

FLORIDA PUBLIC SERVICE COMMISSION

90

1   and I agree and join and concur with the law and the statements

2   that Ms. Masterton on behalf of Embarq made, so I won't rehash

3   what she has said, but I would like to make a couple of

4   additional comments on that issue.

5             There are cases where the Legislature has delegated

6   authority to a state agency or government entity and there's a

7   question about whether there's been an unlawful delegation of

8   authority.  And that originates in Article 3 of the Florida

9   Constitution, which basically says that no branch of government

10   shall exercise powers belonging to another branch of

11   government.  And that is a slightly different issue from the

12   issue that we're facing right here.  There the question is

13   whether the Legislature gave the government agency sufficient

14   guidelines or standards.  We're talking about a situation which

15   is an unlawful exercise of delegated authority where the issue

16   is whether the agency has properly subdelegated its authority

17   or improperly subdelegated its authority in this case to a

18   private entity which has a pecuniary interest or conflict of

19   interest in the outcome of this proceeding.  And so I think

20   when we look at the cases and we look for the reasoning and the

21   principles that are applicable, we really need to look at cases

22   that are more on point factually.  And that's a situation where

23   a government agency is delegating, delegating authority to a

24   private entity.

25             And there's one case I'd like -- you know, throughout

FLORIDA PUBLIC SERVICE COMMISSION

91

1   this proceeding the FCC, the -- we're not the FCC yet -- the

2   FCTA has expressed concerns over the fact that we have a

3   history of over 20 years of litigation with the power

4   companies.  This is nothing personal.  This is business.  And I

5   attached as an exhibit a representative sample of those cases,

6   including cases that have gone to the United States Supreme

7   Court:  One case reversing an attempt by the power companies to

8   increase our pole rental rates 500 percent on the basis that

9   since we were now providing Internet service over the same

10   plant without, without adding any additional plant to the

11   poles, using the same plant that we used to provide video but

12   now we added Internet service over that plant, the power

13   companies claim that the FCC pole rental formula for

14   calculating those pole rates no longer applied, and also took

15   the position just incidentally that the FCC pole formula did

16   not apply to the wireless entities who were attached.  The 11th

17   Circuit ruled in favor of the power companies and the United

18   States Supreme Court reversed on that, just to give you an

19   example.

20             So while we can only speculate as to what might

21   happen as a result of these construction standards, history is

22   very compelling, and it's the only thing we have to look at

23   right now.  I would hope that that history would not continue,

24   but it might be an example of naivety to expect that things

25   would change.

FLORIDA PUBLIC SERVICE COMMISSION

92

1             And there is a federal case which was out of the

2   5th Circuit Court of Appeals in 1983 where the court observed

3   the role of the private firm in this case in the preparation of

4   the draft and final version of the environmental impact

5   statement is particularly troubling in this case because the

6   consulting firm also had a stake in the project which it was

7   evaluating.

8             Now this was a case where the Army Corps of Engineers

9   was supposed to prepare an environmental impact statement and

10   they kind of subcontracted that out to a private entity that

11   had a pecuniary interest in the outcome of the proceeding.  The

12   court went on to say an agency may not delegate its public

13   duties to a private entity, particularly private entities whose

14   objectivity may be questioned on the grounds of conflict of

15   interest.  So I just wanted to add those points to what

16   Ms. Masterton had already said.

17             We think that our proposed amendments to the rules or

18   suggested rule changes address the problem by including a

19   requirement that the standards would be jointly developed.  And

20   even if not jointly developed, even if after an evidentiary

21   hearing or some type of adversarial proceeding, they would in

22   either case have to be submitted to the Commission for

23   approval.

24             Now there's just one more case I want to cite and

25   I'll move on from this point.  But there was a case cited in

FLORIDA PUBLIC SERVICE COMMISSION

93

1   the joint reply comments of the IOUs that actually, I think,

2   supports the, an unlawful exercise of delegated authority more

3   than it does the opposite.  But once again, this is a case

4   where it was a question of whether the Legislature -- well, let

5   me find the case and be sure if I'm -- actually this was a

6   case, Brown v. Apalachee Regional Planning Council, where there

7   was a delegation of a technical matter, and it was a case that

8   held that as long as the Commission, the agency made the

9   fundamental policy decisions, that implementation of technical

10   matters to another entity would not by itself render the

11   delegation an unlawful delegation.  But in this particular case

12   there were sufficient constraints, including considerable

13   detail and specific criteria about a mandatory review process

14   that the council had to follow.  I mean, they had delegated

15   their authority, but they were mandated to review the process.

16   There was specific criteria for that review and there was a

17   specific time when that review had to take place and ultimately

18   approval by the planning council.  And we don't feel that that

19   has been provided for here.  But we think that it could easily

20   be corrected by the Commission, and we feel that the

21   Commission's statutory authority actually requires it to assure

22   that these rules are fair and reasonable and are for the

23   purposes of ensuring reliable provision of service.  The

24   Commission needs to take a look at these standards and make

25   that determination.

FLORIDA PUBLIC SERVICE COMMISSION

94

1             Now as far as the Florida Public Service Commission's

2   jurisdiction over pole attachment, third-party attachment

3   issues, the FCTA agrees that this Commission does, as we've

4   said, has safety and reliability jurisdiction, and the FCC has

5   said that it will show deference for safety and reliability

6   standards developed by states, but reserving a right to preempt

7   them when they feel that there's a conflict with federal

8   policy, but at least, all other things being equal, will show

9   deference to those state standards in connection with a pole

10   attachment dispute that's been brought to the FCC.  But that's

11   how it works.

12             Now on the other hand, as far as the development of

13   the standards, it would be our position that that falls

14   squarely within the power and the jurisdiction of the state.

15   And I won't say just the Commission, but the Commission happens

16   to be the arm of the state that's been given this

17   responsibility.  But we can speak in terms of what the state's

18   jurisdiction is, you know, even in terms of legislative acts by

19   the state.

20             Now I'd like to just respond briefly to some comments

21   that the -- the joint reply comments of the IOUs made arguing

22   that a, a state that has not certified -- and I hope, I

23   shouldn't presume, that all of the Commissioners understand

24   that process, so I apologize if I'm going over something that

25   you already are fully aware of.  But states can certify with

FLORIDA PUBLIC SERVICE COMMISSION

95

1   the FCC following a process that's set forth in Section 224 of

2   the Communications Act, the one that -- and that's the same act

3   that addresses the nondiscriminatory mandatory pole access

4   rights of telecommunications companies and cable companies.

5   But in there they say a state, by meeting certain requirements

6   and making a certain, certifying as to certain facts, can begin

7   to regulate pole access issues.  And that just hasn't been done

8   yet by this Commission.  And we haven't really relied on the

9   Teleprompter case.  Before my time -- I noticed that that case

10   was before my time with the FCTA, but the FCTA just

11   incidentally was an intervenor in that case.  And that case has

12   been very often cited for the proposition, not just in the

13   context of pole attachment jurisdiction, but that in the State

14   of Florida even where there's a federal grant of authority to

15   the states, that in Florida the state legislature still has to

16   enact some enabling legislation allowing a state agency to, to

17   implement that grant of authority given by the federal

18   government.  And I think that's what that case was saying

19   there.  But I don't even think we have to look to that case.

20   We can just look to the more recent FCC pronouncements on this

21   issue.

22             Now contrary to the statements made by the joint

23   reply comments, a noncertified state such as the State of

24   Florida does not, cannot have jurisdiction over pole access

25   disputes.  And I just want to point out that attached to our

FLORIDA PUBLIC SERVICE COMMISSION

96

1   memorandum are excerpts from the order on reconsideration of

2   the FCC's local competition order.  And the power companies

3   quote and cite to Paragraphs 114 and Paragraphs 116 where

4   there's a lot of extensive discussion about the states that if

5   a dispute, for example, is brought to the FCC by a cable

6   company over a denial of access under the pretext of safety

7   reliability issues, that the party asserting that the state has

8   jurisdiction and has, you know -- and that the FCC does not

9   have the jurisdiction, that the FCC will stand down and not

10   take that case if it's persuaded that the state has

11   jurisdiction.  And the power companies are arguing that even --

12   that that applies to noncertified states, not just certified

13   states.  But they have omitted the paragraph in the middle,

14   Paragraph 115.  They've cited to Paragraph 114 and Paragraph

15   116.  We have attached, it's in black and white, you can read

16   it for yourself, it speaks for itself, we've attached the

17   relevant pages.  We quoted from Paragraph 114 which makes it

18   clear that those other two paragraphs are talking about states

19   that have been certified.  So I just wanted to point that out.

20             Now if Florida chooses to regulate pole access

21   issues, it must satisfy the certification requirements.  If the

22   state has not previously certified -- I can't turn this page

23   here -- its authority over rates, terms and conditions of pole

24   attachments and wishes to begin to assert that jurisdiction,

25   including jurisdiction over access to poles, pursuant to

FLORIDA PUBLIC SERVICE COMMISSION

97

1   Section 224 the state must certify its jurisdiction over

2   access.  The FCTA's proposed amendments, we believe, rectify

3   problems with the proposed rules because we have inserted what

4   we call a savings clause for the Section 224 rights.

5             Unless there are any questions now, I would defer to

6   Mr. Harrelson at this time.

7             MR. HARRELSON:  Thank you.  I have previously stated

8   that the relative effectiveness of storm preparedness

9   initiatives should be a major consideration in allocating

10   limited resources to mitigate the outages from hurricanes.  I

11   placed top priority on the initiative to inspect transmission

12   structures and substations and to fund remediation of the

13   defects that might be found.

14             In joint comments on August 26th by the IOUs, they

15   state, "The FCTA contends that it would be more effective to

16   devote additional resources to inspecting and maintaining

17   transmission poles and substations.  However, the IOUs'

18   experience has been that a relatively small portion of the

19   overall storm damage is to transmission lines and substations.

20   The IOUs believe that one of the principal reasons why the

21   transmission system has fared well in recent storm seasons is

22   that it is already built to extreme wind standards."

23             However, in the record as it's stated in FPSC Order

24   060351 in the case background, it was issued April 25 of '06,

25   it quotes, "Failures of various FPL transmission lines

FLORIDA PUBLIC SERVICE COMMISSION

98

1   during Hurricane Wilma caused at least 94 percent of

2   Florida Power & Light's Hurricane Wilma substation outages."

3   So if the power companies are correct, that it was a small

4   portion of the overall storm damage, then I still contend that

5   I'm correct that putting priority on inspecting and remediating

6   transmission lines can do the most good in reducing widespread

7   and frequently long-lasting power outages such as occurred in

8   Wilma during -- due to transmission line failures.

9             In other joint comments filed August 18th, the IOUs

10   criticized the definition of a pole, a distribution pole at

11   full capacity as a pole which can be rearranged -- I'm sorry --

12   as a pole that cannot be rearranged, strengthened or changed

13   out as necessary to accommodate a request for access.  But this

14   is exactly the definition which has been used as standard

15   industry practice for a make-ready on poles to allow cable TV

16   attachments.  The cable operators pay for those make-ready

17   changes typically.

18             The power companies use the exact same definition to

19   decide if a pole needs modifications or replacement to

20   accommodate power facilities.

21             There are limitations to where a taller pole can be

22   placed:  Sometimes under other lines, over other lines, in

23   dense trees, airport glide slopes.  There's a number of field

24   conditions that limit where poles can actually be replaced with

25   taller poles.

FLORIDA PUBLIC SERVICE COMMISSION

99

1             Now getting to the proposed rules, electric power

2   companies must have construction standards which specify

3   generally what materials and what configurations of materials

4   they would use on poles called construction units which they

5   will normally use to achieve the performance standards that's

6   contained in the National Electric Safety Code.  The National

7   Electric Safety Code is not a construction standard.  It's a

8   performance standard.  This is the 2007 code.  It was published

9   August 1st of '07.

10             The NESC clearly and completely states what is to be

11   accomplished for safety, but it doesn't tell how to accomplish

12   it.  The NESC covers both electric and communications lines and

13   work rules for electric and communications workers.  So

14   construction standards, though they're necessary, do not and

15   cannot contain all of the combinations of construction units

16   which are placed on and which are added to poles in practice.

17   Actual field conditions such as terrain, highways to cross,

18   other lines to cross over or under require customizing company

19   construction standards.  And construction standards must be

20   used in conjunction with the National Electric Safety Code to

21   assure that the initial construction and later on added

22   facilities still comply with the applicable version of the

23   National Electric Safety Code.

24             Florida Cable TV members do need access to power

25   company standards during their conducting of business.  The

FLORIDA PUBLIC SERVICE COMMISSION

100

1   Florida Cable Association tends to review power company --

2   intends to review power company construction standards which

3   might adversely affect use of poles for joint use, and we

4   intend to offer input accordingly whenever we have the

5   opportunity.  We do, by the way, endorse the collaborative

6   approach that has been proposed.  And I also agree with the

7   comments by Dr. Slavin which suggest not incorporating the

8   extreme wind standards for distribution poles.

9             I'm going to skip over the part recommending adoption

10   of the 2007 code.  It is in print and will be in effect

11   mandatory by next year.

12             In Paragraph 25-6.034(4)(b), the portion of the rule

13   states that electric facilities are grandfathered to previous

14   editions of the code, and the language there actually misstates

15   the code.  So we suggest that that be rewritten to accurately

16   state the code provision, but that it just plainly say that

17   facilities are subject to prior editions of the code as the

18   language in the code states, not just electric facility.

19   Because the code applies equally to electric and communications

20   lines.

21             Under Rule 25-6.0342, it requires each electric

22   utility to establish third-party attachment standards and

23   procedures.  We feel that attachment standards should have

24   flexibility for IOUs to require standards and clearances that

25   are greater than the NESC requirements, but on poles that have

FLORIDA PUBLIC SERVICE COMMISSION

101

1   adequate height and strength.  If a pole is tall enough and

2   large enough and the electric company desires greater

3   standards, it's good practice to require a greater standard on

4   that pole.  However, Part 2, we would urge that they accept

5   compliance with the NESC as a final criteria before requiring

6   that poles be changed out to taller or stronger poles.  Such

7   flexible attachment standards would allow for the efficient use

8   of available pole space for future attachments by the electric

9   company and communications companies.  If the pole space and

10   strength -- as the pole space and strength capacity is used up,

11   the pole would have to be replaced only when the safety

12   requirements of the NESC can no longer be met by that

13   particular pole.  This is a win-win approach to developing

14   attachment standards.  The attachment procedures associated

15   with those attachment standards must be reasonable and

16   nondiscriminatory.

17             I'd like to quickly just show some photographs that

18   perhaps show at least another view of some cable attachments to

19   some power poles.

20             The first pole is a photograph I took.  In fact, I

21   took all of these photographs in some previous work I was doing

22   in Florida.  This first photograph Number 1 shows a pole where

23   I actually saw the process of adding the electric facilities to

24   an existing pole.  The spacing requirements were violated of

25   the NESC, but it did not affect or overload the pole by any

FLORIDA PUBLIC SERVICE COMMISSION

102

1   means.  The guy wires going across the road make the pole

2   stronger, and the added equipment doesn't adversely affect the

3   strength rating.

4             Number 2, please.  This next pole is leaning, it's

5   unstable.  But the guying, if you can see the yellow guy marker

6   to the right of the pole, that's a very short guy.  But it's

7   the guy that goes to the top of the pole guying the power

8   attachments.  That guy wire and anchor is just simply not

9   holding that pole.  Once you correct those guy wire problems,

10   that pole could be straightened.  And it's a stable pole

11   because it has a support in four directions.  It would not blow

12   over by the wind if properly guyed.

13             Next.  This is a very tall pole.  It's a 50- or

14   55-foot pole, so it would have something greater than 45 feet

15   out of the ground if it's a 55.  It has two electric circuits

16   up top; one cable TV attachment and I think maybe a telephone

17   drop as well.  But it's a tall pole.  It has a lot of stuff on

18   it.  It's not overloaded.

19             This other pole shows another frequent violation of

20   the safety code.  The power line, the triplexed secondary

21   voltage line is not sagged anywhere close to the other power

22   lines and it's hanging down.  And as you might can see on the

23   left side of the photograph, the power cable sags down and

24   touches the cable TV.  It has nothing to do with the strength.

25   The line is surrounded by trees, and there's no strength

FLORIDA PUBLIC SERVICE COMMISSION

103

1   concerns about this pole.

2             Next.  This is a Class N grade of construction type

3   pole.  It has no high voltage line on it.  Dr. Slavin explained

4   very well that these are not covered by the strength

5   requirements of the code, and certainly they should not be

6   confused with any effort to build lines to greater than NESC

7   requirement strength.

8             Next.  This one is a relatively tall pole.  It has an

9   electric circuit on the top.  Then it has a different electric

10   circuit below that for service to the homes coming from another

11   power line on the other side of the street.  Next comes cable

12   TV and then some telephone drop wires.  This pole is a good

13   example of what I suggest:  Leave plenty of extra space on tall

14   poles.  If it's an existing pole and very tall, don't crowd the

15   power facilities with cable and telephone attachments.  Keep

16   them in their relative, useful height on the pole.

17             Next.  This one is another one that has two cables on

18   it, one telephone, one cable TV, one power circuit with a

19   transformer.  It's just a typical pole.  I don't see any

20   concern for extra strength and design on these type poles.

21   There are some issues about attachment regulations, and that's

22   something we really need to work together on.  Next.

23             This one fell through the cracks, so to speak.  It

24   had been there for a year or two when I took the photograph,

25   and I made two different visits five months apart.  It's a

FLORIDA PUBLIC SERVICE COMMISSION

104

1   replacement pole that I believe was set after Hurricane Ivan.

2   The other pole is yet to be transferred from the electric

3   facilities, and one or more of the communications cables has

4   been transferred.  But the tree, I believe, based on what it

5   looked like, part of that tree fell and broke the old pole.  It

6   didn't break it completely down.

7             Next.  This pole has had two different attachments

8   added in violation.  The first was the electric attachments

9   going to the right to serve a new customer violated some of the

10   separation requirements.  The next was an additional

11   communications cable, fiber optic cable was added in violation

12   of the separation rules, but there are no strength issues.  The

13   pole has lines going in four directions.  Unless a tree takes

14   down one of those lines going in one of those four directions,

15   the pole has no strength issues.

16             Next.  This one is even more impressive to me.  It

17   has two vertical electric circuits on it.  Disguised somewhat

18   in the trees below is two cables.  One was added new and in

19   violation of the application permitting and NESC requirements.

20             Next.  This one is a pole with two electric circuits

21   up top.  It had a cable TV.

22             Next, based on information I was given, the light was

23   added as a violation of the separation requirements of the NESC

24   code.  The next was a fiber optic cable added in further

25   violation of the separation requirements.  But I do not believe

FLORIDA PUBLIC SERVICE COMMISSION

105

1   this pole would have any strength problems.

2             Next.  This one is a relatively lightly loaded pole

3   up top with a single high voltage line, one transformer, some

4   service wires going in two different lateral directions, one

5   streetlight, and then it has several cable attachments below

6   that, but they actually strengthen this pole.  They go in four

7   separate directions, making the pole more stable.

8             Next.  This one is another Class N grade construction

9   pole in the foreground.  It has a common problem.  It's not

10   guyed to make it stable in the soft soil.  The electric line is

11   shown sagging dramatically and actually sagging below either

12   telephone or cable TV drop wire.  It needs some maintenance on

13   it.  There's no strength issues involved.  There are NESC

14   safety code violations with respect to the separation of

15   facilities in the span.

16             Next.  Another example of a common field problem, the

17   secondary voltage triplex cable from the transformer in the

18   foreground going to the pole in the background is not sagged up

19   with the other power cables and it's hanging down but not quite

20   touching the cable.  There should be 30 inches of separation

21   out in the span there to satisfy requirements of the code.  As

22   I have stated earlier, the work requirements of the electric

23   and communications workers are covered in the National Electric

24   Safety Code.  They're also covered in OSHA regulations.  But

25   workers can safely work around these type conditions, workers

FLORIDA PUBLIC SERVICE COMMISSION

106

1   who are properly trained and equipped and use safe work

2   practices.

3             And the final slide is a pole that I thought I'd put

4   in because based on my experience I'd do a wind loading

5   analysis on this one.  It has one electric circuit up top, a

6   secondary circuit with a floodlight on it, and then it has five

7   communications cables.  It's a relatively tall pole, so I would

8   not render an opinion as to whether this one meets the

9   requirements of the code until I saw some calculations on it.

10   Thank you.

11             CHAIRMAN EDGAR:  Thank you.  Questions for FCTA?

12   Commissioner Arriaga.

13             COMMISSIONER ARRIAGA:  Mr. Gross, I think I heard you

14   say, and please correct me if I'm wrong, that if we brought the

15   standards back for approval by the Commission, your concerns,

16   as Ms. Masterton just said before, your concerns regarding

17   potential subdelegation of authority would be taken care of?

18   Would you still have any concerns about that?

19             MR. GROSS:  We would not have concerns about it.  We

20   would like some greater degree of -- the input that's provided,

21   we'd put some language in there that would require notice and

22   an opportunity to participate to take into account our own

23   construction needs.  That would be ideal.  But something

24   perhaps in between that language that we've suggested and the

25   mere input; there might be some middle ground there.

FLORIDA PUBLIC SERVICE COMMISSION

107

1             But to answer your question directly, I think the

2   most important thing is whether we -- even if we agree on

3   something jointly with the power companies, I would still have

4   a concern about the Commission's delegation of authority if it

5   didn't review even an agreed upon set of standards and give

6   final approval of it.

7             COMMISSIONER ARRIAGA:  And I think I tend to agree

8   with you, and I have made these comments before to staff.  I

9   really want to make sure that this Commission preserves the

10   jurisdiction, the final authority, and it's not delegating

11   anything.  Because I want to remember something that

12   Commissioner Deason said, I think it was yesterday:  Whatever

13   we do here has to be done in such a way that neither the FCC

14   nor the courts will ridicule us, will turn us down.  So I'm

15   really, really concerned about that.  And I want to make sure

16   that we all, and the staff is listening, so that we all take

17   care of those issues of delegation that concern me.

18             But now -- may I continue, Madam Chair?

19             CHAIRMAN EDGAR:  Yes.

20             COMMISSIONER ARRIAGA:  The process of getting to

21   those standards, there is a proposal by the telephone companies

22   here that we need to probably discuss a little down the line.

23   I have to hear first from the IOUs and all that.  But I think I

24   heard you say that you have a long-standing, 20-year long

25   history of litigation with the power companies.  I'm just

FLORIDA PUBLIC SERVICE COMMISSION

108

1   wondering if we don't give you some kind of guideline, rule to

2   work by in order to get to some definition of the standards,

3   I'm wondering how you're going to be able to get to some kind

4   of agreement in an infrastructure, infrastructure advisory

5   committee, if that were ever to be approved.

6             MR. GROSS:  I am hopeful that we -- and we support

7   that.  We join with the ILECs in moving forward with that

8   proposal.  It certainly would avoid a lot of potential

9   litigation that might be very expensive and have a big

10   delaying, consequence of great delay if the parties could sit

11   down and work this out.  But I agree, we have to be realistic

12   about it.  But I think talking is always good.

13             COMMISSIONER ARRIAGA:  And we encourage that.

14             MR. GROSS:  Whether it's in a personal relationship

15   or between corporations.

16             COMMISSIONER ARRIAGA:  And we encourage that, and you

17   know that this Commission encourages that.

18             MR. GROSS:  Yes.

19             COMMISSIONER ARRIAGA:  What concerns me is that these

20   conversations are going to go on forever because of the

21   long-standing history of litigation and disagreement between

22   you, FCTA, and the power companies.

23             MR. SMITH:  Yes.

24             MR. GROSS:  I think, and correct me if I'm wrong down

25   the table here, that we've agreed on a 30-day limit.  Am I

FLORIDA PUBLIC SERVICE COMMISSION

109

1   correct in that?  Okay.  That we would only -- we would try for

2   30 days and that would be it.  And everything -- failing some

3   real substantial progress, then this proceeding would resume in

4   the natural course.

5             COMMISSIONER ARRIAGA:  And that brings me to the

6   question that Commissioner Deason asked before.  How is it that

7   this supposed committee is not a potential delegation of

8   authority by the Commission?

9             MR. GROSS:  Well, I would say that that's a good

10   question.

11             COMMISSIONER ARRIAGA:  That's Commissioner Deason's

12   question.

13             MR. GROSS:  Yes.  Commissioner Deason, very good

14   question.

15             COMMISSIONER ARRIAGA:  He's the one that makes the

16   good questions here.

17             MR. GROSS:  But I think that it would have to be

18   brought back to the Commission and there would have to be some

19   process by which the Commission assured itself that its

20   statutory mandate was, was carried out by that.  But whatever

21   the work product was.

22             COMMISSIONER ARRIAGA:  One last question.  Would you

23   agree then that if you were -- whether you meet in a committee

24   or meet because you agreed to talk and come to an

25   understanding, would you agree then that you need some guidance

FLORIDA PUBLIC SERVICE COMMISSION

110

1   from this Commission to work you through the process of

2   negotiation with your peers?

3             MR. GROSS:  I think that would be very helpful.

4             COMMISSIONER ARRIAGA:  Would you agree that the rules

5   we're proposing today, which are not final, would be a guidance

6   for you to negotiate?

7             MR. GROSS:  Well, I'm just going to speak for, for

8   my, for the FCTA right now.  I don't want to purport to speak

9   for the ILECs because I'm not sure if they would agree on this

10   or not.  They may very well agree with us.  But I think we

11   could work, the FCTA could work within the structure of these

12   existing rules, that we wouldn't have to just totally scrap the

13   rules.  Probably minor changes to the rules.

14             COMMISSIONER ARRIAGA:  And we're open to the changes,

15   open to discussion.

16             MR. GROSS:  Yes.  Could solve a lot of the problems

17   in our view, in the FCTA's view.

18             COMMISSIONER ARRIAGA:  Thanks.

19             MR. GROSS:  But we're -- I think what this proposal

20   is suggesting is not to promulgate the rules today necessarily,

21   but to allow some time for the parties to try to work through

22   this and bring something back.  And perhaps -- you know,

23   there's been some suggestion that rules might not even be

24   necessary.  But I think, speaking for the FCTA, that we would

25   be willing to work within the, the structure of these rules,

FLORIDA PUBLIC SERVICE COMMISSION

111

1   and I think we could solve at least our concerns using these

2   rules as the template.

3             COMMISSIONER ARRIAGA:  I'm really sorry.  He just

4   brought something up that really caught me off guard.  I didn't

5   hear anything said in this infrastructure hardening proposal

6   that you're not expecting us to do anything regarding with

7   these rules.  Besides my understanding of Regulatory Procedure

8   101 that I got yesterday from the Office of Public Counsel is

9   that we're going to do something today which is going to be

10   actually approved in a future Agenda Conference.  But I think

11   that we should be able to provide you with some kind of

12   guidance as to what is it you're going to negotiate.  Because

13   if not, we're going to find us 60 days from now or 30 days from

14   now, given the long-standing history of litigation, we're going

15   to find ourselves doing nothing 30 days, 60 days from now.

16   That's my concern.  I'm just wondering what kind of guidance

17   can we give you so that your negotiations are in good faith and

18   not a delegation of authority from us which you're questioning?

19   So what I'm suggesting is don't you need the rules as a

20   document by which you need to negotiate under?  Proposed rules,

21   not final approved rules.

22             MR. GROSS:  I think so.

23             COMMISSIONER ARRIAGA:  Thank you, sir.

24             MR. GROSS:  I think so, yes.

25             COMMISSIONER ARRIAGA:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

112

1             CHAIRMAN EDGAR:  Mr. Meza.

2             MR. MEZA:  If I may respond briefly --

3             COMMISSIONER ARRIAGA:  Okay.

4             MR. MEZA:  -- to you, sir.

5             COMMISSIONER ARRIAGA:  Okay.

6             CHAIRMAN EDGAR:  Is there a clarification in there,

7   Mr. Meza, that you would like to make an effort at?

8             MR. MEZA:  Yes.  I'd like to clarify for Mr. Gross if

9   his concern -- or if he has any concern about the DOAH

10   proceedings and the time periods associated with asking for a

11   DOAH hearing as it relates to the IAC in the process.

12             MR. GROSS:  We filed our DOAH proceeding merely to --

13   as a responsible legal act not to commit legal malpractice.  In

14   our judgment, we had a couple of time frames within which we

15   had some options as to when we could file that; ten days after

16   the close of the last public hearing or within 21 days of the

17   notice of publication.  And at that point in time -- and

18   there's more than one way to skin a cat, and this was just the

19   way we decided to go.  So we went ahead and filed that.  And

20   then the DOAH proceedings provide that if the agency, in this

21   case the Public Service Commission and the FCTA could agree, we

22   could hold that case in abeyance.  And the hearing -- the ALJ

23   granted us an abeyance, but requests a -- because we said we

24   wanted to conclude these public hearings first and see if we

25   either resolved the issues or at least narrowed them, and that

FLORIDA PUBLIC SERVICE COMMISSION

113

1   would be very productive and might even avoid the necessity of

2   a DOAH hearing completely.  So we got an order of abeyance, but

3   on September 19th we need to file jointly, the Commission and

4   the FCTA, the status of where we are on September 18th and when

5   we will be ready for a DOAH hearing.  We have to report that to

6   the ALJ.  I don't know.  Did that answer your question, Jim?

7             MR. MEZA:  Yes.  Thank you for the clarification.

8             MR. GROSS:  Okay.

9             CHAIRMAN EDGAR:  Okay.  Thank you, gentlemen.

10             Are there any questions from staff for FCTA?

11             MR. HARRIS:  We just have one question.

12   Mr. Harrelson, the photographs you provided, would it be

13   possible for you to provide the street locations where those

14   photographs were taken?  I believe our Division of Regulatory

15   Compliance might be interested in following up on some of

16   those.  So if you could get the addresses to me, I'll forward

17   that on.

18             MR. HARRELSON:  I do have that in my records.

19             MR. HARRIS:  Great.  If you could provide that to me

20   and I'll forward it.  I think our auditors might be very

21   interested.  Thank you.  I'm sorry, our safety engineers.

22             CHAIRMAN EDGAR:  Okay.  We have run over time a

23   little bit.  Mr. Adams, just as I'm trying to look at our

24   agenda for the rest of the day, you are the next presenter.

25   And can you give me just an estimate maybe of about how much

FLORIDA PUBLIC SERVICE COMMISSION

114

1   time?

2             MR. ADAMS:  No more than ten minutes.

3             CHAIRMAN EDGAR:  Okay.  Then why don't we go ahead

4   and have you come up, if that's all right with you.  And then

5   after the Time Warner presentation, we'll take a break for

6   lunch.

7             MR. ADAMS:  Thank you, Madam Chairman.  We appreciate

8   the opportunity to appear here today.  I am Gene Adams

9   representing Time Warner Telecom.  And with me today is also

10   Ms. Carolyn Marek, Vice-President of Governmental Affairs for

11   Time Warner Telecom.

12             We have participated in the rule development

13   workshops and appreciate the opportunity to appear here today

14   and also give some further comments and testimony.

15             Primarily, our costs, first and foremost, or our

16   concern is the cost of these rules.  We had previously provided

17   in the rule development workshops some of the estimates of

18   costs to Time Warner, and we had filed those under the

19   confidentiality protections that the Commission provides.  But

20   we would like to state today that if the rule is implemented,

21   and if all of the movement from back lot to front lot

22   implications were fully implemented, and if all of the

23   undergrounding contemplated by the rule were to take place,

24   Time Warner could, it could cost Time Warner up to $100 million

25   to move its facilities that are currently in place in Florida.

FLORIDA PUBLIC SERVICE COMMISSION

115

1             For a competitive telecommunications carrier that

2   would be an incredible burden, and one which we are not able to

3   recoup as the IOUs and others could recoup through either the

4   rate mechanisms, the storm recovery costs or some of the other

5   cost recovery mechanisms that the Commission has provided,

6   including the cost-in-aid-of-construction rule that you're also

7   reviewing here today.

8             Secondly, along with that cost concern, we believe

9   that the IOUs and others who are also competitors of ours in

10   the telecommunications business could set these standards.  And

11   this is part of the discussion you were just having with

12   Mr. Gross is the setting of the standard beyond the minimum

13   standard so as to exceed the standard could effectively

14   engineer us off the pole.  I believe, as Embarq has also

15   stated, there doesn't appear to be a limitation on what is, you

16   know, at a minimum or beyond a minimum could be and where that

17   could be.  And, accordingly, in our rule that we filed as

18   attached to our comments, we've also asked that you adopt the

19   2002 rule or the 2007 rule now as may be appropriate and not

20   use the words "at a minimum."  And while I know the Legislature

21   has granted you that authority, we believe that you should set

22   the standard as the rule.  Because to do otherwise, again,

23   invites every utility to set a different standard of X or X

24   plus 1 or X plus 2 or X plus 3, and having to comply with that

25   could be so financially burdensome that we're simply unable to

FLORIDA PUBLIC SERVICE COMMISSION

116

1   be competitive anymore.

2             Further, as those companies, again, get further into

3   the competitive process, whether it may be broadband by wire or

4   whatever, you know, they may be tempted to use it as a means

5   to, to ensure that there is no competition or that that

6   competition is literally driven out of business.  And I know no

7   one would set out to do that intentionally and I know everyone

8   starts out with the best of intentions, but you may just find

9   yourself in a position that you do that nonetheless.

10             Finally, you know, we believe that the Commission

11   should direct staff to work with all the parties.  This may be

12   the first time I'm ever going to say this, it may be the last

13   time I ever say this, but we certainly agree with what the

14   other telephone companies have said here today with regard to

15   participating in some further review processes through an

16   advisory committee.  We feel that might be productive in

17   allowing us to develop some standards, certainly develop some

18   underground processes or process rather for us to work together

19   on undergrounding trenching standards and other things that

20   might let us all share the burdens of this and yet at the same

21   time let us all contribute effectively to protecting the

22   public's telecommunications from storm damage.

23             So, again, we would urge you to adopt the rule

24   amendments that we have suggested which would strike the words

25   "at a minimum."  And also the PSC should and we believe must

FLORIDA PUBLIC SERVICE COMMISSION

117

1   review all of the plants for consistency and adopt a standard

2   so that in fact there is a consistency among all of the

3   utilities in implementing these safety construction standards.

4   And with that, I would have -- Ms. Marek could make any

5   comments, if she has any, to follow up on that.

6             MS. MAREK:  I actually don't have any additional

7   comments to add to that.  Thank you.

8             CHAIRMAN EDGAR:  Okay.  Thank you very much.

9   Commissioners, any questions for Time Warner?  No.  Any from

10   our staff?

11             MR. HARRIS:  No, ma'am.

12             CHAIRMAN EDGAR:  No.  Any from anybody else?  Seeing

13   none, thank you very much.

14             MR. ADAMS:  Thank you.

15             CHAIRMAN EDGAR:  Okay.  It is almost 1:00.  In just a

16   moment I think we will go on break for lunch.  I intend to

17   start back up at 2:00 by the clock on the wall.  We will begin

18   with hearing from the presentations from the representatives of

19   local government that are here with us today, and, Mr. Wright,

20   that will put you up as first.

21             Okay.  We are on a break until 2:00.

22             (Lunch recess.)

23             CHAIRMAN EDGAR:  When we left off, Mr. Wright, I

24   believe that it was your turn next, so we will begin with you.

25             MR. WRIGHT:  Thank you, Madam Chairman and

FLORIDA PUBLIC SERVICE COMMISSION

118

1   Commissioners.

2             It's my pleasure and privilege to be here today on

3   behalf of the Town of Palm Beach, Florida, and the Town of

4   Jupiter Island, Florida.  The Towns and I thank you very much

5   for the opportunity to address you.

6             The Towns have been active participants in these

7   proceedings since before they were docketed.  Both of us

8   participated in the Commission's first workshop on this subject

9   on January 23rd, and we have submitted written comments and

10   participated actively, as you know, at the workshops and agenda

11   conferences as the proceedings have gone along.

12             We, the Towns, are also participating in a

13   comprehensive study of the life-cycle cost-effectiveness of

14   underground and overhead electric distribution facilities

15   through a group of Florida municipalities who have formed the

16   Municipal Underground Utilities Consortium.

17             As an initial and overall comment, I want to the say

18   that the Towns commend the Commission and the staff for their

19   efforts and for the substance of the proposed rules which can

20   be expected to provide significant and meaningful improvements

21   in electric service reliability and provide concomitant

22   increases in total economic value to Floridians, as well as and

23   part of which are, reductions in electric utility operation and

24   maintenance costs.

25             Specifically, the towns support the provisions in

FLORIDA PUBLIC SERVICE COMMISSION

119

1   proposed Rule 25-6.034 that require utilities to establish

2   construction standards guided by the extreme wind criteria of

3   the National Electrical Safety Code.  The Towns support the

4   provisions in several of the proposed rule sections that

5   require that the cost of hardened overhead facilities,

6   facilities built to whatever new standards are adopted pursuant

7   to amended Rule 25-6.034 to be used in computing contributions

8   in aid of construction for underground service and for

9   overhead-to-underground conversion.

10             The Towns support the provisions that require

11   utilities to locate distribution facilities in rights-of-way

12   where local government applicants, such as the Towns, satisfy

13   the utility's legal, financial, and operational requirements.

14   The Towns support the provisions in proposed amended Rules

15   25-6.115 and 25-6.078 that require the inclusion in the CIAC

16   calculation of avoided utility operating and maintenance costs,

17   including vegetation management costs that are avoided by the

18   use of underground facilities, and more significantly, by

19   including the life-cycle expected value of avoided storm

20   restoration costs that are saved through the use of underground

21   facilities as opposed to overhead.

22             The Towns specifically support the proposed treatment

23   of corporate overhead costs in accordance with proposed Rule

24   25-6.115(11)(b).  These provisions are important to prevent

25   utilities from charging municipalities or other applicants,

FLORIDA PUBLIC SERVICE COMMISSION

120

1   potentially, for what I call corporate accounting overheads on

2   work that the utility does not do.

3             These corporate overheads can be significant.  In the

4   estimates that I have seen provided to the Town of Jupiter

5   Island and the Town of Palm Beach they are on the order of 20

6   percent of the total project costs.  We certainly agree that if

7   the utility does the work, then they are entitled to include

8   their corporate overheads in the costs.  However, where the

9   utility does not perform the underground installation work, and

10   I'm sure you know that pursuant to other provisions of

11   25-6.115, and pursuant to the utility tariffs, we are allowed

12   to do the work ourselves.  Where we do the work ourselves, we

13   should receive full credit for all costs that the utility would

14   otherwise charge.  Your proposed rules implement this, we are

15   grateful for that, we support it.

16             We support the proposed provisions in .064, .078, and

17   .115 that allow for consideration and inclusion in CIAC

18   calculations of additional benefits provided by underground

19   facilities beyond just those that can be directly captured in

20   utility accounting.  This is real important in light of what

21   appears to be widely accepted and, even to a more extreme

22   degree than I had thought before this morning, that it is

23   probably not possible to construct even hardened overhead

24   facilities to withstand the impact of stronger wind storms.  I

25   had been thinking that it was Cat 4 and Cat 5 storms that were

FLORIDA PUBLIC SERVICE COMMISSION

121

1   largely vulnerable to flying debris, but according to what

2   Dr. Slavin told us this morning, it seems like the wind speeds

3   at which flying debris becomes problematic for overhead

4   facilities are quite a bit less than that.

5             By comparison, except for the most extreme flooding

6   or storm surge conditions, underground facilities will

7   withstand Category 1, 2, 3, 4, 5 conditions, whatever it is,

8   even where super-hardened overhead facilities would not.  I can

9   state this really concisely, and this is what the rule

10   amendment goes to and it is very, very important.  If you can't

11   build an overhead system that is as reliable as an underground

12   system, then the Commission, we strongly believe, needs to give

13   appropriate recognition to the additional safety and

14   reliability benefits provided by the underground facilities and

15   the underground CIAC calculations.  And your proposed rule

16   amendments will at least enable the utilities and enable other

17   affected parties, like the Towns, to come before you and argue

18   for inclusion of those benefits.

19             The Towns do not want these rulemaking dockets slowed

20   down.  We don't want the Commission's adoption of these rules

21   delayed.  We want the rules implemented as soon as possible,

22   within normal rulemaking procedures, and we are looking forward

23   to filing our post-hearing comments, too.  We want the

24   implementing tariffs processed and put into effect as soon as

25   practical.  We want to get on with our desired

FLORIDA PUBLIC SERVICE COMMISSION

122

1   overhead-to-underground conversion projects with the CIACs

2   computed fairly and consistently with the principles

3   articulated in the Commission's proposed rules.

4             I do have a few more brief comments in response to

5   some of the comments and arguments advanced by the

6   telecommunications companies and the cable television

7   association earlier today.  I think there was a misstatement of

8   what causes prolonged outages probably due, as best I can

9   decipher it, to a misinterpretation of a statement in a related

10   Commission order.  It was suggested to you that it is, in fact,

11   substation outages that caused the prolonged outages associated

12   with Hurricane Wilma.

13             Now, I didn't have a chance since this morning to go

14   back and check the record from FPL's 2005 storm cost-recovery

15   docket that we processed earlier this year and in which, you

16   know, I represented the Florida Retail Federation.  But I did

17   verify my recollection in a side conversation with an FPL

18   employee earlier today, and I believe the following is

19   accurate:  That all of FPL's substations were back in service

20   no later than four days after Wilma passed through FPL's

21   territory.  And that as of five days after Wilma passed through

22   FPL's territory, there were still in excess of 2 million

23   customers' meters not in service, and that the last FPL

24   customers were not restored to service until 18 days

25   afterwards.

FLORIDA PUBLIC SERVICE COMMISSION

123

1             So I don't think the suggestion that it is substation

2   outages due to flying debris are responsible for prolonged

3   outages was accurate, and I wanted to correct that.  By all

4   means ask FPL when they come up if they have a different view

5   of things.

6             Regarding the jurisdictional and standards issues, I

7   think it's clear, and I agree with Mr. Gross on this, that the

8   PSC does have the jurisdiction to set safety standards.

9   Personally, I think it is equally clear that the Public Service

10   Commission has the authority to set standards for construction

11   related to reliability.  It appears to me, based on, you know,

12   the research I have done today, that the Federal Communications

13   Commission does, indeed, have the jurisdiction ultimately to

14   override a state's standards adopted for safety and reliability

15   purposes if its effect was to actually prevent attachments or

16   if it were facially unreasonable and unjust, or if it were

17   unjust -- and if the standards were unjust and unreasonable as

18   applied.

19             But the FCC said real clearly both in their initial

20   order on -- which one was it -- on local competition and in

21   their order on reconsideration, and I'm reading to you now from

22   the order on reconsideration the following:  "The Commission,"

23   the Federal Communications Commission in this instance, "will

24   presume state and local requirements affecting pole attachments

25   to be reasonable and are entitled to deference even if the

FLORIDA PUBLIC SERVICE COMMISSION

124

1   state has not sought to preempt federal regulations under

2   Section 224C."

3             Now, in the simplest terms, it seem to me that what

4   we are here about today is you all adopting standards for

5   construction for safety and reliability purposes.  It seems to

6   me an obvious and fairly easy way to look at it is that

7   everybody, whether it's the electric company, or the cable

8   company, or the other cable company, or the telephone company,

9   or whoever puts their facilities on the poles has to meet the

10   standards and the utility's facilities have to meet the safety

11   and reliability standards.

12             Back to the FCC for a second.  I will say, you know,

13   this would all be subject to litigation on a case-by-case,

14   state-by-state basis, hypothetically, but I'll tell you, I

15   cannot conceive, after the experience of the southeastern

16   United States in 2004 and 2005, that the Federal Communications

17   Commission would override standards adopted by Florida,

18   Louisiana, Mississippi, Alabama, Georgia, South Carolina,

19   Texas, or North Carolina, in response to the state commission's

20   legitimate concerns over reliability and safety following the

21   hurricanes that our region has experienced in these years.

22             Finally -- well, almost finally, with regard to the

23   question posed by Commissioner Arriaga regarding including in

24   the rule a specific provision providing for Commission review

25   and approval, I will offer you my thoughts.  I will say this.

FLORIDA PUBLIC SERVICE COMMISSION

125

1   I am inclined to agree with Mr. Harris' analysis that having a

2   point of entry, which I think is inherent in the APA and

3   inherent in the Commission's organic Chapter 366, satisfies and

4   obviates the nondelegation issue that has been raised.

5             However, I will offer you this.  If you look at

6   366.03, it says that each utility shall provide service upon

7   terms as required by the Commission.  A good argument can be

8   made that the pole attachment standards that the Commission is

9   ultimately requiring through the exercise of its jurisdiction

10   under Chapter 366 as amended this year, and through the rules

11   that we are here about today, are actually getting at

12   prescribing terms required by the condition, terms required by

13   the Commission.  And if you look at it that way, it argues, I

14   think, very strongly for what I understood Commissioner Arriaga

15   to be suggesting, and that is to go ahead and provide

16   explicitly in the rules for a point of entry.

17             Regardless how the legal nuances might play out, I

18   think -- personally, I would offer to you that I think the

19   safest course is simply to do that, provide specifically for a

20   filing of the utility's proposed standards, pursuant to your

21   rules, for Commission review and approval.  That way there is a

22   very clear point of entry.  There will be docket, it might --

23   hopefully in a lot of cases it will be a PAA, but it should be

24   a fairly easy process.

25             Also, I would say that the Towns do not object to the

FLORIDA PUBLIC SERVICE COMMISSION

126

1   Cable Television Association's suggested inclusion of an

2   explicit statement that the rules are not intended to conflict

3   with or impinge upon the FCC's jurisdiction.  Again, frankly I

4   think that goes without saying.  Jurisdiction is what it is,

5   and you couldn't by rule impinge on the FCC's jurisdiction

6   anyway, but saying it in black and white might make things a

7   little bit easier.

8             Again, we really appreciate the opportunity to have

9   participated to date in these proceedings and the opportunity

10   to present these comments to you today, and we look forward to

11   continuing to participate as we get this done, as we go through

12   the rulemaking process and the tariff implementation processes.

13   Thank you very much.

14             CHAIRMAN EDGAR:  Thank you, Mr. Wright.

15             Commissioners, any questions?

16             Commissioner Tew.

17             COMMISSIONER TEW:  Thank you, Mr. Wright.

18             I do have one question with respect to the IAC

19   proposal that I assume you have had a chance to look at now.

20             MR. WRIGHT:  I'm sorry, excuse me?  The which

21   proposal?

22             COMMISSIONER TEW:  The IAC proposal that was put

23   forth by BellSouth and some of the other ILECs and the cable

24   companies.  The proposal that BellSouth outlined in their

25   presentation.

FLORIDA PUBLIC SERVICE COMMISSION

127

1             CHAIRMAN EDGAR:  I think it's IAC that may be

2   throwing Mr. Wright.

3             MR. WRIGHT:  The proposal to have the joint

4   collaborative process on the front end?

5             COMMISSIONER TEW:  Yes.

6             MR. WRIGHT:  Okay, yes.  Conceptually, yes.  I mean,

7   I heard it this morning.

8             COMMISSIONER TEW:  Do you think that that may help us

9   achieve the intended results any sooner than if we end up in

10   litigation over the proposed rules as they are drafted now?

11             MR. WRIGHT:  Yes.  You know, it's always better if

12   the parties sit down and try to resolve their differences on

13   the front end.  And, you know, the way I would look at it is

14   given the 30-day time limit on the prefiling effort, my own

15   view is that the 30 days will be well spent.  In some cases it

16   might indeed obviate the need for contentious litigation.  And

17   on the other end of the spectrum worst-case you have lost 30

18   days and we can probably live with that.

19             COMMISSIONER TEW:  Thank you.

20             CHAIRMAN EDGAR:  Commissioner Carter.

21             COMMISSIONER CARTER:  Where is the front end?

22             MR. WRIGHT:  That's a good question.  The rule as

23   drafted would require the utility to make its filing in

24   compliance with -- excuse me, that's not quite true.  The rule

25   as drafted would require the utility to establish its own

FLORIDA PUBLIC SERVICE COMMISSION

128

1   standards within 180 days of the rules effective date.  I think

2   perhaps you could define the front end as a period of time that

3   ends 180 days after -- if you are going to adopt what I might

4   call the prefiling mediation/collaborative approach, you could

5   define the front end, I think, as that period of time ending

6   180 days after the effective date of the rule and back it up

7   from that.  The folks would have to get together sometime, I

8   would guess, in the window between 120 and 180 days after the

9   rule is adopted.

10             COMMISSIONER CARTER:  You wouldn't say the front end

11   is when this process begun, then?

12             MR. WRIGHT:  Well --

13             COMMISSIONER CARTER:  Because you said 30 days from

14   the front end.  The front end keeps moving, doesn't it?

15             MR. WRIGHT:  I think perhaps we are talking about

16   different front ends.  That is all I can really say.  I thought

17   we were talking about the front end being before the utility

18   actually adopted standards and not really the overall

19   rulemaking process.  I thought we were discussing and my answer

20   was addressed to the utility's adoption of standards as

21   required by whatever rules you all promulgate coming out of

22   these proceedings that we are already in.  I understood it to

23   mean the front end of the filing and review process for

24   approval of the utility standards.

25             COMMISSIONER CARTER:  Not front end as the beginning

FLORIDA PUBLIC SERVICE COMMISSION

129

1   of the process, which is really the front end, wouldn't you

2   agree?

3             MR. WRIGHT:  Yes, sir.  And that would -- it would

4   have been nice if this had been done before, but our front end

5   has been going on for literally years.

6             COMMISSIONER CARTER:  Thank you, Madam Chair.

7             CHAIRMAN EDGAR:  Thank you, Commissioner Carter.  And

8   just if I may for just a moment to follow up on, I think, that

9   line, to note as I'm sure we are all aware that this Commission

10   met and decided to proceed with this rulemaking docket in

11   February.  And since that time three staff level workshops have

12   been held that I certainly hope proceeded in a way that was

13   collaborative and allowed for discussion and an exchange of

14   ideas and for alternate language to be proposed.

15             Commissioner Deason.

16             COMMISSIONER DEASON:  Mr. Wright, I have to ask you

17   this question.  You are here on behalf of the Municipal

18   Underground Utility Consortium?

19             MR. WRIGHT:  No, sir, I am here on behalf of the Town

20   of Palm Beach and the Town of Jupiter Island, who are members

21   of the Municipal Underground Utilities Consortium.  I mentioned

22   that as background because the Municipal Underground Utilities

23   Consortium is funding a six-figure study, a comprehensive life

24   cycle cost study of overhead versus undergrounding.  I

25   mentioned that as background as to the Town of Palm Beach and

FLORIDA PUBLIC SERVICE COMMISSION

130

1   the Town of Jupiter Island.  I don't have a specific

2   representational relationship with the consortium, although I

3   do confer with them in our conference calls.

4             COMMISSIONER DEASON:  Does that consortium have an

5   acronym?

6             MR. WRIGHT:  We pronounce it MUUC, Commissioner

7   Deason.

8             COMMISSIONER DEASON:  Oh, okay.  I was just curious.

9   It seems like particularly in the campaign air that we are in

10   right now, every association or entity has a really nice, neat

11   acronym that the letters fit together.  Your letters don't do a

12   whole lot, do they?  I say yours, I know it is not yours.

13   MUUC, right?

14             CHAIRMAN EDGAR:  It's not M-U-D, so --

15             MR. WRIGHT:  Yes, sir.

16             CHAIRMAN EDGAR:  Commissioners, any further questions

17   for Mr. Wright?  And none from staff.  Anybody else?  I'm

18   seeing no sign.  Okay.

19             Mr. Wright, are you done?

20             MR. WRIGHT:  Yes, Madam Chairman.  Thank you.

21             CHAIRMAN EDGAR:  Okay.  Just checking.  Then next on

22   our list of presenters, Ms. Cox.

23             MS. COX:  Thank you, Madam Chair and members of the

24   Commission.  I'm here for the city of Fort Lauderdale, and I'm

25   here really just to ask a question, try to get a clarification

FLORIDA PUBLIC SERVICE COMMISSION

131

1   on a section of the Rule 25-6.115.

2             In reviewing the rule, the staff interpreted that

3   part of the rule to -- or they felt that it could be

4   interpreted that even though a group of residents of the city,

5   or the city of Fort Lauderdale were to pay for all of the costs

6   for undergrounding, that it would still be owned by the

7   investor-owned utility.  So, they are just trying to get a

8   clarification on whether or not this rule would preclude the

9   people who actually pay for the undergrounding from then owning

10   it.  And I don't know if this is an appropriate forum to get

11   that clarification or not.

12             CHAIRMAN EDGAR:  Mr. Harris.

13             MR. HARRIS:  I think Ms. Kummer can answer that

14   question.

15             CHAIRMAN EDGAR:  Ms. Kummer.

16             MR. HARRIS:  I could try, but she knows a lot more

17   than I do.

18             MS. KUMMER:  The tariffs typically say that even if a

19   customer pays for a distribution facility it does belong to the

20   utility.  And I believe, although I haven't done any research

21   on this, I believe the reason for this is because of grid

22   integrity.  The utility would be hesitant to be responsible for

23   maintaining something they did not own and that could have an

24   impact on the overhead grid.  It is language in all of the

25   tariffs, I believe, for all the IOUs.

FLORIDA PUBLIC SERVICE COMMISSION

132

1             CHAIRMAN EDGAR:  Mr. Breman.

2             MR. BREMAN:  I have some history with this rule.

3   There is also concerns with liability, owner becomes liable for

4   the assets.  And so the other part of the question is what

5   constitutes a utility.  So all of those factors are boiled into

6   the fact that you have one utility serving the area.  The rule

7   does not prohibit Fort Lauderdale from municipalizing and

8   becoming its own utility.

9             CHAIRMAN EDGAR:  Thank you.

10             Mr. Stewart.

11             MR. STEWART:  Thank you, Madam Chairman.  My name is

12   Greg Stewart, and I'm pleased to be here on behalf of the city

13   of North Miami.  I have some very brief comments that they have

14   asked me to make.

15             First of all, having heard Mr. Wright's presentation,

16   the city concurs with those comments that he has made and would

17   adopt those.  I think that generally speaking the city strongly

18   believes that we should move towards undergrounding, both

19   distribution and transmission lines.  We think that that is the

20   ultimate solution for reliability issues.  The city residents

21   have strongly stated their preference that they wish to kind of

22   move towards undergrounding of utility lines, and the city

23   government itself is attempting to move in that direction and

24   assist them as they can.

25             As to the specific rule itself, the city supports the

FLORIDA PUBLIC SERVICE COMMISSION

133

1   inclusion in CIAC of operation and maintenance and storm

2   restoration costs.  We believe that that makes installation of

3   underground lines and facilities less costly and therefore more

4   accessible.  We also support the requirement that the utilities

5   track both overhead maintenance costs and underground

6   maintenance costs.  We think that is a valuable tool for

7   planning purposes in the future.

8             We also support the language in 6.078 and 6.115 which

9   would allow utilities to waive undergrounding cost

10   differentials and to keep facilities in rate base where this

11   Commission finds that there are quantifiable benefits from

12   that.  We believe that that is a first and a positive step

13   towards eventually allocating reliability benefits and costs as

14   necessary.

15             Overall, we are supportive of the proposed rule

16   amendment, and we would ask you to adopt the same.  Thank you.

17             CHAIRMAN EDGAR:  Thank you, Mr. Stewart.  Any

18   questions?  No.  All right.  Thank you very much.  I appreciate

19   your participation.

20             We have tried to put our presentations and presenters

21   in an order by context, basically.  Are there any other

22   representatives from local governments who are here that I

23   didn't recognize earlier that would like to speak or make

24   comment?  Seeing none.  Okay.

25             Any other persons, other than the investor-owned

FLORIDA PUBLIC SERVICE COMMISSION

134

1   utilities, who would like to address the Commission on any of

2   these issues?  Okay.  Then we will move into our next industry

3   grouping.

4             Okay.  I think we are ready, and, Mr. Willis, you are

5   first on my list.

6             MR. WILLIS:  Thank you very much.  I'm Lee Willis, I

7   represent Tampa Electric, but we have coordinated a joint

8   presentation of the large investor-owned utilities in support

9   of the rules.

10             The rules that are before you today are the product

11   of extensive dialogue at three workshops where the language was

12   thoroughly reviewed and considered over time.  We want to

13   commend both your staff and the Commission for the way that

14   this proceeding has proceeded as rapidly as possible while

15   providing numerous opportunities for input from all parties.

16             We believe that this has resulted in a fair and

17   balanced group of proposed rules which should be adopted

18   without delay.  As we will discuss more thoroughly in our

19   presentation, we believe that you should reject further changes

20   in these rules and reject suggestions of additional delay.

21             This proceeding and the other proceedings that have

22   come about before the Commission are a result of the increased

23   hurricane activity in the 2004 and 2005 time frame.  As a

24   consequence, this Commission and the electric utilities have

25   undertaken a comprehensive review of ways that the critical

FLORIDA PUBLIC SERVICE COMMISSION

135

1   infrastructure of the statewide coordinated grid could be

2   improved to withstand severe weather conditions.

3             You have adopted a multi-pronged approach.  In

4   January you had an extensive workshop.  It was followed pretty

5   quickly thereafter with your pole inspection docket and order

6   that was issued on February the 27th.  You followed up again

7   with your storm plan order and with this rulemaking.  So you

8   have a multiple approach to the issues that are before you.

9             I would say that in each of the venues you have

10   considered various factors which could cause a pole to fail and

11   considered ways to avoid those failures.  And pole attachments

12   have emerged as a very significant concern expressed by this

13   Commission at every phase of your review of critical

14   infrastructure.  For example, in your February 27th pole

15   inspection order, you found that nonelectric attachments impose

16   additional strength requirements and that many attachments

17   occur well after the date of installation.  You observed that

18   the National Electric Safety Code requires a pole must be

19   strong enough to support the facilities attached to the pole at

20   all times, and that third parties have completed pole

21   attachments to electric investor-owned utility wood poles that

22   were done without full consideration of the requirement of the

23   National Electric Safety Code.

24             Wood pole strength inspections require remaining

25   strength assessments as well as pole loading assessments.  That

FLORIDA PUBLIC SERVICE COMMISSION

136

1   was in your order, as well.  In your storm plan order you came

2   up with ten initiatives for the companies to review.  Among

3   those was an audit of joint use attachment agreements.  You

4   required that we look at the location of each pole and the type

5   of ownership and the facilities attached to it and the age of

6   the pole and the attachments to verify that the attachments

7   were made pursuant to a current joint use agreement, and that

8   stress calculations shall be made to ensure that each joint use

9   pole is not overloaded or approaching overloading for instances

10   not already addressed in the pole attachment order.

11             Now, your basic theme in all of this is that nothing

12   should be attached to the pole that is not engineered to be

13   there in advance.  And we will have additional presentation in

14   a few minutes which underlines your finding and concerns that

15   pole attachments can have significant wind loading and stress

16   effects on a pole and can cause overloading, and that some

17   attachments are being made without prior notice or prior

18   engineering, and that steps should be taken to assess pole

19   attachment effects on individual poles to prevent overloading.

20             The proposed Rule 25-6.0342, was in recognition of

21   this theme and the very serious situation that the Commission

22   finds exists with respect to pole attachments.  You have come

23   up with a rule which we believe is fairly balanced and is the

24   product, as we have indicated, of extensive discussions and

25   workshops and post-hearing comments, and we feel that it's fair

FLORIDA PUBLIC SERVICE COMMISSION

137

1   and balanced.

2             We now have a presentation by Eric Langley and

3   Natalie Smith with respect to the various legal issues which

4   have been discussed.

5             MR. LANGLEY:  Good afternoon.  I'm Eric Langley.

6             I appreciate the opportunity to talk to you today

7   about two main issues.  The first is the jurisdiction issue and

8   the interplay between this Commission and the Federal

9   Communications Commission.

10             The second issue is more of a responsive issue, and

11   that is addressing a point that BellSouth raised earlier today

12   suggesting that these rules would unlawfully impair their

13   existing contracts with utilities.

14             On this first point, the jurisdictional point, it's

15   important to keep the issues in the proper boxes.  Because for

16   the attachers to come in and say you can't do this because the

17   FCC regulates pole attachments is nowhere near the full story.

18   You have issues of rates, terms, and conditions in one box, and

19   then you have issues of access, safety, reliability, and

20   engineering in another box.

21             The issues of access, safety, reliability, and

22   engineering have always been presumed to be regulated by the

23   states and have never required certification from the Public

24   Service Commission or from any other agency of the state.  That

25   is because a state knows best what standards should apply.  But

FLORIDA PUBLIC SERVICE COMMISSION

138

1   looking at this on a more practical level, the arguments that

2   the attachers are making saying, well, the FCC really has

3   jurisdiction over this, it would completely, completely

4   eviscerate this Commission's safety and reliability

5   jurisdiction.  All you have to do is look at a pole and see the

6   percentage of usable space actually occupied by third-party

7   attachers on that pole to know that you have to have

8   jurisdiction over that.

9             Because, otherwise, you would be trying to exercise

10   safety and reliability jurisdiction, which everyone in the room

11   concedes you have, but then there is this portion of the pole

12   that you can't touch and that just can't be the case from a

13   practical point of view and the law supports that.

14             A point that Mr. Wright made just a minute ago and

15   that I think some of the ILECs touched on this morning is that

16   the FCC has rendered decisions and rulemakings where they are

17   taking up engineering issues.  Well, don't be confused with

18   that somehow pushing the state commission out of this field,

19   because that is a completely different issue.

20             The FCC looking at an engineering standard, whether

21   it is one of the utility-specific standards or whether it is a

22   standard from a state or local regulator is different than the

23   issue of whether the Commission has the authority to enact

24   those in the first instance, and so those issues have got to be

25   separated.

FLORIDA PUBLIC SERVICE COMMISSION

139

1             A few times today we have heard references to the

2   Teleprompter versus Hawkins case, it's a Florida Supreme Court

3   case from, I believe, 1980, and it is true that in that case

4   the Florida Supreme Court said that the Commission had

5   unlawfully certified its jurisdiction over rates, terms, and

6   conditions of pole attachment.  But this is where we go back to

7   those boxes that I was mentioning just a couple of minutes ago.

8   You have these issues of rates, terms, and conditions, but then

9   you have these other issues of access, safety, reliability, and

10   engineering.  And I'm not the one placing them in those boxes.

11   Congress, the U.S. Congress put them in those boxes.

12             When the statute -- when the Pole Attachment Act, as

13   it's called, originally was enacted back in 1978, there was

14   nothing in there that required a utility to grant access.  And

15   so the provisions in Subsection F that except out the mandatory

16   access where there is insufficient capacity or for reasons of

17   safety, reliability, or generally applicable engineering

18   purposes, just it wasn't there.  Because you didn't have to

19   have that exception when the mandatory access rule was not

20   there.  So that's what the statute looked like in 1978, and

21   that was the context in which the Florida Supreme Court said

22   that the Commission had gone beyond its authority in certifying

23   jurisdiction over rates, terms, and conditions.

24             The bottom line there is that Hawkins, the

25   Teleprompter v. Hawkins case in no way requires that this issue

FLORIDA PUBLIC SERVICE COMMISSION

140

1   be certified before the state can regulate safety and

2   reliability, because safety and reliability were simply not

3   issues in Teleprompter v. Hawkins.  But more importantly, the

4   statute, the federal Pole Attachment Act does not require

5   certification of the access, safety, reliability, and

6   engineering issues.

7             The next issue that I wanted to address was the point

8   raised by BellSouth this morning.  But before I move to that

9   issue, did you all want to ask questions about the

10   jurisdictional issues?

11             CHAIRMAN EDGAR:  I think we're ready to move along.

12             MR. LANGLEY:  Okay.  BellSouth had suggested that

13   these third-party attachment rules, and in particular some of

14   the cost allocation rules, would unlawfully interfere with

15   their contracts.  Well, everybody in here knows that utilities,

16   particularly investor-owned utilities, are highly regulated

17   entities.  And one of the things that the courts look to when

18   addressing questions of impairment of contracts, i.e., whether

19   a state legislative action somehow affects those contracts and

20   whether that is an unlawful affect on those contracts, they

21   look to whether the entity is regulated.  And here utilities

22   are heavily regulated.  And the cases are replete with

23   references to this line of analysis.

24             And so for BellSouth to suggest, or for anyone to

25   suggest that these rules somehow are unlawful because they

FLORIDA PUBLIC SERVICE COMMISSION

141

1   impair contracts neglects the threshold question which is are

2   we dealing with a heavily regulated industry.  The answer to

3   which is undoubtedly, yes.

4             And that concludes my portion, unless you all have

5   questions, which I will be very happy to answer.

6             CHAIRMAN EDGAR:  Thank you, Mr. Langley.

7             MS. SMITH:  Good afternoon, Madam Chairman and

8   Commissioners.  My name is Natalie Smith of the Florida Power

9   and Light Company Law Department in Juno Beach, and I thank you

10   for this opportunity to comment on the proposed rules.

11             I will respond to three points raised by the

12   third-party attachers.  First, contrary to their assertions,

13   the Commission's proposed rules do not unlawfully delegate the

14   Commission's regulatory authority to electric utilities.

15   Second, regulation is not a reason to shift costs to electric

16   utilities and their customers.  Third, the Commission has ample

17   evidentiary support for its proposed rules related to

18   third-party attachments.

19             On the first point, contrary to the assertions of the

20   third-party attachers, the proposed rules do not affect an

21   unlawful delegation of Commission regulatory authority to the

22   utilities.  Instead, the proposed amendments to Rule 25-6.034

23   and proposed new Rule 25-6.0342, simply direct utilities to

24   adopt construction and attachment standards that meet clearly

25   articulated safety and reliability criteria.  The Commission

FLORIDA PUBLIC SERVICE COMMISSION

142

1   retains authority to resolve disputes as to whether the

2   criteria are met.

3             As discussed in detail in our written comments,

4   Florida case law is clear that no unlawful subdelegation occurs

5   where the fundamental policy decisions are made by the

6   regulatory authority, and that is the case here.  I know

7   Mr. Breman earlier outlined the standards in the rules.

8             The Commission retains power to decide whether the

9   construction and attachment standards established by electric

10   utilities satisfy the rule and statutory-based parameters for

11   construction and attachment standards.  The Commission makes,

12   one, the fundamental policy decision as to the guidelines that

13   the standards must meet; two, retains discretion to determine

14   whether the utility's construction and attachment standards

15   comply with the proposed rules; and, three, the Commission will

16   resolve complaints regarding the rules' implementation.

17             Because the proposed rules would not delegate

18   regulatory authority to electric utilities, there is no merit

19   to an argument that the proposed amendments and proposed rules

20   are an unlawful delegation of authority.  It is consistent with

21   Commission practice for the Commission to rely upon the

22   principle of management by exception whereby the Commission

23   resolves complaints of any interested party who believes that a

24   particular utility has acted unreasonably in defining and

25   adopting a particular construction or attachment standard.

FLORIDA PUBLIC SERVICE COMMISSION

143

1   Indeed, the IOUs are not aware of another instance where the

2   Commission has preapproved any type of construction standards

3   as opposed to providing guidelines and enforcement mechanisms.

4             The Commission has often stated that its rule is to

5   regulate utilities through continuing oversight as opposed to

6   micromanaging day-to-day utility operations and

7   decision-making.  Here, in charging the utilities with the

8   development of construction and attachment standards, the

9   Commission has recognized that the development of those

10   standards requires expertise and flexibility of the utility to

11   deal with complex and fluid conditions.

12             The utilities are the entities that must design,

13   construct, and maintain their systems, not the Commission or

14   the third-party attachers.  Consequently, the Commission's

15   rules of necessity must be a general statement of Commission

16   policy with the specific implementation left to each utility

17   based on the particular facts and circumstances that each

18   utility faces.

19             I have heard the discussion today about the

20   submission of standards for Commission approval.  While we

21   believe that the proposed rules, as drafted, satisfy the

22   Administrative Procedure Act and do not unlawfully subdelegate

23   authority, we will agree to the concept of submitting standards

24   for approval to the Commission and we will address the

25   specifics of this in our post-hearing comments.

FLORIDA PUBLIC SERVICE COMMISSION

144

1             Turning to my second point, regulation is not a

2   reason to shift costs to electric utilities and their

3   customers.  By ensuring that all attachments meet the required

4   standards, the proposed rules will help ensure the pole owners,

5   third-party attachers, and their customers will experience

6   improved reliability.  The appreciable benefits of the proposed

7   rules, benefits to all electric customers as well as the

8   attaching entities and their customers, do not come without a

9   cost.

10             The attaching entities have presented no valid reason

11   why they should enjoy the benefits of the proposed rules

12   without sharing in the costs that are necessary to achieve

13   those benefits, and there is no reason.  Nonetheless, the

14   third-party attachers assert that the cost of implementing the

15   proposed rules should be shifted to the electric utilities and

16   their customers because the electric utilities are rate of

17   return regulated.  This argument must be rejected.

18             Price cap regulation is not a reason to shift costs.

19   The rules and standards will apply to all attachers in a fair

20   and nondiscriminatory manner.  Increased costs to attaching

21   entities will not be any greater than to any other user of the

22   poles.

23             Finally, turning to the third point that I will

24   address, the Commission has ample evidentiary support for its

25   proposed rules.  The third-party attachers argue that there is

FLORIDA PUBLIC SERVICE COMMISSION

145

1   no factual basis for the proposed rules.  This is incorrect.

2   The Commission has reasonably determined that nothing should be

3   attached to a pole that is not engineered to be there in

4   advance.  It reached this conclusion after finding that pole

5   attachments can have significant wind-loading and stress affect

6   on a pole and can cause overloading, and that some attachments

7   are made without notice or prior engineering.  The Commission

8   consequently concluded that steps should be taken to assess the

9   pole attachment effect on poles and to prevent overloading.

10             The IOUs agree that the wind-loading effect of

11   third-party pole attachments creates stress on utility poles,

12   contributing as much as 40 percent of the overall wind-loading

13   of a typical pole line.  The addition of attachments may force

14   a design to use larger and more expensive poles or to use

15   shorter spans, increasing the total number of poles on a line,

16   therefore affecting the overall cost.  The stress effect of

17   third-party attachments is addressed in greater detail in our

18   written comments filed August 18th, and the IOUs filed

19   affidavits in support of this effect.

20             Thank you.

21             MR. WILLIS:  We will next have a presentation by

22   Kris Angiulli.  Kris is the Manager for Construction Services

23   for Tampa Electric, and her duties include the management of

24   third-party attachments.

25             MS. ANGIULLI:  Good afternoon.  I appreciate the

FLORIDA PUBLIC SERVICE COMMISSION

146

1   opportunity to be able to speak before you this afternoon.  I

2   believe I've got a presentation that's coming up on PowerPoint,

3   and I do not have handouts for you today.

4             I'd like to discuss some of the photos of cable

5   attachments to Tampa Electric poles which we filed with our

6   comments.  These photos demonstrate the various sizes of cable

7   attachments and their effects on our poles.  In this first

8   picture, the problem with this pole is that the midsection of

9   the pole -- I don't think my pointer is working.  I'll do

10   without it.  The midsection of the pole is literally being

11   pulled apart by the cable attachments that you see right around

12   the midsection there.

13             Next slide, please.  In this photo you can see the

14   solution to the problem.  Our engineering staff determined that

15   a spun concrete pole was required to replace the previous pole.

16   Had we been given proper notice, we could have replaced the

17   pole before it began to fail.

18             Next slide, please.  Document 6, up on the screen,

19   addresses an array of five different cables which are

20   significantly larger in size than our service cable.  This is

21   the array here of the five cable attachments.  And although you

22   can't really see it up there, this is the service cable, the

23   electric service cable.

24             Next slide, please.  This picture here is indicative

25   of the significant sagging that the communications cables can

FLORIDA PUBLIC SERVICE COMMISSION

147

1   have on our poles.  I had the privilege of going out and

2   viewing this particular installation.  And in the midsection of

3   the pole, which you can't very easily see in here, the bottom

4   cable attachment was about the size of my leg.

5             Next slide, please.  This is another example of a

6   long span.  Again, I had the opportunity to go out and view

7   this installation, and right around the midsection here of this

8   span, the bottom cable I was almost able to reach with my hand.

9             MR. HARRIS:  Excuse me for a second.  I don't want to

10   interrupt.  These are the pictures that were prefiled by TECO,

11   correct?

12             MR. WILLIS:  They are, yes.

13             MR. HARRIS:  Commissioners, these are in your binder

14   under Tab 13.  I noticed some of you are looking at your

15   screens.  There are hard copies in your binders.

16             CHAIRMAN EDGAR:  Thank you, Mr. Harris.

17             MS. ANGIULLI:  Thank you.  I'll proceed.  Next slide,

18   please.

19             This is an example of at least six or seven

20   overlashed cables.  I would like you to notice the size of the

21   bundle of cables relative to the side of the electric service

22   cable up at the top.

23             Next slide, please.  In this photo, I'd like to draw

24   your attention to, again, another long span where the cable

25   attachment is sagging rather low, and you'll notice the

FLORIDA PUBLIC SERVICE COMMISSION

148

1   proximity of the cable relative to the vehicles and also

2   relative to the entrance of the building.

3             Next slide, please.  In this photo, I'd like to draw

4   your attention to the size of this electric cable as it

5   compares to the streetlight bracket.  The streetlight bracket

6   is approximately two inches in diameter, and then I'd like you

7   to consider that streetlight bracket and its size compared to

8   the cable attachments here which are anywhere from four to six

9   inches in diameter.

10             Next slide, please.  And this brings me back to our

11   example of overlashing.  And at this time I'd like to present

12   you with a physical example which will be handed to you

13   momentarily.  And as you are passing that around, I would like

14   to just continue with my discussion on overlashing.

15             Overlashing is the bundling of cables together with

16   wire around other cable.  Usually this begins with lashing just

17   two cables together, but typically third-party pole attachers

18   continue to add cables as their systems grow in an area.  Tampa

19   Electric has seen as many as seven cable attachments lashed

20   together in a bundle.  What starts out as a single cable may

21   end up to be a bundle of cables about the size of a human leg.

22             Each overlashing adds additional wind-loading and

23   stress effects on the pole.  Cable companies typically don't

24   give notice because they contend that notice is not necessary

25   and not required, because the pole attachment rental rate is

FLORIDA PUBLIC SERVICE COMMISSION

149

1   the same for a single pole attachment as it is for a

2   seven-cable bundle attachment.  This practice ignores the

3   considerable additional wind-load and stress effects that the

4   larger poles can have on our poles -- excuse me, the larger

5   cable can have on our poles.

6             During the initial installation of third-party

7   cables, supporting guys and anchors are required to hold the

8   weight of the cable and structural stress.  As additional

9   cables are overlashed without notice, guys and anchors are not

10   changed out to ones that are strong enough to hold that

11   additional weight.  As discussed in my first photo, Tampa

12   Electric has experienced instances where an unnoticed

13   overlashed attachment has pulled the midsection out of the pole

14   causing that pole to fail.

15             Now, with respect to unnoticed attachments, I'd like

16   to mention that notification of attachments by third-parties

17   is, at best, inconsistent, sporadic, and incomplete.  Tampa

18   Electric has also experienced attachments by third parties who

19   don't even have pole attachment agreements with our company.

20             Overlashings are not typically noticed at all.

21   During Tampa Electric's last pole attachment count in the

22   field, over 21,000 unreported phone attachments were discovered

23   and over 26,000 unreported cable television attachments were

24   discovered.

25             Despite contractual and other written agreements with

FLORIDA PUBLIC SERVICE COMMISSION

150

1   third-party attachers which require advanced authorization of

2   new pole attachments prior to installation, unauthorized and

3   unreported attachments continue to be a problem.  These

4   incidences are not isolated and occur all over Tampa Electric's

5   service territory.

6             And so, in conclusion, I'd like to just ask you, as

7   you begin to become more aware of what we are discussing here

8   in these proceedings, that perhaps as you leave to go home

9   today that you start to look at the poles around here in your

10   territory.  And I believe that you will find that they are very

11   familiar to the pictures that I have shown you here today.

12             And this concludes my presentation.  Thank you.

13             MR. WILLIS:  I would like to now discuss some of the

14   proposed revisions of two of the rules, and then I'll be

15   followed by some comments by John Butler with respect to the

16   balance of the rules.

17             The attachers propose revisions to Rules 25-6.0341,

18   which deals with the location of facilities, should be

19   rejected.  You have found and we believe that it is the case

20   that this rule is needed to facilitate the location of

21   distribution facilities in readily accessible locations, but

22   you put very important language in this rule which says to the

23   extent reasonably practical and cost-effective in order to

24   reduce outage times and restoration costs resulting from

25   extreme weather.

FLORIDA PUBLIC SERVICE COMMISSION

151

1             Now, the various entities have suggested that we must

2   provide a mandatory notice of this activity, and I think one

3   company suggested that that notice should be as much as twelve

4   months.  We feel that that is unworkable and ineffective and

5   that your rule reasonably provides that the utility will seek

6   input, and to the extent practical, coordinate with the others.

7   We believe that this strikes a balance and that mandating, for

8   example, a 12-month advanced notice would just induce gridlock

9   and inaction.  The utilities need flexibility to respond to

10   customer's needs, and we will, of course, continue to seek

11   input and coordinate with the others to the extent practicable.

12             There have been cost calculations that were presented

13   to you which we feel are very much overstated and unreliable.

14   We discussed that in more detail in our filed comments.  And

15   limiting this rule to new construction should also be rejected.

16   We feel that this would undermine one of the primary objectives

17   of the rule, which is enhancing the reliability of existing

18   infrastructure.

19             The attachers have also proposed revisions to the

20   Rule 25-6.0342.  And we believe that those should be rejected,

21   as well.  One of the things that they have asked you to do is

22   to not allow any standard which exceeds the National Electric

23   Safety Code.  We feel that the rule, as written, is appropriate

24   and is consistent with Chapter 366 and the amendments to 366.05

25   that were enacted by the Legislature in 2006, and that it is

FLORIDA PUBLIC SERVICE COMMISSION

152

1   appropriate and consistent to exceed the NESC in certain

2   instances.  In fact, you will find that utilities exceed those

3   standards in many instances now, and that such a proposal would

4   be a step backward and would degradate the system, which is

5   exactly the opposite of what you are trying to do here.

6             We also believe that the suggestions that the

7   standards be adopted by mutual agreement or by a collaborative

8   process is unnecessary and unworkable and inappropriate.  Such

9   a change in the rule would allow third parties to effectively

10   stall the process of finalization of the standards.  And we

11   believe that the rules as written now provide a fair balance

12   and full due process, and we urge that the rule as written be

13   adopted.

14             We will follow now with John Butler's comments on the

15   balance of the rules.

16             MR. BUTLER:  Good afternoon, Commissioners.  I'm John

17   Butler with FPL.

18             On August 21, FPL, Gulf Power, and TECO filed joint

19   reply comments supporting the Commission's proposed Rules

20   25-6.034, .064, .078, and .115.  Now, I will note that these

21   comments are found at Tab 15 of Exhibit 1 that staff handed out

22   at the beginning of the hearing.

23             Let me summarize the comments, hopefully somewhat

24   briefly, and then I'll be happy to respond to questions that

25   the Commissioners may have.  Let me start with some

FLORIDA PUBLIC SERVICE COMMISSION

153

1   perspective.  We want to emphasize the importance of prompt and

2   decisive action to harden Florida's electric distribution

3   system.  I'm sure there are details in the proposed rules that

4   could be debated, but only at a considerable cost of lost time

5   and opportunity.  The old adage that the perfect is the enemy

6   of the good certainly applies here.  The proposed rules are a

7   good example of the Commission's prompt action to address the

8   need for storm hardening, and we hope that they can now be

9   finalized without further delay.

10             Turning to the proposed rules themselves, I would

11   like to address Rule 25-6.034 first.  We believe that it

12   properly promotes hardening electric distribution systems while

13   preserving to individual utilities the flexibility to implement

14   hardening in the most cost-effective and appropriate form for

15   their individual systems.

16             Several of the attachers have criticized the

17   requirement in proposed Rule 25-6.0345 for hardening

18   distribution facilities to NESC extreme wind-loading standards.

19   In our view, the attachers have overlooked the fact that

20   proposed Rule 6.0345 only applies to the extent reasonably

21   practicable, feasible, and cost-effective.  In essence, the

22   attachers question whether applying NESC extreme wind standards

23   is realistic and cost-justified, but the proposed rule already

24   says that the NESC extreme wind standards don't have to applied

25   if it's not reasonably practical, feasible, and cost-effective

FLORIDA PUBLIC SERVICE COMMISSION

154

1   to do so.  In other words, the proposed rule has already

2   anticipated and addressed most of the attachers' criticisms.

3             In any event, the attachers' complaints about using

4   extreme wind-loading standards aren't valid.  The FCTA asserts

5   that hardening distribution facilities to extreme wind

6   standards isn't the most active means of reducing storm impacts

7   and that utilities should, instead, concentrate on inspecting

8   and maintaining transmission poles and substations.

9             This doesn't square with our experience.  Only a

10   relatively small portion of overall storm damage has been to

11   transmission lines and substations.  This is probably due, in

12   large part, to the fact that transmission systems are already

13   built to extreme wind standards.  In turn, this suggests that

14   hardening distribution facilities to extreme winds standards on

15   a targeted basis would also be beneficial.

16             Let me comment a moment on some remarks that were

17   made by Mr. Harrelson earlier, and I can speak at this point

18   specifically with respect to FPL's experience in Hurricane

19   Wilma, but I think some of that is what he was referring to, as

20   well.  FPL had 240 substations that were without power

21   following Hurricane Wilma.  Only eight of those were due to any

22   actual hurricane damage to the substations.  The remaining 232

23   were because the transmission lines had become depowered or

24   deenergized.  For the most part, the overwhelming majority of

25   those instances was simply matters of trips on the transmission

FLORIDA PUBLIC SERVICE COMMISSION

155

1   lines such that once the lines were inspected and it was

2   determined that there was no physical damage to the facilities,

3   the lines were reenergized without further repair or delay.

4             The only real significant portion of structures that

5   had a failure problem were the Conservation Corbett Line, and I

6   imagine you all remember what happened with that.  If you

7   don't, I'll be happy to remind you.

8             The other point that I want to make is that

9   transmission lines and substations as a group were restored

10   very promptly to service.  In almost all cases, that was before

11   the distribution system that they serve was itself restored to

12   the point that power could be reenergized to those distribution

13   facilities.  So the notion that the great majority, at least

14   for FPL, at least in Hurricane Wilma, that the great majority

15   of damage has this connection to transmission facilities and

16   substations just doesn't work.

17             In fact, you know, the reason that customers were out

18   of service for extended periods of time was the damage to and

19   the need for, maybe you'll remember Geisha Williams'

20   expression, hand-to-hand combat of going in and actually

21   repairing neighborhood-by-neighborhood the distribution systems

22   in the neighborhoods that they served.

23             The FCTA also recommends that utilities focus on

24   increased pole inspection and vegetation management rather than

25   on hardening distribution facilities to extreme wind standards.

FLORIDA PUBLIC SERVICE COMMISSION

156

1   But this is a false dichotomy.  In reality, both can be

2   important.  The Commission has already directed utilities to

3   adopt aggressive pole inspection and vegetation management

4   programs.  These programs are likely to result in fewer poles

5   failing due to deterioration and falling trees, but that

6   doesn't address the issue of wind-only pole failures where

7   applying extreme wind standards on a targeted basis should be

8   helpful.

9             I would also like to point out that even with respect

10   to the falling trees, the debris, that sort of thing that

11   Dr. Slavin had referred to earlier, it is both counterintuitive

12   and, I am assured by people who know the engineering better

13   than I, incorrect to assume that once you start having some

14   debris flying around or some tree limbs flying around, it

15   doesn't matter how strong the poles are.  It does.  A stronger

16   pole not only will withstand wind better, but it also has

17   considerable opportunity to withstand at least moderate levels

18   of impact from debris or trees without failing.

19             Dr. Slavin suggests that the Commission should defer

20   rulemaking on extreme wind standards because the NESC committee

21   decided not to apply those standards to distribution poles in

22   the 2007 addition of the NESC.  Dr. Slavin's proposal is

23   tantamount to abandoning the concept of hardening Florida's

24   distribution facilities to extreme wind standards because the

25   next revision to the NESC won't occur until 2012.  Waiting

FLORIDA PUBLIC SERVICE COMMISSION

157

1   until then would be a mistake because it would deprive Florida

2   electric consumers of the potential benefits of hardening for

3   at least five years without any showing that hardening is

4   inappropriate for Florida.

5             On the other hand, I think you heard from several of

6   the attacher comments that the 2007 NESC standards are now,

7   they have now been published and will shortly be effective, I

8   believe in February of 2007, with a suggestion that those

9   standards rather than the 2002 edition should be incorporated

10   into the Commission's rules.  We would have no objection to

11   doing so if that's the Commission's wish, and would agree that

12   doing so would make the rules reflect current standards,

13   current NESC standards more appropriately on a going-forward

14   basis.

15             Let me turn to proposed Rules 25-6.064, .078, and

16   .115, which all deal with the CIAC calculations, and I'll refer

17   to them as the CIAC rules.  The basic purpose of the

18   Commission's revisions to those rules is to reflect potential

19   differences in maintenance and storm restoration costs between

20   overhead and underground distribution service in the

21   calculation of CIAC.  This should help encourage undergrounding

22   of distribution facilities where it is appropriate and

23   beneficial to do so.

24             The FCTA, BellSouth, and Verizon all make essentially

25   the same comment on these proposed rules.  They point to the

FLORIDA PUBLIC SERVICE COMMISSION

158

1   cross-references in the rules to construction standards in

2   proposed Rule 25-6.034, and argue that if those construction

3   standards aren't adopted, aren't valid, then the

4   cross-references wouldn't be valid either.

5             In our opinion, this misunderstands the purpose and

6   effect of the cross-references.  None of the cross-references

7   says what the construction standards are going to be.  Rule

8   25-6.034 already deals with construction standards.  Even if

9   the Commission ultimately decided not to amend Rule 25-6.034 as

10   proposed, it would still contain construction standards that

11   the CIAC rules could properly cross-reference.

12             We think that it is unfortunate that the attachers

13   have chosen to protest the CIAC rules.  Independent of the

14   debate over how to harden Florida's overhead electric

15   distribution system, there is an important role for

16   undergrounding in appropriate settings.  The CIAC rules are the

17   Commission's mechanism for addressing undergrounding, but the

18   attachers have unnecessarily thrown their status into doubt by

19   their challenge.  We urge the attachers to withdraw their

20   objections to the CIAC rules so that they can be put into

21   effect as quickly as possible.

22             Finally, BellSouth asserts that proposed Rule

23   25-6.064 should reduce the historical average pole cost used in

24   calculating joint use pole rental charges in order to reflect

25   CIAC contributions and payments by other attachers.  Joint use

FLORIDA PUBLIC SERVICE COMMISSION

159

1   agreements are negotiated contracts between electric and

2   telephone companies which the Commission does not regulate.

3   Proposed Rule 25-6.064 is not a proper vehicle for debating

4   possible modifications to those joint use agreements.

5             And I thank you for this opportunity to present

6   comments, and I would be happy to address any questions that

7   you or staff might have.

8             MR. WILLIS:  That concludes our presentation.

9             CHAIRMAN EDGAR:  Thank you, Mr. Willis.

10             MR. BURNETT:  May I, Madam Chairman?

11             CHAIRMAN EDGAR:  You may.

12             MR. BURNETT:  Thank you.  John Burnett on behalf of

13   Progress Energy Florida.  Thank you very much.

14             I wanted to make some specific comments to one issue

15   very briefly on behalf of my company.  It goes to the Rule

16   25-6.034, the standard of construction rule, and I wanted to

17   speak about some concerns that my company had over the

18   suggestion that the standard of a -- construction standards be

19   filed with the Commission and the Commission vote and approve

20   those affirmatively.  And this goes to the unlawful delegation

21   and the regulation by exception argument that Ms. Smith made

22   earlier.

23             We wanted to note that under the old standard of

24   construction rule, this Commission has identified that

25   standards of construction should be done to generally accepted

FLORIDA PUBLIC SERVICE COMMISSION

160

1   engineering practices, the Commission defined what that meant,

2   we have implemented that.  All of the utilities have.  And we

3   have never filed the implementation of those standards with the

4   Commission to be voted on, and the Commission has stood to hear

5   any challenges to those standards, the Commission has audited,

6   has monitored, taken reports on those.  The Commission has done

7   exactly what the principles of regulation by exception call for

8   on these.

9             We contend, Progress Energy Florida contends that

10   under the current rule that staff has put forward that

11   recognizes the regulation by exception, the exact same thing is

12   present.  That the Commission has stated what your intention

13   is, just like the old rule.  The utilities have been charged to

14   implement that, which we can.  And others have a point of entry

15   when and if they have a problem with those standards just like

16   they had under the old rule.  The rule makes clear, the

17   proposed rule makes clear that any challenges to the standards

18   can be brought forth to the Commission and that we are to

19   interact with those that would be involved in developing those

20   standards.

21             Our concern would be that the regulation by exception

22   is not just convenient, it is somewhat of a necessity.  And to

23   think about the burden that would be placed on not only the

24   utilities but the Commission, the Commission staff, that if you

25   have to affirmatively vote up all five of our standards and

FLORIDA PUBLIC SERVICE COMMISSION

161

1   standards can be defined as reams of books this big, and then

2   all the other plans or procedures that we may have filed with

3   the Commission, that you five do not affirmatively vote up on

4   but, instead, stand ready to hear challenges on, to our company

5   it seems like a slippery slope.  That if you question your

6   ability to govern by exception in this instance, then it may

7   permeate or be ammunition for others to argue that you don't

8   have the ability to do that as a general matter to other

9   similar things.

10             Some questions that come to mind with us is that if

11   the Commission does vote to take our standards of construction

12   and vote up or down on them, if we change those, if we change

13   them once in a month, twice in a month, three times in a month,

14   do we bring those back to the Commission every time for a vote.

15   Under the current rule the answer to that question would be

16   clearly no.  There is a point of entry, I believe as Mr.

17   Harris, as Ms. Smith, and Mr. Wright have acknowledged that

18   under the current rule there is a point of entry, that that

19   allows someone to come forward and say, if I have a problem

20   with this, I'll bring it to the Commission.

21             Our fear is that if the Commission sets a standard to

22   where this has to brought, these standards have to be brought

23   and affirmatively voted up, if we change them do we have to

24   bring them up every time.  Where is the line of when the

25   Commission does and does not want to vote, and what level of

FLORIDA PUBLIC SERVICE COMMISSION

162

1   detail.  So that is our only concern.

2             We feel like the law is crystal clear and agree with

3   Mr. Harris and Ms. Smith that the Commission has the authority

4   to implement the rule as staff has presented.  And that's --

5   and the law is right.  It's right not only on its face, but on

6   its principle that the Commission, the utilities, and everyone

7   else involved shouldn't be burdened to have to prove up such

8   extensive plans and prove up every aspect of extensive

9   standards.  Rather, the regulation by exception provides that

10   if someone who has a challenge has it, then you bring it

11   forward.  Bring forward a specific small challenge, if you have

12   it at all, rather than putting the burden on your staff and on

13   our company to offer those up every time.  And, again,

14   questioning where does it stop and what level of detail must

15   the Commission see if you feel that that is what you have to

16   do.  Thank you.

17             CHAIRMAN EDGAR:  Thank you, Mr. Burnett.

18             Commissioners, questions for any of the presenters

19   that we have heard from here from the IOUs?

20             Commissioner Deason.

21             COMMISSIONER DEASON:  Yes, I have a question for

22   Mr. Butler.

23             MR. BUTLER:  Yes.

24             COMMISSIONER DEASON:  Mr. Butler, you heard the

25   presentation today by Dr. Slavin or Slavin, is that correct?

FLORIDA PUBLIC SERVICE COMMISSION

163

1             MR. BUTLER:  Yes, I did.

2             COMMISSIONER DEASON:  I understood that a significant

3   portion of the doctor's testimony dealt with the phenomenon of

4   flying debris, downed tree limbs, or downed trees having

5   significant impact on distribution facilities, and that would

6   happen regardless of the standard to which the distribution

7   facilities were built.  Do you recall that general theme that

8   was there in that testimony?

9             MR. BUTLER:  I do, yes.

10             COMMISSIONER DEASON:  And I think it was also his

11   testimony that that phenomenon of falling trees and flying

12   debris and that sort of thing was going to manifest itself even

13   at wind speeds of 70 to 80 miles per hour, generally speaking.

14             MR. BUTLER:  I heard the same testimony, yes.

15             COMMISSIONER DEASON:  Now, given that testimony, it's

16   still your position that the distribution facilities should be

17   hardened, and I think in your presentation you indicated that

18   the hardened facilities would be more likely to withstand

19   moderate trees falling and flying debris.  That's your

20   position, correct?

21             MR. BUTLER:  That's part of it.  The other part of it

22   that I didn't mention, but speaking from FPL's experience,

23   particularly in Hurricane Wilma, there were a very substantial

24   number and a quite high percentage, I believe it was on the

25   order of 50 percent, of the poles that failed that were

FLORIDA PUBLIC SERVICE COMMISSION

164

1   attributed to wind-only failure, meaning there was no obvious

2   debris impacts, no tree sitting on top of it, no obvious

3   evidence of deterioration that would have caused the pole to be

4   weakened.  They just got flat blown over, basically, as far as

5   everybody could tell.  And so, frankly, our experience in Wilma

6   does not, you know, corroborate Dr. Slavin's testimony.

7             I don't know, and I'm only speaking for FPL in that

8   regard, but it was a serious concern to FPL, and I think

9   probably that experience led us to a lot of the interest that

10   we have had and a lot of our promotion of moving the utility

11   poles, distribution poles toward a higher degree of

12   strengthening or hardening.

13             And it is also true, as I mentioned a few moments

14   ago, and you just mentioned, that the main reason for hardening

15   the poles is to avoid wind-only damage to them.  But in the

16   course of doing so there are bigger stronger poles and moderate

17   degrees of debris impacts, or tree limbs, that sort of thing,

18   they are probably going to be in a better position to withstand

19   that sort of impact.  But the main thing driving FPL's, you

20   know, interest in hardening the poles is the experience with

21   wind-only damage to poles that was primarily a phenomenon that

22   we saw after Hurricane Wilma.

23             COMMISSIONER DEASON:  Thank you.

24             CHAIRMAN EDGAR:  Commissioner Arriaga.

25             COMMISSIONER ARRIAGA:  Mr. Harris, a question for

FLORIDA PUBLIC SERVICE COMMISSION

165

1   you.

2             MR. HARRIS:  Yes, sir.

3             COMMISSIONER ARRIAGA:  I think you have heard me

4   express two or three times today that I have serious concerns

5   with the issue of delegation of authority.

6             MR. HARRIS:  Yes, sir.

7             COMMISSIONER ARRIAGA:  And I heard just now as good

8   arguments as I heard this morning for and against the

9   delegation of authority.  Mr. Burnett just came up with a very

10   important point that had not crossed my mind, and I would like

11   you to comment on that or somebody from staff.  The approval of

12   the construction standards by the part of the Commission, is

13   that such a tedious process as Mr. Burnett was indicating?

14             MR. HARRIS:  Let's let technical staff answer that

15   one.

16             MR. TRAPP:  It can be.  It can be a very tedious

17   process.  One of the things that we discussed in the workshops

18   earlier was the administrative burden on both the utilities and

19   the Commission staff and the Commission to approve every piece

20   of paper on every nut and bolt and every cross-arm that is

21   involved in Florida.  And we very quickly decided that that

22   probably was not the way we wanted to, administratively want to

23   go.

24             I have to tell you, it potentially could put strain

25   on staff.  You may have to ask for additional staff.  The

FLORIDA PUBLIC SERVICE COMMISSION

166

1   process as I understand it, much of this information, it was

2   testified, would probably be classified confidential in terms

3   of just the staff perspective.  That would require certain

4   procedures here to determine whether or not those

5   clarifications should be granted.  That's a process that we

6   would have to go through.

7             If granted, those papers would have to be maintained

8   in a locked down room in our Commission Clerk's Office.  There

9   are procedures by which the staff has to go through to get on

10   the list to even check out those documents.  Once we have

11   access to those documents and do check them out, we have to

12   have absolute control over those documents.  The individual

13   staff person that reviews those documents has to return those

14   documents.  If they don't return those documents, I can't tell

15   you the amount of paperwork, bureaucracy we have to go through

16   to account for anything that may come up missing from the

17   confidentiality rule.

18             So, quite frankly, I don't mean to overexaggerate it,

19   but it is quite an involved process.  I have been in this area

20   of standards review and enforcement for sometime now, and,

21   quite frankly, the norm is one of staff audit, review, look

22   over the shoulder type of -- I think it was classified as

23   government by exception, is that what I heard?  I'm not sure of

24   the exact terminology, but that has been the practice as long

25   as I have been here.  And to me it has been a very effective

FLORIDA PUBLIC SERVICE COMMISSION

167

1   process because it focuses your quite limited staff to doing --

2   you know, it concentrates our efforts to where the problem

3   areas are that need to be addressed.  And I think that is the

4   most effective use of us.

5             In addition, you know, we're not just leaving it up

6   to them to come up with standards.  We have already put,

7   through that discussion and that workshop process, came to

8   agreement by which a process -- we will have access to that

9   information.  Our field people will have it in their field

10   offices.  Our local Tallahassee regulatory staff will have it

11   upon request to any company within two days.  We have audit

12   teams that will be combing through this material.

13             My staff -- at least the initial filings will, I'm

14   sure, need a lot of initial scrutiny.  So it's not like we are

15   delegating anything.  What we are trying to do is make our jobs

16   more effect and efficient to get to the problem.  And I'm sorry

17   to talk so long.

18             COMMISSIONER ARRIAGA:  Thank you, sir.

19             Mr. Willis, did I understand correctly that you are

20   speaking on behalf of all the IOUs, or only three of them?

21             MR. WILLIS:  Well, most of our presentation was with

22   respect to all the utilities.  Mr. Burnett had wanted to

23   amplify a position that he had with respect to that particular

24   issue.

25             COMMISSIONER ARRIAGA:  Okay.  So I'm going to assume

FLORIDA PUBLIC SERVICE COMMISSION

168

1   that you are, in a way, representing the opinion of most of the

2   electric utilities, correct, the investor-owned utilities?

3             MR. WILLIS:  Well, with respect to what we presented.

4             COMMISSIONER ARRIAGA:  Here today.

5             MR. WILLIS:  Right.

6             COMMISSIONER ARRIAGA:  Let me go to the specific

7   question.  I think I heard you say that there was a proposal

8   this morning to form some kind of committee to negotiate, and I

9   have also stated that I welcome negotiations.  I encourage you

10   to negotiate.  I will hope you will come to some kind of

11   agreement.

12             Are you telling me, or did I understand you correctly

13   that negotiations are broken, that you can no longer negotiate

14   anything?

15             MR. WILLIS:  No, I didn't say that at all.  What we

16   would encourage you to do is to proceed with your rulemaking,

17   to do exactly what you have been doing, that is, to proceed

18   with all deliberate speed without any delay.  And we would, of

19   course, continue a dialogue that really actually just started

20   in the last couple of days with respect to other matters.  And

21   if we come to something that is worthy of presentation to you

22   or it bears fruit, we would bring it back.  But that would be a

23   separate process.  I think it always is an important process

24   for the various parties to continue to talk to each other and

25   to try to work out solutions that avoids unnecessary litigation

FLORIDA PUBLIC SERVICE COMMISSION

169

1   and unnecessary concern.

2             I think many of the things that they have suggested

3   that we look at are matters of implementation of your rules,

4   but I think that you should proceed on the track that you have

5   been on, that is to continue to stay on your same schedule.  Of

6   course, I would guess have post-hearing comments, and I

7   understand that this is coming back to the agenda sometime like

8   October the 24th as time within that period for us to continue

9   to talk.  But in the meantime, you stick with your rulemaking

10   and continue to proceed.  That rulemaking, as you indicated

11   this morning, provides a framework for us to talk, to continue

12   to talk.  So I think they are two separate processes.

13             COMMISSIONER ARRIAGA:  Okay.  Thank you.

14             CHAIRMAN EDGAR:  Commissioner Tew.

15             COMMISSIONER TEW:  Thank you.

16             Commissioner Arriaga asked questions along the same

17   line that I have, but I will try to clarify some points in my

18   head from some things that were said by several of you.  First,

19   Mr. Willis, I realize that you said that the infrastructure

20   hardening proposal, and I've got the right terminology now,

21   that was spoken about earlier by several the attachers, you

22   said it was unnecessary.  And I just want to clarify that.  And

23   let's assume that there is no delegation issue.  And I have

24   heard different arguments on all sides of that.  But isn't that

25   infrastructure hardening proposal a way to avoid the issue of

FLORIDA PUBLIC SERVICE COMMISSION

170

1   the PSC approving the standards?  I mean, can't that get us to

2   where we want to be sooner, if it works?

3             MR. WILLIS:  Not necessarily.  I think it's incumbent

4   upon us to talk and to try to reach that result.  But at the

5   same time, I think it would be a mistake for you to do anything

6   other than to stay on your track with respect to the adoption

7   of these rules.  Otherwise, I think that the delay will

8   increase.

9             COMMISSIONER TEW:  Just to follow up on that, do you

10   think it will necessarily add delay if we look into that kind

11   of a proposal?  Because it looks like to me the time line

12   follows a time line similar to the rule process we have now.

13   And maybe I don't understand it exactly, but it looked like the

14   180 days sort of tracked the rule process, as well.  I mean, if

15   it's true that you all know that you are not going to get

16   anywhere through that process, then that is probably what we

17   should be talking about.

18             But since we have that proposal before us, I wanted

19   to ask these questions now.  You had mentioned all due

20   deliberate speed, and to me all due deliberate speed might

21   include a lot of time for litigation of these rules.

22             MR. WILLIS:  Well, I think that if you proceed on the

23   track that you have been on and use the same CASR that you have

24   and proceed, there is time between now and the time when you

25   actually come back here for agenda conference to adopt a rule,

FLORIDA PUBLIC SERVICE COMMISSION

171

1   and if through these discussions it does bear fruit, it could

2   be presented to you in the post-hearing comments, if it comes

3   that fast, or all the way up till the time that you are at

4   agenda conference.

5             COMMISSIONER TEW:  Earlier someone had mentioned the

6   proprietary nature of the standards, and I think Mr. Trapp

7   discussed that quite a bit, too.  And I don't know who this is

8   exactly directed to, I guess it is any of you.  Can you help me

9   understand whether the current standards now are proprietary

10   and how we deal with those?  I know they have said that we, as

11   a Commission, that we still audit them and have the ability to

12   review them.  But how does it work now and how do you see it

13   working if we go forward with these rules?

14             MR. BURNETT:  Commissioner, speaking only on behalf

15   of my company, that's the only company I, of course, have

16   knowledge of, we do have portions of our standards that are

17   confidential.  They are not the majority, however.  And if

18   staff was inclined to take a look at any of those, I think we

19   do have an effective process to, on an ad hoc basis, ask for

20   confidential protection in which staff could review those.  So

21   I don't think under the current procedure or under the rule as

22   proposed, Commissioner, that it would add any different burden

23   at all.

24             CHAIRMAN EDGAR:  Commissioner Carter.

25             COMMISSIONER CARTER:  Madam Chairman, have we taken

FLORIDA PUBLIC SERVICE COMMISSION

172

1   all the parties, because I have a couple of questions for

2   staff, but I wanted to wait to make sure that everyone was

3   finished.

4             CHAIRMAN EDGAR:  Thank you very much.  I actually was

5   going to kind of wrap that up there, and Commissioner Arriaga

6   jumped ahead of me.  So we have had all the presentations from

7   people that had let us know they wanted to speak, and I have

8   given an opportunity for any others, so, yes, I would like to

9   more formally concluding the presentation portion of our agenda

10   today.

11             We do have some things to discuss.  We need to give

12   some direction to our staff.  We have the opportunity to ask

13   further questions, and then we do need to talk about

14   post-hearing time schedules from this point forward.

15             So, with that, we will move into that portion of our

16   discussion.  Commissioner Carter.

17             MR. HARRIS:  Excuse me, Chairman, just one

18   housekeeping matter.  The exhibits.  Mr. Willis, the PowerPoint

19   presentation you had, did you intend for that to be marked as a

20   separate exhibit or to refer back to the tab in the composite?

21             MR. WILLIS:  Refer back to the tab in the composite.

22             MR. HARRIS:  And then the cable that was handed out

23   as a tangible, is that supposed to be marked as an exhibit?

24             MR. WILLIS:  We think it should be an exhibit, but --

25             MR. HARRIS:  Chairman, I am hearing a request that it

FLORIDA PUBLIC SERVICE COMMISSION

173

1   be marked --

2             CHAIRMAN EDGAR:  I have never had a cable as an

3   exhibit before at a hearing, but I guess there is always a

4   first time.  So, if that what is our counsel is advising --

5             MR. HARRIS:  I think that would be a demonstrative

6   either exhibit or demonstrative aid.  For the sake of the

7   record, I would suggest we mark it as Number 9, and just list

8   is was --

9             COMMISSIONER DEASON:  Can the Chairman keep that

10   exhibit in her office?

11             MR. HARRIS:  I do believe that is the appropriate

12   place for it, yes.

13             CHAIRMAN EDGAR:  As long as it's not a gift.

14             (Laughter.)

15             CHAIRMAN EDGAR:  Per the recommendation of our

16   counsel, we will have a demonstrative exhibit as Number 9.  And

17   how do we want to describe it?

18             MR. WILLIS:  Example of overlashing.

19             CHAIRMAN EDGAR:  Thank you.  And we have chuckled

20   about it, but actually to have an example that we can look at

21   of things that we are talking about is very helpful, so thank

22   you for that.

23             (Exhibit 9 marked for identification and admitted

24   into the record.)

25             CHAIRMAN EDGAR:  Commissioner Carter.

FLORIDA PUBLIC SERVICE COMMISSION

174

1             COMMISSIONER CARTER:  Thank you, Madam Chairman, for

2   maybe a couple of questions for staff.  In light of the filings

3   that you have received subsequent to the front end and what you

4   have heard today and where we are, do you have recommendations

5   for us on proceeding further?  I mean, I just kind of want to

6   explore that with you.

7             CHAIRMAN EDGAR:  If I may, Mr. Harris, and certainly

8   then you can go back to him, but I think that is one of the

9   things that we need to discuss a little bit amongst ourselves,

10   and then we will look to staff to see if they can give us some

11   recommendations as to how and what time frame to move forward,

12   if that's all right.

13             COMMISSIONER CARTER:  That's fine with me, Madam

14   Chair.

15             CHAIRMAN EDGAR:  So before we talk about time frames

16   and next steps, which I think is where you are going,

17   Commissioner Carter, let me see if I can kick it off, and then

18   please everybody jump right in.

19             First of all, let me say thank you to everybody who

20   has participated today, and thank you for the coordination that

21   went on helping us get an orderly agenda and kind of

22   apportioning the way to address the various issues.  It is

23   helpful for our thought processes.  It's helpful for the next

24   steps.  You know, it is not always -- or it is not often, I

25   guess, is a better way to put it -- it's not often that we have

FLORIDA PUBLIC SERVICE COMMISSION

175

1   a Commission workshop as part of a rule hearing.  In fact, I

2   think it's the first since I have been here, and it shows the

3   importance that each of us, I know, have put on this, and the

4   recognition of the importance of what our decisions will be

5   today and as we move forward with this proceeding.

6             Trying to kind of capsulize or encapsulize some of

7   the comments that we have heard, I have heard concerns about

8   the subdelegation issue, I have heard some concerns about the

9   collaboration language, and we have heard concerns about the

10   FCC potential jurisdiction.  We have also heard concerns about

11   potential costs, and a number of numbers have been put out

12   there.  And I recognize that it is difficult to pin them down

13   at this point.  It's kind of a chicken and an egg.  If you

14   don't have the standard, it is difficult to come up with an

15   accurate cost estimate.  If you have the -- it's hard to come

16   up with a standard if you don't have an accurate cost estimate.

17   So I know that we all kind of recognize the dilemma that we are

18   in.

19             And so with all of that, and I would kind of put out

20   there that I would look to staff, once we have developed a time

21   schedule to take comments, post-hearing comments, and all the

22   comments that we have heard today, and all the comments, of

23   course, that were received at the workshops prior to this on

24   these four issues, subdelegation, looking to perhaps stronger

25   collaboration language, looking at the issue of FCC

FLORIDA PUBLIC SERVICE COMMISSION

176

1   jurisdiction, or recognizing that and seeing if additional

2   language would be appropriate to help tighten up on that issue,

3   and also addressing both the cost estimates and the

4   cost/benefit discussion and analysis that we have had.

5             I know I would like our staff to look at those issues

6   in particular, and then as we move forward, can maybe bring us

7   back at the future agenda conference recommendations that

8   address all of those and some potential language changes for

9   our rules.  And I'm going to open it up to further discussion

10   and comment.

11             COMMISSIONER CARTER:  If I may, Madam Chairman.

12             CHAIRMAN EDGAR:  Yes, Commissioner Carter.

13             COMMISSIONER CARTER:  I hate to think that you have

14   done a Vulcan mind meld on me, but the issues that you have

15   delineated are kind of where I think we need to be, kind of

16   getting our arms around that and give them to staff so we can

17   move forward.  Those issues were pretty much what I was going

18   to ask about in the context of procedurally what do we do and

19   how do we get there.  And I would like to get my fellow

20   Commissioners' thoughts on those, as well.

21             CHAIRMAN EDGAR:  Commissioner Arriaga.

22             COMMISSIONER ARRIAGA:  Thank you.

23             Just a comment to staff.  You have heard me two or

24   three times, and I'm going to repeat it again, because it is a

25   real concern.  The reason I'm repeating that is because I take

FLORIDA PUBLIC SERVICE COMMISSION

177

1   very seriously what Commissioner Deason said, I think it was

2   yesterday.  Whatever we do, please, please, whatever we do

3   don't allow us to be ridiculed in the courts or in the FCC.

4   And if the issue of delegated authority is an issue, think

5   about it.  If it's going to be more work for the Commission,

6   that is what they pay us for.  And I think that we need to look

7   at that very, very seriously.

8             I'm not giving you any instructions, I'm just saying

9   this is a concern that I have, a very serious concern.  There

10   were very serious arguments, legal arguments here that we need

11   to take into consideration about the delegation of authority

12   issue.  And I don't think we lose anything by bringing those

13   standards here for our review.

14             I know it is a very tedious process, Mr. Trapp.  It

15   is very difficult.  It is going to put a burden on your staff.

16   It may be something that you would wish to consider.  That's

17   only a thought.  Thank you.

18             CHAIRMAN EDGAR:  If the degree of tedium was going to

19   be a determining factor in decisions that we made, I'm not sure

20   that we would ever make one.  However, we do, and I do take

21   very seriously, also, both the administrative burden on

22   government resources and the regulatory burden on the private

23   sector and NGO, so we will take that into account.

24             Commissioner Deason, did you have any additional

25   comments?

FLORIDA PUBLIC SERVICE COMMISSION

178

1             COMMISSIONER DEASON:  Well, actually a question for,

2   I guess it would be a question for Mr. Harris and Mr. Trapp.

3   There has been a suggestion of an infrastructure advisory

4   committee, and there has been a time frame set out, a short

5   time frame and a longer term time frame.  Do you have any

6   thoughts on whether such an initiative could obviate the need,

7   in some parties' minds, the need for a rule challenge at DOAH?

8             MR. HARRIS:  We do have thoughts on that.  I will

9   take a stab at it, and then Mr. Trapp can correct me when I'm

10   wrong.  I do believe that the infrastructure advisory

11   committee, the IAC proposal has some merit.  However, I don't

12   see it as a substitute for the rulemaking, and I'll tell you

13   how I see it really being productive and useful.

14             In my mind, staff would like the opportunity to bring

15   a written recommendation to you for your consideration at an

16   agenda conference.  The dates we had sort of tentatively

17   proposed were the post-hearing comments would be due in about

18   two weeks, around September 15th; that we would prepare a

19   written recommendation, that would be filed around October 14th

20   for an October 24th agenda conference.

21             In my mind that gives more than the 30 days that the

22   IAC is asking for.  Because the comments would be due in two

23   weeks, but the recommendation, the staff recommendation is

24   essentially about 45 days out.  So what I would suggest in my

25   mind is that you perhaps direct the parties here today, the

FLORIDA PUBLIC SERVICE COMMISSION

179

1   interested persons here today, the IOUs, the electric, the

2   telecoms, the cable companies, the cities, to the extent they

3   can get involved, to engage in this, to start this IAC project,

4   and really sit down and try to negotiate.  And then keep the

5   staff informed.  And come back to us at the end of the 30 days

6   and say, hey, this has really worked, we're collaborating,

7   we're making progress.  Maybe we could go to the Commission.

8   And I would also ask that you make staff a part of that.  Let

9   us be a part of this process.

10             If it looks like it is really being useful, we can

11   come back to you at an agenda conference on October 3rd, or the

12   October 24th and say this is working, this is great, and they

13   are solving problems.  They are moving forward.  They are

14   resolving things right and left.  And we think a little bit

15   more time would make sense, so we would ask for a further

16   postponement of your rulemaking to get this stuff in there

17   where we can all bring it to you.

18             On the other hand, if in the 30 days they don't get

19   to a point where we feel confident, we have a staff

20   recommendation to be filed.  That gives them another two weeks

21   until October 14th to keep working.  The staff recommendation

22   comes out, everyone can read that.  That might provide an

23   incentive to sharpen their pencils and negotiate a little bit

24   more.  They can still -- we can pull a recommendation up until,

25   you know, two minutes before it goes up to agenda conference.

FLORIDA PUBLIC SERVICE COMMISSION

180

1   And so if someone comes to us the day before the agenda

2   conference and says we need a deferral, we have got 95 percent

3   of it worked out, we don't want the Commission to vote on your

4   staff recommendation, give us some time and bring a new one in

5   two weeks, a revised staff rec that includes the things we have

6   worked out through this IAC process.  Staff is more than

7   interested in doing that.

8             So, in my mind, what I am saying is I think I would

9   encourage you to move forward on a schedule today, a rulemaking

10   schedule, with strong direction to the interested persons to

11   engage in this IAC process, make it work, and the understanding

12   is if they can you will take consideration of that and make the

13   appropriate adjustments to the schedule.

14             Now, Bob, you can tell me why I'm wrong and why you

15   hate me.

16             MR. TRAPP:  I was thinking I was getting one of those

17   Vulcan mind meld things, too, because I concur with Mr. Harris'

18   comments.  And I would say that, I mean, this type of

19   collaborative process, this working together and everything

20   sounds like the input that we were seeking in the rule to begin

21   with, and it looks like a process by which we could avoid some

22   of the complaints that we feared we might get as a result of

23   the rule.  So if they could come to an agreement -- but at the

24   same time I share the comments that staff very much looks

25   forward to an opportunity to providing you a written

FLORIDA PUBLIC SERVICE COMMISSION

181

1   recommendation at an upcoming agenda.

2             CHAIRMAN EDGAR:  You know, on every issue -- it was

3   one of our presenters who said talking is good, I think.

4   Personally, and I don't mean to speak for each of you, but I

5   might in this limited instance, which is to say I think we

6   always try to encourage, cajole, beg, direct, and sometimes

7   even require discussion, collaboration, and I think we have on

8   this issue from the beginning of our discussions earlier this

9   year and at every step of the way.

10             And I'm looking at the schedule again, and I note

11   that our Internal Affairs meeting where we voted to open a

12   docket was on February 27th.  The first draft rules by the

13   staff were distributed on April 3rd.  There was a workshop

14   that, again, I hope was collaborative, and that all interested

15   parties participated openly and fully in at the end of April,

16   there was a second in the middle of May, and there was a third

17   in the middle of July which helped get us to the point that we

18   are today.

19             So this is the fourth workshop, although the first

20   that we have had full Commission participation in as we have

21   moved through this process again from the beginning of the

22   year.  I've been looking at the calendar, and I know that

23   Commissioner Deason is also looking at the calendar, and, you

24   know, thinking about the dates that Mr. Harris has given us,

25   and the fact that we have been told by some of the parties that

FLORIDA PUBLIC SERVICE COMMISSION

182

1   they think they can make additional real progress in 30 days.

2             One option might be to slide back some the date for

3   post-hearing comments, perhaps October 2nd.  I haven't

4   discussed that date with staff yet.  We will want to make sure

5   that are we do allow ample opportunity for them to review

6   thoroughly and analyze those post-hearing comments.  But if we

7   build into the time period to submit written comments, and I

8   adamantly would encourage and request any proposed language

9   changes into those post-hearing comments to be filed, looking

10   at maybe October 2nd, that gives approximately 32 days from

11   today for those comments to be filed.  And I think that that

12   would still give -- I will look to staff, though, for

13   confirmation -- time for our staff to review all of those

14   comments and put together a written recommendation that would

15   come before us at the October 24th conference.  It's a little

16   tight on that back end, I recognize.  Think about that for a

17   moment, if you would.  And, Commissioners, again, any thoughts?

18             Commissioner Deason, again, I know you are looking at

19   the calendar.  Do you --

20             MR. HARRIS:  I'm sorry, Chairman, may I interrupt?  I

21   don't want to interrupt you, but I need to correct something I

22   said earlier.

23             CHAIRMAN EDGAR:  Okay.

24             MR. HARRIS:  This is an evidentiary hearing, in a

25   way, and so we need to have some type of end to the record.

FLORIDA PUBLIC SERVICE COMMISSION

183

1   And, therefore, I was going to suggest that my initial comment

2   of the 15 days for post-hearing comments with some type of

3   follow-up at the end of the 30 days wouldn't make a very clear

4   record.  So I was going to suggest exactly, Chairman, what you

5   suggested, that the post-hearing comments of some type be due

6   30 days from now, which would be around October 2nd, and that

7   those would include the results of this IAC meeting or

8   whatever, as written filed comments that would then become part

9   of this evidentiary record that would be considered.

10             And that would make our record a lot cleaner and

11   prevent any kind of concern over what the record is containing

12   and any type of concern over some verbal communications being

13   made.  If it's in writing, it's government in the sunshine,

14   it's an open record, everybody knows what it is.  So you were

15   getting into some comments among the Commissioners, I didn't

16   mean to interrupt you, but to say that I needed to correct

17   myself, that the 15 days wasn't going to work, basically.

18             CHAIRMAN EDGAR:  An important point that I would like

19   to make is that, as I said earlier, we recognize the importance

20   of the discussions that we have had and the decisions that we

21   will make.  And I want all of our best minds working on this.

22   You know, sometimes a deadline can contribute to creative and

23   productive dialogue.  Perhaps it has in this instance.  But the

24   point is we want to move forward, but we want to do it

25   thoughtfully and professionally with the best information and

FLORIDA PUBLIC SERVICE COMMISSION

184

1   come out with the best product.

2             So we want the best minds of our staff, we want the

3   best minds of all the industry, we want the best minds from

4   local government, from NGOs, from academia, and anybody else

5   that I may have left out of that to help us get the absolute

6   best product.  It's not a race to the finish line, but we do

7   need to move forward within the dynamics of the processes that

8   are allowed to us.

9             Commissioner Arriaga, did you have a comment?

10             COMMISSIONER ARRIAGA:  A clarification for the

11   record.  The IAC has been mentioned several times.  Are you

12   suggesting that we are now constituting an ad hoc IAC or

13   something like that?  Because I think the question of

14   delegation was also raised on the issue of the IAC, or is this

15   an informal industry thing?

16             MR. HARRIS:  It's my understanding that a

17   presentation has been made to you that the parties would like

18   to get together through something they have called an

19   infrastructure advisory committee.  And it is my recommendation

20   to you that you allow them to do that.  And they can include

21   the results of that in their written comments 30 days from now.

22             Mr. Cooke.

23             MR. COOKE:  Mike Cooke, Commission Counsel.  The one

24   thing we are concerned about is we are in a hearing, a

25   rulemaking hearing, and for purposes of the record, today would

FLORIDA PUBLIC SERVICE COMMISSION

185

1   be the final day, with the exception that our rules do allow

2   for written comments to be received.  Our order currently says

3   that they would be received by September 15th. You can change

4   that date at this hearing and make it October 2nd, for

5   example.  I think all we are saying is, and what I have heard

6   the Commission suggest, and everyone I think who has spoken

7   today, encourages voluntary cooperation and collaboration.

8             We are not creating a committee or suggesting

9   creating a committee, but we think it would be valuable to the

10   extent that the interested parties get together and have those

11   discussions and can achieve some of the results they have

12   talked about and submit them to us in writing by that time

13   frame, it can be incorporated into our review for purposes of

14   the recommendation we would submit at the agenda conference.

15             CHAIRMAN EDGAR:  Commissioner Carter.

16             COMMISSIONER CARTER:  Madam Chairman, I applaud your

17   wisdom in the context of where we are.  Because where I was

18   going was going to ask staff a lot of those questions, and you

19   have kind of got your calendar there, as well as the calendar,

20   and kind of laid things out.  And I do think that this gives us

21   an opportunity to move forward, it allows the interested

22   parties to have their dialogue and discussion without us saying

23   that we support a committee or anything like that.  So if they

24   want to talk confidentially until they arrive at a conclusion,

25   they can do that, but this gets us to the 30 days.

FLORIDA PUBLIC SERVICE COMMISSION

186

1             I think from listening Mr. Harris and Mr. Cooke, I

2   don't think it gives us heartburn to do that and still keep it

3   on time for being at an agenda conference.  I mean, that works

4   for me.  I don't know what we need to do, but if we need a

5   motion to that effect, Madam Chairman, I would be more than

6   happy to make it.

7             CHAIRMAN EDGAR:  Thank you, Commissioner Carter.

8             Any further questions, comments?  Okay.

9             COMMISSIONER DEASON:  The only concern that I have is

10   for the staff, and I guess they can speak for themselves.  I

11   mean, we are looking at post-hearing filings being filed on

12   October 2nd, and they have to file a written recommendation

13   ten days later.  And if staff thinks that is sufficient --

14             MR. HARRIS:  I think a comment was made that the

15   staff is here to do a job, and we will get it done in ten days.

16   So we can do that, yes.

17             CHAIRMAN EDGAR:  Okay.  Then we have had discussion,

18   I think we are all on the same page, it sounds like.  As

19   always, I would like to make sure that staff are clear as to

20   what it is we have requested and directed.

21             Mr. Harris, do we need a motion and a vote, or can we

22   do it as direction to our staff and, of course, to the

23   participants?

24             MR. HARRIS:  I don't believe a motion and vote are

25   required.  I think you have given us sufficient direction, and

FLORIDA PUBLIC SERVICE COMMISSION

187

1   we do have a transcript that is recording this.

2             CHAIRMAN EDGAR:  Okay.  My understanding is that the

3   transcript will be ready around about September 8th.  We would

4   ask that post-hearing comments be filed by October 2nd.  We

5   will have our staff review all of those, and working on the

6   time lines that they always do, then prepare a written

7   recommendation that will come before us at the agenda

8   conference presently scheduled for October 24th.

9             Are there any other matters, Mr. Harris, that we need

10   to address while we are all gathered together?

11             MR. HARRIS:  I'm sorry, I think Mr. Meza might have a

12   comment or a question.

13             CHAIRMAN EDGAR:  I'm sorry, Mr. Meza, I didn't see

14   you.  Go right ahead.

15             MR. MEZA:  Thank you, Madam Chairman.

16             I would just ask for clarification for the LECs,

17   mainly the LECs, that under the Administrative Procedure Act

18   the right to file a DOAH challenge for rules that are

19   promulgated is triggered by the conclusion of a public hearing,

20   which is ten days from that date.  And I want to make sure that

21   from our perspective that the Commission believes and staff

22   believes that that date will be at the agenda, such that we

23   don't have to run and file a DOAH challenge, if we choose to,

24   within ten days of today.

25             CHAIRMAN EDGAR:  Okay.  I was --

FLORIDA PUBLIC SERVICE COMMISSION

188

1             MR. HARRIS:  Yes.

2             CHAIRMAN EDGAR:  I was going to say I think I know

3   the answer to that, but let me look to my staff counsel.  That

4   certainly was my intention.

5             MR. HARRIS:  The answer is yes.

6             CHAIRMAN EDGAR:  And with verification from our

7   counsel regarding the Chapter 120 implications, does that give

8   you the clarification that you need?

9             MR. MEZA:  Yes, ma'am, that is all I need to hear.

10   Thank you.

11             CHAIRMAN EDGAR:  Thank you for the question.  Any

12   other matters for clarification?  Closing comments.

13             Mr. Harris.

14             MR. HARRIS:  We don't have anything further, thank

15   you.

16             CHAIRMAN EDGAR:  Okay.  Then this hearing is

17   concluded.  Thank you all again for your participation.

18             (The hearing concluded at 4:05 p.m.)

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

189

1   STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTERS

2   COUNTY OF LEON      )

3

WE, JANE FAUROT, RPR, and LINDA BOLES, RPR, CRR,

4   Official Commission Reporters, do hereby certify that the

foregoing proceeding was heard at the time and place herein

5   stated.

6             IT IS FURTHER CERTIFIED that we stenographically

reported the said proceedings; that the same has been

7   transcribed under our direct supervision; and that this

transcript constitutes a true transcription of our notes of

8   said proceedings.

9             WE FURTHER CERTIFY that we are not a relative,

employee, attorney or counsel of any of the parties, nor are we

10   a relative or employee of any of the parties' attorneys or

counsel connected with the action, nor are we financially

11   interested in the action.

12

13              DATED THIS 9th day of September, 2006.

14

15

____________________________  __________________________

16   JANE FAUROT, RPR              LINDA BOLES, RPR, CRR

FPSC Official Commission      FPSC Official Commission

17   Reporter                      Reporter

(850) 413-6732                (850) 413-6734

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION