# C.6.0  JEA’s Sensitivity Analyses

Several sensitivity analyses were performed to supplement JEA’s base case economic analysis and demonstrate the robustness of the capacity expansion plans, including JEA’s participation in TEC.  These analyses measured the impact of varying the key assumptions used in the base case economic analysis, as well as the effects of considerations not included in the base case.

As described in Section C.5.0, the base case economic analysis compared the CPWC of the optimal capacity expansion plan, including JEA’s participation in TEC, to the optimal capacity expansion plan without participation in TEC.  For the base case analysis that included participation in TEC, the proposed TEC was treated as a committed unit starting May 1, 2012, while in the base case analysis without TEC, no candidate units were committed.  POWROPT, Black & Veatch’s optimal generation and capacity expansion model, was used to select the least-cost expansion plan to meet JEA’s capacity needs.  Once the optimal capacity expansion plan was developed for each case, POWRPRO (Black & Veatch’s production costing model) was used to determine each plan’s production costs, which were used to develop an overall CPWC for each plan.

The general methodology used in the sensitivity analyses is similar to the methodology used in the base case analysis.  POWROPT was used to determine the optimal capacity expansion plan for all cases considered under the various assumptions described in this section.  POWRPRO was then utilized to calculate production costs of each plan, to compare each plan’s CPWC and to determine the least-cost expansion plan.  The remainder of this section presents the methodology and results of the sensitivity analyses.

C.6.1  Input Parameter Sensitivities

The sensitivities described in this section reflect changes to the base case input assumptions, including fuel prices, load forecast, capital costs, emissions allowance prices, and potential environmental regulations related to CO2 emissions.

C.6.1.1  High Fuel Price Forecast

The high fuel price sensitivity analysis is based on Hill & Associates’ high fuel price forecasts and the corresponding emissions allowance price forecasts.  The high fuel price forecasts are presented in Section A.4.0, while the emissions allowance price forecasts corresponding to the high fuel price forecast are presented in Section A.5.0.

As in the base case analysis described in Section C.5.0, the costs of emissions allowances were added to the fuel prices for both the existing and candidate units in the high fuel price sensitivity.  Table C.6-1 presents the emissions cost adders for JEA’s existing units, and Table C.6-2 presents the emissions adders for the candidate units under the high fuel price sensitivity.

Under the high fuel price forecast scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield CFB in 2022, and a brownfield IGCC unit in 2023.  The optimal capacity expansion plan for the case without participation in TEC consists of a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a brownfield IGCC unit in 2019, a second brownfield LMS100 CT in 2021, a greenfield CFB in 2022, a greenfield LMS100 CT in 2023, and a second LMS100 CT in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $15,521.2 million and $15,580.9 million, respectively.  A comparison of these CPWCs shows that the expansion plan with TEC is the least-cost plan by $59.7 million over the evaluation period.

C.6.1.2  Low Fuel Price Forecast

The low fuel price sensitivity analysis is based on Hill & Associates’ low fuel price forecasts and the corresponding emissions allowance price forecasts.  The low fuel price forecasts are presented in Section A.4.0, while the emissions allowance price forecasts corresponding to the low fuel price forecast are presented in Section A.5.0.

As in the base case analysis described in Section C.5.0, the costs of emissions allowances were added to the fuel prices for both the existing and candidate units in the low fuel price sensitivity.  Table C.6-3 presents the emissions cost adders for JEA’s existing system, and Table C.6-4 presents the emissions cost adders for the candidate units under the low fuel price sensitivity.

Under the low fuel price forecast scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a brownfield LMS100 CT in 2015, a second brownfield CFB in 2019, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield LMS100 CT in 2022, two additional greenfield LMS100 CTs in 2023, a fifth LMS100 CT in 2024.  The optimal capacity expansion plan for the case without participation in TEC consists of a brownfield LMS100 CT in 2011, a

| Table C.6-1 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Existing Units – High Fuel Forecast (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Kennedy CT 7 | Northside ST 1 | Northside ST 2 | Northside ST 3 | Northside CTs | Brandy Branch CT 1 | Brandy Branch CC | SJRPP ST 1 | SJRPP ST 2 | Scherer ST 4 |
| 2009 | $0.07 | $0.08 | $0.08 | $0.36 | $0.38 | $0.06 | $0.02 | $0.07 | $0.07 | $0.07 |
| 2010 | $0.10 | $0.17 | $0.17 | $0.72 | $0.53 | $0.08 | $0.03 | $0.16 | $0.16 | $0.18 |
| 2011 | $0.10 | $0.17 | $0.17 | $0.76 | $0.55 | $0.08 | $0.03 | $0.16 | $0.16 | $0.17 |
| 2012 | $0.11 | $0.18 | $0.18 | $0.83 | $0.59 | $0.09 | $0.03 | $0.17 | $0.17 | $0.18 |
| 2013 | $0.12 | $0.19 | $0.19 | $0.88 | $0.63 | $0.10 | $0.03 | $0.17 | $0.17 | $0.19 |
| 2014 | $0.13 | $0.21 | $0.22 | $1.03 | $0.69 | $0.11 | $0.04 | $0.19 | $0.19 | $0.19 |
| 2015 | $0.23 | $0.35 | $0.35 | $1.64 | $1.20 | $0.18 | $0.06 | $0.31 | $0.31 | $0.33 |
| 2016 | $0.21 | $0.33 | $0.34 | $1.59 | $1.09 | $0.17 | $0.06 | $0.30 | $0.30 | $0.31 |
| 2017 | $0.22 | $0.34 | $0.35 | $1.71 | $1.14 | $0.17 | $0.07 | $0.30 | $0.30 | $0.29 |
| 2018 | $0.27 | $0.43 | $0.43 | $2.00 | $1.42 | $0.22 | $0.08 | $0.38 | $0.38 | $0.40 |
| 2019 | $0.28 | $0.45 | $0.45 | $2.12 | $1.49 | $0.23 | $0.08 | $0.40 | $0.40 | $0.42 |
| 2020 | $0.35 | $0.55 | $0.55 | $2.62 | $1.88 | $0.29 | $0.10 | $0.48 | $0.48 | $0.49 |
| 2021 | $0.41 | $0.63 | $0.63 | $3.01 | $2.18 | $0.33 | $0.12 | $0.56 | $0.56 | $0.56 |
| 2022 | $0.46 | $0.70 | $0.70 | $3.30 | $2.45 | $0.37 | $0.13 | $0.62 | $0.62 | $0.62 |
| 2023 | $0.42 | $0.69 | $0.70 | $3.07 | $2.25 | $0.34 | $0.12 | $0.63 | $0.63 | $0.69 |
| 2024 | $0.54 | $0.84 | $0.85 | $3.79 | $2.89 | $0.44 | $0.15 | $0.77 | $0.77 | $0.83 |
| 2025 | $0.60 | $0.96 | $0.97 | $4.13 | $3.18 | $0.48 | $0.16 | $0.89 | $0.89 | $1.01 |
| 2026 | $0.65 | $1.05 | $1.06 | $4.48 | $3.48 | $0.53 | $0.18 | $0.98 | $0.98 | $1.11 |
| 2027 | $0.71 | $1.14 | $1.15 | $4.84 | $3.80 | $0.58 | $0.19 | $1.06 | $1.06 | $1.21 |
| 2028 | $0.77 | $1.24 | $1.24 | $5.22 | $4.14 | $0.63 | $0.21 | $1.15 | $1.15 | $1.32 |
| 2029 | $0.84 | $1.34 | $1.34 | $5.62 | $4.48 | $0.68 | $0.22 | $1.25 | $1.25 | $1.43 |
| 2030 | $0.91 | $1.45 | $1.45 | $6.03 | $4.84 | $0.73 | $0.24 | $1.35 | $1.35 | $1.56 |
| 2031 | $0.98 | $1.56 | $1.57 | $6.48 | $5.23 | $0.79 | $0.26 | $1.46 | $1.46 | $1.69 |
| 2032 | $1.06 | $1.69 | $1.69 | $6.96 | $5.66 | $0.86 | $0.28 | $1.58 | $1.58 | $1.84 |
| 2033 | $1.14 | $1.82 | $1.83 | $7.47 | $6.11 | $0.93 | $0.30 | $1.71 | $1.71 | $2.00 |
| 2034 | $1.23 | $1.97 | $1.97 | $8.03 | $6.60 | $1.00 | $0.32 | $1.85 | $1.85 | $2.17 |
| 2035 | $1.33 | $2.13 | $2.13 | $8.62 | $7.14 | $1.08 | $0.35 | $2.01 | $2.01 | $2.35 |

| Table C.6-2 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Candidate Units – High Fuel Forecast (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LMS100 CT | 7FA CT | 1x1 7FA CC | TEC | CFB (80 percent petcoke 20 percent coal) | CFB (100 percent coal) | IGCC (100 percent petcoke) |
| 2009 | $0.01 | $0.01 | $0.01 | $0.08 | $0.08 | $0.11 | $0.07 |
| 2010 | $0.01 | $0.01 | $0.01 | $0.16 | $0.17 | $0.20 | $0.10 |
| 2011 | $0.01 | $0.01 | $0.01 | $0.16 | $0.17 | $0.20 | $0.11 |
| 2012 | $0.01 | $0.01 | $0.01 | $0.17 | $0.18 | $0.22 | $0.12 |
| 2013 | $0.01 | $0.01 | $0.01 | $0.18 | $0.19 | $0.23 | $0.12 |
| 2014 | $0.02 | $0.02 | $0.02 | $0.20 | $0.21 | $0.25 | $0.14 |
| 2015 | $0.03 | $0.03 | $0.03 | $0.33 | $0.35 | $0.42 | $0.24 |
| 2016 | $0.02 | $0.02 | $0.03 | $0.31 | $0.33 | $0.39 | $0.22 |
| 2017 | $0.03 | $0.03 | $0.03 | $0.32 | $0.34 | $0.40 | $0.23 |
| 2018 | $0.03 | $0.03 | $0.03 | $0.40 | $0.43 | $0.51 | $0.28 |
| 2019 | $0.03 | $0.03 | $0.03 | $0.42 | $0.45 | $0.53 | $0.29 |
| 2020 | $0.04 | $0.04 | $0.04 | $0.52 | $0.55 | $0.65 | $0.37 |
| 2021 | $0.05 | $0.05 | $0.05 | $0.59 | $0.63 | $0.75 | $0.43 |
| 2022 | $0.06 | $0.06 | $0.06 | $0.66 | $0.70 | $0.84 | $0.48 |
| 2023 | $0.05 | $0.05 | $0.05 | $0.65 | $0.69 | $0.82 | $0.45 |
| 2024 | $0.07 | $0.07 | $0.07 | $0.80 | $0.85 | $1.01 | $0.57 |
| 2025 | $0.07 | $0.07 | $0.07 | $0.92 | $0.97 | $1.15 | $0.63 |
| 2026 | $0.08 | $0.08 | $0.08 | $1.00 | $1.05 | $1.26 | $0.69 |
| 2027 | $0.09 | $0.09 | $0.09 | $1.09 | $1.15 | $1.37 | $0.75 |
| 2028 | $0.09 | $0.09 | $0.09 | $1.18 | $1.24 | $1.49 | $0.82 |
| 2029 | $0.10 | $0.10 | $0.10 | $1.28 | $1.35 | $1.61 | $0.89 |
| 2030 | $0.11 | $0.11 | $0.11 | $1.39 | $1.45 | $1.74 | $0.96 |
| 2031 | $0.12 | $0.12 | $0.12 | $1.50 | $1.57 | $1.88 | $1.03 |
| 2032 | $0.13 | $0.13 | $0.13 | $1.62 | $1.70 | $2.03 | $1.12 |
| 2033 | $0.14 | $0.14 | $0.14 | $1.75 | $1.83 | $2.19 | $1.21 |
| 2034 | $0.15 | $0.15 | $0.15 | $1.89 | $1.98 | $2.37 | $1.30 |
| 2035 | $0.16 | $0.16 | $0.16 | $2.05 | $2.14 | $2.56 | $1.41 |

| Table C.6-3 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Existing Units – Low Fuel Forecast (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Kennedy CT 7 | Northside ST 1 | Northside ST 2 | Northside ST 3 | Northside CTs | Brandy Branch CT 1 | Brandy Branch CC | SJRPP ST 1 | SJRPP ST 2 | Scherer ST 4 |
| 2009 | $0.07 | $0.08 | $0.07 | $0.33 | $0.36 | $0.05 | $0.01 | $0.07 | $0.07 | $0.07 |
| 2010 | $0.09 | $0.15 | $0.15 | $0.65 | $0.48 | $0.07 | $0.03 | $0.14 | $0.14 | $0.16 |
| 2011 | $0.09 | $0.16 | $0.16 | $0.67 | $0.50 | $0.08 | $0.03 | $0.15 | $0.15 | $0.17 |
| 2012 | $0.10 | $0.17 | $0.17 | $0.74 | $0.54 | $0.08 | $0.03 | $0.16 | $0.16 | $0.17 |
| 2013 | $0.10 | $0.18 | $0.18 | $0.76 | $0.56 | $0.09 | $0.03 | $0.16 | $0.16 | $0.19 |
| 2014 | $0.11 | $0.18 | $0.18 | $0.85 | $0.59 | $0.09 | $0.03 | $0.16 | $0.16 | $0.17 |
| 2015 | $0.17 | $0.28 | $0.28 | $1.28 | $0.90 | $0.14 | $0.05 | $0.25 | $0.25 | $0.27 |
| 2016 | $0.11 | $0.21 | $0.22 | $1.06 | $0.60 | $0.09 | $0.04 | $0.19 | $0.19 | $0.19 |
| 2017 | $0.13 | $0.24 | $0.24 | $1.21 | $0.68 | $0.11 | $0.05 | $0.21 | $0.21 | $0.20 |
| 2018 | $0.17 | $0.30 | $0.30 | $1.37 | $0.89 | $0.14 | $0.05 | $0.27 | $0.27 | $0.29 |
| 2019 | $0.19 | $0.32 | $0.33 | $1.52 | $0.99 | $0.15 | $0.06 | $0.29 | $0.29 | $0.31 |
| 2020 | $0.19 | $0.33 | $0.33 | $1.54 | $1.03 | $0.16 | $0.06 | $0.29 | $0.29 | $0.31 |
| 2021 | $0.21 | $0.36 | $0.36 | $1.66 | $1.10 | $0.17 | $0.06 | $0.32 | $0.32 | $0.34 |
| 2022 | $0.22 | $0.37 | $0.37 | $1.70 | $1.16 | $0.18 | $0.07 | $0.33 | $0.33 | $0.36 |
| 2023 | $0.24 | $0.43 | $0.43 | $1.88 | $1.29 | $0.20 | $0.07 | $0.40 | $0.40 | $0.45 |
| 2024 | $0.26 | $0.47 | $0.47 | $1.99 | $1.36 | $0.21 | $0.08 | $0.44 | $0.44 | $0.51 |
| 2025 | $0.28 | $0.55 | $0.55 | $2.20 | $1.51 | $0.23 | $0.08 | $0.53 | $0.53 | $0.64 |
| 2026 | $0.29 | $0.57 | $0.57 | $2.24 | $1.54 | $0.24 | $0.09 | $0.55 | $0.55 | $0.68 |
| 2027 | $0.31 | $0.60 | $0.61 | $2.37 | $1.64 | $0.25 | $0.09 | $0.59 | $0.59 | $0.73 |
| 2028 | $0.33 | $0.64 | $0.65 | $2.51 | $1.75 | $0.27 | $0.10 | $0.62 | $0.62 | $0.78 |
| 2029 | $0.35 | $0.68 | $0.69 | $2.65 | $1.85 | $0.28 | $0.10 | $0.66 | $0.66 | $0.83 |
| 2030 | $0.37 | $0.72 | $0.73 | $2.80 | $1.96 | $0.30 | $0.11 | $0.71 | $0.71 | $0.89 |
| 2031 | $0.39 | $0.77 | $0.77 | $2.95 | $2.08 | $0.32 | $0.11 | $0.75 | $0.75 | $0.95 |
| 2032 | $0.41 | $0.82 | $0.82 | $3.12 | $2.20 | $0.34 | $0.12 | $0.80 | $0.80 | $1.01 |
| 2033 | $0.44 | $0.87 | $0.87 | $3.29 | $2.34 | $0.36 | $0.13 | $0.85 | $0.85 | $1.08 |
| 2034 | $0.46 | $0.92 | $0.93 | $3.47 | $2.48 | $0.38 | $0.13 | $0.91 | $0.91 | $1.16 |
| 2035 | $0.49 | $0.98 | $0.98 | $3.67 | $2.62 | $0.40 | $0.14 | $0.97 | $0.97 | $1.23 |

| Table C.6-4 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Candidate Units – Low Fuel Forecast (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LMS100 CT | 7FA CT | 1x1 7FA CC | TEC | CFB (80 percent petcoke 20 percent coal) | CFB (100 percent coal) | IGCC (100 percent petcoke) |
| 2009 | $0.01 | $0.01 | $0.01 | $0.08 | $0.08 | $0.10 | $0.07 |
| 2010 | $0.01 | $0.01 | $0.01 | $0.14 | $0.15 | $0.18 | $0.10 |
| 2011 | $0.01 | $0.01 | $0.01 | $0.15 | $0.16 | $0.19 | $0.10 |
| 2012 | $0.01 | $0.01 | $0.01 | $0.16 | $0.17 | $0.20 | $0.11 |
| 2013 | $0.01 | $0.01 | $0.01 | $0.17 | $0.18 | $0.21 | $0.11 |
| 2014 | $0.01 | $0.01 | $0.01 | $0.17 | $0.18 | $0.21 | $0.12 |
| 2015 | $0.02 | $0.02 | $0.02 | $0.26 | $0.28 | $0.33 | $0.18 |
| 2016 | $0.01 | $0.01 | $0.01 | $0.19 | $0.21 | $0.24 | $0.12 |
| 2017 | $0.02 | $0.02 | $0.02 | $0.21 | $0.23 | $0.27 | $0.14 |
| 2018 | $0.02 | $0.02 | $0.02 | $0.27 | $0.29 | $0.34 | $0.18 |
| 2019 | $0.02 | $0.02 | $0.02 | $0.30 | $0.32 | $0.38 | $0.20 |
| 2020 | $0.02 | $0.02 | $0.02 | $0.30 | $0.32 | $0.38 | $0.21 |
| 2021 | $0.03 | $0.03 | $0.03 | $0.33 | $0.35 | $0.41 | $0.22 |
| 2022 | $0.03 | $0.03 | $0.03 | $0.34 | $0.37 | $0.43 | $0.23 |
| 2023 | $0.03 | $0.03 | $0.03 | $0.40 | $0.43 | $0.50 | $0.26 |
| 2024 | $0.03 | $0.03 | $0.03 | $0.43 | $0.46 | $0.54 | $0.28 |
| 2025 | $0.03 | $0.03 | $0.03 | $0.51 | $0.54 | $0.63 | $0.31 |
| 2026 | $0.04 | $0.04 | $0.04 | $0.53 | $0.56 | $0.65 | $0.32 |
| 2027 | $0.04 | $0.04 | $0.04 | $0.56 | $0.60 | $0.69 | $0.34 |
| 2028 | $0.04 | $0.04 | $0.04 | $0.60 | $0.64 | $0.74 | $0.36 |
| 2029 | $0.04 | $0.04 | $0.04 | $0.63 | $0.68 | $0.78 | $0.38 |
| 2030 | $0.04 | $0.04 | $0.04 | $0.67 | $0.72 | $0.83 | $0.40 |
| 2031 | $0.05 | $0.05 | $0.05 | $0.72 | $0.77 | $0.88 | $0.43 |
| 2032 | $0.05 | $0.05 | $0.05 | $0.76 | $0.81 | $0.94 | $0.45 |
| 2033 | $0.05 | $0.05 | $0.05 | $0.81 | $0.87 | $1.00 | $0.48 |
| 2034 | $0.06 | $0.06 | $0.06 | $0.86 | $0.92 | $1.06 | $0.51 |
| 2035 | $0.06 | $0.06 | $0.06 | $0.91 | $0.98 | $1.13 | $0.54 |

brownfield CFB in 2012, a second brownfield CFB in 2014, a brownfield 1x1 7FA combined cycle unit in 2019, a second brownfield LMS100 CT in 2021, a brownfield IGCC unit in 2022, a greenfield LMS100 CT in 2023, and a second greenfield LMS100 CT in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $12,650.7 million and $12,651.3 million, respectively.  A comparison of these CPWCs shows that the expansion plan with participation in TEC is the least-cost plan by $0.6 million over the evaluation period.

C.6.1.3  High Load and Energy Growth

Load and energy growth sensitivities are important analyses that help to demonstrate the robustness of future capacity additions, since load growth is a fundamental variable in determining an optimal capacity expansion plan.  The high load and energy growth sensitivity demonstrates the effects of planning to meet capacity and energy requirements in a case where both load and energy grow at a rate that is higher than the expected rate used in the base case economic evaluation presented in Section C.5.0.  This scenario requires the addition of more generation to meet reserve margin requirements and, therefore, results in increased CPWCs compared to the base case capacity expansion plan.  The high load and energy growth scenario is based upon the high load and energy growth forecast presented in Section C.3.0.  Tables C.6-5 and C.6-6 present JEA’s projected reliability levels under the high load and energy growth scenario for the winter and summer seasons, respectively.

Although the need for capacity additions is shown as early as 2006 in Tables C.6-5 and C.6-6, this need was not considered in the development of optimal capacity expansion plans, since construction and development schedules would preclude the addition of any of the supply-side alternatives presented in Section A.6.0 to meet this need.  Rather than planning to meet capacity needs in 2006, the need for capacity in both cases (with and without TEC) was not considered until 2007.

In the base case economic evaluation, the capacity expansion plan with JEA’s participation in TEC included a seasonal purchase during the winter of 2011/2012.  This purchase was included and modeled to be consistent with JEA’s 2006 TYSP in the base case.  Since JEA would need to add additional capacity in the high load and energy growth scenario prior to 2011, the seasonal purchase was not included in the evaluation.  All other planned near-term capacity additions and retirements were made consistent with JEA’s 2006 TYSP.

Under the high load and energy growth sensitivity analysis, the optimal capacity expansion plan with TEC in 2012 consists of two brownfield 7FA CTs and two greenfield 7FA CTs in 2007, two brownfield LMS100 CTs in 2011, a brownfield CFB in 2014, a second brownfield CFB in 2015, a brownfield 1x1 7FA combined cycle unit in 2019, a brownfield IGCC unit in 2021, two greenfield LMS100 CTs in 2023, and two additional greenfield LMS100 CTs in 2024.  The optimal capacity expansion plan without participation in TEC consists of two brownfield 7FA CTs and two greenfield 7FA CTs in 2007, a brownfield 1x1 7FA combined cycle unit in 2011, a brownfield CFB in 2013, a second brownfield CFB in 2014, a brownfield IGCC unit in 2018, a brownfield LMS100 CT in 2020, a greenfield CFB in 2021, a second brownfield LMS100 CT in 2022, two greenfield LMS100 CTs in 2023, and two additional greenfield LMS100 CTs in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $17,591.0 and $17,721.5 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $130.5 million over the evaluation period.

C.6.1.4  Low Load and Energy Growth

The low load and energy growth sensitivity demonstrates the effects of planning to meet capacity and energy requirements in a case where both load and energy grow at a rate that is lower than the expected rate used in the base case economic evaluation.  This scenario requires the addition of less generation to meet reserve margin requirements and, therefore, results in decreased CPWCs over the planning period compared to the base case capacity expansion plan.  The low load and energy growth scenario is based upon the low load and energy growth forecast presented in Section C.3.0.  Tables C.6-7 and C.6-8 present JEA’s projected reliability levels under the low load and energy growth scenario for the winter and summer seasons, respectively.

The seasonal purchase described in Section C.5.0 was not considered in this sensitivity, since no capacity is needed during the winter of 2011/2012.  All other capacity additions were included in a manner consistent with JEA’s 2006 TYSP.

Under the low load and energy growth sensitivity analysis, the optimal capacity expansion plan with TEC in 2012 consists of a brownfield CFB in 2021 and a second brownfield CFB in 2024.  The optimal capacity expansion plan without participation in TEC consists of a brownfield CFB in 2014, a second brownfield CFB in 2021, and a brownfield IGCC unit in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $13,371.9 and $13,427.3 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $55.4 million over the evaluation period.

| Table C.6-5 Projected Reliability Levels High Load and Energy Growth - Winter |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Net Generating Capacity (MW)(3) | Non-Partial Requirements Purchases (MW)(4,5) | Non-Partial Requirements Sales (MW)(6) | Net Firm Planned Capacity Retirements (MW)(7,8) | Net Firm Capacity Additions/ (Reductions) (MW)(9,10) | Net System Capacity (MW) | System Peak Demand(1) |  | Reserve Margin(2) |  | Excess/(Deficit) to Maintain 15% Reserve Margin |  |
|  |  |  |  |  |  |  | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) | Before Int. and Load Mgt. (%) | After Int. and Load Mgt. (%) | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) |
| 2005/06 | 3,535 | 229 | 383 | 0 | 18 | 3,399 | 3,553 | 3,349 | -4.3 | 1.5 | (687) | (452) |
| 2006/07 | 3,557 | 229 | 383 | 0 | 36 | 3,439 | 3,669 | 3,462 | -6.3 | -0.7 | (781) | (543) |
| 2007/08 | 3,557 | 229 | 383 | 0 | 36 | 3,439 | 3,688 | 3,481 | -6.8 | -1.2 | (803) | (564) |
| 2008/09 | 3,748 | 229 | 383 | 63 | 36 | 3,567 | 3,808 | 3,596 | -6.3 | -0.8 | (813) | (569) |
| 2009/10 | 3,939 | 229 | 383 | 63 | 31 | 3,752 | 3,931 | 3,713 | -4.5 | 1.1 | (768) | (518) |
| 2010/11 | 4,130 | 22 | 383 | 63 | 31 | 3,736 | 4,057 | 3,833 | -7.9 | -2.5 | (929) | (672) |
| 2011/12 | 4,130 | 22 | 383 | 63 | 31 | 3,736 | 4,184 | 3,954 | -10.7 | -5.5 | (1,075) | (811) |
| 2012/13 | 4,130 | 22 | 383 | 63 | 31 | 3,736 | 4,134 | 4,078 | -9.6 | -8.4 | (1,018) | (953) |
| 2013/14 | 4,130 | 22 | 383 | 63 | 27 | 3,732 | 4,446 | 4,204 | -16.1 | -11.2 | (1,381) | (1,102) |
| 2014/15 | 4,130 | 22 | 383 | 63 | 27 | 3,732 | 4,580 | 4,332 | -18.5 | -13.8 | (1,535) | (1,249) |
| 2015/16 | 4,130 | 22 | 383 | 63 | 27 | 3,732 | 4,717 | 4,462 | -20.9 | -16.4 | (1,692) | (1,399) |
| 2016/17 | 4,130 | 22 | 0 | 63 | 27 | 4,115 | 4,856 | 4,595 | -15.3 | -10.4 | (1,469) | (1,169) |
| 2017/18 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 4,997 | 4,729 | -17.7 | -13.0 | (1,632) | (1,324) |
| 2018/19 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 5,141 | 4,866 | -20.0 | -15.4 | (1,798) | (1,482) |
| 2019/20 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 5,287 | 5,006 | -22.2 | -17.8 | (1,966) | (1,643) |
| 2020/21 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 5,435 | 5,147 | -24.3 | -20.1 | (2,136) | (1,805) |
| 2021/22 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 5,585 | 5,289 | -26.3 | -22.2 | (2,308) | (1,968) |
| 2022/23 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 5,738 | 5,435 | -28.3 | -24.3 | (2,484) | (2,136) |
| 2023/24 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 5,893 | 5,583 | -30.2 | -26.3 | (2,663) | (2,306) |
| 2024/25 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 6,052 | 5,735 | -32.0 | -28.3 | (2,846) | (2,481) |
| (1)Load reflects the end of FPU’s load on December 31, 2007. (2)Reserve margin calculated as (Net System Capacity - System Peak Demand) / (System Peak Demand - Partial Requirements Purchases). (3)Includes peak firing capacity on Kennedy CT 7, Brandy Branch CTs 1 through 3, and Brandy Branch ST 4 upgrade in the summer of 2006. Also includes three 191 MW (winter rating) CTs in 2009, 2010, and 2011. (4)Assumes 207 MW purchase from Southern will expire on May 31, 2010. (5)Assumes no purchases from TEA. (6)Assumes FPL contract to purchase 30 percent of SJRPP will reach contracted energy limitation on October 1, 2016; based on a conservative estimate made by JEA for planning purposes. (7)Assumes the placement of Kennedy CT Unit 3 in reserve shutdown on October 1, 2008. Total capacity loss is 63 MW. (8)Assumes that Girvin Landfill will be retired on October 1, 2017. (9)Assumes turbine upgrades at Northside ST Units 1, 2, and 3 on June 1, 2006; December 1, 2006; and December 15, 2005, respectively. Total capacity increase is 36 MW. (10)Assumes capacity reduction due to auxiliary power required for emissions control in January 2010. Assumes that auxiliary load increase reduces unit capacity. 80 percent of SJRPP 1 and 2, and 23.64 percent of Scherer 4 auxiliary load increases are assigned to JEA. Total assumed loss is 7.2 MW. |  |  |  |  |  |  |  |  |  |  |  |  |

| Table C.6-6 Projected Reliability Levels High Load and Energy Growth - Summer |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Net Generating Capacity (MW)(3) | Non-Partial Requirements Purchases (MW)(4,5) | Non-Partial Requirements Sales (MW)(6) | Net Firm Planned Capacity Retirements (MW)(7,8) | Net Firm Capacity Additions/ (Reductions) (MW)(9,10) | Net System Capacity (MW) | System Peak Demand(1) |  | Reserve Margin(2) |  | Excess/(Deficit) to Maintain 15% Reserve Margin |  |
|  |  |  |  |  |  |  | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) | Before Int. and Load Mgt. (%) | After Int. and Load Mgt. (%) | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) |
| 2006 | 3,390 | 207 | 376 | 0 | 27 | 3,248 | 2,896 | 2,716 | 12.2 | 19.6 | (82) | 125 |
| 2007 | 3,390 | 229 | 376 | 0 | 36 | 3,279 | 2,961 | 2,778 | 10.7 | 18.0 | (126) | 84 |
| 2008 | 3,390 | 229 | 376 | 0 | 36 | 3,279 | 2,943 | 2,760 | 11.4 | 18.8 | (105) | 105 |
| 2009 | 3,538 | 229 | 376 | 51 | 36 | 3,376 | 3,008 | 2,821 | 12.2 | 19.7 | (83) | 132 |
| 2010 | 3,686 | 22 | 376 | 51 | 31 | 3,312 | 3,074 | 2,883 | 7.7 | 14.9 | (223) | (4) |
| 2011 | 3,834 | 22 | 376 | 51 | 31 | 3,460 | 3,139 | 2,943 | 10.2 | 17.6 | (150) | 75 |
| 2012 | 3,834 | 22 | 376 | 51 | 31 | 3,460 | 3,205 | 3,005 | 7.9 | 15.1 | (226) | 4 |
| 2013 | 3,834 | 22 | 376 | 51 | 31 | 3,460 | 3,270 | 3,065 | 5.8 | 12.9 | (301) | (65) |
| 2014 | 3,834 | 22 | 376 | 51 | 27 | 3,456 | 3,336 | 3,127 | 3.6 | 10.5 | (381) | (140) |
| 2015 | 3,834 | 22 | 376 | 51 | 27 | 3,456 | 3,401 | 3,187 | 1.6 | 8.4 | (455) | (209) |
| 2016 | 3,834 | 22 | 376 | 51 | 27 | 3,456 | 3,467 | 3,248 | -0.3 | 6.4 | (531) | (280) |
| 2017 | 3,834 | 22 | 0 | 51 | 27 | 3,832 | 3,532 | 3,308 | 8.5 | 15.8 | (230) | 28 |
| 2018 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,598 | 3,369 | 5.9 | 13.1 | (329) | (66) |
| 2019 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,664 | 3,430 | 3.9 | 11.0 | (405) | (136) |
| 2020 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,729 | 3,490 | 2.1 | 9.1 | (480) | (205) |
| 2021 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,795 | 3,551 | 0.4 | 7.3 | (556) | (275) |
| 2022 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,861 | 3,612 | -1.4 | 5.4 | (631) | (345) |
| 2023 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,927 | 3,673 | -3.0 | 3.7 | (707) | (415) |
| 2024 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,992 | 3,732 | -4.6 | 2.1 | (782) | (483) |
| 2025 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 4,058 | 3,792 | -6.1 | 0.4 | (858) | (552) |
| (1)Load reflects the end of FPU’s load on December 31, 2007. (2)Reserve margin calculated as (Net System Capacity - System Peak Demand) / (System Peak Demand - Partial Requirements Purchases). (3)Includes peak firing capacity on Kennedy CT 7, Brandy Branch CTs 1 through 3, and Brandy Branch ST 4 upgrade in the summer of 2006. Also includes three 148 MW (summer rating) CTs in 2009, 2010, and 2011. (4)Assumes 207 MW purchase from Southern will expire on May 31, 2010. (5)Assumes no purchases from TEA. (6)Assumes FPL contract to purchase 30 percent of SJRPP will reach contracted energy limitation on October 1, 2016; based on a conservative estimate made by JEA for planning purposes. (7)Assumes the placement of Kennedy CT Unit 3 in reserve shutdown on October 1, 2008. Total capacity loss is 51 MW. (8)Assumes that Girvin Landfill will be retired on October 1, 2017. (9)Assumes turbine upgrades at Northside ST Units 1, 2, and 3 on June 1, 2006; December 1, 2006; and December 15, 2005, respectively. Total capacity increase is 36 MW. (10)Assumes capacity reduction due to auxiliary power required for emissions control in January 2010. Assumes that auxiliary load increase reduces unit capacity. 80 percent of SJRPP 1 and 2, and 23.64 percent of Scherer 4 auxiliary load increases are assigned to JEA. Total assumed loss is 7.2 MW. |  |  |  |  |  |  |  |  |  |  |  |  |

| Table C.6-7 Projected Reliability Levels Low Load and Energy Growth - Winter |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Net Generating Capacity (MW)(3) | Non-Partial Requirements Purchases (MW)(4,5) | Non-Partial Requirements Sales (MW)(6) | Net Firm Planned Capacity Retirements (MW)(7,8) | Net Firm Capacity Additions/ (Reductions) (MW)(9,10) | Net System Capacity (MW) | System Peak Demand(1) |  | Reserve Margin(2) |  | Excess/(Deficit) to Maintain 15% Reserve Margin |  |
|  |  |  |  |  |  |  | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) | Before Int. and Load Mgt. (%) | After Int. and Load Mgt. (%) | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) |
| 2005/06 | 3,535 | 229 | 383 | 0 | 18 | 3,399 | 2,558 | 2,385 | 32.9 | 42.5 | 458 | 656 |
| 2006/07 | 3,557 | 229 | 383 | 0 | 36 | 3,439 | 2,636 | 2,461 | 30.5 | 39.7 | 407 | 609 |
| 2007/08 | 3,557 | 229 | 383 | 0 | 36 | 3,439 | 2,631 | 2,456 | 30.7 | 40.0 | 413 | 614 |
| 2008/09 | 3,748 | 229 | 383 | 63 | 36 | 3,567 | 2,712 | 2,532 | 31.5 | 40.9 | 448 | 655 |
| 2009/10 | 3,939 | 229 | 383 | 63 | 31 | 3,752 | 2,795 | 2,610 | 34.3 | 43.8 | 538 | 751 |
| 2010/11 | 4,130 | 22 | 383 | 63 | 31 | 3,736 | 2,897 | 2,689 | 29.0 | 39.0 | 405 | 644 |
| 2011/12 | 4,130 | 22 | 383 | 63 | 31 | 3,736 | 2,965 | 2,770 | 26.0 | 34.9 | 327 | 551 |
| 2012/13 | 4,130 | 22 | 383 | 63 | 31 | 3,736 | 3,053 | 2,853 | 22.4 | 31.0 | 225 | 455 |
| 2013/14 | 4,130 | 22 | 383 | 63 | 27 | 3,732 | 3,141 | 2,936 | 18.8 | 27.1 | 120 | 356 |
| 2014/15 | 4,130 | 22 | 383 | 63 | 27 | 3,732 | 3,231 | 3,021 | 15.5 | 23.5 | 17 | 258 |
| 2015/16 | 4,130 | 22 | 383 | 63 | 27 | 3,732 | 3,323 | 3,107 | 12.3 | 20.1 | (89) | 159 |
| 2016/17 | 4,130 | 22 | 0 | 63 | 27 | 4,115 | 3,416 | 3,195 | 20.5 | 28.8 | 187 | 441 |
| 2017/18 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 3,511 | 3,284 | 17.2 | 25.3 | 77 | 338 |
| 2018/19 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 3,607 | 3,374 | 14.1 | 21.9 | (34) | 234 |
| 2019/20 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 3,704 | 3,465 | 11.1 | 18.7 | (145) | 130 |
| 2020/21 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 3,803 | 3,558 | 8.2 | 15.6 | (259) | 23 |
| 2021/22 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 3,904 | 3,653 | 5.4 | 12.6 | (375) | (87) |
| 2022/23 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 4,006 | 3,749 | 2.7 | 9.7 | (493) | (197) |
| 2023/24 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 4,109 | 3,846 | 0.1 | 7.0 | (611) | (309) |
| 2024/25 | 4,130 | 22 | 0 | 64 | 27 | 4,114 | 4,215 | 3,946 | -2.4 | 4.3 | (732) | (423) |
| (1)Load reflects the end of FPU’s load on December 31, 2007. (2)Reserve margin calculated as (Net System Capacity - System Peak Demand) / (System Peak Demand - Partial Requirements Purchases). (3)Includes peak firing capacity on Kennedy CT 7, Brandy Branch CTs 1 through 3, and Brandy Branch ST 4 upgrade in the summer of 2006. Also includes three 191 MW (winter rating) CTs in 2009, 2010, and 2011. (4)Assumes 207 MW purchase from Southern will expire on May 31, 2010. (5)Assumes no purchases from TEA. (6)Assumes FPL contract to purchase 30 percent of SJRPP will reach contracted energy limitation on October 1, 2016; based on a conservative estimate made by JEA for planning purposes. (7)Assumes the placement of Kennedy CT Unit 3 in reserve shutdown on October 1, 2008. Total capacity loss is 63 MW. (8)Assumes that Girvin Landfill will be retired on October 1, 2017. (9)Assumes turbine upgrades at Northside ST Units 1, 2, and 3 on June 1, 2006; December 1, 2006; and December 15, 2005, respectively. Total capacity increase is 36 MW. (10)Assumes capacity reduction due to auxiliary power required for emissions control in January 2010. Assumes that auxiliary load increase reduces unit capacity. 80 percent of SJRPP 1 and 2, and 23.64 percent of Scherer 4 auxiliary load increases are assigned to JEA. Total assumed loss is 7.2 MW. |  |  |  |  |  |  |  |  |  |  |  |  |

| Table C.6-8 Projected Reliability Levels Low Load and Energy Growth - Summer |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Net Generating Capacity (MW)(3) | Non-Partial Requirements Purchases (MW)(4,5) | Non-Partial Requirements Sales (MW)(6) | Net Firm Planned Capacity Retirements (MW)(7,8) | Net Firm Capacity Additions/ (Reductions) (MW)(9,10) | Net System Capacity (MW) | System Peak Demand(1) |  | Reserve Margin(2) |  | Excess/(Deficit) to Maintain 15% Reserve Margin |  |
|  |  |  |  |  |  |  | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) | Before Int. and Load Mgt. (%) | After Int. and Load Mgt. (%) | Before Int. and Load Mgt. (MW) | After Int. and Load Mgt. (MW) |
| 2006 | 3,390 | 207 | 376 | 0 | 27 | 3,248 | 2,670 | 2,506 | 21.6 | 29.6 | 178 | 366 |
| 2007 | 3,390 | 229 | 376 | 0 | 36 | 3,279 | 2,739 | 2,572 | 19.7 | 27.5 | 129 | 321 |
| 2008 | 3,390 | 229 | 376 | 0 | 36 | 3,279 | 2,724 | 2,557 | 20.4 | 28.2 | 146 | 338 |
| 2009 | 3,538 | 229 | 376 | 51 | 36 | 3,376 | 2,794 | 2,623 | 20.8 | 28.7 | 163 | 360 |
| 2010 | 3,686 | 22 | 376 | 51 | 31 | 3,312 | 2,865 | 2,690 | 15.6 | 23.1 | 17 | 218 |
| 2011 | 3,834 | 22 | 376 | 51 | 31 | 3,460 | 2,936 | 2,757 | 17.8 | 25.5 | 83 | 289 |
| 2012 | 3,834 | 22 | 376 | 51 | 31 | 3,460 | 3,008 | 2,825 | 15.0 | 22.5 | 1 | 211 |
| 2013 | 3,834 | 22 | 376 | 51 | 31 | 3,460 | 3,081 | 2,894 | 12.3 | 19.5 | (83) | 132 |
| 2014 | 3,834 | 22 | 376 | 51 | 27 | 3,456 | 3,154 | 2,962 | 9.6 | 16.7 | (171) | 49 |
| 2015 | 3,834 | 22 | 376 | 51 | 27 | 3,456 | 3,228 | 3,032 | 7.1 | 14.0 | (257) | (31) |
| 2016 | 3,834 | 22 | 376 | 51 | 27 | 3,456 | 3,303 | 3,102 | 4.6 | 11.4 | (343) | (112) |
| 2017 | 3,834 | 22 | 0 | 51 | 27 | 3,832 | 3,378 | 3,173 | 13.4 | 20.8 | (53) | 183 |
| 2018 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,454 | 3,244 | 10.3 | 17.4 | (163) | 78 |
| 2019 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,531 | 3,317 | 7.9 | 14.8 | (252) | (6) |
| 2020 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,608 | 3,389 | 5.6 | 12.4 | (341) | (89) |
| 2021 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,686 | 3,462 | 3.3 | 10.0 | (430) | (173) |
| 2022 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,764 | 3,535 | 1.2 | 7.7 | (520) | (257) |
| 2023 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,843 | 3,609 | -0.9 | 5.5 | (611) | (342) |
| 2024 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 3,923 | 3,684 | -2.9 | 3.4 | (703) | (428) |
| 2025 | 3,834 | 0 | 0 | 52 | 27 | 3,809 | 4,005 | 3,761 | -4.9 | 1.3 | (797) | (516) |
| (1)Load reflects the end of FPU’s load on December 31, 2007. (2)Reserve margin calculated as (Net System Capacity - System Peak Demand) / (System Peak Demand - Partial Requirements Purchases). (3)Includes peak firing capacity on Kennedy CT 7, Brandy Branch CTs 1 through 3, and Brandy Branch ST 4 upgrade in the summer of 2006. Also includes three 148 MW (summer rating) CTs in 2009, 2010, and 2011. (4)Assumes 207 MW purchase from Southern will expire on May 31, 2010. (5)Assumes no purchases from TEA. (6)Assumes FPL contract to purchase 30 percent of SJRPP will reach contracted energy limitation on October 1, 2016; based on a conservative estimate made by JEA for planning purposes. (7)Assumes the placement of Kennedy CT Unit 3 in reserve shutdown on October 1, 2008. Total capacity loss is 51 MW. (8)Assumes that Girvin Landfill will be retired on October 1, 2017. (9)Assumes turbine upgrades at Northside ST Units 1, 2, and 3 on June 1, 2006; December 1, 2006; and December 15, 2005, respectively. Total capacity increase is 36 MW. (10)Assumes capacity reduction due to auxiliary power required for emissions control in January 2010. Assumes that auxiliary load increase reduces unit capacity. 80 percent of SJRPP 1 and 2, and 23.64 percent of Scherer 4 auxiliary load increases are assigned to JEA. Total assumed loss is 7.2 MW. |  |  |  |  |  |  |  |  |  |  |  |  |

C.6.1.5  High Capital Costs

In the high capital cost sensitivity, the capital costs for the candidate units and the proposed TEC are increased by 20 percent.  Considering an increase in capital costs helps capture uncertainty related to the future costs of material, labor, and equipment.  Increasing capital costs can change the emphasis on the timing of capital intensive units and may result in the selection of units with relatively lower capital costs but higher operating and production costs earlier than units with relatively higher capital costs but lower operating and production costs.

Under the high capital cost scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield LMS100 CT in 2022, and a brownfield 1x1 7FA combined cycle unit in 2023.  The optimal capacity expansion plan without participation in TEC consists of a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a second brownfield LMS100 CT in 2019, a brownfield 1x1 7FA combined cycle unit in 2020, a brownfield IGCC unit in 2022, a greenfield LMS100 CT in 2023, and a second greenfield LMS100 CT in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $14,465.4 and $14,500.7 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $35.3 million over the evaluation period.

C.6.1.6  Low Capital Costs

In the low capital cost sensitivity, the capital costs for the candidate units and the proposed TEC are decreased by 20 percent.  Considering a decrease in capital costs helps capture uncertainty related to the future costs of material, labor, and equipment.  Decreasing capital costs can change the emphasis on the timing of capital intensive units and may result in the selection of units with relatively higher capital costs but lower operating and production costs earlier than units with relatively lower capital costs but higher operating and production costs.

Under the low capital cost scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield LMS100 CT in 2022, and a brownfield IGCC unit in 2023.  The optimal capacity expansion plan without participation in TEC consists of a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a brownfield IGCC unit in 2019, a second brownfield LMS100 CT in 2021, two greenfield LMS100 CTs in 2022, and a brownfield 1x1 7FA combined cycle unit in 2023.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $13,788.2 and $13,877.7 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $89.5 million over the evaluation period.

C.6.1.7  High Emissions Allowance Prices

The base economic analysis presented in Section C.5.0 utilizes the base fuel and corresponding emissions allowance price forecasts provided by Hill & Associates.  Historically, prices for emissions allowances have been volatile, and this sensitivity demonstrates the effects of higher allowance prices than the forecasts provided by Hill & Associates.

In the high emissions allowance price sensitivity case, the base case allowance price forecasts provided by Hill & Associates were increased by 25 percent on an annual basis, while the fuel price forecasts were left unchanged from those provided by Hill & Associates in the base case.  Increasing the allowance prices results in a higher fuel cost adder for the fuels being burned in existing and candidate generating units.  The increase in allowance prices results in a greater economic incentive to operate units with lower emissions rates for electric generation, and also results in higher CPWCs relative to the base case economic analysis.  Table C.6-9 presents the emissions allowance prices used in the high emissions allowance price sensitivity analysis.  Tables C.6-10 and C.6-11 present the emissions cost adders included for JEA’s existing and candidate units, respectively, for the high emissions allowance price sensitivity.

In the high emissions allowance price scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield LMS100 CT in 2022, and a brownfield 1x1 7FA combined cycle unit in 2023.  The optimal capacity expansion plan without participation in TEC consists of a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a second brownfield LMS100 CT in 2019, a brownfield 1x1 7FA combined cycle unit in 2020, a brownfield IGCC unit in 2022, a greenfield LMS100 CT in 2023, and a second greenfield LMS100 CT in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $14,427.7 and $14,459.1 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $31.4 million over the evaluation period.

| Table C.6-9 High and Low Allowance Prices All Prices in Nominal Dollars |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | High Sensitivity |  |  | Low Sensitivity |  |  |
|  | SO2 ($/ton) | NOx ($/ton) | Hg ($/lb) | SO2 ($/ton) | NOx ($/ton) | Hg ($/lb) |
| 2009 | -- | $2,864 | -- | -- | $1,718 | -- |
| 2010 | $480 | $3,994 | $21,103 | $288 | $2,397 | $12,662 |
| 2011 | $490 | $4,189 | $21,491 | $294 | $2,513 | $12,894 |
| 2012 | $566 | $4,358 | $17,393 | $340 | $2,615 | $10,436 |
| 2013 | $581 | $4,463 | $22,743 | $348 | $2,678 | $13,646 |
| 2014 | $754 | $4,834 | $13,549 | $452 | $2,900 | $8,129 |
| 2015 | $1,075 | $7,721 | $26,165 | $645 | $4,632 | $15,699 |
| 2016 | $1,247 | $8,346 | $17,456 | $748 | $5,008 | $10,473 |
| 2017 | $1,398 | $7,163 | $16,616 | $839 | $4,298 | $9,970 |
| 2018 | $1,465 | $7,413 | $33,133 | $879 | $4,448 | $19,880 |
| 2019 | $1,493 | $9,725 | $32,251 | $896 | $5,835 | $19,351 |
| 2020 | $1,629 | $11,726 | $33,057 | $978 | $7,036 | $19,834 |
| 2021 | $1,778 | $11,146 | $36,152 | $1,067 | $6,688 | $21,691 |
| 2022 | $1,913 | $10,650 | $38,114 | $1,148 | $6,390 | $22,869 |
| 2023 | $2,076 | $13,676 | $69,280 | $1,246 | $8,206 | $41,568 |
| 2024 | $2,379 | $20,578 | $71,286 | $1,427 | $12,347 | $42,771 |
| 2025 | $2,437 | $22,318 | $113,955 | $1,462 | $13,391 | $68,373 |
| 2026 | $2,479 | $24,131 | $125,244 | $1,487 | $14,479 | $75,146 |
| 2027 | $2,621 | $26,022 | $137,025 | $1,573 | $15,613 | $82,215 |
| 2028 | $2,769 | $27,991 | $149,318 | $1,661 | $16,795 | $89,591 |
| 2029 | $2,923 | $30,043 | $162,139 | $1,754 | $18,026 | $97,284 |
| 2030 | $3,082 | $32,180 | $175,509 | $1,849 | $19,308 | $105,305 |
| 2031 | $3,250 | $34,469 | $189,980 | $1,950 | $20,681 | $113,988 |
| 2032 | $3,428 | $36,921 | $205,645 | $2,057 | $22,153 | $123,387 |
| 2033 | $3,615 | $39,547 | $222,602 | $2,169 | $23,728 | $133,561 |
| 2034 | $3,812 | $42,360 | $240,956 | $2,287 | $25,416 | $144,574 |
| 2035 | $4,021 | $45,373 | $260,824 | $2,412 | $27,224 | $156,495 |

| Table C.6-10 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Existing Units – High Allowance Prices (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Kennedy CT 7 | Northside ST 1 | Northside ST 2 | Northside ST 3 | Northside CTs | Brandy Branch CT 1 | Brandy Branch CC | SJRPP ST 1 | SJRPP ST 2 | Scherer ST 4 |
| 2009 | $0.09 | $0.10 | $0.10 | $0.43 | $0.46 | $0.07 | $0.02 | $0.09 | $0.09 | $0.09 |
| 2010 | $0.12 | $0.20 | $0.20 | $0.87 | $0.64 | $0.10 | $0.03 | $0.19 | $0.19 | $0.21 |
| 2011 | $0.13 | $0.21 | $0.21 | $0.90 | $0.67 | $0.10 | $0.04 | $0.20 | $0.20 | $0.22 |
| 2012 | $0.13 | $0.22 | $0.22 | $0.97 | $0.70 | $0.11 | $0.04 | $0.20 | $0.20 | $0.21 |
| 2013 | $0.13 | $0.23 | $0.23 | $1.00 | $0.72 | $0.11 | $0.04 | $0.21 | $0.21 | $0.24 |
| 2014 | $0.15 | $0.24 | $0.24 | $1.15 | $0.78 | $0.12 | $0.04 | $0.21 | $0.21 | $0.21 |
| 2015 | $0.23 | $0.38 | $0.38 | $1.77 | $1.24 | $0.19 | $0.07 | $0.34 | $0.34 | $0.36 |
| 2016 | $0.25 | $0.40 | $0.40 | $1.96 | $1.34 | $0.20 | $0.08 | $0.35 | $0.35 | $0.35 |
| 2017 | $0.22 | $0.37 | $0.37 | $1.86 | $1.15 | $0.18 | $0.07 | $0.32 | $0.32 | $0.31 |
| 2018 | $0.22 | $0.41 | $0.41 | $1.94 | $1.19 | $0.18 | $0.07 | $0.37 | $0.37 | $0.38 |
| 2019 | $0.29 | $0.49 | $0.49 | $2.30 | $1.56 | $0.24 | $0.09 | $0.43 | $0.43 | $0.45 |
| 2020 | $0.35 | $0.57 | $0.57 | $2.68 | $1.88 | $0.29 | $0.10 | $0.50 | $0.50 | $0.52 |
| 2021 | $0.34 | $0.56 | $0.57 | $2.68 | $1.79 | $0.27 | $0.10 | $0.50 | $0.50 | $0.51 |
| 2022 | $0.32 | $0.56 | $0.56 | $2.68 | $1.71 | $0.26 | $0.10 | $0.50 | $0.50 | $0.51 |
| 2023 | $0.41 | $0.72 | $0.72 | $3.22 | $2.19 | $0.34 | $0.12 | $0.66 | $0.66 | $0.73 |
| 2024 | $0.62 | $0.98 | $0.98 | $4.43 | $3.30 | $0.50 | $0.17 | $0.89 | $0.89 | $0.95 |
| 2025 | $0.67 | $1.11 | $1.11 | $4.72 | $3.58 | $0.54 | $0.19 | $1.03 | $1.03 | $1.17 |
| 2026 | $0.72 | $1.19 | $1.19 | $5.02 | $3.87 | $0.59 | $0.20 | $1.11 | $1.11 | $1.27 |
| 2027 | $0.78 | $1.28 | $1.29 | $5.38 | $4.17 | $0.63 | $0.21 | $1.20 | $1.20 | $1.38 |
| 2028 | $0.84 | $1.38 | $1.38 | $5.76 | $4.49 | $0.68 | $0.23 | $1.29 | $1.29 | $1.49 |
| 2029 | $0.90 | $1.48 | $1.48 | $6.16 | $4.82 | $0.73 | $0.24 | $1.39 | $1.39 | $1.61 |
| 2030 | $0.96 | $1.58 | $1.59 | $6.57 | $5.16 | $0.78 | $0.26 | $1.49 | $1.49 | $1.73 |
| 2031 | $1.03 | $1.70 | $1.70 | $7.01 | $5.52 | $0.84 | $0.28 | $1.60 | $1.60 | $1.86 |
| 2032 | $1.11 | $1.82 | $1.82 | $7.47 | $5.92 | $0.90 | $0.30 | $1.71 | $1.71 | $2.00 |
| 2033 | $1.19 | $1.95 | $1.95 | $7.97 | $6.34 | $0.96 | $0.32 | $1.83 | $1.83 | $2.15 |
| 2034 | $1.27 | $2.08 | $2.09 | $8.51 | $6.79 | $1.03 | $0.34 | $1.97 | $1.97 | $2.31 |
| 2035 | $1.36 | $2.23 | $2.24 | $9.08 | $7.27 | $1.10 | $0.36 | $2.11 | $2.11 | $2.48 |

| Table C.6-11 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Candidate Units – High Allowance Prices (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LMS100 CT | 7FA CT | 1x1 7FA CC | TEC | CFB (80 percent petcoke 20 percent coal) | CFB (100 percent coal) | IGCC (100 percent petcoke) |
| 2009 | $0.01 | $0.01 | $0.01 | $0.10 | $0.10 | $0.13 | $0.09 |
| 2010 | $0.01 | $0.01 | $0.01 | $0.19 | $0.20 | $0.24 | $0.13 |
| 2011 | $0.02 | $0.02 | $0.02 | $0.20 | $0.21 | $0.25 | $0.13 |
| 2012 | $0.02 | $0.02 | $0.02 | $0.20 | $0.21 | $0.25 | $0.14 |
| 2013 | $0.02 | $0.02 | $0.02 | $0.21 | $0.23 | $0.27 | $0.14 |
| 2014 | $0.02 | $0.02 | $0.02 | $0.22 | $0.24 | $0.28 | $0.15 |
| 2015 | $0.03 | $0.03 | $0.03 | $0.36 | $0.38 | $0.45 | $0.24 |
| 2016 | $0.03 | $0.03 | $0.03 | $0.37 | $0.40 | $0.47 | $0.26 |
| 2017 | $0.03 | $0.03 | $0.03 | $0.34 | $0.36 | $0.42 | $0.23 |
| 2018 | $0.03 | $0.03 | $0.03 | $0.37 | $0.40 | $0.47 | $0.24 |
| 2019 | $0.04 | $0.04 | $0.04 | $0.45 | $0.48 | $0.57 | $0.31 |
| 2020 | $0.04 | $0.04 | $0.04 | $0.53 | $0.56 | $0.67 | $0.37 |
| 2021 | $0.04 | $0.04 | $0.04 | $0.52 | $0.56 | $0.66 | $0.35 |
| 2022 | $0.04 | $0.04 | $0.04 | $0.51 | $0.55 | $0.64 | $0.34 |
| 2023 | $0.05 | $0.05 | $0.05 | $0.67 | $0.71 | $0.84 | $0.44 |
| 2024 | $0.07 | $0.07 | $0.08 | $0.93 | $0.98 | $1.17 | $0.65 |
| 2025 | $0.08 | $0.08 | $0.08 | $1.05 | $1.11 | $1.31 | $0.71 |
| 2026 | $0.09 | $0.09 | $0.09 | $1.13 | $1.19 | $1.42 | $0.77 |
| 2027 | $0.09 | $0.09 | $0.10 | $1.22 | $1.29 | $1.53 | $0.83 |
| 2028 | $0.10 | $0.10 | $0.10 | $1.31 | $1.38 | $1.64 | $0.89 |
| 2029 | $0.11 | $0.11 | $0.11 | $1.41 | $1.48 | $1.76 | $0.96 |
| 2030 | $0.12 | $0.12 | $0.12 | $1.51 | $1.59 | $1.89 | $1.02 |
| 2031 | $0.12 | $0.12 | $0.13 | $1.62 | $1.70 | $2.02 | $1.10 |
| 2032 | $0.13 | $0.13 | $0.14 | $1.73 | $1.82 | $2.17 | $1.17 |
| 2033 | $0.14 | $0.14 | $0.15 | $1.86 | $1.95 | $2.32 | $1.26 |
| 2034 | $0.15 | $0.15 | $0.16 | $1.99 | $2.09 | $2.49 | $1.35 |
| 2035 | $0.16 | $0.16 | $0.17 | $2.13 | $2.24 | $2.67 | $1.44 |

C.6.1.8  Low Emissions Allowance Prices

In the low emission allowance price sensitivity case, the base case allowance price forecasts provided by Hill & Associates were decreased by 25 percent on an annual basis, while the fuel price forecasts were left unchanged from those provided by Hill & Associates in the base case.  Decreasing the allowance prices results in a lower fuel cost adder for the fuels being burned in existing and candidate generating units.  The decrease in allowance prices reduces the economic incentive to operate units with lower emissions rates for electric generation, and also results in lower CPWCs relative to the base case economic analysis.  Table C.6-9 presents the emissions allowance prices used in the low emissions allowance price sensitivity analysis.  Tables C.6-12 and C.6-13 present the emissions cost adders included for JEA’s existing and candidate units, respectively, for the low emissions allowance price sensitivity.

In the low emissions allowance price scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield LMS100 CT in 2022, and a brownfield IGCC unit in 2023.  The optimal capacity expansion plan without participation in TEC consists of a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a second brownfield LMS100 CT in 2019, a brownfield 1x1 7FA combined cycle unit in 2020, a brownfield IGCC unit in 2022, a greenfield LMS100 CT in 2023, and a second greenfield LMS100 CT in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $13,850.4 and $13,896.7 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $46.3 million over the evaluation period.

C.6.1.9  Carbon Dioxide Regulations Sensitivity

This sensitivity, which is presented for information purposes only, considers the potential economic impact associated with a regulatory environment in which emissions of CO2 would be subject to a cap-and-trade program, similar to that contemplated under CAIR and CAMR.  To date, the United States has not mandated any reductions in CO2 emissions through nationwide environmental regulations.  However, in the last few years, legislation has been proposed suggesting various approaches to regulating CO2 emissions in the United States.  Section A.4.0 presented a description of Hill & Associates’ assumptions utilized in developing the fuel price forecast and corresponding emissions

| Table C.6-12 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Existing Units – Low Allowance Prices (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Kennedy CT 7 | Northside ST 1 | Northside ST 2 | Northside ST 3 | Northside CTs | Brandy Branch CT 1 | Brandy Branch CC | SJRPP ST 1 | SJRPP ST 2 | Scherer ST 4 |
| 2009 | $0.05 | $0.06 | $0.06 | $0.26 | $0.27 | $0.04 | $0.01 | $0.05 | $0.05 | $0.05 |
| 2010 | $0.07 | $0.10 | $0.10 | $0.36 | $0.38 | $0.06 | $0.02 | $0.10 | $0.10 | $0.12 |
| 2011 | $0.08 | $0.13 | $0.13 | $0.54 | $0.40 | $0.06 | $0.02 | $0.12 | $0.12 | $0.13 |
| 2012 | $0.08 | $0.13 | $0.13 | $0.58 | $0.42 | $0.06 | $0.02 | $0.12 | $0.12 | $0.13 |
| 2013 | $0.08 | $0.14 | $0.14 | $0.60 | $0.43 | $0.07 | $0.02 | $0.13 | $0.13 | $0.14 |
| 2014 | $0.09 | $0.14 | $0.14 | $0.69 | $0.47 | $0.07 | $0.03 | $0.13 | $0.13 | $0.13 |
| 2015 | $0.14 | $0.23 | $0.23 | $1.06 | $0.74 | $0.11 | $0.04 | $0.20 | $0.20 | $0.21 |
| 2016 | $0.15 | $0.24 | $0.24 | $1.17 | $0.80 | $0.12 | $0.05 | $0.21 | $0.21 | $0.21 |
| 2017 | $0.13 | $0.22 | $0.22 | $1.12 | $0.69 | $0.11 | $0.04 | $0.19 | $0.19 | $0.19 |
| 2018 | $0.13 | $0.24 | $0.25 | $1.16 | $0.71 | $0.11 | $0.04 | $0.22 | $0.22 | $0.23 |
| 2019 | $0.18 | $0.29 | $0.29 | $1.38 | $0.94 | $0.14 | $0.05 | $0.26 | $0.26 | $0.27 |
| 2020 | $0.21 | $0.34 | $0.34 | $1.61 | $1.13 | $0.17 | $0.06 | $0.30 | $0.30 | $0.31 |
| 2021 | $0.20 | $0.34 | $0.34 | $1.61 | $1.07 | $0.16 | $0.06 | $0.30 | $0.30 | $0.31 |
| 2022 | $0.19 | $0.33 | $0.34 | $1.61 | $1.03 | $0.16 | $0.06 | $0.30 | $0.30 | $0.31 |
| 2023 | $0.25 | $0.43 | $0.43 | $1.93 | $1.32 | $0.20 | $0.07 | $0.40 | $0.40 | $0.44 |
| 2024 | $0.37 | $0.59 | $0.59 | $2.66 | $1.98 | $0.30 | $0.10 | $0.53 | $0.53 | $0.57 |
| 2025 | $0.40 | $0.66 | $0.67 | $2.83 | $2.15 | $0.33 | $0.11 | $0.62 | $0.62 | $0.70 |
| 2026 | $0.43 | $0.71 | $0.72 | $3.01 | $2.32 | $0.35 | $0.12 | $0.67 | $0.67 | $0.76 |
| 2027 | $0.47 | $0.77 | $0.77 | $3.23 | $2.50 | $0.38 | $0.13 | $0.72 | $0.72 | $0.83 |
| 2028 | $0.50 | $0.83 | $0.83 | $3.46 | $2.69 | $0.41 | $0.14 | $0.78 | $0.78 | $0.90 |
| 2029 | $0.54 | $0.89 | $0.89 | $3.69 | $2.89 | $0.44 | $0.15 | $0.83 | $0.83 | $0.96 |
| 2030 | $0.58 | $0.95 | $0.95 | $3.94 | $3.09 | $0.47 | $0.16 | $0.89 | $0.89 | $1.04 |
| 2031 | $0.62 | $1.02 | $1.02 | $4.20 | $3.31 | $0.50 | $0.17 | $0.96 | $0.96 | $1.12 |
| 2032 | $0.66 | $1.09 | $1.09 | $4.48 | $3.55 | $0.54 | $0.18 | $1.03 | $1.03 | $1.20 |
| 2033 | $0.71 | $1.17 | $1.17 | $4.78 | $3.80 | $0.58 | $0.19 | $1.10 | $1.10 | $1.29 |
| 2034 | $0.76 | $1.25 | $1.25 | $5.10 | $4.07 | $0.62 | $0.20 | $1.18 | $1.18 | $1.39 |
| 2035 | $0.82 | $1.34 | $1.34 | $5.45 | $4.36 | $0.66 | $0.22 | $1.27 | $1.27 | $1.49 |

| Table C.6-13 Combined SO2, NOx, and Hg Emissions Cost Adders for JEA’s Candidate Units – Low Allowance Prices (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LMS100 CT | 7FA CT | 1x1 7FA CC | TEC | CFB (80 percent petcoke 20 percent coal) | CFB (100 percent coal) | IGCC (100 percent petcoke) |
| 2009 | $0.01 | $0.01 | $0.01 | $0.06 | $0.06 | $0.08 | $0.05 |
| 2010 | $0.01 | $0.01 | $0.01 | $0.10 | $0.10 | $0.13 | $0.07 |
| 2011 | $0.01 | $0.01 | $0.01 | $0.12 | $0.13 | $0.15 | $0.08 |
| 2012 | $0.01 | $0.01 | $0.01 | $0.12 | $0.13 | $0.15 | $0.08 |
| 2013 | $0.01 | $0.01 | $0.01 | $0.13 | $0.14 | $0.16 | $0.09 |
| 2014 | $0.01 | $0.01 | $0.01 | $0.13 | $0.14 | $0.17 | $0.09 |
| 2015 | $0.02 | $0.02 | $0.02 | $0.21 | $0.23 | $0.27 | $0.15 |
| 2016 | $0.02 | $0.02 | $0.02 | $0.22 | $0.24 | $0.28 | $0.16 |
| 2017 | $0.02 | $0.02 | $0.02 | $0.20 | $0.22 | $0.25 | $0.14 |
| 2018 | $0.02 | $0.02 | $0.02 | $0.22 | $0.24 | $0.28 | $0.14 |
| 2019 | $0.02 | $0.02 | $0.02 | $0.27 | $0.29 | $0.34 | $0.19 |
| 2020 | $0.03 | $0.03 | $0.03 | $0.32 | $0.34 | $0.40 | $0.22 |
| 2021 | $0.02 | $0.02 | $0.02 | $0.31 | $0.33 | $0.39 | $0.21 |
| 2022 | $0.02 | $0.02 | $0.02 | $0.31 | $0.33 | $0.39 | $0.20 |
| 2023 | $0.03 | $0.03 | $0.03 | $0.40 | $0.43 | $0.50 | $0.26 |
| 2024 | $0.04 | $0.04 | $0.05 | $0.56 | $0.59 | $0.70 | $0.39 |
| 2025 | $0.05 | $0.05 | $0.05 | $0.63 | $0.67 | $0.79 | $0.43 |
| 2026 | $0.05 | $0.05 | $0.05 | $0.68 | $0.72 | $0.85 | $0.46 |
| 2027 | $0.06 | $0.06 | $0.06 | $0.73 | $0.77 | $0.92 | $0.50 |
| 2028 | $0.06 | $0.06 | $0.06 | $0.79 | $0.83 | $0.99 | $0.53 |
| 2029 | $0.07 | $0.07 | $0.07 | $0.85 | $0.89 | $1.06 | $0.57 |
| 2030 | $0.07 | $0.07 | $0.07 | $0.91 | $0.95 | $1.13 | $0.61 |
| 2031 | $0.07 | $0.07 | $0.08 | $0.97 | $1.02 | $1.21 | $0.66 |
| 2032 | $0.08 | $0.08 | $0.08 | $1.04 | $1.09 | $1.30 | $0.70 |
| 2033 | $0.09 | $0.09 | $0.09 | $1.12 | $1.17 | $1.39 | $0.75 |
| 2034 | $0.09 | $0.09 | $0.09 | $1.19 | $1.26 | $1.49 | $0.81 |
| 2035 | $0.10 | $0.10 | $0.10 | $1.28 | $1.34 | $1.60 | $0.87 |

allowance price forecasts for a scenario in which CO2 emissions are regulated and a cap-and-trade market evolves for CO2 allowances.  As described in Section A.4.0 and discussed further in Section A.5.0, the assumptions supporting Hill & Associates’ regulated-CO2 sensitivity case fuel and emissions allowance price forecasts are based on the utility industry complying with the proposed McCain-Lieberman Climate Stewardship Act of 2005 (S. 342, introduced to the 109th Congress).

Similar to the methodology described throughout this Application for consideration of the SO2, NOx, and Hg emissions allowance price forecasts, adders for the regulated-CO2 emissions allowance price forecasts were developed for each existing and candidate unit being considered.  Tables C.6-14 and C.6-15 present the CO2 cost adders for JEA’s existing and candidate units, respectively, for the CO2 regulation sensitivity.  Tables C.6-16 and C.6-17 present the combined adders for CO2, SO2, NOx, and Hg for JEA’s existing and candidate units, respectively, for the CO2 regulation sensitivity.  Tables C.6-14 through C.6-17 were developed utilizing the emissions allowance prices developed by Hill & Associates for the CO2 regulation sensitivity, which are included in Section A.5.0.

Under this scenario, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a second greenfield LMS100 CT in 2022, and a brownfield 1x1 7FA combined cycle unit in 2023.  The optimal capacity expansion plan without participation in TEC consists of a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a second brownfield LMS100 CT in 2019, a brownfield 1x1 7FA combined cycle unit in 2020, a greenfield CFB in 2022, a greenfield LMS100 CT in 2023, and a second greenfield LMS100 CT in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $15,659.2 and $15,712.6 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $53.4 million over the evaluation period.

C.6.1.10  Summary of the Sensitivity Cases for Input Parameters

Table C.6-18 summarizes the results of the sensitivity analyses described in this section.  Appendix C.1 presents the CPWC summary sheets for all of the cases presented in Table C.6-18.  The optimal capacity expansion plan with participation in TEC in 2012 was the least-cost plan in each of the scenarios.  Overall, these results demonstrate the robustness and flexibility of the expansion plan with TEC to overcome variations and deviations from the base case assumptions.

| Table C.6-14 CO2 Emissions Adders for JEA’s Existing Units – Regulated-CO2 Sensitivity Case (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Kennedy CT 7 | Northside ST 1 | Northside ST 2 | Northside ST 3 | Northside CTs | Brandy Branch CT 1 | Brandy Branch CC | SJRPP ST 1 | SJRPP ST 2 | Scherer ST 4 |
| 2009 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 |
| 2010 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 |
| 2011 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 |
| 2012 | $0.29 | $0.52 | $0.59 | $0.36 | $0.29 | $0.29 | $0.29 | $0.52 | $0.52 | $0.53 |
| 2013 | $0.59 | $1.06 | $1.20 | $0.74 | $0.59 | $0.59 | $0.59 | $1.06 | $1.06 | $1.09 |
| 2014 | $0.78 | $1.39 | $1.59 | $0.98 | $0.78 | $0.78 | $0.78 | $1.39 | $1.39 | $1.44 |
| 2015 | $0.74 | $1.32 | $1.50 | $0.93 | $0.74 | $0.74 | $0.74 | $1.32 | $1.32 | $1.36 |
| 2016 | $0.77 | $1.39 | $1.58 | $0.98 | $0.77 | $0.77 | $0.77 | $1.39 | $1.39 | $1.43 |
| 2017 | $0.69 | $1.23 | $1.40 | $0.86 | $0.69 | $0.69 | $0.69 | $1.23 | $1.23 | $1.27 |
| 2018 | $0.19 | $0.34 | $0.39 | $0.24 | $0.19 | $0.19 | $0.19 | $0.34 | $0.34 | $0.36 |
| 2019 | $0.28 | $0.50 | $0.57 | $0.35 | $0.28 | $0.28 | $0.28 | $0.50 | $0.50 | $0.52 |
| 2020 | $0.21 | $0.38 | $0.43 | $0.27 | $0.21 | $0.21 | $0.21 | $0.38 | $0.38 | $0.39 |
| 2021 | $0.25 | $0.45 | $0.52 | $0.32 | $0.25 | $0.25 | $0.25 | $0.45 | $0.45 | $0.47 |
| 2022 | $0.55 | $0.98 | $1.11 | $0.69 | $0.55 | $0.55 | $0.55 | $0.98 | $0.98 | $1.01 |
| 2023 | $0.71 | $1.27 | $1.45 | $0.89 | $0.71 | $0.71 | $0.71 | $1.27 | $1.27 | $1.31 |
| 2024 | $0.56 | $1.01 | $1.15 | $0.71 | $0.56 | $0.56 | $0.56 | $1.01 | $1.01 | $1.04 |
| 2025 | $0.65 | $1.17 | $1.33 | $0.82 | $0.65 | $0.65 | $0.65 | $1.17 | $1.17 | $1.21 |
| 2026 | $0.70 | $1.25 | $1.42 | $0.88 | $0.70 | $0.70 | $0.70 | $1.25 | $1.25 | $1.29 |
| 2027 | $0.77 | $1.38 | $1.57 | $0.97 | $0.77 | $0.77 | $0.77 | $1.38 | $1.38 | $1.43 |
| 2028 | $0.85 | $1.52 | $1.73 | $1.07 | $0.85 | $0.85 | $0.85 | $1.52 | $1.52 | $1.57 |
| 2029 | $0.93 | $1.67 | $1.90 | $1.17 | $0.93 | $0.93 | $0.93 | $1.67 | $1.67 | $1.72 |
| 2030 | $1.01 | $1.82 | $2.07 | $1.28 | $1.01 | $1.01 | $1.01 | $1.82 | $1.82 | $1.88 |
| 2031 | $1.10 | $1.98 | $2.25 | $1.39 | $1.10 | $1.10 | $1.10 | $1.98 | $1.98 | $2.05 |
| 2032 | $1.20 | $2.16 | $2.46 | $1.52 | $1.20 | $1.20 | $1.20 | $2.16 | $2.16 | $2.23 |
| 2033 | $1.31 | $2.35 | $2.68 | $1.65 | $1.31 | $1.31 | $1.31 | $2.35 | $2.35 | $2.43 |
| 2034 | $1.43 | $2.57 | $2.92 | $1.80 | $1.43 | $1.43 | $1.43 | $2.57 | $2.57 | $2.65 |
| 2035 | $1.56 | $2.80 | $3.18 | $1.97 | $1.56 | $1.56 | $1.56 | $2.80 | $2.80 | $2.89 |

| Table C.6-15 CO2 Emissions Adders for JEA’s Candidate Units – Regulated-CO2 Sensitivity Case (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LMS100 CT | 7FA CT | 1x1 7FA CC | TEC | CFB (80 percent petcoke 20 percent coal) | CFB (100 percent coal) | IGCC (100 percent petcoke) |
| 2009 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 |
| 2010 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 |
| 2011 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 | $0.00 |
| 2012 | $0.29 | $0.29 | $0.29 | $0.53 | $0.52 | $0.52 | $0.55 |
| 2013 | $0.59 | $0.59 | $0.59 | $1.09 | $1.07 | $1.07 | $1.13 |
| 2014 | $0.78 | $0.78 | $0.78 | $1.43 | $1.41 | $1.41 | $1.49 |
| 2015 | $0.74 | $0.74 | $0.74 | $1.35 | $1.33 | $1.33 | $1.41 |
| 2016 | $0.77 | $0.77 | $0.77 | $1.42 | $1.40 | $1.40 | $1.48 |
| 2017 | $0.69 | $0.69 | $0.69 | $1.26 | $1.24 | $1.24 | $1.31 |
| 2018 | $0.19 | $0.19 | $0.19 | $0.35 | $0.35 | $0.35 | $0.37 |
| 2019 | $0.28 | $0.28 | $0.28 | $0.52 | $0.51 | $0.51 | $0.54 |
| 2020 | $0.21 | $0.21 | $0.21 | $0.39 | $0.39 | $0.39 | $0.41 |
| 2021 | $0.25 | $0.25 | $0.25 | $0.47 | $0.46 | $0.46 | $0.49 |
| 2022 | $0.55 | $0.55 | $0.55 | $1.00 | $0.99 | $0.99 | $1.05 |
| 2023 | $0.71 | $0.71 | $0.71 | $1.30 | $1.28 | $1.28 | $1.36 |
| 2024 | $0.56 | $0.56 | $0.56 | $1.04 | $1.02 | $1.02 | $1.08 |
| 2025 | $0.65 | $0.65 | $0.65 | $1.20 | $1.18 | $1.18 | $1.25 |
| 2026 | $0.70 | $0.70 | $0.70 | $1.28 | $1.26 | $1.26 | $1.34 |
| 2027 | $0.77 | $0.77 | $0.77 | $1.42 | $1.40 | $1.40 | $1.48 |
| 2028 | $0.85 | $0.85 | $0.85 | $1.56 | $1.54 | $1.54 | $1.63 |
| 2029 | $0.93 | $0.93 | $0.93 | $1.71 | $1.68 | $1.68 | $1.78 |
| 2030 | $1.01 | $1.01 | $1.01 | $1.86 | $1.83 | $1.83 | $1.94 |
| 2031 | $1.10 | $1.10 | $1.10 | $2.03 | $2.00 | $2.00 | $2.12 |
| 2032 | $1.20 | $1.20 | $1.20 | $2.21 | $2.18 | $2.18 | $2.31 |
| 2033 | $1.31 | $1.31 | $1.31 | $2.41 | $2.38 | $2.38 | $2.52 |
| 2034 | $1.43 | $1.43 | $1.43 | $2.63 | $2.59 | $2.59 | $2.74 |
| 2035 | $1.56 | $1.56 | $1.56 | $2.87 | $2.82 | $2.82 | $2.99 |

| Table C.6-16 Combined CO2, SO2, NOx, and Hg Emissions Cost Adders for JEA’s Existing Units – Regulated-CO2 Sensitivity Case (Nominal $/MBtu) |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | Kennedy CT 7 | Northside ST 1 | Northside ST 2 | Northside ST 3 | Northside CTs | Brandy Branch CT 1 | Brandy Branch CC | SJRPP ST 1 | SJRPP ST 2 | Scherer ST 4 |
| 2009 | $0.05 | $0.06 | $0.06 | $0.28 | $0.29 | $0.04 | $0.01 | $0.06 | $0.06 | $0.06 |
| 2010 | $0.07 | $0.12 | $0.13 | $0.52 | $0.38 | $0.06 | $0.02 | $0.12 | $0.12 | $0.14 |
| 2011 | $0.07 | $0.13 | $0.13 | $0.55 | $0.39 | $0.06 | $0.02 | $0.12 | $0.12 | $0.14 |
| 2012 | $0.35 | $0.63 | $0.70 | $0.83 | $0.63 | $0.34 | $0.31 | $0.62 | $0.62 | $0.65 |
| 2013 | $0.66 | $1.19 | $1.33 | $1.28 | $0.94 | $0.64 | $0.61 | $1.18 | $1.18 | $1.23 |
| 2014 | $0.84 | $1.50 | $1.69 | $1.47 | $1.09 | $0.83 | $0.80 | $1.49 | $1.49 | $1.55 |
| 2015 | $0.86 | $1.52 | $1.70 | $1.82 | $1.43 | $0.84 | $0.77 | $1.51 | $1.51 | $1.57 |
| 2016 | $0.91 | $1.60 | $1.79 | $1.95 | $1.50 | $0.88 | $0.81 | $1.57 | $1.57 | $1.63 |
| 2017 | $0.83 | $1.46 | $1.63 | $1.93 | $1.48 | $0.81 | $0.73 | $1.43 | $1.43 | $1.48 |
| 2018 | $0.32 | $0.57 | $0.62 | $1.22 | $0.88 | $0.30 | $0.23 | $0.55 | $0.55 | $0.59 |
| 2019 | $0.41 | $0.73 | $0.80 | $1.35 | $0.98 | $0.39 | $0.32 | $0.72 | $0.72 | $0.76 |
| 2020 | $0.36 | $0.64 | $0.69 | $1.40 | $1.01 | $0.33 | $0.26 | $0.62 | $0.62 | $0.65 |
| 2021 | $0.39 | $0.70 | $0.76 | $1.41 | $0.98 | $0.36 | $0.29 | $0.68 | $0.68 | $0.72 |
| 2022 | $0.68 | $1.23 | $1.37 | $1.83 | $1.27 | $0.66 | $0.59 | $1.21 | $1.21 | $1.27 |
| 2023 | $0.86 | $1.56 | $1.74 | $2.17 | $1.53 | $0.83 | $0.76 | $1.54 | $1.54 | $1.62 |
| 2024 | $0.86 | $1.46 | $1.60 | $2.75 | $2.13 | $0.80 | $0.64 | $1.42 | $1.42 | $1.48 |
| 2025 | $0.96 | $1.69 | $1.85 | $2.96 | $2.31 | $0.91 | $0.74 | $1.66 | $1.66 | $1.78 |
| 2026 | $1.03 | $1.81 | $1.98 | $3.16 | $2.50 | $0.97 | $0.79 | $1.78 | $1.78 | $1.91 |
| 2027 | $1.13 | $1.98 | $2.18 | $3.41 | $2.71 | $1.07 | $0.87 | $1.95 | $1.95 | $2.10 |
| 2028 | $1.24 | $2.17 | $2.38 | $3.68 | $2.93 | $1.17 | $0.95 | $2.13 | $2.13 | $2.30 |
| 2029 | $1.35 | $2.36 | $2.59 | $3.97 | $3.17 | $1.27 | $1.04 | $2.32 | $2.32 | $2.50 |
| 2030 | $1.46 | $2.56 | $2.81 | $4.26 | $3.41 | $1.38 | $1.13 | $2.52 | $2.52 | $2.72 |
| 2031 | $1.58 | $2.78 | $3.05 | $4.57 | $3.67 | $1.49 | $1.23 | $2.74 | $2.74 | $2.95 |
| 2032 | $1.72 | $3.01 | $3.31 | $4.91 | $3.95 | $1.62 | $1.34 | $2.97 | $2.97 | $3.20 |
| 2033 | $1.86 | $3.27 | $3.59 | $5.28 | $4.26 | $1.76 | $1.46 | $3.22 | $3.22 | $3.48 |
| 2034 | $2.02 | $3.54 | $3.90 | $5.67 | $4.59 | $1.91 | $1.59 | $3.50 | $3.50 | $3.78 |
| 2035 | $2.19 | $3.85 | $4.23 | $6.09 | $4.94 | $2.07 | $1.73 | $3.80 | $3.80 | $4.10 |

| Table C.6-17 Combined CO2, SO2, NOx, and Hg Emissions Cost Adders for JEA’s Candidate Units – Regulated-CO2 Sensitivity Case (Nominal $/MBtu) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Calendar Year | LMS100 CT | 7FA CT | 1x1 7FA CC | TEC | CFB (80 percent petcoke 20 percent coal) | CFB (100 percent coal) | IGCC (100 percent petcoke) |
| 2009 | $0.01 | $0.01 | $0.01 | $0.06 | $0.06 | $0.08 | $0.06 |
| 2010 | $0.01 | $0.01 | $0.01 | $0.12 | $0.12 | $0.15 | $0.08 |
| 2011 | $0.01 | $0.01 | $0.01 | $0.12 | $0.13 | $0.15 | $0.08 |
| 2012 | $0.30 | $0.30 | $0.30 | $0.63 | $0.63 | $0.65 | $0.62 |
| 2013 | $0.60 | $0.60 | $0.60 | $1.20 | $1.19 | $1.21 | $1.20 |
| 2014 | $0.79 | $0.79 | $0.79 | $1.53 | $1.51 | $1.53 | $1.55 |
| 2015 | $0.75 | $0.75 | $0.75 | $1.55 | $1.54 | $1.58 | $1.55 |
| 2016 | $0.79 | $0.79 | $0.79 | $1.62 | $1.61 | $1.65 | $1.63 |
| 2017 | $0.70 | $0.70 | $0.70 | $1.48 | $1.47 | $1.51 | $1.47 |
| 2018 | $0.21 | $0.21 | $0.21 | $0.56 | $0.57 | $0.61 | $0.51 |
| 2019 | $0.30 | $0.30 | $0.30 | $0.73 | $0.74 | $0.78 | $0.68 |
| 2020 | $0.23 | $0.23 | $0.23 | $0.63 | $0.64 | $0.68 | $0.57 |
| 2021 | $0.27 | $0.27 | $0.27 | $0.69 | $0.70 | $0.74 | $0.63 |
| 2022 | $0.56 | $0.56 | $0.56 | $1.24 | $1.24 | $1.28 | $1.19 |
| 2023 | $0.73 | $0.73 | $0.73 | $1.57 | $1.57 | $1.62 | $1.53 |
| 2024 | $0.60 | $0.60 | $0.60 | $1.47 | $1.47 | $1.56 | $1.39 |
| 2025 | $0.69 | $0.69 | $0.69 | $1.69 | $1.70 | $1.80 | $1.58 |
| 2026 | $0.74 | $0.74 | $0.74 | $1.81 | $1.82 | $1.93 | $1.70 |
| 2027 | $0.82 | $0.82 | $0.82 | $1.99 | $2.00 | $2.11 | $1.86 |
| 2028 | $0.90 | $0.90 | $0.90 | $2.18 | $2.18 | $2.31 | $2.04 |
| 2029 | $0.98 | $0.98 | $0.98 | $2.37 | $2.38 | $2.51 | $2.23 |
| 2030 | $1.07 | $1.07 | $1.07 | $2.57 | $2.58 | $2.72 | $2.42 |
| 2031 | $1.16 | $1.16 | $1.16 | $2.79 | $2.80 | $2.95 | $2.63 |
| 2032 | $1.27 | $1.27 | $1.27 | $3.03 | $3.04 | $3.20 | $2.86 |
| 2033 | $1.38 | $1.38 | $1.38 | $3.29 | $3.29 | $3.47 | $3.10 |
| 2034 | $1.50 | $1.50 | $1.50 | $3.57 | $3.57 | $3.76 | $3.37 |
| 2035 | $1.64 | $1.64 | $1.64 | $3.87 | $3.88 | $4.08 | $3.66 |

| Table C.6-18 Summary of Sensitivity Analyses (Varying Base Case Input Parameters) |  |  |  |
| --- | --- | --- | --- |
| Sensitivity Case | Expansion Plan CPWC Cost ($ million) |  |  |
|  | With TEC | Without TEC | Differential CPWC Savings with TEC |
| Base Case | $14,139.0 | $14,178.1 | $39.1 |
| High Fuel Prices | $15,521.2 | $15,580.9 | $59.7 |
| Low Fuel Prices | $12,650.7 | $12,651.3 | $0.6 |
| High Load and Energy Growth | $17,591.0 | $17,721.5 | $130.5 |
| Low Load and Energy Growth | $13,371.9 | $13,427.3 | $55.4 |
| High Capital Cost | $14,465.4 | $14,500.7 | $35.3 |
| Low Capital Cost | $13,788.2 | $13,877.7 | $89.5 |
| High Emissions Allowance Costs | $14,427.7 | $14,459.1 | $31.4 |
| Low Emissions Allowance Costs | $13,850.4 | $13,896.7 | $46.3 |
| Regulated CO2 | $15,659.2 | $15,712.6 | $53.4 |

C.6.2  External Parameter Sensitivities

The sensitivities described in this section reflect changes to the base case external parameter assumptions, including the opportunity to participate in joint development capacity additions other than TEC, consideration of different types of generating technologies to meet capacity needs, and consideration of an alternative coal source for TEC.  For each of the sensitivities described in this section, the base case input parameters (fuel prices, emissions allowance prices, load forecast, and capital cost estimates) have not been altered.

C.6.2.1  3x1 CC Joint Development Project

To demonstrate that participation in TEC in May 2012 is part of the least-cost capacity expansion plan for JEA, sensitivities were developed assuming that JEA had the option to participate in other jointly owned projects with different generating technologies.  Since participation in another jointly owned generation project would provide JEA with similar economies of scale to participation in TEC, this sensitivity allows a more comparable evaluation of the economics of different generating technologies than the base case analysis.

In this sensitivity, it was assumed that JEA would participate in a jointly owned 3x1 7FA combined cycle unit with a commercial operation date of May 1, 2012, in lieu of participation in TEC.  In this analysis, JEA would retain the same expected ownership share percentage in the 3x1 7FA combined cycle unit as in the proposed TEC, which provides JEA with a similarly sized amount of capacity compared to JEA’s share of the proposed TEC.  Section A.6.0 presented cost, performance, and availability estimates for the jointly owned 3x1 7FA combined cycle option.

The jointly owned 3x1 combined cycle unit is assumed to be located at the TEC site to make the alternative as similar as possible to TEC.  All relevant costs associated with the development of a generating alternative at the TEC site were considered and included for the 3x1 combined cycle alternative, including the community contribution assumed for TEC, and the transmission tariffs and losses described in Section C.5.0.

Table C.6-19 presents the output and performance of JEA’s share of the jointly owned 3x1 combined cycle alternative, including transmission losses.  Using the methodology described in Section C.5.0, the total annual firm transmission cost to JEA for its share of the 3x1 combined cycle alternative is $8,761,331 per year.

| Table C.6-19 JEA’s Share of a Jointly Owned 3x1 7FA Combined Cycle Unit Output and Performance Considering Transmission Losses (Average Ambient Conditions) |  |  |  |
| --- | --- | --- | --- |
| Without Transmission Losses |  | Including Transmission Losses(1) |  |
| Output (MW) | Net Plant Heat Rate (Btu/kWh) | Output (MW) | Net Plant Heat Rate (Btu/kWh) |
| 285.8 | 7,412 | 273.7 | 7,740 |
| 232.4 | 7,006 | 222.5 | 7,317 |
| 182.8 | 7,282 | 175.0 | 7,605 |
| 134.9 | 7,877 | 129.2 | 8,226 |
| 50.4 | 10,826 | 48.3 | 11,306 |
| (1)Assumes losses of 4.24 percent. |  |  |  |

JEA’s share of the fixed O&M cost for the 3x1 combined cycle alternative is $1.4 million or about $5.25 per kW-year (net after considering transmission losses) in 2006 dollars.  As described in Section C.5.0, an adder for firm natural gas transportation of $2.89 per kW-month was included to provide JEA’s system with an additional 35,305 MBtu/day of firm natural gas transportation.  Section A.6.0 presented the nonfuel

variable O&M cost for the 3x1 combined cycle before transmission losses as $4.29 per MWh.  With transmission losses considered, JEA’s net nonfuel variable O&M cost is $4.49 per MWh in 2006 dollars.

The optimal capacity expansion plan involving participation in the 3x1 combined cycle option consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield IGCC unit in 2020, a brownfield LMS100 CT in 2022, a brownfield and a greenfield LMS100 CT in 2023, and a second greenfield LMS100 CT in 2024, with a CPWC of $14,362.4 million.  A comparison of the CPWCs for this case and the base case capacity expansion plan that includes participation in TEC (presented in Section C.5.0) shows that this plan is $223.4 million higher in CPWC than the expansion plan that includes participation in TEC.

C.6.2.2  Three-Train 1x1 IGCC Joint Development Project

In this sensitivity, it was assumed that JEA would participate in a jointly owned three-train 1x1 IGCC unit with a commercial operation date of May 1, 2012, in lieu of participation in TEC.  Although it is unlikely that the Participants would construct an IGCC unit prior to 2018 for the reasons described in Sections A.6.0 and C.5.0, it is important to compare the emerging IGCC technology with the supercritical pulverized coal technology proposed for TEC in an economic analysis, to demonstrate that participation in TEC is part of the least-cost expansion plan for JEA.

In this analysis, JEA would retain the same expected ownership share percentage in the three-train 1x1 IGCC unit as in the proposed TEC, which would provide JEA with a similarly sized amount of capacity compared to JEA’s share of the proposed TEC.  Section A.6.0 presented cost, performance, and availability estimates for the jointly owned three-train 1x1 IGCC.

The jointly owned three-train 1x1 IGCC unit is assumed to be located at the TEC site to make the alternative as similar as possible to TEC.  All relevant costs associated with the development of a generating alternative at the TEC site were considered and included for the three-train 1x1 IGCC alternative, including the community contribution assumed for TEC, and the transmission tariffs and losses described in Section C.5.0.

Table C.6-20 presents the output and performance of JEA’s share of the jointly owned three-train 1x1 IGCC alternative, including transmission losses.  Using the methodology described in Section C.5.0, the total annual firm transmission cost to JEA for its share of the three-train 1x1 IGCC alternative is approximately $8,401,035 per year.  This cost is included as of May 1, 2012, and is not escalated with inflation.

| Table C.6-20 JEA’s Share of a Jointly Owned Three-Train 1x1 IGCC Unit Output and Performance Considering Transmission Losses (Average Ambient Conditions - 100 Percent Petcoke) |  |  |  |
| --- | --- | --- | --- |
| Without Transmission Losses |  | Including Transmission Losses(1) |  |
| Output (MW) | Net Plant Heat Rate (Btu/kWh) | Output (MW) | Net Plant Heat Rate (Btu/kWh) |
| 272.2 | 10,018 | 260.6 | 10,462 |
| 211.4 | 10,576 | 202.4 | 11,045 |
| 148.1 | 11,601 | 141.8 | 12,115 |
| (1)Assumes losses of 4.24 percent. |  |  |  |

JEA’s share of the fixed O&M cost for the three-train 1x1 IGCC alternative is $10.5 million or about $40.11 per kW-year (net after considering transmission losses) in 2006 dollars.  Section A.6.0 presented the nonfuel variable O&M cost for the three train 1x1 IGCC before transmission losses as $5.86 per MWh.  With transmission losses considered, JEA’s net nonfuel variable O&M cost is $6.12 per MWh in 2006 dollars.

The optimal capacity expansion plan involving participation in the three-train 1x1 IGCC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield 1x1 7FA combined cycle unit in 2020, a brownfield LMS100 CT in 2022, a second brownfield LMS100 CT in 2023, and two greenfield LMS100 CTs in 2024, with a CPWC of $14,176.1 million.  A comparison of the CPWCs for this case and the base case capacity expansion plan that includes participation in TEC (presented in Section C.5.0) shows that this plan is $37.1 million higher in CPWC than the capacity expansion plan that includes participation in TEC.

C.6.2.3  Second Jointly Owned Pulverized Coal Unit

Currently, there are no coal fired generation projects identified that JEA could participate in before TEC.  Furthermore, JEA has no firm plans for participation in a large, jointly developed pulverized coal unit in the near term.  As such, no additional pulverized coal units were considered as supply-side alternatives after construction of TEC in the base case analysis.  This sensitivity considers the possibility of joint participation in a second pulverized coal unit located at either the TEC site or another unidentified site in Florida.

The costs and performance of a second supercritical pulverized coal unit are assumed to be identical to those presented for TEC in Section A.3.0, to reflect indicative estimates for a large coal unit.  Section C.5.0 presents JEA’s share of the capital and O&M costs for TEC, which are assumed to be the same as those for the second pulverized coal option.  Since the TEC Participants would not likely engage in the construction of another pulverized coal unit with a construction schedule that overlaps the construction of TEC, the second pulverized coal unit was not assumed to be available until 2016, to allow for a 4 year construction schedule for the second potential unit.

In this sensitivity case, the optimal capacity expansion plan for the case with TEC in 2012 consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, participation in a supercritical pulverized coal unit in 2020, two brownfield LMS100 CTs in 2022, a greenfield LMS100 CT in 2023, and two additional greenfield LMS100 CTs in 2024.

The CPWC for the expansion plan with TEC and a second jointly owned pulverized coal unit is $14,109.2 million, which represents a decrease in CPWC of $29.8 million over the evaluation period, compared to the base case TEC CPWC.

C.6.2.4  All Natural Gas Capacity Expansion Plan

To develop a more complete understanding of the economics associated with the expansion plan (including JEA’s participation in TEC), a sensitivity case was developed to reflect costs associated with a capacity expansion plan that only includes natural gas fired capacity expansion alternatives.

In this scenario, POWROPT and POWRPRO were used to determine the least-cost capacity expansion plan for the case without TEC, if the CFB and IGCC supply-side alternatives are not considered as alternatives to meet JEA’s capacity needs.  This sensitivity analysis results in higher CPWCs relative to the base case expansion plans because of the higher costs of natural gas generation compared to solid fuel alternatives.

In this sensitivity case, the optimal capacity expansion plan (including only natural gas fired capacity additions) consists of a brownfield 1x1 7FA combined cycle unit in 2011, a brownfield LMS100 CT in 2013, a second brownfield LMS100 CT in 2014, a greenfield 1x1 7FA combined cycle unit in 2015, a greenfield LMS100 CT in 2020, two greenfield LMS100 CTs in 2021, a second greenfield 1x1 7FA combined cycle unit in 2022, and a fourth greenfield LMS100 CT in 2024.

The CPWC for the all natural gas capacity expansion plan is $15,055.2 million.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $916.2 million over the evaluation period.

C.6.2.5  Direct-Fired Biomass Supply-Side Alternative

This sensitivity includes the 30 MW direct-fired biomass (stoker-fired) alternative presented in Section A.6.0 as a committed unit in 2011, in the cases with and without TEC, since this is the first year that JEA would need capacity under the base case assumptions.  In the case including participation in TEC, JEA’s seasonal purchase was reduced by 30 MW, corresponding to the additional capacity provided from the direct-fired biomass alternative.

Cost and performance estimates for the direct-fired biomass alternative are presented in Section A.6.0.  The unit was modeled as a “must run” unit, without consideration of emissions allowance costs, to allow for a conservative economic analysis and because biomass emissions are highly dependent on the type of biomass utilized in power generation.

In this sensitivity case, the optimal capacity expansion plan for the case with TEC in 2012 consists of a 30 MW biomass unit in 2011, a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a second brownfield LMS100 CT in 2021, two greenfield LMS100 CTs in 2022, and a brownfield 1x1 7FA combined cycle unit in 2023.  The optimal capacity expansion plan without participation in TEC consists of a 30 MW biomass unit and a brownfield LMS100 CT in 2011, a brownfield CFB in 2012, a second brownfield CFB in 2014, a second brownfield LMS100 CT in 2019, a brownfield 1x1 7FA combined cycle unit in 2020, a brownfield IGCC unit in 2022, and two greenfield LMS100 CTs in 2024.

The CPWCs for the expansion plan with TEC and the plan without participation in TEC are $14,218.3 and $14,230.1 million, respectively.  A comparison of the CPWCs shows that the case with TEC is the least-cost plan by $11.8 million over the evaluation period.  However, compared to the base case TEC CPWC, including the 30 MW biomass resource in 2011 increases the CPWC by $79.3 million.

C.6.2.6  Powder River Basin Coal for TEC

The base case economic analysis and all other sensitivity analyses performed assume that TEC will burn a blend of Latin American coal and petcoke.  However, as described in Section A.3.0, TEC will be designed to be capable of burning blends of PRB coal and petcoke, as well as blends of Central Appalachian coal and petcoke.  This sensitivity assumes that TEC will burn a blend of PRB coal and petcoke and is based on the corresponding operating cost and performance estimates provided by Sargent & Lundy, which were presented in Section A.3.0.

Hill & Associates’ forecast of Latin American coal prices is lower than the forecasts of PRB coal prices, and the corresponding operating costs of TEC are expected to be lower when burning a blend of Latin American coal and petcoke than when burning a blend of PRB coal and petcoke.  However, this sensitivity is intended to demonstrate that the additional flexibility of TEC resulting from its capability to burn multiple types of coal allows TEC to be a cost-effective alternative, if the preferred (Latin American) coal source is unavailable for any reason.

The optimal capacity expansion plan involving operation of TEC on a blend of PRB coal and petcoke consists of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a brownfield IGCC unit in 2023, and a second greenfield LMS100 CT in 2024.  This plan has a CPWC of $14,159.5 million.  A comparison of the CPWCs for this case and the base case capacity expansion plan that includes participation in TEC (presented in Section C.5.0) shows that the plan with TEC’s operation on a blend of PRB coal and petcoke is $20.5 million higher in CPWC than the plan with TEC’s operation on a blend of Latin American coal and petcoke, but is still lower in CPWC than the base case capacity expansion plan without participation in TEC by $18.6 million over the evaluation period.

C.6.2.7  Summary of the Sensitivity Cases for External Parameters

Appendix C.1 presents the CPWC summary sheets for all of the cases presented in Table C.6-21.  The optimal capacity expansion plan with TEC in 2012 was the least-cost plan in each of the scenarios, except for the second jointly owned pulverized coal unit sensitivity.  Overall, these results demonstrate the robustness and flexibility of the expansion plan with TEC to overcome external variations and deviations from the base case assumptions.

C.6.3  Analysis of RFP Responses

As described in Section A.7.0, Southern Power Company (Southern) responded to the Participants’ RFP and provided bids for a pulverized coal unit and a 2x1 combined cycle unit.  Southern’s proposed costs and estimated performance for the units are confidential.  Although both of Southern’s bids were determined by R.W. Beck to not be least-cost to TEC on a levelized cost basis, each bid has been evaluated for JEA’s system as a sensitivity to further assess the cost-effectiveness of JEA’s participation in TEC.  This section briefly describes the bids and the resulting optimal capacity expansion plans under each scenario.

| Table C.6-21 Summary of Sensitivity Analyses (Varying External Parameters) |  |  |  |
| --- | --- | --- | --- |
| Sensitivity Case | Expansion Plan CPWC Cost ($ million) |  |  |
|  | Sensitivity Scenario | Base Case TEC in 2012 | Differential CPWC Savings of Base Case |
| 3x1 Combined Cycle Joint Development | $14,362.4 | $14,139.0 | $223.4 |
| Three-Train 1x1 IGCC Joint Development | $14,176.1 | $14,139.0 | $37.1 |
| Second Jointly Owned Pulverized Coal Unit | $14,109.2 | $14,139.0 | ($29.8) |
| All Natural Gas Capacity Expansion Plan | $15,055.2 | $14,139.0 | $916.2 |
| Biomass Supply-Side Addition with TEC | $14,218.3 | $14,139.0 | $79.3 |
| Biomass Supply-Side Addition without TEC | $14,230.1 | $14,139.0 | $91.1 |
| PRB Coal for TEC | $14,159.5 | $14,139.0 | $20.5 |

C.6.3.1  Southern’s Pulverized Coal Unit Bid

Southern’s pulverized coal unit bid was considered a committed unit for JEA, and all costs and performance for the unit were made to be consistent with Southern’s bid.  The optimal expansion plan for JEA’s system with Southern’s pulverized coal bid, which was considered a committed unit in 2012, consisted of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a brownfield IGCC unit in 2022, and a second greenfield LMS100 CT in 2024, with a CPWC of $14,626.1 million.  A comparison of CPWCs shows that the base case expansion plan with JEA’s participation in TEC is $487.1 million lower in CPWC than the expansion plan with Southern’s pulverized coal bid over the evaluation period.

C.6.3.2  Southern’s 2x1 Combined Cycle Bid

Southern’s 2x1 combined cycle unit bid was considered a committed unit for JEA, and all costs and performance for the unit were made to be consistent with Southern’s bid.  The optimal expansion plan for JEA’s system with Southern’s 2x1 combined cycle bid, which was considered a committed unit in 2012, consisted of a brownfield CFB in 2013, a second brownfield CFB in 2015, a brownfield LMS100 CT in 2020, a brownfield and a greenfield LMS100 CT in 2021, a brownfield IGCC unit in 2022, and a second greenfield LMS100 CT in 2024, with a CPWC of $14,446.7 million.  A comparison of CPWCs shows that the base case expansion plan with JEA’s participation in TEC is $307.7 million lower in CPWC than the expansion plan with Southern’s combined cycle bid over the evaluation period.

C.6.3.3	Summary of the Sensitivity Cases for JEA’s Share of the RFP

Responses

As shown in Table C.6-22, JEA’s optimal capacity expansion plan with TEC in 2012 was the least-cost plan compared to JEA’s share of both of Southern’s bids.

| Table C.6-22 Summary of JEA’s Share of Southern’s Bids |  |  |  |
| --- | --- | --- | --- |
| Sensitivity Case | Expansion Plan CPWC Cost ($ million) |  |  |
|  | Sensitivity Scenario | Base Case TEC in 2012 | Differential CPWC Savings of Base Case |
| Southern’s Pulverized Coal Unit | $14,626.1 | $14,139.0 | $487.1 |
| Southern’s 2x1 Combined Cycle Unit | $14,446.7 | $14,139.0 | $307.7 |