## F-1
Gallons of Water Pumped, Sold and Unaccounted For | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [10 empty] | Page 1 of 1
Docket No.: 060253-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2005
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
[6 empty] | * |  |  |  | Unaccounted |  | %
Month/ |  | Total Gallons |  | Corrected Gallons |  | Gallons |  | Other |  | For Water |  | Unaccounted
Year |  | Pumped |  | Pumped |  | Sold |  | Uses |  | (2)-(3)-(4) |  | For Water
_ |  | _ |  | _ |  | _ |  | _ |  | _ |  | _
2005-01-01 |  | 4.848 |  | 4.0363 |  | 3.415 |  | 0 |  | 0.62134 |  | 15.39%
2005-02-01 |  | 4.226 |  | 3.5185 |  | 3.424 |  | 0.058 |  | 0.03648 |  | 1.037%
2005-03-01 |  | 4.562 |  | 3.7982 |  | 3.415 |  | 0 |  | 0.38323 |  | 10.09%
2005-04-01 |  | 5.236 |  | 4.3594 |  | 4.212 |  | 0.041 |  | 0.10638 |  | 2.44%
2005-05-01 |  | 5.057 |  | 4.2104 |  | 4.025 |  | 0.042 |  | 0.14335 |  | 3.405%
2005-06-01 |  | 4.636 |  | 3.8598 |  | 3.534 |  | 0.047 |  | 0.27884 |  | 7.224%
2005-07-01 |  | 4.754 |  | 3.9581 |  | 3.48 |  | 0.058 |  | 0.42008 |  | 10.61%
2005-08-01 |  | 4.362 |  | 3.6317 |  | 3.588 |  | 0.041 |  | 0.0027104 |  | 0.07463%
2005-09-01 |  | 4.71 |  | 3.9214 |  | 3.775 |  | 0.067 |  | 0.079448 |  | 2.026%
2005-10-01 |  | 5.38 |  | 4.4793 |  | 3.778 |  | 0.094 |  | 0.60728 |  | 13.56%
2005-11-01 |  | 5.658 |  | 4.7107 |  | 4.348 |  | 0.065 |  | 0.29773 |  | 6.32%
2005-12-01 |  | 4.32 |  | 3.5967 |  | 3.748 |  | 0.109 |  | -0.26026 |  | -7.236%
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 57.749 |  | 48.0806 |  | 44.742 |  | 0.622 |  | 2.7166 |  | 5.65%
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)
* Total Gallons Sold includes water sold to Golden Hills and Crownwood subdivisions.
Note: Recent tests with a portable flow meter indicate that water well flow meters have been
reading high. The comparative results are:
Portable
|  |  |  | Flow |  | Flow
|  |  |  | Meter, gpm |  | Meter, gpm
| Well No. 1 |  |  | 224 |  | 192
| Well No. 2 |  |  | 439 |  | 360
| Total |  |  | 663 |  | 552
| Correction factor |  |  |  |  | 83.26%
The correction factor has been applied to the total gallons pumped in Col. (1) and the
corrected gallons are shown in Col. (2). The unaccounted for water in Col. (5) and the
% unaccounted for water in Col (6) are based on the corrected pumped water amounts.

## F-2
Gallons of Wastewater Treated | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [10 empty] | Page 1 of 1
Docket No.: 060253-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2005
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | Crownwood |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment | ADF | 3MADF
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2005-01-01 |  | 0.62 | [7 empty] | 0.62 |  | 0 | 0.02
2005-02-01 |  | 0.606 | [7 empty] | 0.606 |  | 0 | 0.021643
2005-03-01 |  | 0.737 | [7 empty] | 0.737 |  | 0 | 0.023774 | 0.021806
2005-04-01 |  | 0.693 | [7 empty] | 0.693 |  | 0 | 0.0231 | 0.022839
2005-05-01 |  | 0.629 | [7 empty] | 0.629 |  | 0 | 0.02029 | 0.022388
2005-06-01 |  | 0.628 | [7 empty] | 0.628 |  | 0 | 0.020933 | 0.021441
2005-07-01 |  | 0.714 | [7 empty] | 0.714 |  | 0 | 0.023032 | 0.021419
2005-08-01 |  | 0.67 | [7 empty] | 0.67 |  | 0 | 0.021613 | 0.021859
2005-09-01 |  | 0.556 | [7 empty] | 0.556 |  | 0 | 0.018533 | 0.021059
2005-10-01 |  | 0.619 | [7 empty] | 0.619 |  | 0 | 0.019968 | 0.020038
2005-11-01 |  | 0.597 | [7 empty] | 0.597 |  | 0 | 0.0199 | 0.019467
2005-12-01 |  | 0.642 | [7 empty] | 0.642 |  | 0 | 0.02071 | 0.020192
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 7.711 |  | 0 | [5 empty] | 7.711 |  | 0 | 0.023774 | 0.022839
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)

## F-3
Water Treatment Plant Data | [6 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [9 empty] | Schedule F-3
Docket No.: 060253-WS | [9 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [9 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [8 empty] | 600000
on the DEP operating or construction permit, provide an explanation.
2 | Maximum Day
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2005-04-30 | 221471.6
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2005-11-13 | 184837.2
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2005-11-14 | 184837.2
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2005-11-23 | 197326.2
| these days. | [6 empty] | (4) | 2005-11-17 | 202321.8
[8 empty] | (5) | 2005-11-10 | 218141.2
[9 empty] | AVERAGE | 197492.72
[9 empty] | Max Month | 157024.4344
4 | Average Daily Flow | [7 empty] | Annual | 131727.7134
5 | Required Fire Flow | [7 empty] | 500 gpm for 2 hours
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.
Note: As indicated in Schedule F-1, it was determined that flow meters were reading high.
The correction factor of 83.26%, determined in Schedule F-1, is reflected in all of the
above numbers.

## F-4
Wastewater Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [9 empty] | Schedule F-4
Docket No.: 060253-WS | [9 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [9 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
[9 empty] | _ |  | _
1. | Plant Capacity (Three Month Average Daily Flow (TMADF) | [9 empty] | 40000
The hydraulic rated capacity. If different from that shown
on the DER operating or construction permit, provide an explanation.
2. | Average Daily Flow Max Month (a) | [7 empty] | 2005-03-01 |  | 23774.1935
| Highest TMADF | [7 empty] | 2005-04-01 |  | 22839.0169
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.
2a.

## F-5
Used and Useful Calculations |  |  |  | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [5 empty] | Schedule F-5
Docket No.: 060253-WS | [5 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 770 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 330 | gpm
| Ground storage capacity, gal. |  |  |  | 0 | gallons
| Usable ground storage (90%), gal. |  |  |  | 0 | gallons
| Hydropneumatic storage capacity, gal. |  |  |  | 20000 | gallons
| Usable hydropneumatic storage capacity (33.33%), gal. |  |  |  | 6666.6667 | gallons
| Total usable storage, gal. |  |  |  | 6666.6667 | gallons
| High service pumping capacity, gpm |  |  |  | 0 | gpm
| Average day demand, maximum month |  |  |  | 157024.4344 | gpd
| Maximum day, maximum month demand, |  |  |  | 218141.2 | gpd
| Peak hour demand = 2 x max day |  |  |  | 436282.4 | gpd
| Fire flow requirement |  | 500 gpm for 2 hours |  | 60000 | gpd
| Unaccounted for water |  | 5.65% | of water pumped | 7442.7819 | gpd, avg
| Acceptable unaccounted for |  | 12.5% |  | 19777.0548 | gpd, avg
| Excess unaccounted for |  |  |  | 0 | gpd, avg
Used & Useful Analysis:
Used & useful was last set for this system in Docket No. 020071-WS. The Commission found the system
to be 100% used & useful, as it had been in past cases. There have been no significant changes in the system.
ERCs appear to be increasing somewhat at a slow, erratic pace.
This system treats water by simple chlorination. The only storage is in hydropneumatic tanks and there is
no high service pumping. All demands must be met by well pumping capacity. Used and useful is
therefore determined on the basis of instantaneous demand. For this system, all components are
considered together for purposes of determining used & useful. The current analysis supports the previous
findings that the production, treatment, pumping and storage facilities are 100% used & useful.
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand |  |  | 302.9739 | gpm
| B = | Property needed to serve five years after TY |  |  | 29.9788 | gpm
| C = | Fire flow demand |  |  | 500 | gpm
| D = | Excess Unaccounted for water |  |  | 0 | gpm
| E = | Firm Reliable Capacity |  |  | 330 | gpm
The above used and useful factor is applicable to all source of supply, pumping and treatment accounts,
as well as the land, structures and distribution resrvoir accounts.

## F-6
Used and Useful Calculations |  |  | FPSC
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) |  |  |  | Schedule F-6
Docket No.: 060253-WS |  |  |  | Page 1 of 1
Test Year Ended: December 31, 2005 |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
INPUT INFORMATION:
| Permitted capacity, Three month average daily flow (TMADF) |  |  |  | 40000 | gpd
| Annual average daily flow |  |  |  | 21126.0274 | gpd
| Maximum month, average daily flow |  |  |  | 23774.1935 | gpd
| Highest TMADF |  |  |  | 22839.0169 | gpd
Used & Useful Analysis:
Used & useful was last set for this system in Docket No. 020071-WS. The wastewater treatment system was found to
be 68.65% used & useful. Although there has been virtually no change in the customer base, the billed wastewater
gallons for the Crownwood development has decrease by 9% since the last case (TY 2001) and the BFF flows
have remained steady. Water flows for the system have also decreased. Whether this is a result of conservation or
a side effect of the 2005 hurricane season, the utility should not be penalized by assigning a U&U percentage less
than that last assigned. The plant is no less useful and the utility must be prepared for what may be a return
to previous demand levels.
| Percent Used & Useful = (A + B - C)/D x 100%, where: |  |  |  | 61.26%
|  |  | Use (see discussion above) |  | 68.65%
| A = | Peak demand, TMADF |  |  | 22839.0169 | gpd
| B = | Property needed to serve five years after TY (see Sch. F- 8 &10) |  |  | 1664.2292 | gpd
| C = | Excess treated wastewater |  |  | 0 | gpd
| D = | Permitted Capacity, TMADF |  |  | 40000 | gpd
The above used and useful factor is applicable to all treatment and disposal plant accounts.

## F-7
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [7 empty] | Schedule F-7
Docket No.: 060253-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Water Distribution System
Used & useful was last set for this system in Docket No. 020071-WS. The water distribution system was found to be
100% used & useful based on existing connections and an allowance for growth. Circumstances have not significantly
changed. No additional lots have been added. The system remains at 100% used and useful.
Wastewater Collection System
The wastewater collection system serves only the Crownwood area. In Docket No. 020071-WS , the collection
system was found to be 100% used & useful. As indicated in that docket, the area served is compact and of such
a configuration (a quadraplex development) that the collection system serving the existing buildings, although
capable of serving others, could not be any less, even if no other buildings were built.

## F-8
Margin Reserve Calculations |  |  | Florida Public Service Commission
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) |  |  |  |  | Schedule F-8
Docket No.: 060253-WS |  |  |  |  | Page 1 of 1
Test Year Ended: December 31, 2005 |  |  |  |  | Preparer: Seidman, F.
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5,F-6,F-7
Water Pumping, Treatment & Storage
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs | 10.0097 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. | 0.59899 | gpm/ERC *
| PN = | Property needed expressed in U units | 29.9788 | gpm
* Based on the 2005 Peak Hour Demand (Sch. F-5) divided 2005 ERCs (Sch F-9).
Wastewater Treatment & Disposal
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs | 7.3714 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. | 45.1539 | gpd/ERC
| PN = | Property needed expressed in U units | 1664.2292 | gpd
* Based on the 2005 TMADF (Sch. F-6) divided 2005 ERCs (Sch F-10).
Water Distribution System
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs | 10 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. | 1 | ERC
| PN = | Property needed expressed in U units | 50 | ERCs
Wastewater Collection System
Built out. Per Docket No. 020071-WS.

## F-9
Equivalent Residential Connections - Water | [7 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [10 empty] | Schedule F-9
Docket No.: 060253-WS | [10 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [10 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2001 | 414 | 432 |  | 423 |  | 40712673 | 96247.4539 | 45217393 |  | 469.8035
2 | 2002 | 432 | 458 |  | 445 |  | 40995498 | 92124.7146 | 43049778 |  | 467.2989 | -0.5331%
3 | 2003 | 458 | 444 |  | 451 |  | 40789255 | 90441.8071 | 42258275 |  | 467.2427 | -0.01202%
4 | 2004 | 444 | 463 |  | 453.5 |  | 45762590 | 100909.7905 | 50514446 |  | 500.5901 | 7.137%
5 | 2005 | 463 | 456 |  | 459.5 |  | 40597000 | 88350.3808 | 44688000 |  | 505.8043 | 1.042%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 1.908%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 450.5601 |  | 1 | 469.8035
[6 empty] | X Coefficient: |  | 10.5293 |  | 2 | 467.2989
[6 empty] | R^2: |  | 0.74168 |  | 3 | 467.2427
[10 empty] | 4 | 500.5901
[10 empty] | 5 | 505.8043
[10 empty] | 10 | 555.8528
[7 empty] | Five year growth |  |  |  | 50.0485
[7 empty] | Annual average |  |  |  | 10.0097

## F-10
Equivalent Residential Connections - Wastewater | [6 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida (630/635-Golden Hills/Crownwood) | [10 empty] | Schedule F-10
Docket No.: 060253-WS | [10 empty] | Page 1 of 1
Test Year Ended: December 31, 2005 | [10 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2001 | 66 | 69 |  | 67.5 |  | 2285113 | 33853.5259 | 2789693 |  | 82.4048
2 | 2002 | 69 | 72 |  | 70.5 |  | 2608480 | 36999.7163 | 7507710 |  | 202.9126 | 146.2%
3 | 2003 | 72 | 69 |  | 70.5 |  | 2791320 | 39593.1915 | 7776950 |  | 196.4214 | -3.199%
4 | 2004 | 69 | 71 |  | 70 |  | 2754400 | 39348.5714 | 8276582 |  | 210.3401 | 7.086%
5 | 2005 | 71 | 70 |  | 70.5 |  | 2508000 | 35574.4681 | 8036000 |  | 225.8923 | 7.394%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 39.38%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 95.2735 |  | 1 | 82.4048
[6 empty] | X Coefficient: |  | 29.4403 |  | 2 | 202.9126
[6 empty] | R^2: |  | 0.65258 |  | 3 | 196.4214
[10 empty] | 4 | 210.3401
[10 empty] | 5 | 225.8923
[10 empty] | 10 | 389.676
[7 empty] | Five year growth |  |  |  | 163.7837
[7 empty] | Annual average |  |  |  | 32.7567
Prior to 2001, the system had been built out and stable. In 2001, a bulk utility customer, BFF Corp. was added.
The significant increase in gallons from 2001 to 2002 represents that addition. The average growth rate shown
is distorted by the entry of BFF into the system. A more reasonable indication of the growth rate is shown by the
regression below beginning with 2002, when BFF was on the system:
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 188.1772 |  | 1 | 202.9126
[6 empty] | X Coefficient: |  | 8.2858 |  | 2 | 196.4214
[6 empty] | R^2: |  | 0.71162 |  | 3 | 210.3401
[10 empty] | 4 | 225.8923
[10 empty] | 9 | 262.7492
[7 empty] | Five year growth |  |  |  | 36.8569
[7 empty] | Annual average |  |  |  | 7.3714