741

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

3                                      DOCKET NO. 070098-EI

4   In the Matter of:

5   PETITION FOR DETERMINATION OF NEED

FOR GLADES POWER PARK UNITS 1 AND

6   2 ELECTRICAL POWER PLANTS IN GLADES

COUNTY, BY FLORIDA POWER & LIGHT

7   COMPANY.

_____________________________________/

8

9

10

ELECTRONIC VERSIONS OF THIS TRANSCRIPT ARE

11                 A CONVENIENCE COPY ONLY AND ARE NOT

THE OFFICIAL TRANSCRIPT OF THE HEARING,

12            THE .PDF VERSION INCLUDES PREFILED TESTIMONY.

13                              VOLUME 6

14                        Pages 741 through 861

15   PROCEEDINGS:        HEARING

16   BEFORE:             CHAIRMAN LISA POLAK EDGAR

COMMISSIONER MATTHEW M. CARTER, II

17                       COMMISSIONER KATRINA J. MCMURRIAN

18   DATE:               Wednesday, April 25, 2007

19   TIME:               Commenced at 9:45 a.m.

20   PLACE:              Betty Easley Conference Center

Room 148

21                       4075 Esplanade Way

Tallahassee, Florida

22

REPORTED BY:        LINDA BOLES, RPR, CRR

23                       JANE FAUROT, RPR

Official FPSC Reporters

24                       (850) 413-6734/(850) 413-6732

25   APPEARANCES:        (As heretofore noted.)

FLORIDA PUBLIC SERVICE COMMISSION

742

1                              I N D E X

2                              WITNESSES

3   NAME:                                               PAGE NO.

4   DAVID HICKS

5        Direct Examination by Mr. Anderson              747

Prefiled Direct Testimony Inserted              749

6        Errata Sheet to Prefiled Direct Testimony       777

Inserted

7        Cross Examination by Mr. Guest                  782

Cross Examination Mr. Krasowski                 843

8

9

10

11

12

13   CERTIFICATE OF REPORTERS                       861

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

743

1                                 EXHIBITS

2   NUMBER:                                        ID.   ADMTD.

3   166  NETL's Materials Research Program         786

4   167  EPA Final Report, Environmental           790

Footprints and Costs IGCC vs. PC

5

168  Black & Veatch Supercritical              792

6        Plant Technology Overview

7   169  Ten-Year Site Plan for Electrical         799

Generating Facilities and Associated

8        Transmission Lines, 4-1-06

9   170  "Refinery IGCC plants are Exceeding 90%   803

capacity factor after 3 years"

10

171  First page and Page 10 of Petition        824

11        by FPL

12   172  (No description)                          824

13   173  Proposed projects IGCC and

polygeneration in North America           826

14

174  Proposed IGCC Plants other than           828

15        North America

16   175  Cost of Electricity Comparison            830

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

744

1                        P R O C E E D I N G S

2             (Transcript continues in sequence from Volume 5.)

3             CHAIRMAN EDGAR:  Good morning.  We will get started

4   here in just a moment.  And I will call this hearing to order,

5   continuation of the hearing.

6             Before I ask for preliminary matters, I see that we

7   do have some new faces that are joining us since, since we were

8   all gathered together last week.  It was last week.  It seems

9   like only yesterday.  Okay.  So let's go ahead, if we can, and

10   start by taking appearances again.  That will be a duplicate

11   for some of you and maybe some new names so I can help keep

12   track, and for the court reporter as well.  We will begin with

13   you.

14             MR. ANDERSON:  Good morning.  My name is Bryan

15   Anderson.  I'd like to enter the appearances, please, of Wade

16   Litchfield, Natalie Smith and myself on behalf of Florida Power

17   & Light Company, 700 Universe Boulevard, Juno Beach, Florida

18   33408.

19             CHAIRMAN EDGAR:  Thank you.

20             MS. PERDUE:  Tamela Ivey Perdue with the law firm of

21   Stiles, Taylor & Grace on behalf of Intervenor Associated

22   Industries of Florida.

23             CHAIRMAN EDGAR:  Thank you.

24             MR. GUEST:  David Guest and Monica Reimer,

25   R-E-I-M-E-R, representing the environmental intervenors.  Our

FLORIDA PUBLIC SERVICE COMMISSION

745

1   law firm's address is 111 South Martin Luther King Boulevard,

2   Tallahassee, 32301.

3             CHAIRMAN EDGAR:  Thank you.

4             MR. BECK:  Good morning, Madam Chairman and

5   Commissioners.  Charlie Beck and Steve Burgess, Office of

6   Public Counsel, on behalf of Florida's citizens.

7             CHAIRMAN EDGAR:  Thank you.

8             MR. KRASOWSKI:  Good morning, Commissioners.  My name

9   is Bob Krasowski.  I'm here representing myself and my wife Jan

10   as ratepayers and customers of FP&L, and also as interested

11   people who have an interest in the environmental economic

12   aspect of this hearing.

13             CHAIRMAN EDGAR:  Thank you.  And staff.

14             MS. BRUBAKER:  And for the Commission, Jennifer

15   Brubaker, Katherine Fleming, Lorena Holley and Larry Harris.

16             CHAIRMAN EDGAR:  Thank you all.

17             And, Ms. Brubaker, preliminary matters.

18             MS. BRUBAKER:  Staff is aware of really none to speak

19   of.  I would note that there was discussion since the

20   continuation of the last hearing date about witnesses, and my

21   understanding is that everybody is in agreement that we will

22   simply resume examination of witnesses in the order in which

23   they appear on the prehearing order beginning on Page 4.  By my

24   count we would begin with Mr. Hicks this morning.  It's also my

25   understanding that FPL Witness Mr. Yeager can be taken, his

FLORIDA PUBLIC SERVICE COMMISSION

746

1   rebuttal and direct together.  And to the extent FPL is able to

2   make that accommodation with any other witnesses, we'll simply

3   let them address it as they're able to make that accommodation.

4   And with that, staff --

5             CHAIRMAN EDGAR:  No other matters?

6             MS. BRUBAKER:  -- has no further matters.

7             CHAIRMAN EDGAR:  Okay.  Before we call the next

8   witness, any matters to be raised by any of the parties?  No?

9   Ready to get started.

10             Okay.  Just a very few brief comments.  As you

11   recall, because we have, because the hearing has covered a

12   number of days and travel schedules and all we did not swear

13   the witnesses in as a group.  So if your witness has been

14   sworn, let me know that, please.  And remind your witnesses

15   that they have been sworn.  And for those who have not, we will

16   do that individually as they get settled in.

17             And as always, would ask that we recognize the time

18   frames that we have and that we cooperate together to get

19   through everything that we need to do.  And with that, it is

20   your witness.

21             MR. ANDERSON:  Thank you.  If the Chair wishes, there

22   are three witnesses you could swear at once, the next three

23   people.

24             CHAIRMAN EDGAR:  Okay.  We can do that.  And that

25   would be Mr. Hicks, Mr. Jenkins and Mr. Kosky?

FLORIDA PUBLIC SERVICE COMMISSION

747

1             MR. ANDERSON:  That's exactly right.

2             CHAIRMAN EDGAR:  Okay.  If the three of you gentlemen

3   will stand with me, raise your right hand, and we will do this,

4   the three, together.

5             (Witnesses collectively sworn.)

6                             DAVID HICKS

7   was called as a witness on behalf of Florida Power & Light

8   Company, and, having been duly sworn, testified as follows:

9                         DIRECT EXAMINATION

10   BY MR. ANDERSON:

11        Q    Good morning, Mr. Hicks.

12        A    Good morning.

13        Q    Would you please tell us your name and your business

14   address.

15        A    David Hicks, 700 Universe Boulevard, Juno Beach,

16   Florida 33408.

17        Q    By whom are you employed and in what capacity?

18        A    I'm employed by Florida Power & Light as the Senior

19   Director of Project Development.

20        Q    Have you prepared and caused to be filed 28 pages of

21   prefiled direct testimony in this proceeding?

22        A    Yes, I have.

23        Q    Did you also cause to be filed errata to your direct

24   testimony on April 13th, 2007?

25        A    Yes, I have.

FLORIDA PUBLIC SERVICE COMMISSION

748

1        Q    Do you have any further changes or revisions to your

2   prefiled direct testimony?

3        A    No, I do not.

4        Q    With the changes in your errata, if I asked you the

5   same questions contained in your prefiled direct testimony,

6   would your answers be the same?

7        A    Yes, they would.

8             MR. ANDERSON:  FPL asks that Mr. Hicks' prefiled

9   direct testimony be inserted into the record as though read.

10             CHAIRMAN EDGAR:  The prefiled direct testimony with

11   the errata will be entered into the record as though read.

12   BY MR. ANDERSON:

13        Q    Are you sponsoring any exhibits to your direct

14   testimony?

15        A    Yes, I am.

16        Q    Those are documents DNH-1 through DNH-14?

17        A    Yes, they are.

18             MR. ANDERSON:  Madam Chairman, I'd note that

19   Mr. Hicks' exhibits have been premarked for identification as

20   25 through 38.

21             CHAIRMAN EDGAR:  Thank you.

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

778

1   BY MR. ANDERSON:

2        Q    Have you prepared a summary of your testimony?

3        A    Yes, I have.

4        Q    Please provide your summary to the Commission.

5        A    Good morning, Chairman Edgar and Commissioners.  As

6   the Senior Director of Project Development I am responsible for

7   the development of power generation projects to meet the needs

8   of FPL's customers.

9             Beginning in 2003, FPL conducted a thorough and

10   extensive investigation into the potential for adding solid

11   fuel generation to its resource mix and concluded that

12   significant improvements had been made in solid fuel

13   technology, emissions control technologies and plant designs

14   such that FPL had a number of technology options, all of which

15   would provide fuel diversity to FPL's system.

16             After a detailed analysis of the available technology

17   options, we determined that the addition of an

18   ultra-supercritical pulverized coal plant augmented with a

19   complete suite of state-of-the-art emissions control equipment

20   will best meet the power generation needs identified in the

21   2012 to 2014 period and provide FPL's customers reliable,

22   cost-effective and environmentally sensitive fuel to pursue.

23             In March of 2005, FPL filed with this Commission the

24   Report on Clean Coal Generation, a comprehensive study on

25   current opportunities and issues regarding solid fuel

FLORIDA PUBLIC SERVICE COMMISSION

779

1   generation.  In 2006, we developed the FPL Glades Power Park,

2   including site selection, engineering and plant layout, and the

3   negotiation of construction and major equipment contracts.  In

4   January 2007, we completed the Clean Coal Technology Selection

5   Study incorporating the most current information available in

6   the industry concerning solid fuel generating technology.  As a

7   result of this study, FPL reconfirmed that ultra-supercritical

8   technology will materially outperform all available alternative

9   coal generation technologies including integrated gasification

10   combined cycle or IGCC.

11             When comparing technologies, it's important to look

12   at seven factors:  Technological maturity, reliability,

13   construction risk, life cycle costs, generation efficiency,

14   environmental performance and CO2 emissions.

15             As summarized on these charts, the

16   ultra-supercritical plant proposed for FPL Glades Power Park is

17   superior to IGCC in six of the categories.  And in terms of

18   environmental performance, the next-generation IGCC plants will

19   have roughly the same emissions profile as the Glades Power

20   Park if the IGCC plants achieve their projected environmental

21   performance.

22             By the United States Department of Energy definition

23   of ultra-supercritical pulverized coal there are over 30

24   ultra-supercritical units in commercial operation and

25   construction.  In contrast, there are only four relatively

FLORIDA PUBLIC SERVICE COMMISSION

780

1   small coal-to-electricity IGCC demonstration plants in

2   operation, each delivering less than 300 megawatts, which all

3   required large government subsidies without which they would

4   not have been built.  Ultra-supercritical plants have a proven

5   track record of greater than 90 percent availability.  In

6   contrast, three of the four IGCC coal-to-electricity plants

7   have never achieved the lower 80 percent availability level and

8   the fourth has barely met that lower level of performance.  In

9   large part, due to its technological maturity and proven

10   performance, FPL has been able to negotiate an engineering

11   procurement and construction or EPC contract and major

12   equipment supplier contracts with guarantees on performance,

13   schedule and cost.  In contrast, IGCC developers have yet to

14   secure a viable EPC contract.

15             Life cycle costs for ultra-supercritical plants are

16   significantly lower than IGCC due to much lower capital costs,

17   lower operations and maintenance costs and higher efficiency.

18   The ultra-supercritical generation efficiency at the Glades

19   Power Park will exceed both current IGCC performance and the

20   projected, but as yet unrealized, generation efficiency for

21   next-generation IGCC plants.  This means that FPL's Glades

22   Power Park will use less coal to deliver electricity to FPL's

23   customers.

24             The guaranteed environmental performance of the FPL

25   Glades Power Park, which will be protective of human health and

FLORIDA PUBLIC SERVICE COMMISSION

781

1   the environment, exceeds today's IGCC plants and will be

2   similar to next-generation IGCC, if next-generation IGCC

3   operates as projected.  It should be noted, however, that the

4   significant efficiency advantage of Glades Power Park over IGCC

5   will result in lower CO2 emissions for the Glades Power Park.

6             In summary, the FPL Glades Power Park employing

7   ultra-supercritical generating technology, a complete suite of

8   state-of-the-art emissions control equipment and incorporating

9   a plant design that will allow for the recycling of the

10   by-products from the combustion emissions control processes

11   sets a new standard of excellence for coal-fired electric

12   generating stations in the United States.  The FPL Glades Power

13   Park will meet the need requirements for the 2012 to 2014 time

14   period, providing FPL's customers with reliable, cost-effective

15   and environmentally sensitive fuel-diverse electric power.

16   Thank you.

17             MR. ANDERSON:  Mr. Hicks is available for

18   cross-examination.

19             CHAIRMAN EDGAR:  Thank you.

20             Ms. Perdue, any questions?

21             MS. PERDUE:  No.

22             CHAIRMAN EDGAR:  No questions.

23             Mr. Beck?

24             MR. BECK:  No questions.

25             CHAIRMAN EDGAR:  Mr. Guest.

FLORIDA PUBLIC SERVICE COMMISSION

782

1             MR. GUEST:  Thank you, Madam Chairman.

2                          CROSS EXAMINATION

3   BY MR. GUEST:

4        Q    Good morning, Mr. Hicks.  I'd like to just ask a few

5   questions to get some clarification on some of these items that

6   you've testified about.

7             CHAIRMAN EDGAR:  I need you to pull the microphone

8   closer or make sure it's on.

9             MR. GUEST:  Okay.  It's on.  Well, I think that -- is

10   that right?

11             CHAIRMAN EDGAR:  That's better.

12             MR. GUEST:  Okay.  May I bellow, Madam Chairman?

13             CHAIRMAN EDGAR:  You may bellow.  We want to make

14   sure that we all hear you clearly.

15   BY MR. GUEST:

16        Q    Good morning, Mr. Hicks.

17        A    Good morning.

18        Q    I'd like to just go through and get some

19   clarification on some items on your chart back there.  The

20   first item I see here is that you refer to USCPC.  That stands

21   for ultra-supercritical pulverized coal.

22        A    That is correct.

23        Q    And the concept of ultra-supercritical means that

24   it's extremely efficient; isn't that right?

25        A    Ultra-supercritical pulverized coal uses advanced

FLORIDA PUBLIC SERVICE COMMISSION

783

1   engineering techniques and advanced metals to burn coal and

2   produce steam at much higher efficiencies, much higher

3   pressures and steam temperatures to result in a much more

4   efficient production of electricity.

5        Q    And the concept here is that by having very, very

6   high pressure in the boiler, you have a higher fraction of

7   water as compared to steam so that you get higher conductivity

8   and you're able to extract more of the heat and thus become

9   more efficient; isn't that the concept?

10        A    That's, that's a good summary of it.

11             I would mention that the Japanese have done a

12   considerable amount of research on this issue both in terms of

13   pressure and temperature, and what they have found is that

14   temperature incrementally -- increases in temperature

15   incrementally have a much greater impact on efficiency than

16   pressure.

17             Let's take a 2,400-pound pressure subcritical unit

18   operating at 1,000 degrees Farenheit.  What they found was

19   by -- if you increase that pressure from 2,400 pounds to 4,500

20   pounds, an increase of about 75 percent, you get about a 2.5

21   percent incremental increase in efficiency.  Contrast to that,

22   if you took the 2,400-pound pressure and the 1,000-pound

23   temperature and increased the temperature by 10 percent to

24   1,100 degrees, that would actually get about a 4.5 percent

25   increase in efficiency.  So they have focused a lot on

FLORIDA PUBLIC SERVICE COMMISSION

784

1   temperature.

2        Q    Now I think that you testified previously that the

3   proposed Glades coal plant would operate at 3,700 pounds per

4   square inch; is that correct?

5        A    That is correct.

6        Q    And that, that would produce an efficiency of about

7   38 or so percent, 39?

8        A    The combination -- as I stated before, it's both

9   pressure and temperature.  The combination of the 3,700-pound

10   pressure and the 1,112, 1,130-degree Fahrenheit temperature

11   would produce an average annual heat rate over the life of the

12   facility of 8,800 Btus per kWh.

13        Q    And that translates to an efficiency rate of about

14   38.8 percent?

15        A    Roughly, yes.

16        Q    Okay.  So you say that those characteristics show

17   that this is an ultra-supercritical state-of-the-art coal-fired

18   power plant; is that correct?

19        A    The U.S. Department of Energy defines

20   ultra-supercritical as temperature -- pressures above 3,600

21   pounds, 3,600 pounds or greater, and temperatures approaching

22   1,100 degrees Fahrenheit.  By that definition this is an

23   ultra-supercritical pulverized coal plant.

24        Q    You're familiar, are you not, with the National

25   Energy Technology Laboratory at the Department of Energy?

FLORIDA PUBLIC SERVICE COMMISSION

785

1        A    I'm aware of them.  Yes, I am.

2        Q    And they're an authoritative source on matters like

3   this.

4        A    They are a source of information on coal technology,

5   yes.

6        Q    An authoritative source.

7        A    I don't know, I don't know how you're defining

8   "authoritative," so I can't comment on that.

9        Q    Well, it's the National Environmental -- National

10   Energy Technology Laboratory at the Department of Energy.

11        A    It's a government agency that does work on coal

12   plants.  Yes.

13        Q    Okay.  I have to -- I would like to show you a, a

14   document from the National Energy Technology Laboratory at the

15   Department of Energy, and it's called the Materials Research

16   Program.

17             I'd like to distribute it, if I may, to various

18   people.

19             CHAIRMAN EDGAR:  You may.  Obviously, yes, to our

20   staff, to the Commissioners, to the court reporter and to the

21   other attorneys.  Should we go ahead and mark this?  Are you

22   going to want to --

23             MR. GUEST:  I'm just going to ask him some questions

24   on it.

25             CHAIRMAN EDGAR:  Okay.

FLORIDA PUBLIC SERVICE COMMISSION

786

1             MR. ANDERSON:  May I have a copy?

2             CHAIRMAN EDGAR:  You may.  We'll give it a minute to

3   have it distributed.

4             Ms. Brubaker.

5             MS. BRUBAKER:  Just if it's going to be identified, I

6   think we are at Number 166.

7             CHAIRMAN EDGAR:  We are at Number 166.  Should we go

8   ahead and do that for clarify?  We will do that for clarity.

9   We will number this one 166 and label it NETL Materials

10   Research Program.  And once that is passed out, then, Mr.

11   Guest, when you are ready.  I'll guess we'll give it a minute.

12             MR. GUEST:  Everybody has it.

13             (Exhibit 166 marked for identification.)

14   BY MR. GUEST:

15        Q    Mr. Hicks, would you be so kind as to turn to the

16   one, two, three, four, five, six, seven, eighth page.  It's the

17   chart that looks like this.  Can everyone see it?  This is the

18   chart.

19             Have you had an opportunity to review that,

20   Mr. Hicks?

21        A    I just looked at it.  Yes, I did.

22        Q    Okay.  So now what this chart from the National

23   Energy Technology Laboratory indicates is that

24   ultra-supercritical has an efficiency rate of 47 to 49 percent,

25   almost 10 percent higher than what you're calling

FLORIDA PUBLIC SERVICE COMMISSION

787

1   ultra-supercritical; isn't that right?

2        A    This chart right here is not indicative of the

3   general consensus with regard to ultra-supercritical

4   technology.  The United States Department of Energy, of which

5   NETL is a part of that, defines ultra-supercritical as

6   temperatures above or approaching 1,100 degrees and pressures

7   at 3,600 pounds or greater.

8             In addition, the Japanese, who also build

9   ultra-supercritical plants, use as a bright white (phonetic)

10   line 1,100 degrees Fahrenheit.  It is a general consensus in

11   this industry that the pressures and temperatures of this plant

12   represent ultra-supercritical technology.

13             It should also be -- it's also important to realize

14   in terms of efficiency and in terms of heat rate average

15   degraded over the life of the plant you have to take into

16   consideration degradation, you have to take into consideration

17   ambient air temperatures, et cetera.

18             So this plant represents a -- the efficiency that's

19   calculated for this plant represents an average degraded heat

20   rate over the life of the plant, which is important to

21   customers, but also represents the ambient air temperatures

22   that are consistent in South Florida.

23        Q    Okay.  Looking, continuing on this same page, I see

24   that it's got -- in addition to an efficiency rate for

25   ultra-supercritical, this chart shows that the psi is 4,500,

FLORIDA PUBLIC SERVICE COMMISSION

788

1   which is by my count 800 psi higher than what you're talking

2   about for the proposed Glades plant; is that right?

3        A    I see that on this chart, yes.  But, once again, I

4   would comment that the United States Department of Energy

5   explicitly defines ultra-supercritical as 3,600 pounds pressure

6   greater, temperatures approaching 1,100 degrees Fahrenheit, and

7   the general consensus in this industry is that this is an

8   ultra-supercritical plant.

9             I'm not denying that if you went to these much higher

10   temperatures and pressures, you would still be

11   ultra-supercritical.  But the plant that we're proposing for

12   Glades County is an ultra-supercritical plant.

13        Q    Okay.  Now --

14             CHAIRMAN EDGAR:  Mr. Guest, excuse me.  I'm sorry to

15   interrupt.  But one of the copies that was distributed up here

16   does not have this page, and so I need to ask you if you

17   have -- I'm sure it was just collating.  But if you have

18   another copy available, that would be useful to us.

19             MR. GUEST:  You know, I'll just stick it in my --

20   that's great.

21             CHAIRMAN EDGAR:  Okay.  Thank you.

22             MR. GUEST:  That's a collating error.  I actually, I

23   could blame it on someone else.

24             CHAIRMAN EDGAR:  There's no need to blame anyone at

25   all.  Thank you.  Go right ahead.

FLORIDA PUBLIC SERVICE COMMISSION

789

1             (Laughter.)

2   BY MR. GUEST:

3        Q    Now continuing to look at this page, Mr. Hicks, from

4   the National Energy Technology Laboratory, you're looking -- if

5   you look at the front page, this is from the Department of

6   Energy; correct?

7        A    Yes.

8        Q    Okay.  And so we're looking at this page.  And now if

9   you look at the middle box, it has pressures greater than 3,500

10   psi and efficiencies of 41 to 45 percent.  So using this page

11   from the National Environmental Technology Laboratory -- you

12   know, I always say environmental, I mean energy -- and the

13   41 to 45 percent, that's really, according to this document,

14   what the proposed Glades Power Plant is is actually

15   supercritical according to this document.

16        A    No, I would disagree with that.  This plant, the

17   Glades Power Park has a pressure of 3,700 pounds per square

18   inch, temperatures of 1,112 degrees and 1,130 degrees

19   Fahrenheit.  With South Florida conditions, average degraded

20   heat rate over the life of the plant, it's around 38.8 percent

21   efficiency.  That is recognized by the industry as an

22   ultra-supercritical pulverized coal plant.

23        Q    Okay.  And I would note just to -- if you would look

24   at that center box under supercritical, you see the bird's

25   mouth that indicates greater than, greater than 3,500 psi, and

FLORIDA PUBLIC SERVICE COMMISSION

790

1   that also applies to 41 to 45 percent efficiency.

2        A    Uh-huh.

3        Q    Okay.  So let me turn to another document which we're

4   going to hand out.

5             CHAIRMAN EDGAR:  Okay.  While that's distributed, we

6   will go ahead and mark, and it will be Number 167.  And, Mr.

7   Guest, can you give me a title?

8             MR. GUEST:  This is the United -- this is a document

9   by the EPA, Federal Environmental Protection Agency.  It's

10   called Final Report, Environmental Footprints and Costs of

11   Coal-Based Integrated Gasification Combined Cycle and

12   Pulverized Coal Technologies dated July 2006.

13             CHAIRMAN EDGAR:  Okay.  And for, for my listing I'm

14   going to abbreviate to EPA Final Report, Environmental

15   Footprints and Costs, IGCC.

16             MR. GUEST:  Well, what they mean is IGCC versus PC.

17   I mean, that's what that's a comparison of.

18             CHAIRMAN EDGAR:  Versus PC.  We can do that.  Okay.

19             (Exhibit 167 marked for identification.)

20   BY MR. GUEST:

21        Q    And I would -- just a very simple point, Mr. Hicks.

22   If you turn to the second page of this document, at the very

23   bottom line it reads, "PC plants."  That means pulverized coal

24   plants; right?

25        A    That's correct.

FLORIDA PUBLIC SERVICE COMMISSION

791

1        Q    "With ultra-supercritical steam conditions of 4,500

2   psi and 1,100 to 1,100 F double reheat," is the description of

3   ultra-supercritical.

4        A    Yes.  And that is consistent, once again, with the

5   U.S. Department of Energy definition, which is plants that have

6   steam pressures 3,600 psi or greater and temperatures

7   approaching 1,100 degrees Fahrenheit, those plants are

8   ultra-supercritical.  This plant would be an

9   ultra-supercritical under that definition.

10        Q    Okay.  So but you're 800 psi short and you're not

11   anywhere close to the 45 percent efficiency that you'd get for

12   ultra-supercritical.

13        A    No.  This, this plant represents a, a combination of

14   temperature and pressure that is unique, would be unique for

15   the United States.  It represents the cutting edge of

16   ultra-supercritical technology in the world.  It is state of

17   the art and meets the definition of ultra-supercritical

18   technology.

19        Q    Now FP&L hired a consulting firm called

20   Black & Veatch, V-E-A-T-C-H; is that correct?

21        A    We hired Black & Veatch as a, to assist us in

22   preparing the Clean Coal Technology Selection Study.

23        Q    And do you know a person named Mr. Ron Ott, O-T-T?

24        A    I'm familiar with him, yes.

25        Q    Could you tell us who he is?

FLORIDA PUBLIC SERVICE COMMISSION

792

1        A    He's an employee of Black & Veatch or was an employee

2   of Black & Veatch as of two years ago when I last talked to

3   him.

4        Q    Was he the Senior Vice President and Coal Program

5   Director?

6        A    I'm not sure.

7             MR. GUEST:  Okay.  I'd like to show you a document

8   which is a presentation by your consultants, Black & Veatch.

9             CHAIRMAN EDGAR:  Okay.  We will mark 168, Black &

10   Veatch Supercritical Plant Technology Overview.

11             (Exhibit 168 marked for identification.)

12             MR. GUEST:  Does everybody have one?  Okay.

13   BY MR. GUEST:

14        Q    Do you have it?

15        A    Yes, I do.

16        Q    I would like to turn first to the -- let's just go

17   from backwards here.  It would be the third last page of this

18   document.  But before I do that, does it reflect your

19   recollection seeing the front page of it that says Mr. Ott is

20   the Senior Vice President and the Coal Program Director?

21        A    It doesn't, doesn't refresh my memory.  I know of a

22   gentleman named Ron Ott that worked at Black & Veatch a couple

23   of years ago.  I have not had discussions with him since then.

24        Q    Okay.  And I would turn now to the third page from

25   the beginning.  Are you with me?

FLORIDA PUBLIC SERVICE COMMISSION

793

1        A    Yes.

2        Q    And the title is Thermal Generation Technology

3   Spectrum.  Are you on that page with me?

4        A    Yes.

5        Q    And if we turn to the bottom of that page under the

6   description of ultra-supercritical, it shows a net plant

7   efficiency of 44 percent; is that correct?

8        A    It does.  I'm not -- you know, once again, you have

9   to look at ambient air temperatures, what is the -- what

10   efficiency are you looking at, are you looking at design

11   efficiency, are you looking at initial test efficiency, are you

12   looking at efficiency over the life of the plant?

13             What we're reporting for this plant is the efficiency

14   over the life of the plant, including degradation, including

15   forced outages, et cetera.

16        Q    And when you look to the item that's called

17   supercritical, which is two above that, it identifies the net

18   plant efficiency at 38 percent.

19        A    I see that on the page.  Yes, sir.

20        Q    And that's very close to the 38.8 that you testified

21   to.

22        A    It is close to the 38.8.  But, once again, I'll say

23   it again, the 38.8 that we are representing is an average

24   degraded efficiency over the life of the plant.  It is not

25   indicated here what this efficiency represents.

FLORIDA PUBLIC SERVICE COMMISSION

794

1        Q    And it also refers to -- I'm still on the same page.

2   Under supercritical it refers to a pressure of 3,500 psi;

3   correct?

4        A    It does on this page, yes.

5        Q    Which is close to your 3,700 psi; correct?

6        A    I would not necessarily say it's close to the 3,700.

7   It's approximately 200 psi lower.

8             MR. GUEST:  May I have a moment?

9             CHAIRMAN EDGAR:  Yes.

10             MR. GUEST:  This came up just at the last moment,

11   Madam Chairman, so I don't have copies for everybody, but this

12   is already in the record.  Maybe he'll recall this so we don't

13   have to fool around with it.

14   BY MR. GUEST:

15        Q    I'm on the determination of needs, the needs study

16   that was actually filed with the petition.  And on Page 22 at

17   the top under the diagram Figure III.A.5 it reads, underneath

18   that is B, and it's Unit 1 and 2 design, and the first line

19   reads, "Each unit will consist of a supercritical steam

20   generator."  Does that refresh your recollection?

21        A    I'd have to see it.  I don't have the document with

22   me.  It would be helpful if I could see the document.

23             CHAIRMAN EDGAR:  Mr. Guest, why don't you approach

24   and let the witness -- and actually why don't you start with

25   Mr. Anderson so that he is sure of --

FLORIDA PUBLIC SERVICE COMMISSION

795

1             (Pause.)

2   BY MR. GUEST:

3        Q    Have you had an opportunity to look at that,

4   Mr. Hicks?

5        A    Yes, I have.

6        Q    So the description of this plant in the needs

7   determination was that it was supercritical; is that correct?

8        A    The boiler was supercritical.  The plant is

9   ultra-supercritical because a supercritical boiler is a boiler

10   that's above, has a pressure above 3,208.  Ultra-supercritical

11   as defined by the Department of Energy, which is the definition

12   we used for this plant, is pressures above 3,600 pounds psi or

13   above and temperatures approaching 1,100 degrees Fahrenheit.

14        Q    Did FP&L do any internal studies that examined the

15   matter of whether this was critical or ultra-supercritical?

16        A    FPL examined various technologies, invited vendors to

17   meet with us, went through various technology assessments with

18   those vendors, did internal studies, negotiated the contracts,

19   and this plant, as a result of all that analysis, internal

20   analysis and external work, this plant as defined by the

21   Department of Energy is an ultra-supercritical pulverized coal

22   plant that will bring levels of pressure and temperature unique

23   to the United States that will result in, when looking at the

24   plant over the life of the plant, the heat rate of the plant,

25   the life of the plant, including forced outages, et cetera,

FLORIDA PUBLIC SERVICE COMMISSION

796

1   would be the most efficient coal plant in the United States,

2   meeting the definition for ultra-supercritical.

3        Q    The question was whether or not FP&L had hired

4   consultants to examine the issue.

5        A    Yes.  We internally looked at that issue also.

6             MR. GUEST:  Okay.  May I have a moment, Your Honor?

7   I'm sorry.  Madam Chairman is what I mean.

8             CHAIRMAN EDGAR:  Yes.

9             (Pause.)

10             MR. GUEST:  Madam Chairman, there's a confidential

11   document that was produced in discovery.  We did not anticipate

12   having a need to use it.  What we've made a decision to do is

13   work with counsel to come up with a way to work through that so

14   that the parts that are trade secrets or whatever else can be

15   kind of separated and just this issue can be isolated and

16   presented somehow.  So we'll move on from there.

17             CHAIRMAN EDGAR:  Mr. Anderson.

18             MR. ANDERSON:  In fact, if counsel just wants to give

19   us the page he's interested in, we can look at it on the side

20   while he continues to interrogate so we can continue moving on.

21   BY MR. GUEST:

22        Q    Okay.  Let's press on.

23             The next item you have on your, on your demonstrative

24   exhibit over here after you -- I guess the first item is

25   technological maturity.  Let me jump over from that to the

FLORIDA PUBLIC SERVICE COMMISSION

797

1   reliability issue.

2             Now we have a number of different terms that are used

3   here.  Availability means the percent of time that the plant is

4   capable of producing electricity; is that correct?

5        A    Yes.

6        Q    And then reliability goes to unplanned outages;

7   correct?

8        A    Reliability is also another, another way of defining

9   availability.  Yes.

10        Q    Okay.  And so availability together really is planned

11   plus unplanned outages.

12        A    Yes.

13        Q    Okay.  And the capacity factor, excuse me, is the

14   time plant -- the time the plant can operate at its maximum

15   output.

16        A    The capacity factor is the, is the, taking the total

17   amount of generation divided by the total potential amount of

18   generation from the plant over the course of a year.

19        Q    Thank you.  I'd like to return now to the document

20   that we talked about earlier by the consulting firm hired by

21   FP&L, Black & Veatch, that we previously identified as Exhibit

22   Number -- or you gave it a number of 168.  And I think this

23   time I would like to go -- I think I want to go three pages

24   from the back this time.  Yes.  Three pages from the back,

25   three pages from the end, the third last page.  And I see

FLORIDA PUBLIC SERVICE COMMISSION

798

1   here -- are you with me?

2        A    Could you tell me which page exactly you're on?

3        Q    It's the one that reads Supercritical Versus --

4   "Subcritical versus Supercritical Technology."

5        A    Yes.  I see that.

6        Q    And I see that, if you go down to the column under

7   "Supercritical" and the row that reads "Availability Factor,"

8   the availability factor for supercritical plants is

9   83.2 percent; is that correct?

10        A    That's using NERC GADS data for 1994 to 1998.  That

11   would include supercritical plants that could have been built

12   as early as 1957.

13        Q    I'd like to turn now to a new document -- may I have

14   a moment?

15             CHAIRMAN EDGAR:  Yes.

16             MR. GUEST:  This document is the Ten-Year Site Plan

17   for Electrical Generating Facilities and Associated

18   Transmission Lines, January 2006 to December 2015, from TECO.

19   It's dated -- Tampa Electric Company, dated April 1, 2006.

20             CHAIRMAN EDGAR:  Okay.  Is this already in the

21   record?

22             MR. GUEST:  I don't believe so.  Oh, wait a minute.

23   Yes, it is.  No.  No.

24             CHAIRMAN EDGAR:  No.  Okay.  And Ms. Brubaker concurs

25   that it is not, so we will mark it 169.

FLORIDA PUBLIC SERVICE COMMISSION

799

1             (Exhibit 169 marked for identification.)

2             MR. GUEST:  This is 169; is that correct?

3             CHAIRMAN EDGAR:  Yes, sir.

4   BY MR. GUEST:

5        Q    Have you had an opportunity to review that?

6        A    Yes, I have.

7        Q    I'm turning to the second page and I'm looking under

8   the number 12.  Do you see the 12 in the columns on the left?

9        A    Yes, I do.

10        Q    It's under the group called projected unit

11   performance data.  And I see that it has a -- the second last

12   line under number 12 is resulting capacity factor of 87 percent

13   and an equivalent availability factor of 85.07 percent; is that

14   correct?

15        A    Yes, I do.  I see those.

16        Q    And that's for an IGCC plant.

17        A    And let me mention that is an IGCC plant that would

18   be used in baseload, as a baseload plant in the TECO system.

19             The FPL facility, the FPL Glades Power Park will be a

20   baseload facility in the FPL system.  Our internal analysis and

21   also our hands-on external review of ultra-supercritical plants

22   in Japan has led us to project with great confidence that we

23   will have a 92 percent capacity factor at our plant, at the FPL

24   Glades Power Park.

25             I think it's also important to look at the next line

FLORIDA PUBLIC SERVICE COMMISSION

800

1   which has an arrow next to it, and that arrow says average net

2   operating heat rate of 9,306.  That average net operating heat

3   rate is 506 Btus higher than the ultra-supercritical plant

4   proposed for Glades Power Park.

5             But what's also very important, and this goes to what

6   I had discussed earlier, is there is a footnote, footnote

7   number one.  And footnote number 1 says, "Based on in-service

8   year."  So that's the average annual heat rate for the first

9   year of the plant, not the average annual heat rate over the

10   life of the plant.  Due to degradation in the performance and

11   the equipment one would expect a higher average heat rate over

12   the life of the plant.

13             In fact, our own internal analysis and the analysis

14   of Black & Veatch has demonstrated that an IGCC plant would

15   incur average degradation over the life of the plant of about

16   2.5 percent.

17             What's interesting about this number right here is if

18   you take this number, 9,306, and you multiply by 1.025, which

19   is the average degradation rate, you get an average annual heat

20   rate over the life of the plant of 9,538.  What's interesting

21   about it is AEP, American Electric Power, filed air permit

22   applications for two IGCC plants, 600-megawatt demonstration

23   plants or 600-megawatt plants, one in Ohio and one in West

24   Virginia.  In those air permit filings the calculated heat rate

25   using the same technology that TECO is proposing for this plant

FLORIDA PUBLIC SERVICE COMMISSION

801

1   is 9,538, exactly the same number as taking this number and

2   multiplying by 1.025.  That leads me to believe that the

3   average annual heat rate over the life of this TECO plant will

4   be 9,538, 738 Btus higher than the average annual heat rate for

5   the FPL Glades Power Park, approximately 10 percent less

6   efficient.  That means 10 percent more coal burned to produce

7   the same amount of electricity and more CO2 emissions.

8             MR. GUEST:  May I have a moment, Your Honor, or Madam

9   Chairman?

10             MR. ANDERSON:  While counsel is looking, just to

11   close the loop on the confidential point, I brought over to

12   counsel the portion of the prehearing order that lays out the

13   instructions for how confidential things are handled at the

14   Commission with envelopes and things.  And if those are

15   complied with, we're fine, but we don't know that the materials

16   are had by Intervenors here.

17             CHAIRMAN EDGAR:  Mr. Guest, why don't we go ahead and

18   take ten minutes, and, and during that time maybe you could get

19   with our staff and with Mr. Anderson and work through the

20   confidentiality issue as well.  And we'll come back ten minutes

21   from now.

22             MR. GUEST:  Thank you, Madam Chairman.

23             CHAIRMAN EDGAR:  Thank you.

24             (Recess taken.)

25             CHAIRMAN EDGAR:  We will get started again.

FLORIDA PUBLIC SERVICE COMMISSION

802

1             Mr. Guest.

2             MR. GUEST:  I think we've reached an intelligent

3   stipulation here to deal with the matter of the confidential

4   study by reading only a couple of sentences.  One of them might

5   be two sentences, and then not putting the document in.  We

6   have a stipulation to do that.

7             CHAIRMAN EDGAR:  Mr. Anderson.

8             MR. ANDERSON:  That's acceptable, and we recognize

9   that that couple of sentences will be in the public record.

10   We've reviewed it and it is acceptable.

11             CHAIRMAN EDGAR:  All right.  Then thank you for the

12   cooperation on both parts.  And we are ready to go forward.

13             MR. GUEST:  Thank you.

14   BY MR. GUEST:

15        Q    Mr. Hicks, there was a confidential study in

16   April 2006 prepared by M.J. Bradley and Associates on behalf of

17   Florida Power and Light concerning the proposed power plant?

18        A    Yes, a confidential study done by M.J. Bradley and

19   Associates, an environmental consulting firm.

20        Q    And the study has in it a statement that FPL is

21   continuing to evaluate the efficacy of pursuing a new

22   supercritical PC plant in Florida, and this was dated

23   April 2006?

24        A    I don't have it in front of me, so I'll accept your

25   reading.

FLORIDA PUBLIC SERVICE COMMISSION

803

1        Q    Turning now to the matter of efficiency.  You agree,

2   do you not, that IGCC plants can achieve an efficiency of 90 to

3   94 percent?

4        A    No, I don't agree that they can achieve an efficiency

5   of 90 to 94 percent.

6        Q    I'd like to show you -- we are going to hand this

7   out.

8             MR. GUEST:  I will identify it for the record, if I

9   might.  This is an article in Gas Turbine World, and it's

10   entitled, "Refinery IGCC Plants are Exceeding 90 Percent

11   Capacity Factor After Three Years."

12             CHAIRMAN EDGAR:  Okay.  And this will be Number 170.

13             (Exhibit 170 marked for identification.)

14             MR. GUEST:  Just for the record, I see my document

15   here has, also, that notation "Supplemental Exhibit RCF-29" on

16   it, which means that it's going to bounce in under Mr. Rich

17   Furman's testimony.

18   BY MR. GUEST:

19        Q    Mr. Hicks, do you have that before you?

20        A    Yes, I do.

21        Q    And I would like to direct your attention to the

22   first page of this document, and you see there's three boxes

23   there in the left column after the second paragraph, three

24   boxed paragraphs, do you see those?

25        A    Yes, I see those.

FLORIDA PUBLIC SERVICE COMMISSION

804

1        Q    And the first one is in the first year of commercial

2   operation syngas, it was 93 percent.  Do you see that one?

3   That is ISAB Energy.

4        A    I see that, yes.

5        Q    And the next one is Sarlux Saras has a 90 percent

6   efficiency.  And then the third one is that Api Energia has

7   94 percent efficiency.

8        A    I don't think those are efficiencies.  I think what

9   they are referring to there is capacity factors, and that is

10   different from efficiency.  And I also note that the three

11   facilities that are on this page are not coal-based IGCC

12   plants.  They are asphalt residues, and residues.  There is a

13   substantial difference between IGCC plants that run on asphalt,

14   residue, et cetera.  No one is proposing to do those in the

15   United States.  Mr. Jenkins, who is our expert, our retained

16   expert on IGCC, can provide you greater detail about the

17   differences between the two.

18             So I think, Counsel, you are confusing efficiency and

19   capacity factor, first of all, in your question to me; and,

20   second of all, you are making an apples-to-oranges comparison

21   by pulling up this document, which I would mention is not a

22   document that is peer reviewed.  It's this gentleman's opinion.

23             But, most importantly, Mr. Jenkins can provide the

24   Commissioners detail with regard to why comparing IGCC plants

25   that run on such feed stocks as asphalt and residues should not

FLORIDA PUBLIC SERVICE COMMISSION

805

1   be compared to coal-based IGCC plants.

2        Q    Well, IGCC plants run on a diverse array of fuels, do

3   they not?

4        A    I would disagree with that.  IGCC plants, just like

5   pulverized coal plants, you design that plant for a specific

6   type of fuel type.  If you deviate from that fuel type, that

7   can cause considerable problems.  It's called a design point.

8   So, for example, there is two design points for the pulverized

9   coal plant at the FPL Glades Power Park.  One design point is

10   bituminous coal.  The second design point is bituminous coal

11   with 20 percent petroleum coke.  That gives us great fuel

12   flexibility in sourcing bituminous coals and petroleum cokes

13   throughout the United States and also throughout the world.

14             Now, we can run that plant on other types of fuel,

15   such as subbituminous coals.  We would take a slight derate on

16   capacity or a slight derate on efficiency, but we can run on

17   other fuels.  But we have designed that plant for certain types

18   of fuel.  It's the same thing with IGCC.  You design it for a

19   specific type of fuel.  If you deviate from that fuel, that can

20   cause considerable problems.

21             Mr. Jenkins, once again, can provide additional

22   detail on the issues associating with designing an IGCC for a

23   particular type of fuel and then deviating from those fuels and

24   the impacts on the IGCC operation.  But it's not a correct

25   statement to say that an IGCC plant can run on a diverse set of

FLORIDA PUBLIC SERVICE COMMISSION

806

1   fuels.

2        Q    Well, we have IGCC plants that run on coals of all

3   types, is that right?

4        A    They are designed for specific types of coals, but

5   they can be designed to run on different types of coals,

6   correct.  Just like a PC plant can be designed to run on

7   different types of coals.

8        Q    And they can run on petcoke?

9        A    They can run on petcoke.  If designed specifically to

10   run on petcoke, they can run on petcoke.  Just like a PC plant,

11   such as FGPP, can be designed to run on petroleum coke as a

12   portion of the overall fuel mix.

13        Q    The maximum amount of petcoke that can be used in the

14   Glades proposed coal plant is 20 percent?

15        A    It is 20 percent based upon an average weighted

16   sulfur content of two percent for the total fuel supply.  I

17   would mention to you that we have done feasibility studies on

18   IGCC plants and the standard reference plant, particularly with

19   one vendor that we are working with, that plant has a maximum

20   sulfur content that is allowable in the design point of

21   4 percent, which does not allow it to be run on 100 percent

22   petroleum coke.  We could design that plant to run on 100

23   percent petroleum coke as a design point, but it would cost

24   substantially more to do so in terms of capital cost.

25        Q    And in addition to petroleum coke, or petcoke -- just

FLORIDA PUBLIC SERVICE COMMISSION

807

1   while we're talking about petcoke, we will come to this

2   probably several times in this hearing.  Now, as I understand

3   it, petcoke is a waste product from the process of refining

4   crude oil where you take the aromatic bottoms that are below

5   asphalt, and then crack them through a chemical process where

6   you add hydrogen molecules and make them as a waste product

7   that has some energy source value, is that the case?

8        A    That's generally the case.  It is also considered to

9   be an opportunity fuel in the sense that it's virtually

10   impossible to contract for it on a long-term basis.  Because it

11   is a waste product from the refinery process, refiners are

12   reluctant to sign long-term contracts for it.  We looked at the

13   petroleum coke market and determined that because it is an

14   opportunity fuel, because it is a fuel that doesn't have the

15   capability for long-term contracting, we considered it an

16   opportunity fuel and that although it is an opportunity fuel,

17   we include it as part of the plant design.

18        Q    What fraction of petcoke does the TECO plant run on?

19        A    I'm not sure.

20        Q    Does 60 percent sound right?

21        A    I'm not sure.

22        Q    The TECO plant could run on 100 percent petcoke?

23        A    Mr. Jenkins is actually the deputy project manager

24   for TECO, and he can provide you additional information on

25   that.

FLORIDA PUBLIC SERVICE COMMISSION

808

1        Q    Okay.  So an IGCC plant could run on all type of coal

2   and on petcoke.  Biomass?

3        A    Pulverized coal plants can also --

4             MR. ANDERSON:  We object to form.  The witness very

5   clearly said that that wasn't so.

6             MR. GUEST:  Well, let me just get some clarification,

7   then.

8   BY MR. GUEST:

9        Q    Do you know whether an IGCC plant could run on

10   biomass?

11        A    An IGCC plant can be designed, if you put it into the

12   original design, it can be designed to co-fire for some portion

13   of the fuel on biomass.  Similarly, a pulverized coal plant can

14   be designed to run on biomass, co-fire with biomass.

15        Q    And an IGCC plant can run on natural gas?

16        A    No, an IGCC plant cannot run on natural gas.  An IGCC

17   plant, if you were to eliminate the IGCC function and just

18   concentrate on the combined cycle portion of it, it can run on

19   natural gas.  But I have to mention that when an IGCC plant, a

20   plant that is designed to be an IGCC plant is shifted over to

21   natural gas, then the efficiency suffers versus a dedicated

22   combined cycle plant.

23        Q    So just to be clear here, you're saying that if you

24   have got natural gas as a back-up to run the turbine and the

25   steam boiler at an IGCC plant that you get a lower heat

FLORIDA PUBLIC SERVICE COMMISSION

809

1   efficiency by switching to natural gas rather than the syngas

2   produced by the IGCC, is that your testimony?

3        A    When you design an IGCC plant, and that IGCC plant

4   doesn't run on syngas, but runs on natural gas, it will be less

5   efficient than a dedicated combined cycle facility.  Now, one

6   has to note that if you design an IGCC plant to have natural

7   gas backup, you have to pay the costs associated with that.

8   For example, let's say that FPL were to design an IGCC plant at

9   the FPL Glades Power Park site.  The situation that we would be

10   faced with is both gas pipelines, both major gas pipelines come

11   into the state after FPL signed the gas contract for West

12   County.  Both of those pipelines are fully allocated, there's

13   no firm capacity left.

14             In order to get natural gas backup, we would have to

15   contract for an upgrade of that pipeline.  In order to

16   contract, you would have to contract under a long-term

17   take-or-pay agreement.  In other words, that firm gas supply we

18   would have to either take it or pay for it.

19             So to try to compensate for the deficiency in overall

20   availability between an IGCC plant and the ultra-supercritical

21   plant, one way of doing that would be to put in natural gas

22   backup, but that would be at a substantial additional cost to

23   the facility.  The IGCC without natural gas backup is

24   significantly more expensive in terms of life-cycle cost.

25   Adding natural gas backup to try to make up for that deficiency

FLORIDA PUBLIC SERVICE COMMISSION

810

1   in availability would only exacerbate that delta in terms of

2   life-cycle costs.

3        Q    Now, let we continue on the fuel issue.  I think we

4   talked about biomass, natural gas, petcoke, coal of all types.

5   I take it you are familiar with the new IGCC plant in the

6   Netherlands that uses 40 percent wood waste?

7        A    I'm aware of an IGCC plant in the Netherlands that

8   was not originally designed for biomass, but has made charges

9   so that it can burn some biomass, yes.  That plant -- by the

10   way, that plant has a very low average annual availability

11   factor.  It has suffered through significant forced outages,

12   and it has never met an average annual availability of

13   80 percent.

14        Q    We'll deal with that issue separately, too.  Now,

15   diesel fuel, that's another available fuel for an IGCC plant?

16        A    An IGCC plant, you can design it to run on syngas or

17   natural gas as a back-up; you could design it to run on syngas

18   and fuel oil as a back-up, but you couldn't design it to run on

19   all three.

20        Q    Asphalt, can they run on asphalt?

21        A    You could design an IGCC plant to run on asphalt as

22   the design point.  If you deviated from that feedstock, there

23   would be significant penalties.  And Mr. Jenkins can provide

24   you additional information on the issues associated with that.

25        Q    And they could also run on tar?

FLORIDA PUBLIC SERVICE COMMISSION

811

1        A    You could design -- I'm not aware of a tar-based IGCC

2   plant.  Mr. Jenkins could provide you additional information,

3   once again, with regard to designing a plant to run on

4   different types of feedstocks or a different type of feedstock

5   and the implications for that in terms of fuel supply.

6        Q    A lot of the products that I listed there that we

7   have been through are waste materials, are they not?

8        A    It depends on whose perspective you are looking at.

9   It could be characterized as a waste material.

10        Q    Well, the one in the Netherlands is using wood waste.

11   That's waste, isn't it?

12        A    It could be characterized as a waste material.

13        Q    Let's turn directly to the matter of petcoke.  And,

14   you know, do you not, that the Polk Plant, the TECO Polk Plant

15   uses a high fraction of petcoke in addition to coal?

16        A    Once again, with regard to the fuel type for the TECO

17   plant, I think that question is best addressed to Mr. Jenkins

18   who was a deputy project manager of the facility.

19        Q    Do you know anything about petcoke at all?

20        A    I'm aware of petcoke.  I'm aware of it as an

21   opportunity fuel, where it comes from, the economics of it and

22   the fact that it is an opportunity fuel.

23        Q    It is a whole lot cheaper than coal, isn't it?

24        A    Not necessarily.  In fact, FPL in conjunction with

25   the Jacksonville Electric Authority sometimes uses petroleum

FLORIDA PUBLIC SERVICE COMMISSION

812

1   coke at the power park that we have in Jacksonville.  And, in

2   fact, over the last year or so FPL and Jacksonville Electric

3   Authority have actually cut back on petroleum coke because the

4   price has either met or exceeded the price of coal, and I

5   believe Mr. Schwartz actually has this in his testimony.

6        Q    Yes.  So let's -- I'm going to show you a piece, an

7   exhibit from Mr. Schwartz' testimony which we are distributing

8   here.  I believe this is in evidence.  It's identified as

9   SS-19.

10             CHAIRMAN EDGAR:  Okay.  And SS-19, which was labeled

11   91 in the comprehensive exhibit.

12             MR. GUEST:  Thank you, Madam Chairman.

13   BY MR. GUEST:

14        Q    Have you had an opportunity to review this document,

15   Mr. Hicks?

16        A    I looked at it just now, yes.

17        Q    This was an exhibit to Mr. Schwartz' testimony.  You

18   see there that the dotted line at the bottom represents Florida

19   Power and Light's medium case forecast of delivered coal

20   prices, and this dotted line is the medium case forecast of

21   delivered petcoke prices, correct?

22        A    Yes.

23        Q    And what it shows, also, is that the solid line is

24   the Central Appalachian coal that FPL proposes to use at the

25   proposed Glades coal plant?

FLORIDA PUBLIC SERVICE COMMISSION

813

1        A    FPL proposes to use, as a base combination,

2   40 percent Central Appalachian, 40 percent foreign, and

3   20 percent petroleum coke, and did an economic analysis based

4   upon that.  In addition, we did economic analysis, both FPL and

5   through the clean coal technology selection study looking at

6   use of petroleum coke both for the PC technology, the

7   ultra-supercritical technology, and IGCC technology.  The

8   results were that the IGCC -- delivered cost of IGCC power was

9   greater than 40 percent over the life of the plant versus an

10   ultra-supercritical pulverized coal plant.  And that's

11   contained in the clean coal technology selection study, both in

12   the summary and in the text of the document.

13             And that delta in terms of significantly higher

14   delivered cost over the life of the plant for an IGCC plant

15   that's burning 50 percent petroleum coke was consistent,

16   including without emissions, with emissions, with degradation

17   on heat rate, and also with CO2 emissions.

18        Q    Well, the big picture that you see from Exhibit 91 is

19   that petcoke per million Btu is consistently a dollar or two or

20   perhaps even three cheaper than your coal source, isn't that

21   right?

22        A    Not necessarily.  Because, once again, the coal

23   source that is assumed for FPL Glades Power Park includes

24   petroleum coke.  It includes petroleum coke, foreign coal, and

25   Central Appalachian coal.  Once again, it has to be -- this

FLORIDA PUBLIC SERVICE COMMISSION

814

1   document also has to be, it has to be understood that petroleum

2   coke is an opportunity fuel.  It's not a fuel that one can sign

3   long-term contracts for.  And because it is an opportunity

4   fuel, you need to be careful about the usage of that fuel when

5   you look at your fuel mix.

6        Q    There's a 20 percent limit on how much you can put in

7   the proposed Glades coal plant?

8        A    That is correct.

9        Q    For petcoke.  And this document, Exhibit 91, has the

10   projected price, correct?

11        A    Yes, it does.

12        Q    And you have no reason to think that price is wrong,

13   do you?

14        A    It's a projection.  It's a projection of future

15   prices.

16             MR. GUEST:  Let's turn to the matter of, you know,

17   I'm going through the items on your benefits list here, let's

18   turn to the matter of capital cost of building the proposed

19   Glades pulverized coal plant.  I think it might be useful at

20   this juncture to compare some very gross numbers from the

21   petition to do a comparison.  So we're going to hand out Page

22   10, I think, of the petition so we can look at some base

23   numbers.  Should this be separately marked as an exhibit even

24   though it's Page 10 of the petition?

25             MS. BRUBAKER:  I don't believe it needs to be

FLORIDA PUBLIC SERVICE COMMISSION

815

1   separately marked.  And, actually, on that note, I would note

2   that what has been identified as Exhibit 170 has actually been

3   marked as Exhibit 121, it's Mr. Furman's Supplemental Exhibit

4   RCF-29.  The only difference, that we can tell, is that it is

5   in color.  If that's significant, we can certainly leave it

6   marked as 170.  If it's not --

7             MR. GUEST:  We would prefer to leave it in color.

8             MS. BRUBAKER:  That's fine.  I just wanted that

9   clarification.  Thank you.

10             MR. GUEST:  Is everyone together here with us?

11   BY MR. GUEST:

12        Q    Now, Mr. Hicks, we start with a total estimated cost

13   of 5.7 billion, is that correct?

14        A    That is correct, in 2014 dollars.

15        Q    And then you could take out some numbers, $125

16   million for land acquisition for the site and 73 million for

17   transmission line land.  That is about 200 million, right?

18        A    The document that I have before me says that there is

19   125 million for land acquisition, which is correct, and

20   73 million for land acquisition for off-site transmission

21   systems, included in the 5.7 billion.

22        Q    Right.  So if you wanted to take out land acquisition

23   costs, you would take out about 200 million?

24        A    Correct.

25        Q    So that would leave you at about 5.5 billion, is that

FLORIDA PUBLIC SERVICE COMMISSION

816

1   right?

2        A    In 2014 dollars, yes.

3        Q    And so, you have 18, I'm sorry, 1960 kilowatt hour,

4   megawatt capacity -- pardon me for garbling this story -- and

5   so if you take that 5.5 billion, and divide it by 1960, your

6   cost per kilowatt hour comes out to $2,704.

7        A    No, that's not correct.  The cost per kilowatt hour

8   would not be $2,704.

9        Q    I'm sorry, the cost per kilowatt.

10        A    The cost per kilowatt installed, yes, in 2004

11   dollars.  And I don't have a calculator in front of me, so I

12   don't have a way of verifying your --

13        Q    Well, let me supply you with a state-of-the-art

14   calculator.  It may take a minute, because that is a

15   solar-powered calculator just to conserve energy.

16        A    What was the number you came up with?

17        Q    2,704, $2,704.

18        A    In 2014 dollars?

19        Q    Yes.

20        A    At the summer-rated capacity of the unit, 1,960

21   megawatts.

22        Q    That's it.  And if you were to compare that to a

23   document we used a few moments ago, Number 169, do you have

24   that with you?

25        A    Yes, I do.

FLORIDA PUBLIC SERVICE COMMISSION

817

1        Q    Under Number 13, the third line, this is for the TECO

2   Polk Unit Plan, the new one that's going to come on-line in

3   2013, the third line shows the total installed cost is

4   $2,626.70.

5        A    I see that, but I believe that calculation is done on

6   the winter capacity and not the summer capacity.  There is

7   nothing in here that indicates it is done on summer capacity.

8   Second of all, it is a 2013 number rather than a 2014 number.

9   Number three, it fails to account for the delta in terms of

10   transmission upgrades necessary.  A proper comparison would be

11   for an IGCC plant that's is built at the Glades Power Park site

12   and has an equivalent amount of transmission costs.

13             Now, we did that analysis for the FPL clean coal

14   technology selection study.  And what we found was that the

15   capital cost of a similarly sized IGCC unit would be

16   36.8 percent higher in same year dollars.

17             The other important thing to understand here is that

18   this is a 2006 document, and what it represents is an estimate

19   before feasibility and frontend engineering and design studies

20   are done.  The way an IGCC plant is developed is you single

21   source it.  There's about six different developers out there,

22   but you single source with a vendor.  You pick a vendor, and

23   you engage that vendor in a contract and they do a feasibility

24   study for you, and that takes up to a year.  At the end of that

25   feasibility study period, you get a cost with a very wide, a

FLORIDA PUBLIC SERVICE COMMISSION

818

1   very large error factor in it.  Then you do what's called a

2   frontend engineering and design study, which is a much more

3   detailed study to come up with a much more detailed cost.

4             This does not represent -- what's in this document

5   does not represent the results of a frontend engineering and

6   design study analysis.  And what is very important about that

7   is what we're seeing over and over again is when the frontend

8   engineering design study is completed, the costs rise

9   dramatically.

10             And there's a number of examples of that over the

11   last four months.  The first example is American Electric

12   Power.  They are proposing a 600-megawatt IGCC plant in Ohio

13   and one in West Virginia.  When they proposed the plant cost

14   early in that process similar to this, they proposed a cost of

15   about 1.1 billion.  Then they worked on the frontend

16   engineering and design study with GE and Bechtel.  In December

17   of 2006, they were scheduled to file, make a filing with the

18   Ohio Public Utilities Commission on the cost of the plant.

19   Their goal was to get the cost of that 600-megawatt IGCC plant

20   to within 20 percent of a similarly sized pulverized coal

21   plant.

22             Now, should we mention that going from a 600-megawatt

23   pulverized coal unit to a 980-megawatt unit, which is the size

24   of one of the two at FPL Glades Power Park, there's economies

25   of scale there, coal technologies and economies of scale

FLORIDA PUBLIC SERVICE COMMISSION

819

1   technologies.  The larger you build it, the smaller the capital

2   cost per kilowatt hour installed.

3             So moving from a 600-megawatt pulverized coal unit to

4   a 980-megawatt pulverized coal unit you get about a 15 percent

5   decrease in cost per kW installed.  So if AEP was able to

6   achieve its goal of being within 20 percent of a similarly

7   sized pulverized coal unit, they would be about 35 percent more

8   expensive on a dollars per kW basis versus a 980-megawatt unit.

9   At the end of December, they made a filing with the Ohio Public

10   Utilities Commission saying that they were going to have to

11   delay their filing on cost to the late summer to early fall of

12   2007 because they were unable to achieve their stated goal of

13   20 percent.

14             The second example of the rising costs with respect

15   to IGCC capital costs as you move down the engineering path,

16   was a filing made on April 2nd, 2007 by Duke Indiana before the

17   Indiana Utilities Regulatory Commission.  On April 2nd, they

18   filed the results of their frontend engineering design study.

19   They stated that that feed study took 13 months, 11 full-time

20   employees, 15 part-time employees, and 30,000 man hours.

21             As a result of that study, the cost that they

22   reported to the Indiana Utilities Regulatory Commission had

23   risen to $2 billion in 2011 dollars.  Escalating that to 2014

24   puts it at about $3,500 a kW, which is very similar to the

25   price, the cost that we had in the FPL Clean Coal Technology

FLORIDA PUBLIC SERVICE COMMISSION

820

1   Selection Study.

2             In addition to that, another data point was the

3   Masaba Project (phonetic), which is a 600-megawatt IGCC project

4   proposed for Minnesota.  The Masaba Project filed for tax

5   credits under the Energy Policy Act of 2006, and there is a DOE

6   document associated with that on the award of those tax

7   credits.  The cost, the estimated cost of the plant in the

8   spring of 2006 was $2,155,000,000 for a 600-megawatt plant.

9   Over $3,500 per kilowatt installed in 2011 dollars, once again.

10             It should be mentioned that 12 days ago, April 12th,

11   two administrative law judges in the state of Minnesota after

12   hearing testimony on the Masaba Project recommended that the

13   Minnesota Public Utilities Commission deny the Masaba Project's

14   contract or proposed contract with Excel because it was not in

15   the best interest of the customers of Minnesota in great part

16   because the costs were unreasonable.

17             So when you look at IGCC projects, it's very

18   important to understand the delta between the original

19   estimates, feasibility study estimates and when you go through

20   that feasibility and more detailed engineering analysis and how

21   those costs rise.  If you look at what happened with AEP, you

22   look at what happened with Duke Indiana, and you look at the

23   actual numbers, the proposed numbers for the Masaba Project,

24   those numbers are consistent with the numbers that are in the

25   FPL Clean Coal Technology Study, which indicate a cost premium,

FLORIDA PUBLIC SERVICE COMMISSION

821

1   a capital cost premium of about 37 percent for an IGCC plant.

2        Q    Tampa Electric Company had actually constructed an

3   IGCC plant in 1996.

4        A    Yes, they did.  And the original cost of that

5   plant -- the original projected cost of that plant was

6   $303 million of which 50 percent of it was funded by the DOE.

7   The actual cost of the plant as reported by the DOE was

8   $606 million, double the original projected cost.

9        Q    And based on the experience that TECO has had, they

10   are building another one.

11        A    They are proposing to build a 600-megawatt unit, a

12   coal-to-electricity 600-megawatt IGCC plant that has never been

13   built before, and they have not completed the feasibility and

14   feed study analysis to the best of my knowledge.

15        Q    Now, let's turn to another item on your list here.

16   We have dealt already with the fuel costs, petcoke, et cetera,

17   petcoke and coal.  Let's turn to -- we dealt with reliability.

18   Let's turn to technological maturity and construction risk.

19             Now, it's your testimony -- well, first, let me ask a

20   basic background question.  It's true, isn't it, that

21   electrical powered utilities tend to be risk averse?  Is that

22   right?

23        A    I don't think that's a good question to ask me.  I

24   can't really comment on that, whether they are risk averse or

25   not risk averse.  I think, generally, utilities have a mandate

FLORIDA PUBLIC SERVICE COMMISSION

822

1   to produce reliable cost-effective power for their customers,

2   and they take actions to produce that type of power for their

3   customers.  Your characterization of risk averse is one that I

4   can't really comment on.

5        Q    You have testified that IGCC is not really

6   commercially available, is that right?

7        A    No.  What I have testified is that IGCC plants, there

8   have been four coal-based IGCC plants built in the world,

9   relatively small, government subsidized, and that the next wave

10   of IGCC plants in the 600-megawatt range have not been built

11   yet.  So are they commercially available?  You could design and

12   build one if you wanted to, if that was your choice, if that

13   was the utility's choice, but those plants are not in operation

14   today.

15        Q    The earliest one is actually 13 years ago.

16        A    That was a demonstration.  Actually the earliest IGCC

17   plant that I am aware of is the Coolwater Facility (phonetic),

18   which was constructed in Southern California.  It operated for

19   a few years, had significant problems, and then was torn down.

20             There were four coal-based IGCC plants, relatively

21   small demonstration projects built in the early 1990s.

22   Actually, I correct myself.  There was actually five built,

23   three in the United States and two in Europe.  One of the three

24   in the United States, Pinyon Pine (phonetic), was constructed

25   by Sierra Pacific Power with a grant from the Department of

FLORIDA PUBLIC SERVICE COMMISSION

823

1   Energy.  It was a complete failure.  It never operated.  The

2   gasifier was never able to operate, so it was shut down.  So

3   there was actually five built, four in operation.

4             MR. GUEST:  I would like to ask the witness some

5   questions about a document that has been previously admitted as

6   Staff Exhibit Number 2, composite exhibit, and the Bates stamp,

7   which I think is the exhibit number, or the subnumber is 313.

8   Those being the last three digits.  And 314, it is two pages.

9             CHAIRMAN EDGAR:  Ms. Brubaker.

10             MS. BRUBAKER:  Madam Chairman, if I could just

11   actually step back a second.  Earlier a couple of pages from

12   FPL's petition was handed out.  At the time the document was

13   being identified verbally, I misunderstood what was being

14   described.  If Sierra Club wishes, I think it would be

15   appropriate to identify that document separately.  And, if so,

16   that would be 171.

17             CHAIRMAN EDGAR:  Okay.  For clarity we can go ahead

18   and do that.

19             MR. GUEST:  Certainly.  171 is the first page and

20   Page 10 of the petition by FPL.

21             MS. BRUBAKER:  Which would have us at Number 172 for

22   the document just handed out.  Just for clarity, this is

23   straight from the staff exhibit.  You do wish it separately

24   identified?

25             MR. GUEST:  For simplicity, yes.

FLORIDA PUBLIC SERVICE COMMISSION

824

1             CHAIRMAN EDGAR:  Okay.  Thank you.

2             (Exhibit 171 and 172 marked for identification.)

3   BY MR. GUEST:

4        Q    Have you had an opportunity to review this exhibit,

5   Mr. Hicks?

6        A    I am looking at it right now.  Yes, I have looked at

7   the document.

8        Q    Let's start with the total number of coal plants.

9   There is the one in Nuon in the Netherlands from 1994 that runs

10   on coal and biomass, correct?

11        A    I see a Nuon (Demkolec), 253-megawatt net rating of

12   power from coal and biomass, yes.

13        Q    And below that is the Wabash unit in Indiana from

14   1995 that runs on coal?

15        A    Yes.  One of the four coal-to-electricity plants that

16   are in operation, IGCC plants.

17        Q    The third one is the TECO 1996 plant.

18        A    Yes.  I would note that the TECO, this line for the

19   TECO plant has an inaccurate capital cost number.  It has the

20   original projected cost of 303 million, which was 50 percent

21   funded by the DOE.  The actual cost of the plant reported by

22   the DOE was 606 million, double the original projected cost.

23        Q    The next one is the Czech Republic plant, which is

24   coal and coke from 1996.  That is coal and coke.  I'm just

25   going through the coal plants first.  Do you see that one?

FLORIDA PUBLIC SERVICE COMMISSION

825

1        A    Yes, I see that one.

2        Q    Now we are up to four.  Then you have got the one in

3   Spain, three down from that.

4        A    And, you know, one thing I would caution you on is

5   Mr. Jenkins has a greater knowledge of some of these other

6   plants, such as the Czech Republic plant, et cetera, and how

7   much of those plants are actually operating on steam.

8        Q    Well, we're just counting them right now.  And then

9   we have -- you actually have the Schwarze plant that operates

10   on lignite and waste.  Lignite is a kind of coal, is that

11   right?

12        A    It's a very small plant, a 40-megawatt plant, and my

13   understanding of it, it produces mainly methanol.

14        Q    But the question was is lignite a kind of coal?

15        A    Yes, it is.

16        Q    And then we have two plants at the end of this second

17   page in China that run on coal.

18        A    I don't know.  Once again, I don't have any

19   verification that these plants are actually in operation.  I

20   don't know from this document whether those two Chinese plants

21   are in operation.  One appears to be a 2007.  I don't know

22   whether they are announced in operation and construction, don't

23   have any verification on that.

24        Q    So what we have on this list is eight plants that are

25   IGCC plants that are operating partly or entirely on coal.

FLORIDA PUBLIC SERVICE COMMISSION

826

1        A    And may or may not be producing power at all or

2   relatively small, yes.

3        Q    And then if you look at the total number of operating

4   IGCC facilities, which is what this document is, the total

5   number is 17.

6        A    And it includes various fuels.  As I stated earlier,

7   there is a significant difference between operating on coal to

8   produce power versus other types of fuels.  Once again, Mr.

9   Jenkins can provide you greater detail on that.

10        Q    And now turning to plants that are in the works, I

11   would like to refer to Staff Exhibit Number 2 at Bates stamp

12   Pages 309 to 11, which we are fixing to distribute here.

13             MR. ANDERSON:  Just as a suggestion as things are

14   being passed out, Mr. Jenkins is probably the witness for all

15   the international projects if you have questions, but however

16   you want to proceed.

17             MR. GUEST:  I think we can just make a couple of

18   quick points here.

19             CHAIRMAN EDGAR:  Okay.  So I'm on 173, proposed

20   projects IGCC and polygeneration in North America?

21             MR. GUEST:  Right.

22             (Exhibit 173 marked for identification.)

23   BY MR. GUEST:

24        Q    And I would like you to either count them or assume

25   that I am correctly counting that there is 39 plants in the

FLORIDA PUBLIC SERVICE COMMISSION

827

1   works in North America that are IGCC plants.

2        A    I think you are mischaracterizing by calling them "in

3   the works".  I think those are proposed plants.  Many of those

4   plants you can see the start up here is not available.  There

5   is a big difference between a proposed plant and one that

6   actually gets built.  For example, there is over -- I believe

7   over 150 pulverized coal plants proposed for the United States.

8   It's clear to us that many of those will not be built.

9             There are literally thousands of pulverized coal

10   plants proposed in the world, many of those will not be built.

11   This type of difference between proposed and actual built is

12   something that we have seen over and over again.  Many, many,

13   many gas-fired combined cycles were proposed during the gas

14   bubble in the late part of the last decade, early part of this

15   decade.  The overwhelming majority of those have never been

16   built.

17             I would also mention that some of these are, for

18   example, you have the TXU 2014 Colorado City and Henderson

19   plants, those are announcements that they are looking at the

20   possibility of building those plants.  So saying those plants

21   are in the works is, I think, a mischaracterization of those

22   facilities, many of which are proposed or announcements of

23   potential plants.

24        Q    Well, with that correction, you would agree with me

25   then that there is about 39 proposed IGCC plants in the United

FLORIDA PUBLIC SERVICE COMMISSION

828

1   States?

2        A    It appears to be somewhere around 35 to 40 proposed

3   facilities in the United States.  Many of them appear to not be

4   producing power, to be producing other types of chemicals.

5        Q    And almost all of these are operating on some kind of

6   coal or coal waste.  That's the proposal, isn't that correct?

7        A    That's the listed fuel on this sheet.

8        Q    Now, I would like to turn on this issue lastly to

9   Staff Exhibit Number 2, Page 316 and 317, which will be

10   following our numbers, 174.

11             CHAIRMAN EDGAR:  Yes.

12             MR. GUEST:  Which is Proposed IGCC Plants Other Than

13   in North America.

14             CHAIRMAN EDGAR:  Thank you.

15             (Exhibit 174 marked for identification.)

16   BY MR. GUEST:

17        Q    Have you had an opportunity to review that?

18        A    Yes, I have.

19        Q    So we have about another 27 proposed plants?

20        A    Proposed, yes.  And I don't know what state they are

21   in, how much is behind them, are they just an initial

22   announcement, et cetera.  As a sort of point on this, if you

23   look at Germany's long-run supply plan through the year 2020,

24   they propose 37,150 megawatts of coal-fired power plants.  Of

25   those 37,150 in their official supply plan about

FLORIDA PUBLIC SERVICE COMMISSION

829

1   36,700 megawatts are pulverized coal and circulating fluidized

2   bed and only 450 in their official plan is IGCC.  Once again,

3   what information proposed really gives you is rather nebulous,

4   because many proposed plants are never built.

5        Q    And most of the ones on this list are coal or coal

6   waste?

7        A    Yes.

8        Q    So if you put together that 27 and the 39 proposed

9   for the United States, we have 66 around the world, and

10   presumably they are basing their proposals on the experience of

11   the 17 existing plants that have been in service for up to 13

12   years, is that correct?

13        A    I have no evidence to support whether or not they are

14   based on the operations of existing plants or not.  One thing I

15   would note is each one of these plants with the exception of

16   the Nuon plant in the Netherlands, which is mischaracterized as

17   a 1200-megawatt plant, that's actually a 600-megawatt IGCC and

18   a 600-megawatt combined cycle, that all of those plants are

19   less than -- appear to be less than 600 megawatts.

20        Q    Now, continuing on our comparison of benefits of the

21   proposed Glades plant versus IGCC, let's turn to carbon capture

22   costs under the assumption that there will be some sort of

23   regulatory system or tax or cap and trade or something that

24   will provide an incentive in the future to capture and

25   sequester carbon dioxide.

FLORIDA PUBLIC SERVICE COMMISSION

830

1             MR. GUEST:  And in that connection, I think I would

2   like to hand out and show the witness a Department of Energy

3   exhibit from the National Energy Technology Laboratory at the

4   Department of Energy.

5             CHAIRMAN EDGAR:  Okay.  175, Cost of Electricity

6   Comparison.

7             (Exhibit 175 marked for identification.)

8   BY MR. GUEST:

9        Q    Have you had an opportunity to review this, Mr.

10   Hicks?

11        A    I am currently looking at it.  I note it says, "Note:

12   Preliminary results as of September 2006.  Final report release

13   date January 2007."  It does not say where these plants are

14   located, it does not give any backup with regard to how these

15   costs were calculated.

16        Q    Okay.  I would like to note that this is also listed

17   as RCF-7, just for the record.  And I guess this is Number --

18             CHAIRMAN EDGAR:  175.

19   BY MR. GUEST:

20        Q    So let's just look at a comparison of the carbon

21   capture costs that you can infer from this bar graph, starting

22   with the tan bars, the two of them on the far left.  Do you see

23   those?

24        A    Yes, I do.

25        Q    And you see that by having carbon dioxide capture you

FLORIDA PUBLIC SERVICE COMMISSION

831

1   add an additional 1.58 cents to the cost per kilowatt hour.  Do

2   you see that?

3        A    I'm not sure how that's calculated, what the basis

4   for that is, what type of plant they are looking at, what type

5   of carbon capture system they are using, et cetera.  So it

6   shows that.  What value that has without looking at the backup

7   to that you just can't make a determination of what the value

8   of that is.

9        Q    But you agree with me that the difference is 1.58

10   cents?

11        A    On this diagram, yes, 1.58 cents.

12        Q    Per kilowatt hour.  And let's assume that we have

13   800 -- I'm sorry, 8,760 hours in a year, because there is 24

14   hours in a day and 365 days in a year.  And further that you

15   will operate the plant at 90 percent of the time at its

16   capacity of 1960 megawatts.

17             I don't see you working the calculator, Mr. Hicks.

18        A    Yes, because there is nothing in here that says this

19   is a 1960-megawatt plant, nothing in here that indicates to me

20   what the -- where these costs were derived from.  We know from

21   our own analysis the NETL capital costs and operating costs

22   that they are significantly below the industry.  They are as

23   much as 100 percent below the recent indications of costs that

24   I mentioned to the Commission, et cetera.

25        Q    Just let's continue with this calculation.  I

FLORIDA PUBLIC SERVICE COMMISSION

832

1   understand the point that you have made.  Using the Department

2   of Energy document here, and applying the 1.58 cents to the

3   number of hours in the year to the capacity of the plant

4   assuming it's on line 90 percent of the time, you come up with

5   a carbon capture cost for IGCC estimated at about $241 million

6   per year.  Is that correct?

7        A    Without sitting down and doing the calculation, I

8   can't verify that.

9        Q    Well, you have got a calculator right next to you.  I

10   gave it to you.

11        A    But I would prefer to take my time and do the

12   calculation rather than --

13             MR. GUEST:  Okay.  Well, maybe what we can do is I

14   would like the record to reflect that that is what I have done,

15   and give the witness an opportunity after a break to correct

16   the error if there is one.  May we do that?

17             CHAIRMAN EDGAR:  Mr. Anderson.

18             MR. ANDERSON:  No, we don't agree with that.  We

19   think it is an entirely inappropriate comparison.  It is well

20   known this document is based upon -- I think it was a generic

21   midwest plant.  The witness has testified numerous bases why

22   there is really no foundation for this type of computation.  If

23   counsel's client wishes to introduce a computation, they should

24   do it with their own witness.

25             MR. GUEST:  This is something that one can take

FLORIDA PUBLIC SERVICE COMMISSION

833

1   official recognition of because this is the communicative

2   property of multiplication.  That is all this is.  My point is

3   very simple, is that 1.58 cents applied to the number of

4   kilowatt hours being generated at 90 percent capacity produces

5   a cost of 244 million.  That's multiplication, that's all.  It

6   is another way of expressing 1.58 cents.

7             CHAIRMAN EDGAR:  Ms. Brubaker.

8             MS. BRUBAKER:  It seems to me that we are kind of

9   talking past each other.  The pure math, I don't think anyone

10   is disputing.  I think what the witness is disputing is the

11   underlying facts and assumptions which he doesn't actually have

12   available to him.  Even if he did, I suppose he might take

13   still some exception to those underlying assumptions.  The math

14   is what it is.  With that understanding, can you rephrase the

15   question, or --

16             MR. GUEST:  Well, all I'm trying to do is, I'm making

17   one very narrow point, which is that a difference of 1.58 cents

18   translates, if that were correct, would translate to a

19   difference of about $244 million a year.  That's all.

20             CHAIRMAN EDGAR:  Do you have further questions?

21             MR. GUEST:  Yes.  Then I want to compare to

22   supercritical, the right set of green bars.

23   BY MR. GUEST:

24        Q    And, if you look at those, Mr. Hicks, you see that

25   that is comparing 8.35 cents 4.97 cents, which gives you a

FLORIDA PUBLIC SERVICE COMMISSION

834

1   difference of 3.38 cents.  Is that correct?

2        A    That is what it says on this document, yes.  But,

3   once again, you don't know where this plant was built, you

4   don't know what the basis for the capital costs are, you don't

5   know what the basis is for the carbon capture system that's on

6   here.  Is this an MEA system; is it an ammonia chill system?

7   So without having that knowledge and being able to comment on

8   that, I can't comment on the veracity of these numbers whether

9   they make any sense or not.

10        Q    Well, my point very simply is that using the

11   Department of Energy document that we have before us, you would

12   agree with me that 3.38 cents per kilowatt hour translates to

13   an additional cost of $522 million per year.  Those are

14   equivalent numbers.

15        A    That is your calculation.  I will agree that is your

16   calculation.

17        Q    Okay.  And I can assure you that I did it several

18   times.  And then the last issue is that if this is correct,

19   based on this issue, and if those numbers are correct, and I

20   assure you they are, the difference in carbon capture costs is

21   a quarter of a billion dollars every year, if this is right?

22        A    And I would say from what we know of NETL, that that

23   NETL analysis is not correct, and does not include the most up

24   to date carbon capture systems.

25        Q    Now, our previous stipulation that we reached was the

FLORIDA PUBLIC SERVICE COMMISSION

835

1   confidential study for Florida Power and Light by M.J. Bradley

2   and Associates, that we agreed to read a sentence into the

3   record and ask the question of the witness but not introduce

4   the document.  And so here we have this.  Let me see if it

5   actually is -- it is actually two sentences.  And it is IGCC

6   versus supercritical PC comparison, that is what it is under.

7   And it reads, "Generally speaking, IGCC plants are viewed as

8   cleaner than conventional PC plants in that they have equal or

9   lower emissions of conventional and hazardous air pollutants,

10   use less water, and produce smaller amounts of solid wastes.

11   IGCC plants are also generally more efficient than PC plants,

12   and perhaps, more importantly, they have the ability to capture

13   and collect CO2 much more cost-effectively than PC plants."

14             Do you disagree with the conclusions of these

15   consultants?

16        A    Yes, I do.  I disagree with those conclusions.  That

17   is an environmental consulting firm.  That is a firm that has

18   never designed a coal power plant of any technology.  Never

19   built one, never operated one.  That an opinion of an

20   environmental consulting firm.  And there is ample evidence

21   that indicates that many of those conclusions are incorrect.

22             MR. GUEST:  May I have a moment?  May we have a

23   couple of minutes?  I'm having trouble making a conversion.

24             CHAIRMAN EDGAR:  Take five in place.  Everybody stay

25   close.

FLORIDA PUBLIC SERVICE COMMISSION

836

1             (Brief recess.)

2             CHAIRMAN EDGAR:  Okay.  We are going to go back on

3   the record from break.

4             Mr. Guest.

5             MR. GUEST:  We have reached an agreement where what

6   we are going to do is I'm going to read a sentence or two of

7   the same confidential report to the witness, but he's going

8   have an opportunity to review the preceding pages and think

9   about it before he answers.  That's our compromise.

10             CHAIRMAN EDGAR:  Mr. Anderson.

11             MR. ANDERSON:  Yes.  We just wanted the witness to

12   have the context of the sentence or two he is looking at.

13   BY MR. GUEST:

14        Q    Do you have it, Mr. Hicks?

15        A    I have two pages in front of me.  One that's labeled

16   5-3 in the bottom right corner and one that is labeled 5-2 in

17   the bottom right corner.

18        Q    Would you be kind enough to review those two pages,

19   and when you have reviewed them I may ask you a question or

20   two.

21        A    Okay.  I have looked through them.

22        Q    This is yet another excerpt from the confidential

23   Bradley study of the proposed Glades coal plant, and on one of

24   the pages it reads --

25             MR. ANDERSON:  If we might pause for a moment.  I

FLORIDA PUBLIC SERVICE COMMISSION

837

1   don't think that is the right characterization of the document.

2             MR. GUEST:  Go ahead.  Maybe we can --

3             MR. ANDERSON:  Do you have the first page?  Just tell

4   us the title of the document, because I think it was pre-FGPP.

5             MR. GUEST:  Okay.  Assessment of future environmental

6   liabilities --

7             MR. ANDERSON:  Right.  Thank you.

8             MR. GUEST:  -- facing a new coal-fired power plant in

9   Florida, April 2006 Report Update prepared by M.J. Bradley and

10   Associates on behalf of Florida Power and Light.

11             MR. ANDERSON:  Thank you for being clear.  That was

12   exactly my point that it wasn't FGPP specific.

13             CHAIRMAN EDGAR:  Okay.  Thank you, Mr. Anderson.

14             Mr. Guest.

15   BY MR. GUEST:

16        Q    And on one of the pages, the second one that you

17   have, it reads, "The avoided cost of carbon dioxide from the

18   IGCC is less than half that from the PC plant.  Similar studies

19   by EPRI and others have produced similar results."

20             And my question is I just showed you a set of

21   computations that showed that according to the Department of

22   Energy, Number 175, according to the Department of Energy

23   National Energy Technology Laboratory Report, the cost would be

24   about double.  Isn't it true that the confidential report that

25   says about half, one, in the first sentence, and, two, the

FLORIDA PUBLIC SERVICE COMMISSION

838

1   similar studies by EPRI and others, are all consistent with

2   that finding that the cost for IGCC of carbon capture is about

3   half?

4        A    No, I would not agree with that, and let me give you

5   some more clarity, some more color on that.  Many of these

6   studies, and this is an example of it, were done on older types

7   of carbon capture systems.  If I were to come before the

8   Commission two months ago, I would have told you there's about

9   25 different R&D programs out there for carbon capture from

10   pulverized coal plants.  Today I can come here and tell you

11   there is well over 30 because of the concentration now on

12   carbon capture.

13             One of the most promising examples of carbon capture

14   for pulverized coal plants is a system being developed by

15   Alstom (phonetic) called an ammonia chill system.  That ammonia

16   chill system has been recognized by many as being a quantum

17   leap in technology with regard to carbon capture for pulverized

18   coal systems.  One indication of that is in the second

19   paragraph of Page 5-2, where it talks about the volume of

20   syngas being an issue.

21             One of the challenges for IGCC is that about

22   20 percent of the total amount of electricity produced by IGCC

23   plants is actually burned up inside the plant to keep the plant

24   running.  For a PC plant, about 6.5 to 7 percent is actually

25   used up.  So it is a big advantage for a PC plant.

FLORIDA PUBLIC SERVICE COMMISSION

839

1             One way of substantially reducing the cost of CO2

2   capture for a PC plant is to chill or bring down the

3   temperature of the flue gas.  By bringing down the temperature

4   of the flue gas from 120 to 140 degrees down to about

5   35 degrees Fahrenheit, the volume of that flue gas is

6   dramatically reduced, dramatically reducing the cost of

7   subsequent capture.  This ammonia chill process has actually

8   been embraced by several utilities, including We Energies

9   (phonetic), which now is a 5-megawatt test pilot at their

10   Pleasant Prairie project, and by AEP.  AEP is doing a

11   30-megawatt project in West Virginia and then following up with

12   a much larger project that will commercially demonstrate this

13   technology.

14             So things are changing very rapidly with regard to

15   carbon dioxide capture.  So these type of statements based upon

16   older obsolete technologies may or may not be true,

17   particularly when you look at the differences between a

18   600-megawatt IGCC plant updated for those feed costs, those

19   more robust costs that come from going through the feasibility

20   and frontend engineering design analysis versus a 980-megawatt

21   or 2000-megawatt plant at the FGPP site.

22             It is fairly widely recognized by many that the costs

23   for carbon capture for both IGCC and PC will converge over

24   time.  This study mentions an EPRI study.  There is a recent

25   EPRI study done for CPS in Texas looking at the comparison

FLORIDA PUBLIC SERVICE COMMISSION

840

1   between an ultra-supercritical plant and an IGCC plant.  The

2   conclusion is both with and without capture, the cost of

3   electricity from the ultra-supercritical plant is less.

4             Also, the MIT study that recently came out in March,

5   a well-received MIT study stated that they also anticipated the

6   cost for the two types of capture systems to converge.  And

7   given the uncertainty of future costs, it makes a very primary,

8   a first and very primary recommendation.  The first and primary

9   recommendation of the MIT study is that entities such as

10   utilities that are designing and building coal-fired power

11   plants today, that they design those plants to be as efficient

12   as economically justifiable.  And by doing so you reduce the

13   amount of CO2 that has to be dealt with no matter what regime

14   or what control mechanism is employed.

15             With FGP, with the Glades Power Park, that is exactly

16   what FPL is doing.  It is building the most efficient

17   coal-fired power plant ever proposed for the United States, and

18   that coal-fired power plant will be advantaged versus every

19   other type of coal plant.  Just during this cross-examination,

20   I showed you that the next generation TECO proposed IGCC plant

21   was almost 10 percent less efficient, meaning almost 10 percent

22   more CO2 that is going to have to be captured at a later date.

23   So, I don't agree with what is in this thing because technology

24   is changing rapidly.

25        Q    Just one final follow-up.  A second to final

FLORIDA PUBLIC SERVICE COMMISSION

841

1   follow-up apparently, is you do agree that the quantity of flue

2   gases pouring out of the smoke stack, if you will, in your

3   pulverized coal plant is 160 times larger?

4        A    No, I don't.  That depends on the type of IGCC

5   technology that's employed.  The amount of flue gas volume

6   coming out of a PC plant versus an oxygen-blown IGCC plant is

7   different than a comparison of volume between a pulverized coal

8   plant and an air-blown IGCC plant.

9        Q    Okay.  I want the comparison to be syngas, like the

10   TECO plant, versus a supercritical pulverized coal plant.  That

11   is 160 to one, isn't it?

12        A    I don't know whether it is 160 or not.  I do know the

13   volume is higher, but as I mentioned earlier, with the ammonia

14   chill process for a very small penalty it terms of parasitic

15   load, or the energy that is used up inside the plant, you can

16   dramatically reduce that volume of flue gas that needs to be

17   treated for CO2 emissions.

18             Remember I said earlier, an IGCC plant, about

19   20 percent of the gross power from that plant is used up

20   internally to run the plant versus about 6.5 percent for

21   pulverized coal plant.  For a penalty of only about a percent

22   or two more you can dramatically reduce the volume of flue gas

23   that needs to be treated in a pulverized coal plant by chilling

24   that, and that is exactly what this Alstom ammonia chill

25   program is addressing.

FLORIDA PUBLIC SERVICE COMMISSION

842

1        Q    That is not part of this plant, is it?

2        A    This plant can be readily modified to include a wide

3   variety of carbon capture, carbon conversion, and advanced

4   combustion techniques.  This plant is on a site that is 4,900

5   acres, of which 4,000 will be on the plant side, and we are

6   leaving space in the design to allow this plant to be readily

7   upgraded to include carbon capture systems when and if they are

8   needed.

9        Q    So what you have now is basically a footprint.  Does

10   it have grass on it?

11        A    We have a footprint, we have a design for the plant,

12   and that is very similar to IGCC plants.  IGCC plants from the

13   major vendors are leaving a space for carbon capture in the

14   plant design similar to what is being done with the FPL Glades

15   Power Park.  In fact, General Electric will tell you that they

16   are leaving a space that is 500 feet by 500 feet in the design

17   for potential future carbon capture.

18        Q    That's about four acres of grass, right?

19        A    It about four acres.  It may have grass on it or not.

20   I would mention that most of this site is in sugarcane

21   production right now.

22             MR. GUEST:  Okay.  No further questions at this time.

23             CHAIRMAN EDGAR:  Mr. Krasowski, do you have questions

24   on cross for this witness?

25             MR. KRASOWSKI:  Yes, I have a few, Madam Chair.

FLORIDA PUBLIC SERVICE COMMISSION

843

1   Thank you.

2                          CROSS EXAMINATION

3   BY MR. KRASOWSKI:

4        Q    Hello, Mr. Hicks.

5        A    Hello.

6        Q    Mr. Hicks, I noticed in your testimony that you

7   are -- let's see, you're in charge specifically of the -- you

8   head up this project, the development of this specific project?

9        A    Yes, I am.  I am the senior director of project

10   development.  I have direct responsibility for the FPL Glades

11   Power Park.

12        Q    So in doing so, you are specifically focussed on this

13   project.  Have you done an evaluation or been involved in the

14   evaluation of alternatives or energy efficient programs?

15        A    Prior to about May of 2006, I was the development

16   group at FPL, and I had responsibility for the -- well, I was

17   the Director of Project Development responsible for the West

18   County Energy Center, which was granted a site certificate in

19   December.  I was in charge of the nuclear development.  I was

20   in charge of coal-fired development.

21             I have also worked on the wind demonstration project

22   that FPL is working on in the state of Florida.  I would say

23   around the late fall of 2005, I commissioned a study, a mapping

24   of the state of Florida with regard to potential wind

25   generation.  And we used a firm called Wind Logics, which is a

FLORIDA PUBLIC SERVICE COMMISSION

844

1   firm that we use on the FPL Energy side.  And I know that being

2   a customer of FPL that you are probably aware that FPL Energy

3   competes with a utility out of Spain of being the largest

4   developer of wind turbines in the world.

5             So we employed Wind Logics to do wind mapping of the

6   state of Florida, and there are three conclusions that came out

7   of that wind mapping.  Number one, the State of Florida is a

8   relatively poor state with regard to wind resources.  It

9   doesn't have the type of wind energy necessary to make wind

10   generation commercially viable, particularly with regard to

11   independent power development.

12             Number two, the wind that is available in the state

13   is really concentrated on the coastline between South

14   Hutchinson Island in St. Lucie County up to Jacksonville on the

15   east coast of the state and sort of around the horn between

16   Sarasota and Naples on the west coast.

17             The maximum capacity factors, or availability factors

18   for wind in those areas range between 15 to 20 percent.  As a

19   rule of thumb, a typical capacity factor that one needs with

20   production tax credits to make wind viable is about 33 percent.

21             And then the third conclusion we came to was that

22   wind is a seasonal resource in the state of Florida.  Really

23   what you see is that what wind there is is really concentrated

24   between October through April of the next year.

25             Given that set of data, I then commissioned two

FLORIDA PUBLIC SERVICE COMMISSION

845

1   additional studies.  One that focussed just on the east coast

2   of Florida from South Hutchinson Island up to Jacksonville and

3   one from Sarasota down to Naples.  And those were concentrated

4   studies in those areas.  And what we found, the conclusion we

5   found is if you are right on the coastline, you can get a 15 to

6   20 percent availability factor.  If you move even a half a mile

7   inland, it drops to about 5 percent.

8             With that information in tow, we attempted to build

9   or attempted to permit a wind demonstration project of about

10   ten megawatts.  And that ten megawatt facility, we are actually

11   on our fifth site right now.  The first site was in New Smyrna.

12   I got voted down by the city commission there four-to-one.

13             We then went to Cape Canaveral.  Cape Canaveral juts

14   out.  It is part of the development business.  You don't always

15   get your first one, so you pick up the pieces and you move on.

16   So then we moved on to Cape Canaveral.  And if you look at the

17   geography of the state, Cape Canaveral sort of juts out and

18   gets natural wind.  We looked both at the Cape Canaveral Air

19   Force Station, and were rejected there by the Air Force, and

20   then we went to NASA.

21             Now, we learned something new when we went to NASA.

22   That north/south access along the east coast of the state,

23   that's where you get a lot of bird migration.  In fact, one of

24   the largest bird refuges in the state is just north of Cape

25   Canaveral.  Well, NASA was very keen on employing this

FLORIDA PUBLIC SERVICE COMMISSION

846

1   technology, but Fish and Wildlife won out at the end of the

2   day.

3             Then we went to Sarasota.  We got rejected there.

4             And we are on our fifth site that we are working on

5   right now.  So, we have looked at renewables.

6             We also looked at solar.  We looked at commercial

7   solar.  FPL Energy, our subsidiary, is one of the largest solar

8   developers in the world, and has the largest plant in the

9   Mojave Desert.  And a couple of conclusions we came to by

10   levering their expertise is solar in the state of Florida, you

11   are looking at about a 15 to 20 percent, or 15 to 17 percent

12   availability factor and very high costs.

13             So, yes, we have looked at renewables.  I have not

14   looked at energy efficiency and demand-side management.  That

15   is the purview of others within our company.

16        Q    All right.  Thank you.  I wasn't expecting such a

17   long answer, but I appreciate it.  It's good to know these

18   things.

19             Let me ask you, earlier you said something about the

20   difference between a proposed plant and one that will actually

21   be built.  What is the status of this FGPP plant, is it

22   proposed, as well?

23        A    It is a proposed facility.

24        Q    Okay.  Thank you.  That's good enough.  I mean, I

25   just wanted to make that point.  If you don't mind, I don't

FLORIDA PUBLIC SERVICE COMMISSION

847

1   want to take too much time.  I'm not an expert lawyer, so I

2   don't want to be burdened with delaying everyone else.  Okay.

3   If we can keep it brief and to the question.

4             Now, this plant, as you specified, is very important

5   and has been designed for bituminous coal.  Is that Appalachian

6   coal?

7        A    It has been designed with two design points.  One is

8   for bituminous coal.

9        Q    Exactly.

10        A    And the second design point is bituminous coal and

11   petroleum coke.

12        Q    Is the bituminous coal Appalachian coal?

13        A    It could be Appalachian coal, it could be western

14   coal, it could be foreign coals.  This plant could also, with

15   derates also burn subbituminous coal.  So, you could source

16   coal, bituminous coals domestically and foreign coals.

17        Q    Do you have any concern with the fact that the

18   Peabody Coal Company has pulled out of Kentucky and Appalachia?

19        A    They have not pulled out of Kentucky and Appalachia.

20   What they have done is it looks like what they are going to do

21   is spin-off their Central Appalachian facilities.  I don't view

22   it as a concern.  I view it as an opportunity to potentially

23   maybe through an equity investment or some other vehicle gain

24   long-term very good long-term pricing for our customers.

25        Q    Are you aware of the recent determination in the Ohio

FLORIDA PUBLIC SERVICE COMMISSION

848

1   Valley Environmental Coalition versus the United States Army

2   Corps of Engineers --

3        A    I'm not aware of that.  I think Mr. Schwartz was

4   aware of that.

5        Q    Okay.  Are you concerned that this case shows that

6   there is a large community effort to restrict the use of

7   mountaintop removal and other practices?

8        A    I'm not aware of that.

9        Q    Now, you said if the Commission would have asked you

10   two months ago about sequestration technologies that you would

11   have been able to tell them about 25 methods?

12        A    About 25 R&D programs, yes.

13        Q    Now we are up to 30?

14        A    Well over 30, yes.

15        Q    How many opportunities will there be in a year or

16   two?  How many opportunities for sequestration, or different

17   technologies, or methods do you think there will be in a year

18   from now?

19        A    What I was discussing was carbon capture.  Carbon

20   capture and sequestration is a sort of horse and cart issue.

21   Where the horse is sequestration, the cart is carbon capture.

22   Without sequestration it doesn't matter what the carbon capture

23   system is.  But nevertheless, there are a number of carbon

24   capture programs in place.

25             In terms of sequestration, one of the primary

FLORIDA PUBLIC SERVICE COMMISSION

849

1   potential sequestration types, or sequestration areas,

2   potential sequestration areas is deep saline aquifers.  The

3   estimated total capacity of deep saline aquifers in the world

4   is about 9,600 gigatons.  A gigaton is about a billion tons.

5   About 40 percent of that world potential capacity is in the

6   United States.

7             FPL has a service territory of about 27,650 square

8   miles.  Of that 27,650 square miles, virtually all of it is

9   characterized geologically by deep saline aquifers.  In

10   addition, there was oil drilling that occurred about 75 miles

11   southwest of the plant.  That has left depleted oil well fields

12   which is also a potential reservoir for carbon sequestration.

13   So there is another option there available, also.

14             Last of all, there has been discussion or there has

15   been research into using the different levels of the sea to

16   capture carbon, and the Gulf of Mexico is within striking

17   distance of this plant.  So there is a number of different

18   options out there available for sequestration.

19             Once again, the MIT study recognizes that not a lot

20   has been done in the United States.  Not in the United States,

21   but in the world, not a lot has been done in terms of

22   sequestration.  And it recommends, given that lack of

23   uncertainty, and it makes recommendations with how to address

24   it, but given that lack of uncertainty, coal plant developers

25   should build their plants as efficient as economically

FLORIDA PUBLIC SERVICE COMMISSION

850

1   justifiable.

2        Q    Now, why would you capture the carbon and what would

3   you do with it if you weren't going to sequester it?

4        A    There are other potential things that can be done

5   with carbon.  For example, enhanced oil recovery is generically

6   a way of doing it.  Now, there isn't enhanced oil recovery

7   fields field close and in Florida, but that is another option

8   available.

9        Q    Okay.  And there is a lot of debate and analysis as

10   to how effective or what amount of sequestration could occur

11   with that, and what is the cost/benefit of doing that in the

12   oil that you then reclaim and then the pollution associated

13   with the oil that you burn after you go through the effort of

14   bringing it out of the ground and how much pollution that

15   creates.

16        A    I wouldn't necessarily characterize it as a lot of

17   debate.  I think that, you know, enhanced oil recovery is one

18   option.  And there is a lot of work that's going to be done on

19   that and other sequestration efforts in the country and around

20   the world.

21        Q    Are you familiar with the Department of Energy --

22   they are participating in a project near Orlando for IGCC?  Is

23   that what you referred to earlier when you said -- when you

24   mentioned something about the DOE having a project in --

25        A    DOE is cofunding a number of projects.  One of them

FLORIDA PUBLIC SERVICE COMMISSION

851

1   in the Stanton B project, which is a 283-megawatt IGCC project

2   in which they provided about $230 million of funding.  That

3   project appears to be going forward in Orlando.  I would

4   mention that the emissions profile of that plant is

5   significantly worse than the emissions profile for the FPL

6   Glades Power Park, particularly with regard to nitrogen oxide

7   and mercury.

8        Q    And when will the study associated with that project,

9   when will the results be understood for analysis?

10        A    I believe that that is a -- it is a project to

11   demonstrate the ability of IGCC to operate on Powder River

12   Basin.  That is my understanding of it.  And I believe it is a

13   four year -- it is projected to come on-line in 2011 and be a

14   four-year demonstration of whether or not that technology

15   actually works.

16             That technology has never been built greater than, I

17   believe, four or six megawatts.  So you are scaling that

18   technology up about 50 to 60 times.  So there is a question

19   about whether or not the technology would actually work, and it

20   is a demonstration to see if that technological works, and

21   particularly if that technology can work with Powder River

22   Basin.

23        Q    Being that the ratepayers, and if certain laws are

24   passed, being that the ratepayers will pay one way or the other

25   for this plant that you propose to build, how does the cost

FLORIDA PUBLIC SERVICE COMMISSION

852

1   compare between IGCC and what's proposed now, whether it is

2   ultra-supercritical, the plant you are proposing to build?

3        A    I think Mr. Sim actually did an analysis on that and

4   he is going to testify, and you can ask him that question.  But

5   it is a substantially higher present value of revenue

6   requirements for an IGCC plant at the site versus an

7   ultra-supercritical plant.

8        Q    I have just a few more questions.  How does the

9   requirement to use lower level aquifer waters impact the cost

10   being that the lower level waters -- because there is a drought

11   now, and there is a discussion with the South Florida Water

12   Management District, okay, as far as what waters you will be

13   able to access.  If you have to go lower, how will that impact

14   the cost of the plant?

15        A    The water supply plan for the project involves four

16   types of water.  Number one is what we call the Upper Floridan,

17   which is a nonpotable or non-drinking water source that has

18   saline qualities to it.  The operations and maintenance costs

19   associated with using that are in the project budget.

20             The second type of water resource is what we call

21   excess stormwater.  There are discharges from the lake every

22   year.  Those discharges cause environmental issues both in the

23   St. Lucie estuary and in the Fort Myers area.  Under the supply

24   plan that we have proposed that we are working with with the

25   South Florida Water Management District, they would notify us

FLORIDA PUBLIC SERVICE COMMISSION

853

1   when we should use that excess stormwater to better utilize

2   that water.

3             Number three, this is a 5,000 acre site.  We are

4   going to have significant catchment ponds, or water storage on

5   the site, so we will use that as a third water supply.  Last of

6   all --

7        Q    Mr. Hicks, could you just stick to my question, which

8   was how --

9             CHAIRMAN EDGAR:  Mr. Krasowski, let me do that, okay?

10             MR. KRASOWSKI:  Yes, ma'am.  I was trying to focus.

11   I'm sorry.  My apologies.  I didn't mean to offend you.

12             CHAIRMAN EDGAR:  We have been trying to focus for a

13   couple of days actually.  But, why don't you pose your question

14   to the witness.

15             MR. KRASOWSKI:  Yes.

16   BY MR. KRASOWSKI:

17        Q    The question is how will the need, if necessary, if

18   it is necessary to draw from a lower aquifer impact the cost of

19   operating the plant, whether it be IGCC or the plant you

20   propose, given that that lower material is understood to

21   require more treatment for it to be used in the method you want

22   to use it?

23        A    If you could clarify your question.  We are using one

24   of the four water sources, the Upper Floridan.  Are you talking

25   about the Upper Floridan?

FLORIDA PUBLIC SERVICE COMMISSION

854

1        Q    Well, that is the one that there is a problem with

2   because of the drought.

3        A    No, we have not got an indication from the South

4   Florida Water Management District that there is a problem with

5   that.

6        Q    Oh, really?

7        A    No.

8        Q    You are not aware that they have issued a declaration

9   that they will no longer be permitting extractions from the

10   Everglades Water Basin to build homes or businesses?

11        A    No, I'm not aware that.  In fact, we are in constant

12   communication with them.  We have had on-going meetings, and

13   they have not expressed, to my knowledge, any reticence with

14   regard to our drawing from the Upper Floridan.

15             The water supply plan we are for FPL Glades Power

16   Park is very similar to the water supply plan that the South

17   Florida Water Management District approved for the West County

18   Energy Center.

19        Q    Okay.  Have you identified your fly ash and bottom

20   ash and other byproduct buyers?

21        A    Yes.  We have had on-going discussions with a number

22   of buyers.  One buyer -- I could sign contracts for both fly

23   ash and the bottom ash and the synthetic gypsum.  Synthetic

24   gypsum is a direct result of the flue gas desulphurization

25   process.  Limestone is used in that flue gas desulphurization

FLORIDA PUBLIC SERVICE COMMISSION

855

1   process, and the byproduct is synthetic gypsum which is

2   actually of a higher quality gypsum than naturally occurring

3   gypsum for the use in wallboard.  And I could sign contracts

4   very quickly for 100 percent of all of those resources.  In

5   fact, one wallboard manufacturer is very keen to get access to

6   this because they claim that if they could gain access to this

7   synthetic gypsum they could control the wallboard market south

8   of Orlando.  So very keen interest.

9             One opportunity that I'm pursuing on that is an

10   overall opportunity that would involve getting limestone from a

11   limestone supplier for free and then providing them the

12   byproducts and they would take the byproducts.  So from a plant

13   perspective, the plant manager would not have to worry about

14   either limestone supply or dealing with the byproducts

15   themselves.  So, a number of different options available to us.

16        Q    What are you going to do with the ash if it

17   becomes -- if it has to be held on-site?

18        A    If it had to be held on-site, it would be landfilled

19   in a double-lined landfill that meets all federal and state

20   requirements.

21        Q    And where is that, on-site?

22        A    It would be on-site, yes, sir.

23        Q    And how much of a capacity do you have on-site for

24   the ash byproduct?

25        A    We have ample capacity on-site.  Even though it

FLORIDA PUBLIC SERVICE COMMISSION

856

1   appears that all of those byproducts will be sold, we have

2   ample capacity on-site for the entire life of the plant.

3        Q    Really.  And who was responsible for, or will it be

4   included in your costs, the train, the repair or bringing up to

5   standards the train tracks?  I understand they are not in any

6   shape to be taking these coal shipments.

7        A    No, that is not correct.  This site is advantaged in

8   the sense that the southern boundary of the site is the South

9   Central Florida Express.  The South Central Florida Express

10   connects to two major networks, the Northfolk Southern and the

11   CSX.  That gives us rail competition, origin and destination,

12   foreign and domestic.  Very important for the life-cycle

13   economics of a power plant.

14             The South Central Florida Express, and I think this

15   is what you are alluding to, has signed two agreements with the

16   DOT.  In those two agreements, the DOT is funding 75 percent of

17   the total upgrades necessary to bring those lines up to a

18   status that will allow heavy trains such as the coal trains and

19   heavy equipment trains to access the site.  The first contract

20   is from Lakeport, which is a town on the south side of the

21   lake, to Morehaven, which is in Glades County.  That upgrade

22   has already been completed.

23             The second contract has already been let out, and

24   that upgrade will be completed by the Spring of 2008, in time

25   for us to start construction and reduce the transportation cost

FLORIDA PUBLIC SERVICE COMMISSION

857

1   for major equipment to the site.  So, those issues have been

2   resolved.  Those issues would have been resolved whether or not

3   we built the plant.

4        Q    So it is not a cost to you?

5        A    We have a contract with the South Central Florida

6   Express for the life of the plant, and that's about 99 percent

7   completed.  But the costs associated with those upgrades, they

8   were funded 75 percent DOT, 25 percent South Central Florida

9   Express.  They would have been completed regardless of whether

10   or not this plant is actually built.

11        Q    75 percent was funded by the DOT?

12        A    Florida Department of Transportation, yes, sir.

13        Q    Florida Department of Transportation.  And I assume

14   that is taxpayer money?

15        A    I don't know where that money comes from.

16        Q    They don't print it, right?  Okay.  You don't know.

17             And my last question is how does the close proximity

18   to the Everglades National Park and the monies dedicated to the

19   Lake Okeechobee cleanup enter into the appropriateness of your

20   site selection for this FGPP project?

21        A    FPL takes its responsibility as an environmental

22   steward very, very seriously.  And we have designed this plant

23   with six separate pollution control devices, almost a billion

24   dollars worth.  Four of those pollution control devices -- all

25   of those pollution control devices are wrapped under a single

FLORIDA PUBLIC SERVICE COMMISSION

858

1   air quality control system contract where the supplier

2   guarantees the emissions control.  Four of those are proven

3   technologies in operation, state of the art.  Two are next

4   generation technologies.  With all of those pollution control

5   technologies this project will be very environmentally

6   sensitive for its location.  I should mention that there is a

7   landfill to the east of the site, and a state penitentiary to

8   the south, and it's in an agriculture area, so it is well

9   suited.  It also provides a substantial economic benefit to the

10   people of Glades County and surrounding areas.

11        Q    One more last question if, I may.  I apologize.  What

12   is the cost to the DOT for their participation in the rail

13   contract?

14        A    They are not participating in the rail contract.

15   They have two separate -- before we even got involved with

16   them, the DOT and South Central Florida Express put together a

17   package to upgrade those rail lines.  So DOT is not part of the

18   contract for rail service between the South Central Florida

19   Express and FPL.  Those upgrades would have been completed

20   whether or not the power plant was built there.

21             The contract we have is with the South Central

22   Florida Express for transportation to pick up trains from CSX

23   at Sebring, bring them to the plant site, pick up trains from

24   the Northfolk Southern FEC at Fort Pierce and bring them to the

25   plant site.

FLORIDA PUBLIC SERVICE COMMISSION

859

1        Q    So I suppose I should ask DOT what that cost was?  I

2   mean you, are not involved in that?

3        A    That's not my bailiwick, no.

4             MR. KRASOWSKI:  Okay.  Thank you very much, Mr.

5   Hicks.

6             THE WITNESS:  You're very welcome.

7             MR. KRASOWSKI:  Thank you, Madam Chair.

8             CHAIRMAN EDGAR:  Thank you.

9             Are there questions from staff for this witness?

10             MS. BRUBAKER:  Yes.

11             CHAIRMAN EDGAR:  Any idea of how long?

12             MS. BRUBAKER:  I would say about ten or fifteen

13   minutes, depending on the length of the answers.

14             CHAIRMAN EDGAR:  Okay.  Why don't we go ahead and,

15   Commissioner McMurrian, I will give you the option.  Would you

16   like to ask your questions now or go on lunch break and you can

17   start then?  You're fine either way?  Okay.  Commissioner

18   Carter, your preference?

19             I'm hungry, so let's take a lunch break and we will

20   come back at 2:00 o'clock.  And we will continue with this

21   witness at that time.

22             Thank you.

23             (Transcript continues in sequence with Volume 7.)

24

25

FLORIDA PUBLIC SERVICE COMMISSION

860

1

2   STATE OF FLORIDA    )

3                       :         CERTIFICATE OF REPORTERS

4   COUNTY OF LEON      )

5             WE, JANE FAUROT, RPR, and LINDA BOLES, RPR, CRR,

Official Commission Reporters, do hereby certify that the

6   foregoing proceeding was heard at the time and place herein

stated.

7

IT IS FURTHER CERTIFIED that we stenographically

8   reported the said proceedings; that the same has been

transcribed under our direct supervision; and that this

9   transcript constitutes a true transcription of our notes of

said proceedings.

10

WE FURTHER CERTIFY that we are not a relative,

11   employee, attorney or counsel of any of the parties, nor are we

a relative or employee of any of the parties' attorneys or

12   counsel connected with the action, nor are we financially

interested in the action.

13

14              DATED THIS 25TH DAY OF APRIL, 2007.

15

16   ____________________________   ____________________________

JANE FAUROT, RPR               LINDA BOLES, RPR, CRR

17   FPSC Official Commission       FPSC Official Commission

Reporter                         Reporter

18   (850) 413-6732                 (850) 413-6734

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION