1

1                             BEFORE THE

FLORIDA PUBLIC SERVICE COMMISSION

2

DOCKET NO. UNDOCKETED

3

In the Matter of

4

2008 HURRICANE SEASON PREPARATION

5   BRIEFING BY ELECTRIC UTILITIES

AND THE THREE INCUMBENT LOCAL

6   EXCHANGE CARRIERS.

________________________________/

7

8

9

10

PROCEEDINGS:        WORKSHOP

11

BEFORE:             CHAIRMAN MATTHEW M. CARTER, II

12                       COMMISSIONER LISA POLAK EDGAR

COMMISSIONER KATRINA J. McMURRIAN

13                       COMMISSIONER NANCY ARGENZIANO

COMMISSIONER NATHAN A. SKOP

14

DATE:               Thursday, May 1, 2008

15

TIME:               Commenced at 9:30 a.m.

16                       Concluded at 1:08 p.m.

17   PLACE:              Betty Easley Conference Center

Room 148

18                       4075 Esplanade Way

Tallahassee, Florida

19

REPORTED BY:        LINDA BOLES, RPR, CRR

20                       Official FPSC Reporter

(850) 413-6734

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

2

1   PRESENTATIONS:                                       PAGE:

2   RICHARD SHAHEEN, Florida Power & Light                 7

3   JASON CUTLIFFE, Progress Energy Florida               18

4   REGAN HAINES, Tampa Electric Company                  27

5   ANDY McQUAGGE, Gulf Power Company                     38

6   DON MEYERS, Florida Public Utilities Company          46

7   BARRY MOLINE, Florida Municipal Electric Association  51

8   KEVIN WAILES, City of Tallahassee Electric Utility    53

9   REBECCA MATTEY, Ocala Electric Utility                67

10   MICHELLE HERSHEL, Florida Electric Cooperatives       73

Association

11

SCOTT NEWBERRY, Florida Keys Electric Cooperative     74

12

JERRY TWIGGS, Peace River Electric Cooperative        83

13

MILES GREEN, Peace River Electric Cooperative         84

14

KIRK SMITH, AT&T                                      94

15

JANICE DOHERTY, AT&T                                 102

16

DEMETRIA CLARK, Verizon                              104

17

LONNIE LEWIS, Verizon                                105

18

SANDY KHAZRAEE, Embarq                               117

19

20

21   ALSO PRESENT:

22             LISA BENNETT, ESQUIRE, Commission staff.

23             KEINO YOUNG, ESQUIRE, Commission staff.

24             STEVE GARL, Commission staff.

25

FLORIDA PUBLIC SERVICE COMMISSION

3

1                         P R O C E E D I N G S

2             CHAIRMAN CARTER:  Good morning.  I'd like to convene

3   this workshop, and we'll begin by asking staff to read the

4   notice.

5             MS. BENNETT:  By notice duly given, this time and

6   place has been set for the Commission workshop regarding 2008

7   hurricane season preparation briefing by electric utilities and

8   the three major incumbent local exchange carriers.  The purpose

9   of the workshop is more specifically stated in the notice.

10             CHAIRMAN CARTER:  Okay.  Let's take appearances.

11             MR. BUTLER:  John Butler on behalf of Florida Power &

12   Light Company.  I have Richard Shaheen here, who will be making

13   the presentation for FPL.

14             CHAIRMAN CARTER:  Okay.  It's just FPL?

15             MS. BENNETT:  Lisa Bennett and Keino Young on behalf

16   of staff.

17             CHAIRMAN CARTER:  Okay.  Let's make a few --

18   Commissioners, I'll make a few opening statements and then ask

19   if any of you have some comments that we'll make before we

20   proceed further.

21             In 2006, the Florida Public Service Commission

22   adopted a multifaceted approach and a response to ensure all

23   utilities' infrastructures will be better able to withstand the

24   impact of hurricanes and implement lessons learned from the

25   '04/'05 seasons.  We adopted ten storm hardening initiatives

FLORIDA PUBLIC SERVICE COMMISSION

4

1   and required investor-owned utilities to file formal storm

2   hardening plans subject to our approval.

3             The initiatives were as follows:  First, a three-year

4   vegetation management cycle for distribution lines.  Second,

5   audit of joint use attachment agreements.  Third, six-year

6   transmission structure inspection program.  Fourth, hardening

7   of existing transmission structures.  Number five, development

8   of a transmission and distribution Geographic Information

9   System.  Number six, post-storm data collection and forensic

10   analysis.  Number seven, detailed outage data differentiating

11   reliability of overhead and underground facilities.  Number

12   eight, increased utility coordination with local governments.

13   Number nine, collaborative research on effects of hurricane

14   winds and storm surge.  And finally number ten, a natural

15   disaster preparedness and recovery program.

16             In our July 2007 report to the Legislature we cited

17   our most critical recommendation that Florida maintain a high

18   level of storm preparation.  The annual hurricane season

19   preparation workshop provides utilities and local exchange

20   companies a forum to advise us of their individual hurricane

21   season preparation activities.  This is the third year that

22   we've done this.

23             The hurricane forecasting experts at Colorado State

24   University updated their forecast for the '08 hurricane season

25   last month.  Their report tells us to expect a "well above

FLORIDA PUBLIC SERVICE COMMISSION

5

1   average" hurricane season.  Specifically, they expect 15 named

2   storms in the Atlantic Basin, including the Gulf of Mexico,

3   with eight reaching hurricane status and four of the eight

4   growing to Category 3, 4 or 5 in intensity.

5             Historically we have seen that the single greatest

6   detriment to hurricane preparation is time, specifically time

7   since the last hurricane.  We all know memories fade with time,

8   specifically the lag time between each hurricane that makes

9   landfall in the State of Florida.  As a Commission we must

10   remain diligent.  We cannot allow the lag time between

11   hurricanes that make landfall keep us from protecting the

12   consumers of our great state.  Therefore, we ask each of our

13   presenters to candidly address the status of their company's

14   preparation for the '08 hurricane season.  Please include the

15   status of work achieved to protect facilities to date, work in

16   progress and work to be accomplished in the near future, and

17   areas of concern or areas of vulnerability.

18             It's understood that while the electric utilities own

19   the vast majority of the electric transmission and distribution

20   infrastructure in the state, local exchange companies own many

21   of the poles upon which the electric utility infrastructure is

22   placed.

23             Commissioners, at this point in time I would like to

24   open it up for comments that any of you may have.

25             Commissioners?  Commissioner Edgar, you're

FLORIDA PUBLIC SERVICE COMMISSION

6

1   recognized.

2             COMMISSIONER EDGAR:  Thank you, Mr. Chairman.  And I

3   appreciate very much your comments and your overview of some of

4   the things that we've done here as a Commission over the past

5   few years to discuss and to address some of these issues.

6             I remember my first two years as Commissioner in

7   '05 and '06 when we would travel to customer meetings, no

8   matter what the topic, and also when I would meet with

9   legislators or local governmental officials, no matter what the

10   official topic, the issue of hurricane response, hurricane

11   preparedness and hurricane cost recovery was always one of the

12   central issues that would come up.  And we had so many just

13   excellent discussions with local residents, with local

14   government officials, with the industry representatives over

15   the past few years.  And I appreciate very much your overview

16   as to kind of what has brought us here today, and I'm looking

17   forward to hearing more about what our excellent utilities have

18   done in the past year.

19             You know, this Commission took on the Governor's at

20   the time direction to all of us to embrace a culture of

21   preparedness and to take to heart lessons learned, and some of

22   what you've described and what we will hear today is the

23   further extension of the Commission and the industry doing just

24   that.  And also I know that one of the things that we've talked

25   about and that our utilities have also looked very closely at

FLORIDA PUBLIC SERVICE COMMISSION

7

1   is that cost-benefit analysis, which I think is a very

2   important component of this issue.  So thank you for scheduling

3   this and I look forward to the presentations.

4             CHAIRMAN CARTER:  Thank you, Commissioner.  Now

5   giving the opportunity for staff.  Staff, you're recognized.

6             MR. GARL:  Thank you, Mr. Chairman.  I'd just make

7   one housekeeping comment.  Those of you that would like copies

8   of the presentations that will be given today, paper copies are

9   available over to your left.  And there's also a sign-in book

10   over there for the workshop, if you'd be sure to put your names

11   in there and take credit for your attendance.

12             Thank you, Mr. Chairman.

13             CHAIRMAN CARTER:  Thank you.  Thank you.

14   Commissioners, anything further?  Staff, anything further?

15             Okay.  Our first presentation will be FP&L.  You're

16   recognized -- or FPL.

17             MR. SHAHEEN:  Good morning, Commissioners and staff.

18   My name is Richard Shaheen.  I'm FPL's Director of

19   Distribution, Engineering and Technical Services.  Included in

20   my responsibilities are oversight of FPL's storm restoration

21   and preparedness activities, hardening and pole inspection

22   program.  Thank you for allowing me the opportunity today to

23   review FPL's hurricane preparedness plans for the 2008 storm

24   season.  My presentation will address activities and results

25   for our distribution and transmission systems.

FLORIDA PUBLIC SERVICE COMMISSION

8

1             Let me start off by saying FPL is well prepared and

2   we are ready to respond should our communities be faced with

3   hurricane activity this year.  Additionally, our continued

4   efforts to improve our systems and processes as well as

5   strengthen our distribution and transmission infrastructure are

6   also better preparing us for future storm seasons as well.

7             2008 preparations.  FPL's hurricane preparations are

8   a year-long effort that is concentrated on four key elements.

9   First, we're strengthening our distribution and transmission

10   infrastructure.  This is being accomplished through, one, our

11   hardening plans, two, our pole inspection programs and, three,

12   our vegetation management programs, all of which the Commission

13   has recently reviewed and approved.

14             Second, we're preparing our storm organization.  We

15   ensure we have the right people in the right roles with the

16   necessary training and knowledge so that they can respond

17   quickly and safely.

18             Third, we continue to improve and refine our already

19   well-tested restoration plan by incorporating lessons learned

20   and utilizing technology.

21             Finally, we continue to look for ways to provide more

22   and better information for our customers.  Now allow me to

23   discuss each of these elements in a little more detail.

24             Strengthening the infrastructure for distribution in

25   regards to hardening.  Hardening is a key component of our plan

FLORIDA PUBLIC SERVICE COMMISSION

9

1   to strengthen our systems.  For our distribution system FPL is

2   using a three-prong approach.  One, we're hardening our

3   critical infrastructure facilities, our CIFs, to extreme wind

4   loading criteria.  For example, hardening hospitals,

5   911 centers, police and fire stations.

6             Two, we're incrementally hardening up to and

7   including extreme wind loading what we refer to as our

8   community projects.  These are major thoroughfares where key

9   community needs are located like grocery stores, gas stations

10   and pharmacies.

11             And, three, we're utilizing our new design guidelines

12   to construct all new facilities, major planned work, relocation

13   projects and our daily work activities to extreme wind loading

14   criteria.

15             Specific to critical infrastructure facilities or our

16   CIFs we're initially concentrating on infrastructure serving,

17   infrastructure serving acute care facilities throughout our

18   system.  In 2007, we hardened 28 acute care facilities and

19   we're planning to harden another 49 in 2008.

20             We're also targeting what we refer to as critical

21   poles.  Initially these include poles where our lines cross

22   highways as well as our 01 switch poles, the first poles

23   outside of our substations.  These poles are crucial to our

24   overall restoration plan.

25             Also, as you can see, we completed 34 community

FLORIDA PUBLIC SERVICE COMMISSION

10

1   projects in 2007 and plan to complete another 21 in 2008.  For

2   2007, all planned hardening projects are complete, with the

3   exception of one community project feeder which will be

4   complete before June.

5             Finally, as a result of our agreement reached with

6   joint pole owners and other attaching entities during the

7   hardening proceeding we're holding joint predesign and

8   preconstruction meetings for every project to identify and

9   resolve any and all issues raised by any party.

10             Strengthening the infrastructure for transmission in

11   regards to hardening.  As far as hardening our transmission

12   system, which is already constructed to extreme wind loading

13   criteria, our 2007 hardening plan focused on two key programs

14   which were identified through our 2004 and 2005 storm seasons

15   lessons learned.

16             First, replacing single pole unguyed wood structures

17   and, second, replacing ceramic post insulators.  In 2007, we

18   exceeded our plan on both of these projects, and our plan for

19   2008 is similar to what we planned for in 2007.  Additionally

20   in 2008 we're expanding our transmission hardening strategy.

21   We're now upgrading each wood transmission structure in our

22   system to meet current standards.  This is a long-term effort.

23   We anticipate that it will take us 25 years to complete this

24   initiative; however, this effort will provide us with an even

25   stronger transmission system than we have today.

FLORIDA PUBLIC SERVICE COMMISSION

11

1             Strengthening the infrastructure for distribution in

2   regards to pole inspections.  2007 was the first full year of

3   implementation for our eight-year distribution pole inspection

4   program where each wood pole is being tested to make sure that,

5   one, it has the required strength and, two, that it is not

6   overloaded.

7             FPL owns over 1.1 million poles.  We completed over

8   140,000 pole inspections, approximately one-eighth of our

9   poles, in 2007 and we expect to do approximately the same for

10   2008.  These pole inspections are taking place throughout our

11   entire service territory.

12             We are also successfully working with our joint pole

13   owners, for instance, AT&T, to make sure that all poles with

14   FPL facilities attached, whether owned by FPL or not, are being

15   inspected, repaired or replaced as necessary.

16             Strengthening the infrastructure for transmission in

17   regards to inspections.  All of our transmission structures are

18   required to be inspected on a six-year cycle.  We have 64,000

19   structures systemwide.  In 2007, we inspected over 13,500 of

20   these structures, exceeding the one-sixth per year requirement.

21   For 2008 we will again inspect at least one-sixth of our

22   system.

23             Additionally this year to compliment our distribution

24   hardening and storm preparation efforts, we plan to complete

25   inspections on all 500kV lines and transmission facilities

FLORIDA PUBLIC SERVICE COMMISSION

12

1   serving critical infrastructure facilities before June 1.  And

2   I'm pleased to report that this has already been completed as

3   of today.

4             Strengthening the infrastructure for distribution in

5   regards to vegetation management.  Like hardening, vegetation

6   management is a key component in our plan to strengthen the

7   infrastructure.  For 2007, we executed and met our plan for the

8   distribution system.  We continued to maintain our feeders on a

9   three-year average trim cycle, and in 2007 we began to

10   implement our approved six-year average trim cycle for

11   laterals.  We're continuing this initiative in 2008 as well.

12             And consistent with efforts over the last couple of

13   years, we're completing the trimming of all lines serving our

14   top critical infrastructure facilities prior to June 1.  Today

15   we're 90 percent complete with this effort and we will be

16   100 percent complete by June 1.

17             Finally, as we all know, no vegetation management

18   program can be effective without the cooperation of our

19   customers.  We continue our proactive promotion of our Right

20   Tree Right Place Program with our community leaders to ensure

21   that future planting of trees will avoid conflicts with our

22   lines.  We're also seeking their support in trying to remove

23   existing trees that are interfering or endangering our lines as

24   well.

25             Strengthening the infrastructure for transmission in

FLORIDA PUBLIC SERVICE COMMISSION

13

1   regards to vegetation management.  Our vegetation management

2   plan for our transmission right-of-way is very straightforward.

3   Twice a year we inspect all of our transmission right-of-way

4   and we make sure that the required NERC, FERC standard

5   clearances are maintained.  This was completed in 2007 and we

6   are on schedule to complete this again in 2008.

7             Preparing the storm organization.  Each year we

8   ensure that all storm roles and key personnel are identified

9   and placed into the right roles.  We also make sure our

10   training reflects the latest process changes incorporating

11   recent lessons learned and new technologies.  We conduct

12   extensive training, including our annual hurricane dry run

13   exercise.  This year's exercise will be held one week from

14   today.  This is a company-wide exercise that includes our field

15   as well as support personnel.  This exercise tests our systems

16   and processes to ensure they're ready.  We also typically

17   include a couple of unexpected and unique practice situations

18   that allow us to stress our systems and processes, since it

19   seems each and every storm season brings new and unexpected

20   challenges.

21             We've also now established the roles of our forensic

22   teams within the storm organization.  These teams will be

23   responsible for observations and the collection of data

24   associated with damaged infrastructure.  This will allow us to

25   better understand how our infrastructure performed and provide

FLORIDA PUBLIC SERVICE COMMISSION

14

1   valuable lessons for future evaluation and action:  For

2   example, hardened versus nonhardened performance.

3             Our restoration plan has one clear objective:  To

4   safely restore our community's critical infrastructure

5   functions and needs along with the greatest number of customers

6   in the shortest time possible.  For the 2008 storm season all

7   of our resource plans are in place:  For example, arrangements

8   for catering, housing and water, all of our staging sites

9   throughout our system are arranged, equipment for these sites,

10   arrangements for foreign utilities through our mutual

11   assistance agreements, arrangements with contract crews and

12   increased material and fuel inventories.

13             We also make refinements in our plan as a result of

14   lessons learned through our own experience, benchmarking storm

15   processes with other utilities as well as technology.  For

16   example, to improve our own internal communications network

17   we've added more satellite dishes.  Additionally, we've made

18   changes to several of our systems that will enable us to better

19   monitor the progress of restoration work and improve our

20   dispatch operations.

21             And once power is restored our work is still not

22   done.  That's when our recovery plans take over.  We've refined

23   and improved these plans as well.  For example, we've refined

24   our final patrol sweep process to ensure that all

25   infrastructure damage is identified, repaired and returned to

FLORIDA PUBLIC SERVICE COMMISSION

15

1   pre-storm conditions.

2             After the 2004 and 2005 storm seasons we learned that

3   communicating with our customers and communities can be just as

4   important to them as our restoration efforts.  As a result, we

5   meet annually with county emergency managers to identify the

6   critical infrastructure locations within each jurisdiction.  We

7   also make certain that we've assigned representatives to

8   support each of the 27 county and seven satellite EOCs located

9   throughout our service territory.

10             We have also developed a dedicated government update

11   website to be utilized for major storm events.  This has been

12   customized to provide information that government leaders rely

13   on to assist them with their recovery efforts.  This include

14   media alerts and releases, customer outage information and maps

15   specific to their municipality, critical infrastructure

16   facility information, staging site locations, crew work

17   location maps, as well as estimated times of restoration

18   information.

19             Also in 2007, we initiated our community outreach

20   program which sent teams of FPL personnel to address the needs

21   of local community-based organizations, educating them on

22   various topics of interest including service reliability and

23   storm readiness.

24             And finally, the most frequent question asked of us,

25   "When will my power be back on?"  In regards to this, we've

FLORIDA PUBLIC SERVICE COMMISSION

16

1   made improvements to our outage communications system that will

2   allow us to provide even more accurate estimated times of

3   restorations for our customers.

4             Commissioners, we were all asked to address in our

5   presentation any areas of concern or vulnerability.  We've

6   identified four items we thought worth mentioning.  The first

7   one is that it's likely that our service territory will be

8   affected by a storm or storms before we're able to complete all

9   of our hardening efforts.  As you know, we've made significant

10   changes in our construction standards which require certain

11   portions of our systems to be upgraded, and our system is

12   geographically large and diverse.  Unfortunately these changes

13   will take a number of years to complete.

14             The other three items include concerns or

15   vulnerabilities that are not new, yet their nature make them

16   difficult to prepare for.  These are being affected by multiple

17   storms over a short period of time like we experienced in 2004

18   and 2005, catastrophic storms or Category 5 storms like

19   Hurricane Andrew or Hurricane Katrina that can destroy

20   everything in their path, and the lack of sufficient resources,

21   whether it be materials, equipment and/or personnel.  We do

22   what we can to reasonably mitigate these occurrences, but the

23   bottom line is there are certain things that are beyond control

24   and means to prepare for.

25             In summary, FPL is confident that it is well prepared

FLORIDA PUBLIC SERVICE COMMISSION

17

1   for the 2008 season.  Our hardening, vegetation management and

2   pole inspection plans and programs are strengthening our

3   system.  Our storm organization is in place, well trained and

4   ready.  We have refined our already well-tested restoration

5   plan.  And, lastly, we are in position to better communicate

6   with our customers.  We, like all of you, are hoping for an

7   inactive hurricane season; however, should hurricanes affect

8   our communities in 2008, FPL is ready to respond.  Thank you.

9             CHAIRMAN CARTER:  Thank you.

10             Commissioners, any questions?  Staff?

11             MR. GARL:  Thank you, Mr. Chairman.

12             Mr. Shaheen, you mentioned that FPL will be

13   conducting its exercise next week.  In some of the

14   conversations you've had with local governments, counties, I

15   was curious if they, those counties that you serve are inviting

16   you to participate in any exercises that they may have?

17             MR. SHAHEEN:  Yes.  We keep open dialogue, especially

18   during this preparation time of the season, to where actually

19   some of them visit and participate during our dry run exercise,

20   and we equally are invited and visit some of their exercises as

21   well.  So it goes both ways.

22             MR. GARL:  Thank you.

23             CHAIRMAN CARTER:  Commissioners, any further?

24             Thank you so kindly.

25             MR. SHAHEEN:  Thank you.

FLORIDA PUBLIC SERVICE COMMISSION

18

1             CHAIRMAN CARTER:  Next we'll hear from Progress

2   Energy.

3             MR. CUTLIFFE:  Good morning.

4             CHAIRMAN CARTER:  Good morning.

5             MR. CUTLIFFE:  My name is Jason Cutliffe.  I'm the

6   Director of Distribution Asset Management with Progress Energy

7   Florida, and my section is responsible for reliability,

8   planning and major storm restoration for the distribution

9   delivery system.

10             I will be referencing some facts and figures that

11   aren't contained in this presentation, and we will make that

12   available to you by the end of the week so you have that

13   information to share.

14             Mr. Chairman, Commissioners, I appreciate the

15   opportunity to report to you today the status of Progress

16   Energy Florida's 2008 hurricane season preparation.

17             In summary, our transmission and distribution systems

18   have been well maintained and thoroughly inspected.  Our storm

19   response organization is drilled and prepared and critical

20   labor and material resources have been obtained in advance or

21   secured through commitments from external suppliers.  Our T&D

22   delivery infrastructure performed well during the 2004 and 2005

23   hurricane season, and we've improved those systems since that

24   time.  We've taken additional aggressive steps to harden our

25   system in conjunction with Public Service Commission

FLORIDA PUBLIC SERVICE COMMISSION

19

1   initiatives such as the wood pole inspection process, the

2   ongoing ten-point preparedness plan and the hurricane hardening

3   docket.

4             Our hurricane restoration operational plan also

5   performed well in 2004 and 2005.  Here too we've made

6   improvements.  All lessons learned from storms, drills, other

7   utility experience have been incorporated into our written

8   response plan and is included in our 2008 hurricane drill to be

9   conducted at the end of this month.  PEF's organization and T&D

10   delivery system are prepared for the 2008 hurricane season.

11             I would like to comment briefly on a reality made

12   clear in recent storm seasons.  Experience demonstrates two

13   things:  First, no system, no matter how hardened, can

14   withstand a catastrophic hurricane without damage and extensive

15   service interruptions.  Second, multiple hurricane events in

16   the Gulf region have the potential to greatly dilute

17   restoration resources; therefore, everyone, utility operators,

18   emergency response professionals, community leaders and Florida

19   citizens, must be prepared in advance.

20             With that said, I will now discuss the four key

21   components of our annual storm preparedness:  Distribution

22   system readiness, transmission system readiness, organizational

23   readiness and local government coordination.

24             Distribution system inspection, maintenance and

25   replacement work is the cornerstone of our overall annual

FLORIDA PUBLIC SERVICE COMMISSION

20

1   resource plan.  Manpower and material needs are identified in

2   the prior year to ensure that work is prioritized, efficiently

3   constructed and completed on schedule.  The wood pole plant is

4   on a firm eight-year inspection cycle, and maintenance is in

5   compliance with the Commission's storm preparedness initiative.

6   Inspections are targeted and prioritized.  Since this time last

7   year over 96,000 poles have been inspected, over 63,000 have

8   been treated to prevent decay and over 1,100 replaced.  Other

9   system maintenance activities include over 530 pad mount

10   transformer replacements and 110,000 circuit feet of hardening

11   pilot projects completed.

12             Our 2008 vegetation management program is on

13   schedule.  In addition to production trimming, we will again

14   complete a full survey of all backbone feeder miles prior to

15   June 1.  To date, 74 percent of our 3,800 miles of feeder

16   backbone have been surveyed and 92 percent of the identified

17   priority pruning is complete.  We've removed over 700 trees,

18   272 overhang limbs, hot spot trimmed over 624 trees, and

19   applied herbicide to nearly 800 miles of right-of-way floor.

20             We have implemented the Public Service Commission's

21   ten-point preparedness plan.  A full system audit of joint use

22   attachments was completed in 2007.  A GIS upgrade is currently

23   underway, with completion expected in the third quarter of this

24   year.  Post-storm forensic data collection teams were

25   established and formed and deployed following tropical storms

FLORIDA PUBLIC SERVICE COMMISSION

21

1   in 2006 and the devastating tornadoes of February of 2007, and

2   with each deployment the forensics process has been improved.

3             We've increased linkage and engagement with the

4   academic community by sponsoring work through the University of

5   Florida's Public Utility Research Center.  As part of this

6   effort, we're currently working with the university staff to

7   assimilate statewide weather station information into our

8   forensics results.  And as mentioned earlier, review and update

9   of our written hurricane response plan is complete for 2008.

10             And finally, as described in our storm hardening plan

11   filed last May, we have deployed a comprehensive process to

12   identify, prioritize, measure and analyze storm hardening

13   options within our service territory.

14             Transmission system readiness begins with structure

15   inspections and system maintenance.  In 2007, inspections were

16   completed on 159 transmission circuits, which included over

17   13,000 structures.  Over 12,000 wood pole structures were

18   inspected and more than 2,400 replaced with steel or concrete

19   in accordance with the NESC extreme wind design.  Aerial

20   patrols of all circuits were completed in April of this year

21   and a second pass will be completed in July.  Inspections have

22   also been completed on all of our 461 substations, and critical

23   follow-up work identified in those inspections has been

24   completed.

25             2008 transmission vegetation management work is also

FLORIDA PUBLIC SERVICE COMMISSION

22

1   on schedule.  Since this time last year over 800 circuit miles

2   have been trimmed or cleared, including removal of over 25,000

3   danger trees.  And here again the PSC ten-point storm

4   preparedness plan and storm hardening rule have been

5   implemented, including GIS capability, post-storm forensic data

6   collection, PSC-initiated inspection cycles, and, most notably,

7   the hardening of transmission structures continues through wood

8   pole replacement with steel or concrete assets.

9              The annual storm plan review and update process is

10   complete for the 2008 season.  New this year was enhancement of

11   proactive communication to critical care customers.  Prior to a

12   hurricane making landfall, customers identified as having a

13   critical care need will receive a phone call from Progress

14   Energy Florida agents with information concerning preparation

15   for the incoming storm.  The information will include locations

16   of area shelters equipped to provide critical care assistance

17   and a reminder to check the working condition of all backup

18   life support equipment in advance.

19             We will complete our annual storm drill on May 30th.

20   Individual storm organizations and process owners are tested on

21   their preparation efforts and ability to react to changing

22   storm conditions.  This year's drill scenario will be based on

23   a Category 4 hurricane moving northwesterly across Central

24   Florida impacting all four of our management regions and

25   exiting near Homosassa into the Gulf of Mexico as a Category 1.

FLORIDA PUBLIC SERVICE COMMISSION

23

1   The drill is designed to clearly demonstrate our readiness for

2   the 2008 season.

3             We've also taken steps to ensure that critical

4   restoration material and fuel are ready and available from

5   multiple sources.  Inventory levels of critical materials have

6   been increased over and above normal stock levels in

7   preparation for the upcoming storm season.

8             Our supply team organization has assembled 16 storm

9   kits at our central warehouse.  Each kit contains enough

10   emergency material to supply 400 linemen for up to three days.

11   Our transmission organization has increased its inventory of

12   poles, insulators and other hardware to supply contract and

13   company resources for three to five days.  And we have

14   negotiated retainer contracts with the fuel vendors to ensure

15   our fuel needs are met, arrangements that also improve our

16   access to fuel when sending Progress repair crews off system in

17   support of our mutual assistance partners here in Florida and

18   outside the state.

19             We're in the planning stage for installation of 500

20   gallon biodiesel tanks at strategic locations within our

21   territory for normal use, which will also augment our available

22   storm supply.  Even though we have supplier agreements in

23   place, these additional measures ensure that restoration can

24   begin as soon as the weather clears.

25             External line and tree trimming resources are

FLORIDA PUBLIC SERVICE COMMISSION

24

1   critical components of a successful restoration effort.  And

2   here too we've taken steps to ensure they are ready and

3   available through arrangements with contractors and

4   relationships with other utilities through regional mutual

5   assistance agreements like the Southeastern Electrical Exchange

6   and the Edison Electric Institute.

7             And our communication and coordination with local

8   governments is stronger than ever.  We've established

9   year-round cross-functional government coordination teams that

10   ensure a high level of critical information sharing and engage

11   in both internal and external storm planning and preparation

12   activities.  We're equipped to provide local governments with

13   resource and restoration information before, during and after

14   storm events to assist them with local emergency response.

15             In 2007, the ability to produce electronic outage

16   information for each county EOC during storm events was

17   introduced.  By placing PEF contacts inside each county

18   Emergency Operation Center and sharing information we're able

19   to incorporate local government restoration priorities into our

20   overall restoration plan.  And we continue the Know Where You

21   Grow Program, which informs the public and community

22   organizations of the most compatible tree species near power

23   lines.  And as part of Arbor Day events, last month over 6,000

24   low-growing tree species were given away.  We also cosponsor

25   public expos and emergency first responder events designed to

FLORIDA PUBLIC SERVICE COMMISSION

25

1   educate and increase preparedness.

2             In conclusion, Commissioners, Progress Energy

3   Florida's transmission and distribution systems which performed

4   well in 2004 and 2005 have been checked and maintained.  The

5   storm response organization is drilled and prepared and

6   internal and external resources have been secured or committed.

7   As a six-time Edison Electric Institute Restoration Performance

8   Award winner we have a track record of superior performance.

9   We believe our system will continue to perform well, especially

10   in light of the new initiatives implemented since the PSC began

11   its ongoing storm preparedness efforts.  And Progress Energy's

12   organization and T&D systems are prepared for the 2008 season.

13             This concludes my prepared remarks.  Commissioners,

14   thank you for your attention, and I'll be happy to answer any

15   questions you have at this time.

16             CHAIRMAN CARTER:  Commissioners, just briefly.  I did

17   have one question.  Is that -- maybe I missed it.  Areas of

18   concerns or vulnerability, did you address that?

19             MR. CUTLIFFE:  I can address that now.

20             CHAIRMAN CARTER:  Okay.

21             MR. CUTLIFFE:  I would characterize it as three

22   areas.  First would be a catastrophic event that is a direct

23   strike to our territory accompanied by storm surge.  That is,

24   that is a grave concern.  To that end, we have collaborated

25   with the Coast Guard in a Tampa Bay tabletop exercise that

FLORIDA PUBLIC SERVICE COMMISSION

26

1   simulated an 18-foot storm surge event.  So we're beginning

2   some participation with other community and government

3   organizations to make sure that we're all in alignment with how

4   we're going to respond in the days after such an event.  But

5   that would be number one.

6             Number two would be successive events to the Gulf of

7   Mexico region, which can greatly dilute availability of

8   resources.

9             And then the third thing would be, quite candidly, in

10   our organization we have, like many organizations, a fair

11   amount of attrition, and a lot of our folks are in, in new

12   roles or they are new to our organization since 2004 and 2005.

13   And it has been a top priority in our drill preparation to

14   ensure that all employees receive comprehensive training on

15   their storm duties.

16             CHAIRMAN CARTER:  Commissioners, questions?  Staff?

17             MR. GARL:  Thank you, Mr. Chairman.

18             Just one question, Mr. Cutliffe.  You mentioned the

19   ongoing work in hardening the transmission system.  Can you

20   give us an estimate about how long you think that will take to

21   complete?  I take it it's more than a one-year effort.

22             MR. CUTLIFFE:  It is.  The systematic replacement of

23   all wood transmission poles with steel or concrete has been

24   underway since 2004.  I will have to get back to you on the

25   exact time frame for that to occur.  I can share with you that

FLORIDA PUBLIC SERVICE COMMISSION

27

1   that is a major portion of our ongoing hardening effort, and

2   we're investing in excess of $40 million a year in ensuring

3   that that transition takes place.  I will add that time frame

4   to my remarks and provide that for you by the end of the week.

5             MR. GARL:  Thank you.

6             CHAIRMAN CARTER:  Thank you very much.

7             MR. CUTLIFFE:  Thank you.

8             CHAIRMAN CARTER:  Next we'll have Tampa Electric

9   Company.

10             MR. HAINES:  Good morning, Mr. Chairman,

11   Commissioners and staff.  My name is Regan Haines, and I am the

12   Director of Engineering for Energy Delivery with Tampa Electric

13   Company.  And I appreciate the opportunity to be with you today

14   to update you on Tampa Electric's activities as we are prepared

15   and ready for the upcoming storm season.

16             My briefing today will cover various components of

17   Tampa Electric's storm preparedness initiatives.  I will start

18   out by first giving a brief overview of Tampa Electric's

19   service territory and our electrical system and then present

20   the key elements of Tampa Electric's storm hurricane

21   preparedness activities.  This will include our inspection and

22   maintenance programs, vegetation management activities,

23   coordination with our local governments, community groups and

24   other utilities, pre-storm season activities such as training,

25   mock storm drills and our inventory reviews.  I will also give

FLORIDA PUBLIC SERVICE COMMISSION

28

1   you an update on some of our system hardening projects and our

2   post-storm forensic analysis plans.

3             Tampa Electric's service territory covers

4   approximately 2,000 square miles in West Central Florida,

5   including Hillsborough County and parts of Polk, Pasco and

6   Pinellas Counties.  We serve over 670,000 customers and operate

7   roughly 4,450 megawatts of generation.  I have listed several

8   other statistics about our system as key to this presentation.

9   And Tampa Electric's electric system is fairly dense and is

10   comprised of over 15,000 miles of distribution circuits and

11   338,000 poles.

12             The first three elements of our storm preparation

13   involve ensuring that the electric system is in good condition

14   and is able to withstand the types of winds that it has been

15   designed for.  This consists of system inspections and

16   maintenance on our system and vegetation management program.

17             Tampa Electric has been increasing its transmission

18   inspection and maintenance programs following the Commission's

19   actions on storm hardening.  In 2007, the company completed

20   3,900, over 3,900 aboveground inspections, which is roughly

21   17 percent of our system and well above the required limits as

22   dictated by the Commission.  The aboveground inspections were

23   performed by helicopter to identify issues such as broken

24   crossarms, cracked insulators, woodpecker holes and potential

25   conductor problems.

FLORIDA PUBLIC SERVICE COMMISSION

29

1             We also performed groundline inspections on over

2   3,600 wooden structures, which led to approximately

3   565 structures identified for replacement.

4             A wind load screening analysis was also performed on

5   over 1,000 structures with joint use attachments.  Of the

6   structures requiring wind loading screening, 723 passed and

7   290 required a comprehensive loading analysis which is

8   currently in progress.  We also replaced 397 wooden structures

9   with steel or concrete poles and replaced 127 sets of polymer

10   insulators.

11             For 2008, we're planning to perform aboveground

12   inspections on almost 3,800 structures and groundline

13   inspections on over 3,400 wooden structures.  Our annual

14   infrared helicopter patrol was completed in March, and ground

15   patrols are underway with the goal of patrolling our critical

16   230kV, 138kV and critical 69kV transmission circuits by the

17   peak of this year's storm season, with the remainder followed

18   by the, by the end of the year.

19             Thus far in 2008 we have replaced 252 wooden

20   structures on the transmission system with steel or concrete

21   and have also replaced 33 sets of insulators.  It is

22   anticipated that we will replace a total of 560 structures and

23   over 100 sets of insulators by the end of the year, and this

24   will significantly harden our transmission system.

25             The company continues to execute its transmission

FLORIDA PUBLIC SERVICE COMMISSION

30

1   structure inspection program with a priority given to critical

2   and coastal facilities.  As inspections are completed on

3   critical and coastal facilities, the inspections will move

4   inland towards our older inland circuits.

5             Tampa Electric has also increased its distribution

6   inspection, maintenance programs over the last three years.  In

7   2007, the company completed almost 50,000 groundline

8   inspections resulting in the hardening of over 3,000

9   distribution wooden poles by either reinforcement or

10   replacement.  In addition, over 200 structural repairs were

11   made as a result of these inspections.  That will also harden

12   our distribution system.

13             For 2008, there are over 38,000 groundline

14   inspections planned, which represents about 13.5 percent of our

15   system.  These inspections also include performing wind load

16   screening analysis on all joint use poles.  For all the issues

17   found, the company targets having repairs made prior to June of

18   the following year.

19             Tampa Electric's vegetation management program is a

20   key element of the day-to-day reliability of our system as well

21   as preparing our system for hurricane season.  As filed in our

22   2006 storm implementation plan, the company is transitioning to

23   a three-year tree trim cycle on our distribution system which

24   includes all main feeders and laterals.  Tampa Electric's

25   methodology combines cycle trimming with the reliability-based

FLORIDA PUBLIC SERVICE COMMISSION

31

1   trimming, which takes into account several factors including

2   circuit priority, last date trimmed, reliability performance

3   and the number of tree-related outages seen by those circuits.

4             The current methodology is flexible enough to move

5   tree trim resources to priority-based circuits within our

6   service area or region to enhance system reliability, and all

7   our hot spot trimming is performed by the peak of hurricane

8   season.  The company has increased the level of tree trim

9   resources by 80 percent since 2005.

10             On the transmission system the company patrols our

11   230kV circuits twice a year and our 69 and 138kV transmission

12   system once a year for vegetation issues.

13             While having a sound functional electric system is

14   critical prior to storm season, hurricane planning and

15   emergency management and Emergency Operation Centers are

16   paramount to ensure a synchronized response.  Tampa Electric

17   Emergency Management coordinates with our local governmental

18   agencies like the EOCs, hazard mitigation groups and those fire

19   departments acting as EOCs, along with regional planning

20   councils and other utilities on an ongoing basis.

21             The company began annual planning meetings with all

22   our service territory EOCs in 2006.  These meetings consist of

23   a review of the critical facilities in our service territory,

24   development and updating our communication and response plans

25   and a discussion of any coordination needs during a response.

FLORIDA PUBLIC SERVICE COMMISSION

32

1             In addition, the need to train local governmental

2   agencies such as local police and fire on damage assessment

3   techniques was identified early on in the Commission's storm

4   hardening review.  Tampa Electric has developed a training

5   program to address this and has offered this training to all

6   our local governmental agencies.

7             The company also participates in and helps develop

8   many storm preparedness training exercises and workshops with

9   governmental and private industry groups each year such as the

10   ones listed.

11             Coordination with other utilities as it relates to

12   business continuity and emergency management is also very

13   important.  Our mission of sharing information allows all to

14   benefit from lessons learned, and the work through EEI and EPRI

15   are vital towards this end.  We participate in the EEI Business

16   Continuity Work Group and have made presentations at several of

17   their conferences.  We are also supporting EPRI in their

18   development of the emergency management guidance document.

19             At a local level the company meets with agency and

20   EOC officials at our Energy Control Center to discuss the

21   restoration process and their required communication

22   coordination needs.  We also work with government officials to

23   discuss the need for appropriate vegetation management in

24   preparation of the storm season and to communicate the balanced

25   approach taken between aesthetics and sufficient clearance to

FLORIDA PUBLIC SERVICE COMMISSION

33

1   prevent vegetation contact during high winds.

2             Finally, the company has worked with local officials

3   to make sure we have established incident bases in all of our

4   service areas.  These incident bases are needed to provide

5   logistical bases for visiting crew operations, including

6   staging material, trucks, meals and the distribution of our

7   work order assignments.

8             Coordination with other utilities is also an

9   important element in our preparations.  As experienced in each

10   of the 2004 hurricanes that impacted Tampa Electric, mutual

11   assistance from other electric utilities is absolutely critical

12   to quick restoration.  The company actively participates in the

13   Southeastern Electric Exchange Mutual Assistance Group and the

14   Edison Electric Institute Mutual Assistance Committee.  Through

15   these organizations the company has access to other utility

16   resources available from across the nation.

17             In addition to the coordination with fellow electric

18   utilities, it is essential that we coordinate our activities

19   with the telecommunications, cable and other utilities that may

20   attach to our poles.

21             The company completed a physical audit of 25 percent

22   of its joint use poles in 2007 and plans to complete the audit

23   on 37.5 percent of our system by the end of 2008.  It is the

24   company's goal to complete this type of joint use audit every

25   three years.  This will help ensure that each of our poles has

FLORIDA PUBLIC SERVICE COMMISSION

34

1   been designed to accommodate everything that is attached to it

2   and that it will meet the company's wind loading criteria.

3             The company also has held several meetings in 2007

4   and this year with our third party attachers to review and

5   coordinate our storm hardening plans and specific storm

6   hardening projects.

7             As storm season approaches each year, Tampa Electric

8   performs several pre-storm season activities that assist in the

9   company's preparations.  This includes a review of our disaster

10   recovery plans where they are exercised and updated annually.

11   In addition, we have started to meet with the EOC starting with

12   Hillsborough County to review and synchronize our security

13   priority list.

14             The company also conducted a mock storm circuit

15   patrol training exercise to familiarize new personnel on what

16   to look for and how to assess the system for damage.  All

17   inventory levels of storm material will be reviewed and

18   ordered, and on May 13th the company will conduct its mock

19   storm exercise with several other functional areas within the

20   company that are involved in restoration activities.

21             Finally, the company has reviewed and updated its

22   storm damage model that is used to estimate the number of

23   resources needed as well as material required based on the

24   predicted strength, size and landfall of a hurricane.

25             In addition to the previous activities mentioned that

FLORIDA PUBLIC SERVICE COMMISSION

35

1   will benefit Tampa Electric and its customers during hurricane

2   season, I also wanted to briefly mention some of the storm

3   hardening items that were approved in our three-year hardening

4   plan filed in 2007.  While most of these items will provide

5   future benefit, a key element of our plan that has been

6   benefiting Tampa Electric customers for many years is our

7   distribution system construction standard.

8             While the National Electric Safety Code is the

9   guideline that most utilities utilize with a minimum

10   requirement of Grade C in most situations, Tampa Electric

11   constructs its system to Grade B, which is approximately

12   50 percent stronger than the minimum requirements.  Some of the

13   hardening projects that the company completed last year

14   included the conversion of four overhead interstate crossings

15   to underground, the engineering needed to convert our remaining

16   4kV overhead system to our standard 13kV, and the inspection

17   and repair of nine critical network protectors in low-lying

18   areas within downtown Tampa.  We also completed a majority of

19   the engineering for Phase 1 of our Port of Tampa extreme wind

20   pilot project.

21             In 2008, the company plans to continue with the storm

22   hardening initiatives, which will include the conversion of

23   four additional overhead distribution interstate crossings to

24   underground, completing our 4kV conversion project in South

25   Tampa, inspecting six additional network protectors in downtown

FLORIDA PUBLIC SERVICE COMMISSION

36

1   Tampa, and completing construction on our extreme wind pilot

2   projects which will include Phase 1 of our Port of Tampa

3   project and St. Joseph's Hospital hardening project.  We'll

4   also be transitioning to stainless steel as a new standard for

5   all of our pad-mounted equipment.

6             We will also be completing the implementation of our

7   new geographical information system or GIS system in June, and

8   continuing our participation in various joint research projects

9   with PURC and the other Florida utilities.

10             And the final component of Tampa Electric's storm

11   preparation is ensuring that resources and processes are in

12   place to acquire forensic data following a hurricane.  The

13   company has contracted with a consultant that has expertise in

14   this area of post-storm forensic analysis.  Their task will

15   include the determination of which areas to patrol, how much of

16   the system should be patrolled, the patrols themselves, the

17   evaluation of the damaged equipment and the development of a

18   report outlining the findings, analysis, conclusion and

19   recommendation for any changes and/or improvements to the

20   company's construction standards or practices.

21             In summary, Tampa Electric continues to make

22   improvements to our storm preparedness activities each year,

23   including the number of inspections and repairs we are making,

24   the amount of tree trimming performed, increasing coordination

25   with our local governments, communities and fellow utilities

FLORIDA PUBLIC SERVICE COMMISSION

37

1   and improving our pre-storm season training programs.  Our

2   storm hardening plans are well underway and we have established

3   forensic data collection analysis in place.  Tampa Electric is

4   well prepared and ready for the 2008 storm season.  I'd be

5   happy to answer any questions you may have at this time.

6             CHAIRMAN CARTER:  Just one moment, Commissioners.  I

7   just want to ask again areas of concern and vulnerability.

8             MR. HAINES:  I would have to concur with what's been

9   said.  Our main concern would be getting hit with a

10   catastrophic hurricane with, with severe storm surge as well as

11   getting hit with multiple hurricanes in the same season.  I

12   think it was also mentioned that just obtaining the number of

13   resources that we would need to restore quickly is also always

14   a concern that we would have.

15             CHAIRMAN CARTER:  Okay.  Commissioners?  Commissioner

16   Edgar, you're recognized.

17             COMMISSIONER EDGAR:  Thank you, Mr. Chairman.  I did

18   have one question.

19             A few pages back in your presentation you mentioned

20   completing the undergrounding of some interstate crossings and

21   then also some other similar actions that will be taking place.

22   And I was just wondering is the decision to go from overhead to

23   underground for those interstate crossings, is that primarily a

24   storm-related preparedness decision and/or related to other

25   reliability issues or were there other, other factors that

FLORIDA PUBLIC SERVICE COMMISSION

38

1   contributed to that decision?  And then if you can, speak a

2   little bit as to how that cost-benefit analysis or thought

3   process went.  Thank you.

4             MR. HAINES:  Okay.  Yes.  The main drivers there are

5   for our storm hardening.  The thought behind it is that

6   following a major storm, if you have overhead facilities laying

7   across major evacuation routes such as I-275, I-75 or I-4 in

8   our area, that it could delay first responders, it could delay

9   customers and have a major impact just following a major storm

10   event.  So that's kind of what we looked at when we decided to,

11   to convert those to overhead, I mean, to underground.

12             COMMISSIONER EDGAR:  Thank you.

13             CHAIRMAN CARTER:  Commissioners, any further

14   questions?  Staff?  Thank you very kindly.

15             MR. HAINES:  Thank you.

16             CHAIRMAN CARTER:  Next we'll hear from Gulf Power.

17   And by the way, Commissioners, as the next person is coming up,

18   after the Gulf Power presentation we'll be taking our first

19   break, give the court reporter a break and go from there.

20             Good morning.  You're recognized, sir.

21             MR. McQUAGGE:  My name is Andy McQuagge, and I'm the

22   Power Delivery Services Manager for Gulf Power Company and I'll

23   be providing our hurricane preparedness briefing this morning.

24             Our storm preparedness activities can really be

25   broken down into two main areas:  Our storm hardening projects

FLORIDA PUBLIC SERVICE COMMISSION

39

1   and initiatives, which includes our vegetation management

2   program, our inspections and maintenance program, our extreme

3   wind loading projects, our Grade B construction and our third

4   party attachers and local government coordination.

5             The second prong of our preparedness activities is

6   really storm restoration and recovery plans, and included in

7   that is our storm recovery plan, our Southern Company affiliate

8   and other mutual assistance support, our supply chain area,

9   post-storm forensic data collection and local government

10   coordination.

11             In the area of transmission vegetation management, of

12   the 444 miles of 230kV right-of-way, we have completed all of

13   our inspections, we're at 100 percent, and any vegetation

14   hazard that has been identified has been corrected.  On our

15   1,037 miles of 115kV line we're 80 percent complete with our

16   inspections.  We're correcting those vegetation hazards as we

17   find them and we're on schedule to be complete by June 1st of

18   2008.

19             On our 114 miles of 46kV right-of-way our inspection

20   patrols are actually scheduled to begin today, and we're on

21   schedule to complete both the inspections and the corrections

22   by June 30th of '08.

23             In the area of distribution vegetation management, on

24   our mainline annual trim schedule, our MATS program, which is

25   our three-year cycle in which we look at and do a maintenance

FLORIDA PUBLIC SERVICE COMMISSION

40

1   trim on one-third of our system, and then in Bullet 2 you will

2   see our MICS program, which is the other two-thirds of our

3   system that we make any quick corrections, any hot spot trims.

4             But going back to Bullet 1 on our MATS program, we've

5   completed 225 miles of the 265 miles that we have scheduled for

6   2008.  On the other two-thirds of the mainline feeders in which

7   we will inspect and correct any vegetation hazards we find we

8   have completed 760 miles of the 803 that we have scheduled.

9             On our annual lateral trim, which is our six-year

10   cycle on our lateral lines, we've completed 310 miles of the

11   843 that we have scheduled for 2008.

12             And on the fourth prong, our storm hardening annual

13   removal program, which we had set an annual goal of 5,000

14   danger tree removals, we have actually removed in 2007 and year

15   to date 2008 almost 14,000 trees.  And if you'll remember from

16   our discussion last year, that is mainly dead or dying trees

17   that are off right-of-way that could cause us problems in the

18   event of everyday reliability or storms.  We do anticipate that

19   number will probably drop a little bit as the program evolves

20   and we go to removing green trees that may be off right-of-way

21   that could present a danger.  But the program has been very

22   well received so far because it is dying and dead trees off

23   right-of-way.

24             In the area of transmission inspections and

25   maintenance, we have flown our transmission system once.  We do

FLORIDA PUBLIC SERVICE COMMISSION

41

1   that quarterly, so we should have another flight of our system

2   in the next month.

3             On our comprehensive walking and climbing six-year

4   inspection program, it's scheduled to commence on June 1st and

5   it's scheduled to go through September 30th.  As far as

6   additional activities in the area of transmission, we have

7   storm hardened by installing additional guys 170 structures.

8   We have replaced 214 wood crossarms with steel crossarms.

9   That's a ten-year program, and we're actually at 24 percent and

10   we're only two years into that program.  We've completed all of

11   our steel groundline inspections for 2008, which is 140

12   structures.  And our wood groundline treatment inspections for

13   2008, which was a little over 1,000, are also fully complete.

14             In our distribution pole inspections we transitioned

15   in 2007 from our current, from the ten-year inspection cycle we

16   had to the eight-year cycle.  We rebid our contract and the

17   contract inspections were awarded to Osmose.  And we met our

18   target of inspecting one-eighth of our system, which was about

19   33,000 poles during the last quarter of 2007.  We have another

20   eighth of our poles, which will be around 33,000, scheduled for

21   the last quarter of this year.

22             In the area of joint use audit, pole strength

23   analysis assessments, we had committed to do 5 percent of the

24   poles 20 years or older that had three or more attachers, which

25   comes out to about 450 poles.  We looked at 500 poles in 2007.

FLORIDA PUBLIC SERVICE COMMISSION

42

1   We had 41 failures due to loading and two failures due to

2   damage to the actual pole.  We have another 516 that we are

3   currently looking at for 2008.  And we have conducted our first

4   series of semiannual third party attachers meetings, and we

5   held three of those, one in each of our district offices, in

6   February.

7             As far as our annual infrared inspections on our

8   distribution systems, when I put this presentation together we

9   were at 75 percent.  In checking with the engineer yesterday,

10   we were at about 98 percent and he assured me we would be

11   complete by today.  So we're 100 percent complete.  And the

12   things that we find on those inspections should be fixed by the

13   end of June.

14             We transitioned at Gulf Power to Grade B, from

15   Grade C to Grade B construction in January of 2008.  We have

16   completed training on what Grade B construction requires for

17   all of our field personnel and have trained them on the

18   software program that we use to actually model the poles, which

19   is Pole Foreman (phonetic.)  That training has been completed

20   and that program is fully underway.

21             As far as our extreme wind loading projects, the

22   focus of these projects has been interstate crossings and lines

23   serving critical infrastructure facilities such as fuel depots,

24   hospitals and sewage treatment facilities.  Our storm hardening

25   plan as approved identified 19 projects for 2007 and 2008, and

FLORIDA PUBLIC SERVICE COMMISSION

43

1   as of May 1st we have completed 14 of those projects.  Three

2   are under construction with a July 1st completion date and two

3   are in the design phase.

4             As far as our third party attachers and local

5   government coordination, as I mentioned earlier, we continue

6   our meetings with our third party attachers.  We participated

7   in a public information workshop in Escambia County.  We were

8   the primary sponsor for My Safe Florida Hurricane Expo in

9   Escambia County during April.  We have conducted hurricane

10   preparedness seminars with our EOC personnel and our news media

11   during April.  We participated in an EOC workshop on hurricane

12   season in Escambia County in March.

13             Our bill inserts in June will have hurricane

14   preparedness and safety information for our customers.  We have

15   three Community Leader Forums scheduled in June and July to

16   discuss issues including hurricane readiness, and at the end of

17   this month we'll be doing a presentation for the Escambia

18   County healthcare facilities on storm preparedness.

19             As far as our storm recovery plan, our 2008 storm

20   procedures are completed and have been updated.  Our employee

21   storm assignments are complete, with an emphasis on the right

22   person for the right job.  And our storm training and refresher

23   courses, if not already completed, are underway.  And most of

24   our field personnel, our team leader evaluator, drivers, have,

25   all those have been completed, but we have a few of the support

FLORIDA PUBLIC SERVICE COMMISSION

44

1   functions that are still doing some training.

2             In the area of mutual assistance, we have our

3   Southern Company affiliate support from our sister companies,

4   Alabama, Georgia, and Mississippi, that we can count on in case

5   of a catastrophic event.  And as others have mentioned, we are

6   also members of the SEE Mutual Assistance and EEI Mutual

7   Assistance Groups.

8             In the area of, in the area of supply chain, our

9   storm supply materials will be available by June 1st.  In the

10   area of post-storm forensic teams, we have hired a contractor

11   and we've held two drills to make sure that our system talks to

12   the data gathering system and that we can import the data back.

13   And we held two, two drills in late '07 and those processes

14   worked fine.

15             In the area of local government coordination, our EOC

16   representatives are assigned, trained and are actively engaged

17   not only in storm restoration, but any time those EOCs are open

18   we provide 24-hour coverage.

19             We were, the question was asked earlier, do we

20   participate in county drills?  We actually participated in

21   Santa Rosa County's drill last week.  Last year we participated

22   in actually five county drills.  So I anticipate that as we get

23   closer to storm season, that we'll be asked to participate in

24   other county drills.

25             I did not put it on the slide, but the question has

FLORIDA PUBLIC SERVICE COMMISSION

45

1   been asked on our areas of concern.  One of the issues that I

2   had brought up last year was the availability of tree

3   contractors, that we were having a bit of an issue with

4   certification and finding qualified people.  We've worked

5   through that issue and I feel like we have a very good staff.

6   And as you can see from the progress on our goals, I think we

7   are, we're sitting good on that issue that we had last year.

8             As far as areas of concern for this year, it's very

9   consistent with the others.  The potential for multiple events

10   or a catastrophic event does concern me.  The availability of

11   resources, even though we do have mutual assistance contacts,

12   is a concern area in the event of a catastrophic event.

13             In summary, Gulf is fully prepared as we enter the

14   2008 storm season.  We're on target with our transmission and

15   distribution storm hardening initiatives.  We continue our

16   ongoing coordination with government, community groups, third

17   party attachers and other utilities.  We have a storm recovery

18   plan that is proven and battle tested, as evidenced by our

19   response during Ivan and Dennis.  We constantly make

20   improvements based on lessons learned.  We have contracts in

21   place, staging site agreements in place.  As I mentioned

22   earlier, our training and refreshers are ongoing and we have

23   experienced teams ready, if needed.  In summary, Gulf Power is

24   fully prepared for whatever the 2008 storm season may bring.

25             CHAIRMAN CARTER:  Thank you.  Commissioners?  Staff?

FLORIDA PUBLIC SERVICE COMMISSION

46

1             MR. GARL:  Thank you, Mr. Chairman.

2             Just one simple question.  Could you discuss a little

3   bit the vulnerability of your repair and restoration plans

4   should that I-10 bridge get taken out again by a major storm?

5             MR. McQUAGGE:  That was a considerable issue during,

6   during Ivan.  And basically we don't have a whole lot of

7   options other than 98 or back up through Milton on Highway 90.

8   It's just an issue that we'll have to work through.  Hopefully

9   the new bridge will, will hold up a little better than the

10   other.  But that is another potential area of vulnerability as

11   far as transportation.

12             MR. GARL:  Thank you, Mr. McQuagge.

13             CHAIRMAN CARTER:  Commissioners, nothing further?

14             Thank you very much.

15             Commissioners, staff and those involved here, we're

16   getting ready to take a, take a break, give our court reporter

17   a break.  We'll -- I'm looking at, I'm looking at 10:44 but it

18   says 10:45 on the wall.  So let's come back at 11:00.  We're on

19   recess.

20             (Recess taken.)

21             We are back on the record with our workshop.  And

22   first we'll start with, for this section here we'll go with

23   Florida Public Utilities Company.  You are recognized, sir.

24             MR. MEYERS:  All right.  Thank you.  Good morning,

25   Commissioners and staff.  My name is Don Meyers.  I'm the

FLORIDA PUBLIC SERVICE COMMISSION

47

1   General Manager for the Northwest Florida Division.  I'd like

2   to first apologize if my voice appears a bit scratchy and gives

3   out on me a few times.  I've recently quit smoking and it's

4   probably affected me more than when I used to smoke.  Anyway,

5   I'll do the best I can.

6             CHAIRMAN CARTER:  You sound better already.

7             MR. MEYERS:  I won't spend a lot of time on this

8   first slide since we've recently spent quite a time, quite a

9   while before this Commission.  But we are a small

10   investor-owned utility; we serve approximately 28,000 electric

11   customers.  They are probably equally divided between our two

12   divisions:  Our Northeast Division, which is northeast, north

13   of Jacksonville is on an island that is four miles wide by

14   11 miles long right on the coast, while our Northwest Division

15   is primarily rural, includes parts of Jackson County, Calhoun

16   County and Liberty County.

17             As far as our hurricane season preparations, on our

18   vegetation management we focused on our main feeders and areas

19   with reliability issues.  Pole replacement, our main focus has

20   been on replacing deteriorated poles.  In our Northeast

21   Division they for many years, a good many years have continued

22   beach inspections.  They replace deteriorated hardware along

23   the beach.

24             We are in the process of reviewing our emergency

25   procedures this month, and we'll be holding training for our

FLORIDA PUBLIC SERVICE COMMISSION

48

1   employees later this month.  We have completed all our

2   substation inspections and made corrections to things we found.

3             Our inventory needs have been evaluated and to make

4   sure that there are adequate supplies for in the event of a

5   hurricane.  We have continued involvement with the mutual

6   assistance groups, primarily the Southeast Electric Exchange

7   Mutual Assistance Group as well as the Florida --

8             CHAIRMAN CARTER:  Excuse me.  I think your, I think

9   your slide zigged when you should have zagged on that.

10             MR. MEYERS:  Okay.  I forgot to --

11             CHAIRMAN CARTER:  Chris, can you show him how to --

12             MR. MEYERS:  I've got it.

13             CHAIRMAN CARTER:  You've got it?  Okay.

14             MR. MEYERS:  We have identified additional manpower

15   and resources.  We have completed a Graphical Information

16   System and SCADA system for several years now.  It's been

17   complete in our Northwest Division.  Our Northeast Division

18   just recently completed the Graphical Information System.  Now

19   we're, our entire system is on a computer and that ties into an

20   outage management system.  So we are much more able to

21   communicate where outages are and maybe give better dates of

22   restoration time.

23             Issues included in Docket Number 070304-EI and Docket

24   070300-EI were resolved recently on April 22nd.  A small

25   utility like ours, we were not able to take on some of the

FLORIDA PUBLIC SERVICE COMMISSION

49

1   storm initiatives without rate recovery.  That was resolved in

2   those two dockets.

3             Initiatives for vegetation management and

4   transmission storm hardening will be revised based on the final

5   decisions.  Implementation of other initiatives will begin

6   during the second half or third quarter of 2008.

7             Now going into a little more detail for our storm

8   hardening initiatives.  Pole inspections, visual inspections of

9   approximately 2,800 poles were completed in 2007.  Detailed

10   inspections in accordance with storm plan will begin in

11   July 2008.  Transmission inspections, visual inspections --

12   whoops, I need to go one more.  All right.  Visual inspections

13   completed in 2007, climbing inspections in accordance with the

14   storm plan to begin during 2008.

15             Management, vegetation management emphasis on moving

16   to a 3/6-year crew or cycle with existing crews, areas with

17   reliability will be addressed.  Joint use audits will begin

18   during 2008 with pole loading issues identified.

19             Company personnel will be located in EOCs in order to

20   enhance communication with local governments.  We have already

21   participated with a trial run with the County of Calhoun

22   County.  Forensics data collections procedure is being

23   completed with a contractor to be identified prior to September

24   '08.  We hope to have one identified much sooner than that.  We

25   have, one of our employees is going to be attending a workshop

FLORIDA PUBLIC SERVICE COMMISSION

50

1   in Orlando next week on what kind of forensic data do you need

2   to collect, and we'll be proceeding with that.

3             During 2007, we completed two projects that included

4   our extreme wind loading standards in the design.  One was out

5   at the federal prison and another was on Highway 90, both in

6   Northwest Florida.

7             During 2008, two projects are included for extreme

8   wind loading standards.  These include approximately 82 poles

9   that provide critical, or service to critical infrastructure:

10   One, the Baptist Hospital in Fernandina Beach, and our sewer

11   treatment plant on Highway 90 in Marianna.

12             Our conclusion is that Florida Public Utilities is

13   adequately prepared for the 2008 hurricane season.  Decisions

14   from the recent dockets provide the ability for FPU to address

15   the initiatives and projects in an effective and productive

16   manner.

17             Any questions?

18             CHAIRMAN CARTER:  Thank you.  Commissioners, I'm

19   going to ask my standard question.  On the -- for your company,

20   did you find any areas of concern or vulnerability?

21             MR. MEYERS:  Like everybody else, a catastrophic

22   storm as well as multiple strikes.  Being that we participate

23   in the Southeast Electric Exchange Mutual Assistance Group --

24   and 2004 was a tough, a particularly tough year, we had Rita,

25   Hurricane Katrina and Rita out in West Texas followed by

FLORIDA PUBLIC SERVICE COMMISSION

51

1   several storms in the peninsula part of Florida.  We

2   participated in restoring on those storms.  But when all that

3   activity was going on, if a hurricane had struck in our area,

4   we would have been very limited in resources and as well as

5   material.  That's always a concern.

6             Also our Northeast Division lying right on the coast,

7   an island, storm surge is always a concern.  And we've begun

8   making sure our pad-mounted transformers, we pour an additional

9   concrete pad going down to a certain depth and tie, make sure

10   the pad mounts tie down on that.  So storm surge is a major

11   concern in our Northeast Division.

12             CHAIRMAN CARTER:  Okay.  Commissioners?

13             Staff, you're recognized.  No questions?

14             Thank you very kindly.

15             MR. MEYERS:  Okay.

16             CHAIRMAN CARTER:  Next, Commissioners, we'll hear

17   from Florida Municipal Electric Association.

18             MR. MOLINE:  Thank you, Mr. Chairman and

19   Commissioners.  My name is Barry Moline.  I'm with the Florida

20   Municipal Electric Association.  And we have three

21   presentations.  I'm going to give a brief introduction, and

22   then we'll have Kevin Wails from the City of Tallahassee and

23   Rebecca Mattey from the City of Ocala give you some examples of

24   what goes on at municipal electric utilities.

25             It's always nice when the very first word in your

FLORIDA PUBLIC SERVICE COMMISSION

52

1   presentation is a typo, but there are actually 34 municipal

2   electric utilities, and I have no one to blame but myself for

3   that.

4             We serve 1.3 million customers, which is about

5   14 percent of the state's population.  And we're characterized

6   by large and small utilities.  Jacksonville and Orlando are the

7   two largest.  But we all -- and Tallahassee, 111,000 customers.

8   We have Bushnell, Blountstown, Chattahoochee in the Panhandle

9   with around 1,000 customers each.  So we have this disparity in

10   the number of customers that we serve.  But combined we're the

11   third largest utility, we would be the third largest utility

12   behind FPL and Progress Energy.  This is where we are, from

13   Blountstown in the Panhandle down to Key West.

14             And, again, just as a general introduction, do all

15   the small utilities generate, and the answer is that they

16   don't.  Only 13 out of the 34 actually generate electricity or

17   have a power plant.  Fifteen purchase all their power from the

18   Florida Municipal Power Agency, a wholesale power supplier in

19   Orlando.  And then eight purchase some from there and the rest

20   purchase from the investor-owned utilities.  And this is a

21   breakout of how the market share is for the state's utilities.

22             We depend on mutual aid to help each other.  And we

23   have mutual aid agreements in Florida; we have a southeastern

24   group as well as national mutual aid.  This is our mutual aid

25   agreement for, and our procedures for Florida.  And, and for

FLORIDA PUBLIC SERVICE COMMISSION

53

1   the hurricanes that we had in '04 and '05 we had national

2   assistance from these states.

3             Today we're going to hear from the City of Ocala and

4   the City of Tallahassee.  But the message I want to leave with

5   you is that while we may be small and may be spread out across

6   the state, we work together on mutual aid to make sure that

7   customers are well served during storms.

8             CHAIRMAN CARTER:  Thank you, Mr. Moline.

9             Kevin Wailes.

10             MR. WAILES:  Thank you.  Good morning, Mr. Chairman

11   and Commissioners.  I'm Kevin Wailes.  I'm the General Manager

12   of the City of Tallahassee Electric Utility, for many of you

13   your hometown utility.

14             The presentation I have today might be just a little

15   different than what you've seen because we're not here

16   routinely in front of you.  So I'm going to try to give you a

17   little more of a higher level overview.  Certainly we have a

18   lot of the detail, we filed the storm hardening report in

19   February, so a lot of the detail, the number of poles and all

20   that, can be had.  But I thought maybe what makes us a little

21   different on the way we handle those responses might be a

22   little more interesting.

23             So overall what we'll talk about is we'll just do a

24   brief system overview, talk about briefly our experience in

25   dealing with storms, our preparation, emergency operations, our

FLORIDA PUBLIC SERVICE COMMISSION

54

1   emergency response, and then somewhat other unique features

2   associated with how we as an electric utility integrated into a

3   local government deal with many of these issues.

4             As Barry said, we have a little over

5   110,000 customers.  We serve a 210 square mile area.  We have

6   185 miles of transmission in three counties, both 115 and 230kV

7   lines.  Unlike when you're talking to Florida Power & Light and

8   they've got something like, I don't know, I think it was 60,000

9   transmission poles, we have 3,000.  So there's a scale

10   difference in what we deal with, but there's lot of commonality

11   in how we have to deal with those issues as well.

12             We have 2,600 miles or over 2,600 miles of

13   distribution.  Of that, interestingly enough, over 60 percent

14   of that is underground.  You'll find that virtually everything

15   we construct anymore is underground utilities.  We have 24

16   substations, 12kV, 115 and 230kV.

17             I thought it might be appropriate to talk a little

18   bit about our power plants from the perspective that, as you

19   all know, we're one of the only major generators in this part

20   of the state.  So if we have a catastrophic event that takes

21   out a significant amount of transmission, our generation ends

22   up being relatively key to what's happening in this part of the

23   panhandle.

24             We operate three power generation facilities.  One of

25   them is very small, which is the C. H. Corn Hydro Unit.

FLORIDA PUBLIC SERVICE COMMISSION

55

1             The first of them is Purdom Plant.  That's a 300

2   megawatt plant.  The largest unit is a 250 megawatt unit that

3   was commercial in 2000.  As we went through the permitting

4   associated with that unit, it was, there was a great deal of

5   discussion regarding storm surge, how do we deal with that.

6   That plant was constructed so that everything was either

7   constructed above or protected to the 100-year flood plain.

8   It's five and a half miles from the coast.  So we have a number

9   of plans in place to deal with that, including ultimately

10   potential evacuation of the site if we need to secure it and

11   move our people, the people there to the other plant.  The key

12   thing about that is that it's black start capable.  So we don't

13   have to have an outside power source to bring the plant up, and

14   that's kind of the key that we have done with all of our

15   facilities because we recognize the transmission provides a

16   vulnerability to us given the network that we have.  And the

17   other key, I guess, to think about with respect to that

18   particular facility is, you know, it is near the coast.  But as

19   we've, as we've addressed a variety of issues, it's been there

20   for a long time and we've just taken a look at all the

21   vulnerabilities associated with being on that river as well.

22             The Hopkins Plant, on the other hand, is seven miles

23   west of town.  It's a 430 megawatt facility and it's also black

24   start capable.

25             The hydro unit, the reason I wanted to mention that

FLORIDA PUBLIC SERVICE COMMISSION

56

1   is one of the challenges we have when we're in storm events

2   like tropical storms or hurricane events is we also have to

3   manage flood control for the Ochlockonee River.  And that ends

4   of up being quite a challenge between dealing with lake levels

5   and river levels, trying to anticipate what the water flows are

6   going to be.  Under normal operation that's a run-of-river

7   project.  As you know, it's only one of two hydro projects in

8   Florida.  So we don't peak with it.  We basically, what water

9   comes in we release.  When we do flood control, however, we do

10   try to manage it.  We'll lower the lake trying to anticipate

11   what the flow is going to be into it so we cannot flood the

12   downstream.  It makes for a challenging time.  And although we

13   have lots of models that tell us what rainfall is going to be

14   in the basin, it's still, there's a lot of art to the folks

15   that are trying to make that happen.

16             Our experience, I started with Kate.  That's really

17   the last major storm that hit this area.  And as you'll see, we

18   had over 300 mutual aid people supporting that restoration.  I

19   didn't come to Tallahassee until 1987, so I didn't get to

20   experience that.  Back in those days I was dealing with ice

21   storms.  But one of the things I think that we ought to

22   remember about that for those of you that were here, I believe

23   the restoration effort took about ten days.  And you ought to

24   think about that was just barely a Category 1 storm hitting

25   Tallahassee.

FLORIDA PUBLIC SERVICE COMMISSION

57

1             When, Mr. Chairman, when you talk about

2   vulnerabilities, if you fly into Tallahassee, all you see is

3   trees.  You don't see rooftops.  And trees are our

4   vulnerability in this system.  We all love them, we're proud of

5   them, we try to take care of them, but they do provide

6   vulnerability during storms.

7             I won't go through all this list of storm, list of

8   storm activities, but the key to this is, if you'll note,

9   several of these what we've identified is where we've provided

10   mutual aid.  Some of them we've had never a direct hit; we've

11   had impacts from them.  But we've provided mutual aid ranging

12   from Homestead to Georgia Power Company, Lakeland, Gainesville,

13   Orlando, even Louisiana on a couple of occasions, for example,

14   during Rita.  And, of course, Homestead and Florida Power &

15   Light.

16             One of the reasons I, I bring that up is because even

17   though we're small, we do provide a lot of mutual aid.  And the

18   other thing you do is build relationships.  We find when you

19   have storms that are potentially identified as targeting, we'll

20   get calls, for example, from Louisiana saying do you want us to

21   start coming your way, that type of thing.  You build

22   relationships under those mutual aid agreements, and it's

23   interesting how strong those community bonds come up.

24             Under the standard preparation discussion, we

25   obviously do our NESC, the extreme wind loading standards.  It

FLORIDA PUBLIC SERVICE COMMISSION

58

1   is interesting, we've done front lot line construction in this

2   system since the '70s, so that does, that was one of those

3   issues that came up on the storm restoration discussions, and

4   it does make restoration a lot easier when you've got that kind

5   of access and particularly for some of the challenges we have

6   with our trees.

7             95 percent of our new distribution construction is

8   underground and any new area you go into you have pretty much

9   evidence of that.  All of our new transmission poles or

10   scheduled replacements are steel or concrete.

11             Moving to vegetation management, that's kind of a

12   little different for us.  We had a three-year trim cycle on

13   this system ranging from the late '80s through about the mid

14   '90s.  That three-year trim cycle had us trimming trees back to

15   ten to 12 feet.  What we experienced was a significant amount

16   of community concern about that.  We had an 18-month citizen

17   process going through reviewing our tree trimming processes and

18   cycles, including our forestry group and a whole bunch of

19   folks.  The outgrowth of that was kind of interesting.  They

20   said they wanted us to go to an 18-month trim cycle, trim less

21   but trim more often.  Candidly, our staff, particularly our

22   foresters who understood the three-year industry standard

23   cycle, were very skeptical about whether we could make that

24   work or not.

25             We're probably in our sixth 18-month cycle now after

FLORIDA PUBLIC SERVICE COMMISSION

59

1   that process and, of course, we've refined it as we go.

2   There's a pro and con to it.  You have less trimming.  So from

3   a, from a visual standpoint it's more attractive.  But by the

4   same token then, the trees are closer to the lines when you've

5   trimmed them.  So you see the lines a lot more often, you have

6   folks there trimming them, so you're getting a lot more review.

7   But on the other hand, it's closer for squirrels to jump to

8   them.  I hate to say that, but we had that happen this morning.

9   You know, we have, we have a little more exposure to those

10   kinds -- or if there is a significant wind, having that

11   proximity closer.  That's a choice our community has made.

12   That's what we think makes public power a little different is

13   our community has provided that input saying here what's we

14   want.  We want the trees.  You know, we're going to -- now I

15   will tell you that those same customers really aren't happy

16   about those outages caused by squirrels and things like that.

17             But the other thing we try to do with that less

18   clearance is we try to use tree growth regulators more often.

19   So that, in fact, what happens is we somewhat retard the growth

20   of those trees, particularly that new growth that might come

21   back.  We also have a fairly active training program with our

22   contractors with respect to proper trim techniques to try to

23   get the optimum time span we can out of that 18 months.

24             On the transmission side we have a three-year minimum

25   trim cycle.  The right-of-way is mowed at least annually.  It's

FLORIDA PUBLIC SERVICE COMMISSION

60

1   actually mowed probably four times a year in more urban areas

2   just because it's a visual issue that is raised up by those

3   adjacent property owners, and so it's a fairly aggressive cycle

4   as well.

5             We have a distribution pole inspection program that's

6   been every eight years.  I think we've completed two cycles.

7   We'll be going into our third.  That process takes us three

8   years on the system but we do it every eight years.  We have --

9   our transmission poles are done at the same time as the

10   distribution on that part.

11             The transmission inspection program is literally a

12   climbing inspection that we have our folks do once every five

13   years all over the system so that we can check, physically

14   check hardware with people on the pole when we do it.

15             We have transmission that we fly our transmission

16   twice a year and we do have infrared capability associated with

17   an arrangement we have.  We jointly purchased with the police

18   department and the sheriff's department infrared looking radar

19   and put it on the sheriff's helicopter.  And for that, in turn

20   for that investment we get a certain amount of time from the

21   sheriff's department.  So it's how we've, as a small utility

22   how we've optimized our ability to use those kinds of resources

23   that we wouldn't normally have.

24             In addition, we increased our material inventory

25   actually fairly significantly after the more significant storms

FLORIDA PUBLIC SERVICE COMMISSION

61

1   a couple of years ago.  And originally we believed we were

2   going to cycle that material up and then cycle down on the off

3   hurricane time and cycle it back up.  We thought we had a real

4   scientific way to do that.  Given a lot of the challenges with

5   getting material period, we've just left the higher inventories

6   in recognition of that.  However, material is always going to

7   be a vulnerability if you're in a storm situation.

8             We have -- our emergency response is tied directly

9   into what the City of Tallahassee does.  The City of

10   Tallahassee operates under an Incident Management Plan, which

11   includes the National Incident Management System, Instant

12   Command System, the same system the state operates under and

13   federal government operates under.  We utilize an area command

14   concept for the operations.  What that means is we have a

15   central Emergency Operation Center that the City operates, but

16   in turn we have separate command centers.  For example, our

17   Electric Control Center that is doing the electric restoration

18   is separate from that.  We have links back, we have staff in

19   the central area command.  We also have our -- the data

20   associated with what we're doing is there as well.  But we

21   manage the restoration itself through the Electric Control

22   Center but just keep a very close link.

23             One of the things that's kind of neat about that is

24   we've actually placed -- our Outage Management System is

25   located, also is viewed in the Emergency Operation Center.  So

FLORIDA PUBLIC SERVICE COMMISSION

62

1   the Incident Commander and the folks there can physically see

2   the screens for where the outages are because that can make a

3   difference with how they're responding to different things

4   associated with police and fire resources as well.

5             Like everybody else, we watch several days out when

6   storms are coming.  We have the equipment crew doing that

7   near-term preparation.  We do storm assignments based on what

8   the severity of the storm is going to be.  We have, also have

9   Integrated Outage Management and GIS system.  That also, as I

10   said, is in both our control center where we actually

11   physically use it and it's also displayed at the Emergency

12   Operations Center.  We have established restoration priorities

13   with respect to public safety in all those facilities as well.

14             But one of the neat things about that is we have a

15   very close integration with the Emergency Operation Center.  As

16   different issues come up that are brought to the attention of,

17   of local government, whether it's police, fire, we get that

18   pretty much instantaneously because we're also tied into what

19   we call Web EOC.  We have a Web-based emergency operations,

20   it's like a visual emergency operations network that's at our

21   different command centers.  So when there's trees down or

22   whatever, we get that information another way.

23             We pre-stage road clearing task forces.  This may be

24   a little unique in that we place some of our, actually two of

25   our folks not -- we don't tie up a trouble truck, for example,

FLORIDA PUBLIC SERVICE COMMISSION

63

1   a bucket truck, but we take a couple of people that have hot

2   glove sticks and, of course, radio communications to us that

3   are pre-staged with five different road clearing task forces in

4   this community.

5             There's been a determination that if you get a

6   catastrophic event coming through here, one of the key issues

7   is just going to be opening major roads for emergency vehicles.

8   So we have a team that consists of both fire, police, electric

9   and public works to clear those roads safely for, to get the

10   avenues to go to the hospitals and the various key parts of

11   the, parts of the community.  We also have assessment teams

12   that are made up.

13             And in order to optimize, for example, how we do

14   that, we use, you know, there will be one of the engineering

15   staff and maybe somebody from meter services or something like

16   that so you're not tying up all your technical staff at one

17   point.  We have continual communications between the EOC and

18   our control centers we talked about.

19             We have mutual aid agreements both with FMEA, as

20   Barry talked about, the American Public Power Association and

21   the Florida Electric Coordinating Group, which gives us a wide

22   reach with respect to where we can get resources if we do need

23   them.

24             Some of the other interesting features that we have,

25   we have a complete backup control center that runs in parallel

FLORIDA PUBLIC SERVICE COMMISSION

64

1   to our normal operation.  That's really a part of our meeting

2   the NERC mandatory reliability requirements, but also, of

3   course, gives us a very functional way -- if a catastrophic

4   event took out our main control center, we actually have a

5   separate facility that's up and running parallel.

6             We have different locations for backup call center

7   locations.  To the extent that a call center is, is rendered

8   useless, even including our control center, we have a whole

9   bunch of phones in a closet, designated jacks where you can

10   actually bring portions of call centers up in other remote

11   areas.

12             As I mentioned, the sheriff's helicopter access is a

13   valuable tool for us.  We recognize immediately during the

14   event it may be busy, but we've had pretty good luck in being

15   able to access it after an event to help us do a quick patrol

16   and assessment of transmission, which has been very helpful as

17   well.

18             95 percent of our staff have been trained in the four

19   different levels of the Instant Command System, which gives us

20   a lot of functionality with respect to both mutual aid support

21   as well as if we have people coming in that have that same kind

22   of training and how we can operate.  We talked about the outage

23   management displays at the City EOC.

24             And the logistic support we get through the EOC is

25   kind of interesting.  Since we're working through the ICS

FLORIDA PUBLIC SERVICE COMMISSION

65

1   system, the ICS has a command structure.  As a part of that, we

2   get logistic support from the City that we integrate with.  The

3   keys to that might be when people are making on, on-the-spot

4   decisions about, you know, what will work for certain parts of,

5   let's say, debris storage, issues like that, there's a bunch of

6   preidentified debris storage areas.  So we don't conflict with

7   where public works might be doing when we're doing our tree

8   trimming crews to do that as well, or possibly where you stage

9   mutual aid crews, all that type of thing, we've got a central

10   way to do that.  So we try to reduce as much as possible the

11   conflict we might have in trying to run our operations for the

12   electric utility restoration as well as the rest of the

13   community restoration activities.

14             Public information, I guess we talked about the Web

15   EOC and how we, how we use that.  That's a pretty, pretty

16   active system to be able to have that kind of data continually

17   for everybody across the system.  The public information, we

18   have the standard media, we have the Internet, which

19   interestingly enough, you know, your first reaction is during a

20   storm you don't have power.  How are you going to do that?  We

21   have a number of people who give a lot of positive impact

22   about, or positive feedback about having Internet capability to

23   look at things.  They call their friends who don't have power.

24   That same thing happens with WCOT, which is the City's

25   television channel.  We both use crawls as well as posted

FLORIDA PUBLIC SERVICE COMMISSION

66

1   information on it.  And we've actually recently gotten access

2   to the university paging system that was deployed as a result

3   of many of these campus catastrophic events that have happened,

4   and we have access to that system as well.  And that's, you

5   know, probably about a 60,000 student population that we can

6   reach if we need to that way.

7             We have radio communications capability with public

8   safety because we're on the same 800 megahertz system.  So we

9   can switch over to public safety channels if we need to and get

10   different call groups associated with that, and we also have a

11   fairly detailed continuity of operation plan that looks at if

12   certain parts of our facilities are rendered just unusable, you

13   know, where do we go next?  Where do you set up offices?  How

14   do you do it in order to manage the restoration?  And that's

15   it.

16             CHAIRMAN CARTER:  Kevin, as usual, very, very

17   thorough.  Very, very thorough.  Hang on a second.  Let me see.

18   Commissioners, Commissioner Argenziano, you're recognized.

19             COMMISSIONER ARGENZIANO:  Thank you.  And it sounds

20   like you guys are doing an awesome job.

21             MR. WAILES:  Thank you.

22             COMMISSIONER ARGENZIANO:  Just one question out of

23   curiosity on the hydro plant.  As far as, you know, heavy

24   waters coming in, do you get any assistance from the water

25   management districts or USGS, any monitoring stations?

FLORIDA PUBLIC SERVICE COMMISSION

67

1             MR. WAILES:  Yeah.  Actually, you know, it's

2   interesting.  Part of the monitoring we do use is USGS

3   monitoring stations.  When you get into a large event,

4   sometimes those gauges go out.  So there's, but there's a

5   number of them along the river system that monitor the

6   different rivers that give us those river levels that key into

7   the models.

8             COMMISSIONER ARGENZIANO:  Okay.

9             MR. WAILES:  And some of the models are theirs as

10   well.

11             COMMISSIONER ARGENZIANO:  That's not an easy job.

12   Thanks.

13             CHAIRMAN CARTER:  Commissioner Skop, you're

14   recognized -- Commissioner?  Thank you, Kevin.  Staff, do you

15   have any?  Thank you.  Once again, thorough.

16             MR. WAILES:  Thank you, Commissioners.

17             CHAIRMAN CARTER:  Next, Commissioners, we'll have

18   Ms. Rebecca Mattey, the Director for the City of Ocala Electric

19   Utility.  Good morning and welcome to Tallahassee.  Welcome to

20   the PSC.

21             MS. MATTEY:  Good morning.  Thank you.  I am Rebecca

22   Mattey.  I'm the Director of Ocala Electric Utility, and I'll

23   just step right into it.

24             I do have to say though to start off I arrived in

25   Florida in, in 2004 just before all the hurricanes hit, so I

FLORIDA PUBLIC SERVICE COMMISSION

68

1   had trial by fire.  But Ocala is centrally located.  It's

2   80 miles from the west coast.  We have 160 square miles of

3   service area and 800 miles of overhead lines.  We serve just

4   about 50,000 customers.  The majority of those are residential

5   at about 41,000.

6             We have implemented an eight-year cycle inspection of

7   our wood poles.  In 2007, our results were 7.1 percent of our

8   distribution poles required attention, and 80 were restored,

9   100 were replaced.  We are on schedule with those.  5.2 percent

10   of our transmission poles required attention.  23 will be

11   restored by our contractor and 12 need to be replaced.  The

12   design is done and construction will be underway soon.  We have

13   found that those inspections have provided us with a lot of

14   information.  We believe it's a good program and we're excited

15   to continue it.

16             Our hurricane readiness, as Tallahassee does, we do

17   stage personnel at the fire departments because we realized

18   after 2004 that it was very critical for the fire department to

19   get our help during that initial search and rescue.

20             We also place trouble crews in each quadrant during

21   our restoration process.  We found during, during those

22   hurricanes that those houses that had individual service line

23   problems tended to have to wait a long time because we were

24   very busy putting up our main circuit.  So we put a trouble

25   crew in each quadrant and it significantly reduced the time

FLORIDA PUBLIC SERVICE COMMISSION

69

1   that those individual problems had to wait.

2             We also were requested and provided training to

3   county employees who had to clear roads.  And they had concerns

4   about electric lines and whether they were energized, so we do

5   provide training every year for county employees.

6             We also train and equip personnel in our electric

7   engineering to provide assistance to our contractors and other

8   utilities that are in our, providing us with mutual aid.  We

9   found that our GIS maps are critical to this process.  We have

10   all of the hospitals, sewer lift stations, critical care

11   facilities on those GIS maps, and it provides engineering with

12   the ability to assist the restoration crews.

13             We train and equip our meter readers and our other

14   nontechnical personnel to be runners for our restoration crews.

15   They run supplies, tools, food so that, so that our technical

16   expertise can remain focused on the restoration.

17             We also work closely in conjunction with the Ocala

18   Fire Department for the National Incident Command System.  Most

19   of our employees that are, that are involved in the process are

20   qualified for that.

21             We coordinate with FMEA.  They are our mutual aid

22   coordinator.  We rely heavily on them.  And we also on a

23   regular basis report to them our outages.  On a daily basis,

24   sometimes hourly basis we talk with FMEA on what's going on

25   with our restoration process.

FLORIDA PUBLIC SERVICE COMMISSION

70

1             OUC, Orlando Utility Commission, is our balancing

2   authority.  Seminole and Progress Energy provide transmission

3   operation for our system.  And the Florida Municipal Power

4   Agency is a centralized collection agency for our monthly

5   outage and reliability information.

6             Our coordination efforts, we work closely with the

7   Marion County Emergency with their EOC.  We have two trained

8   employees, so we provide 24-hour coverage any time that the EOC

9   is open.  We coordinate with the local law enforcement.  We

10   work closely with the Ocala Police Department with outages at

11   traffic signals.  We can give them quick information about how

12   quickly we believe that the traffic signals will we restored

13   and so they don't have to waste critical time taking generators

14   out.

15             We also, I don't have it down, but we work closely

16   with the water and sewer department.  We did find that it's

17   important for them to know when we can get sewer lift stations

18   back up.  So we have all those sewer lift stations on our GIS

19   maps.

20             We work with the Ocala Tree Commission, I do sit on

21   the tree commission, and with the Marion County Planning Board.

22   We also work closely with hospitals and critical care

23   facilities to make sure that their needs are taken care of

24   during the restoration process.

25             Our vegetation management efforts, we comply with the

FLORIDA PUBLIC SERVICE COMMISSION

71

1   NERC standards.  We have an arborist on staff.  She works very

2   closely with the community and coordinating with other City

3   departments.  We, again, we're on a three-year trim cycle for

4   both our distribution and transmission, and we are on schedule

5   so far.

6             We do have policies that we, that help us to deal

7   with problem trees.  We do, we do remove trees for our

8   customers if they're a threat to our service lines.  And we

9   also budget money every year so that we can replace those trees

10   but replace the appropriate tree in the appropriate spot.

11             I worked very closely on the tree commission this

12   year and with the City Planning Department to change the

13   ordinance language that made it stricter about planting trees

14   around our utilities and our lines, and we, we were able to

15   come to an agreement that works for the City and also works for

16   the utility.

17             The City Council recently approved a new ordinance

18   that requires all new developments to be underground.  And we

19   also implemented the evaluation of new pole attachments for

20   wind loading.  Our engineering staff now does that.  We no

21   longer install wood poles for transmission.  All transmission

22   poles are mostly steel.  Occasionally because of aesthetics

23   we'll put in concrete, but mostly we prefer steel.

24             Post-storm recovery, you know, of course we go right

25   into our emergency restoration plan, and we put all of that all

FLORIDA PUBLIC SERVICE COMMISSION

72

1   into action, all the training that we have provided to our

2   employees prior to the storm.  And we always prepare for

3   equipment, and, and so we make sure that we have everything

4   that we need to continue.

5             Through FMEA we are participating in the storm

6   hardening research through the University of Florida.

7   Post-storm we also do forensic assessment damage with our

8   engineering staff.  We're constantly updating our emergency

9   plan, making notes so that the next time we can do it better.

10   And our engineering staff also identifies those field

11   facilities that need to be upgraded while they're out there

12   working the storm.

13             Our areas of concern, OU is served by a 230kV line

14   and right now it's a radial and we do have redundancy in our

15   system, but at some point in time as growth continues we will

16   need to loop that 230 line.

17             The availability of emergency restoration

18   contractors, I think everyone has mentioned that, and with

19   multiple storms it's hard to get contractors.  However, I have

20   to say being a member of FMEA and having the contacts through

21   the municipals, we, we have been able to, to count on our

22   sister cities for help.

23             Housing is also an issue I think in Ocala because

24   we're centrally located and many of the hotels are filled up

25   with evacuees, so housing for those restoration crews can

FLORIDA PUBLIC SERVICE COMMISSION

73

1   sometimes be a little difficult.  We do have a facility where

2   we can house about 100.  But for, for a critical storm or an

3   active season, housing may become an issue.  I don't have --

4   that's all I have.  If you have any questions.  Thank you.

5             CHAIRMAN CARTER:  Thank you, Becky.  You did a fine

6   job.  And, I mean, they picked the right person.  You said they

7   picked you just before the storm.  They made a good choice.

8             Commissioners, any questions?  Staff?  Thank you so

9   kindly.

10             MS. MATTEY:  Thank you.

11             CHAIRMAN CARTER:  Commissioners, I think where we are

12   now, we can -- I'd like to plod on a little more, if that's

13   okay with everyone.  So let's call up for Florida Electric

14   Cooperatives Association Michelle Hershel.

15             MS. HERSHEL:  Thank you, Mr. Chairman.  I'm usually

16   here by myself.  It's nice having people with me.

17             CHAIRMAN CARTER:  Brought reinforcements today, huh?

18             MS. HERSHEL:  I just have a short introduction and

19   then I'll introduce the co-ops that I have today.

20             The member cooperatives of our association are as

21   prepared as they can possibly be for future hurricanes that may

22   hit Florida and are committed to harden or upgrade our

23   facilities when necessary.  All of FECA's members have

24   submitted their annual reports on construction standards and

25   their efforts to mitigate damages caused by extreme weather

FLORIDA PUBLIC SERVICE COMMISSION

74

1   pursuant to Rule 25-6.0343.

2             Our members comply with the standards set forth in

3   the National Electrical Safety Code, as well as RUS

4   requirements, which include facility inspections which are on

5   par with the IOU's pole inspection cycles.  In addition, the

6   co-ops continue to review and upgrade their vegetation

7   management practices to avoid damage from trees and other

8   vegetation during a severe storm.  FECA is also a member of the

9   PURC Research Group, and all of our members will have access to

10   the underground model that is being developed to determine

11   costs and benefits associated with specific projects as well as

12   the wind data that is being collected.

13             And I'd like to introduce the two co-ops that we are

14   showcasing here today.  I hope you're not disappointed that we

15   didn't bring all 17 of our members.  I think the Florida Keys

16   is going to go first.  This is Scott Newberry and John Stuart

17   from the Florida Keys.  And then Peace River, Jerry Twiggs and

18   Miles Green.

19             CHAIRMAN CARTER:  Michelle, good to see you again.

20   We're glad to see your fine efforts before us here at the

21   Commission, as well over at the Florida Energy Commission and

22   other areas.  Good to see you again.

23             MR. NEWBERRY:  Well, good morning.  As Michelle said,

24   I'm Scott Newberry.  I'm the CEO of Florida Keys Electric

25   Co-op.  And it's a pleasure to be here today to talk to you

FLORIDA PUBLIC SERVICE COMMISSION

75

1   about our storm hardening efforts over the past few years.

2             I've been with the co-op nearly 19 years now and I

3   think this is the first time we've had the opportunity to

4   address the Commission, so I thought I'd start by giving you

5   just a little bit of an idea of who we are.  We were

6   established in 1940 as a member-owned rural electric co-op.  We

7   serve in the Upper and Middle Florida Keys from the Dade/Monroe

8   County line through and including Marathon.  We have currently

9   about 25,000 members, which represent about 31,000 accounts.

10   Our power supplier is Florida Power & Light.  Our main power

11   supply is from the mainland into the Keys.  Our system peak

12   capacity is roughly 160 megawatts.

13             We, we serve our members with 100 miles of 138kV

14   transmission lines.  That transmission line is insulated at

15   230kV, which gives a little bit more strength than a standard

16   138kV would have.  We have 647 miles of 24kV distribution line.

17   Again, that, those lines are overinsulated as well.  44 miles

18   of underground 24kV distribution.  Of the 100 miles of

19   transmission we have, roughly nine miles of that is actually

20   over water, which presents us a challenge getting out there by

21   boat essentially and barge to make any repairs we would have to

22   do.  We do have six 138 to 24kV substations, eight diesel

23   generators in Marathon that can supply a total of 22 megawatts

24   of peaking.  We don't use it for peaking nearly as much now as

25   for emergency power.  And we do have a 12 megawatt purchase

FLORIDA PUBLIC SERVICE COMMISSION

76

1   power agreement with Keys Energy Services out of Key West for

2   additional capacity if we need it.

3             Our storm hardening initiatives have, we've really

4   kind of broken this down into four pieces:  Design,

5   infrastructure, maintenance and then our restoration efforts.

6             To get there design-wise, we did adopt in 2006 the

7   extreme wind construction standard from the NESC and have been

8   working since then to get our facilities engineered to meet

9   that.  We have increased our wood distribution -- our pole

10   class sizes up one class per, per height, and we are working on

11   engineering specifically for those concrete poles,

12   self-supporting poles.  One of the problems we have is narrow

13   right-of-ways make it hard to properly guy some of our

14   structures.  So we're looking at actually having designed for

15   us and constructed for us self-supporting poles.

16             On the infrastructure side, we have always pretty

17   much kept up with a five-year inspection cycle on our wooden

18   distribution poles.  We have about 15,000 of those in our

19   system.  We're currently working to inspect and treat about

20   3,000 of those each year.  Last year and the year before we're

21   experiencing roughly an 8 percent failure rate on those poles.

22   We did replace over the last year 200 distribution primary and

23   secondary poles.  Beyond -- one thing I haven't heard of a lot

24   today that I think may be a little bit unique to us now is that

25   we look beyond just the strength of our distribution and

FLORIDA PUBLIC SERVICE COMMISSION

77

1   transmission facilities.  We've actually looked at the strength

2   of our headquarter's warehouse facilities as well.

3             A few years ago we did complete construction of a

4   fully storm hardened administrative and warehouse facility in

5   our Marathon district, and we're currently about halfway

6   through construction of about a $14 million fully storm

7   hardened administrative operations warehouse and fleet

8   maintenance headquarters facility in our Tavernier area.  So we

9   have expanded just beyond the poles and wires to the facilities

10   we need to work out of after a storm as well.

11             We also, after, after looking at our system -- our

12   attachments, we do not attach very much of our stuff to other

13   people's facilities.  Most of the attachments with Comcast,

14   BellSouth are on our poles.  We did an inspection last year of

15   their anchoring guy attachments to our poles to make sure that

16   they were sound.  We identified quite a few areas that needed

17   attention.  We provided a list to all of our attachees

18   essentially and they have worked to correct that as well.  It

19   seemed to us it doesn't make a lot of sense to try and build

20   all our stuff strong if their attachments aren't maintained as

21   well.

22             Just to give you a little bit of an idea of our

23   transmission system, we put this map in for you.  You can see

24   that we're essentially a radial system from Tavernier, which is

25   at Mile Marker 91, all the way south to Marathon.  But we are

FLORIDA PUBLIC SERVICE COMMISSION

78

1   looped in the Upper Keys.  Our original transmission line was

2   built in the late '70s.  That's the blue line there coming down

3   Card Sound Road.

4             About a year after Hurricane Andrew we did construct

5   a new 138kV line from the Florida City substation, FP&L's

6   substation there, down to Tavernier.  It's an express feed.

7             All of our transmission structures are either

8   concrete or steel.  The new line that you see there, the red

9   line, was actually built to standards that FP&L found served

10   best through Hurricane Andrew.  So we did take advantage of

11   their research there when we built this line.

12             Under preventative maintenance, vegetation

13   maintenance, we have always attempted a three-year trim cycle.

14   We trim approximately 215 miles of line each year.  All main

15   feeder work is completed prior to January or July 1st each

16   year.  An additional advantage that we have based on our

17   location is the fact that all of our main three-phase

18   distribution feeders are located on transmission structures, so

19   that provides a little bit of additional strength to our

20   distribution system as well.

21             Annual aerial patrols, every year we fly the entire

22   transmission system top to bottom doing a visual and infrared

23   inspection of all transmission structures that we have.  On a

24   side note, we actually inspect this every single day.  We have

25   one road.  The transmission line runs right down the road, so

FLORIDA PUBLIC SERVICE COMMISSION

79

1   we're out there all day looking at those.  But we go above and

2   beyond once a year with that, with that inspection.  Any

3   problem areas that are identified we do correct as soon as we

4   possibly can.

5             So that's kind of an overview of what we do prior to

6   a storm to be ready for one.  But in my experience with, I

7   don't know how many, ten, 12, 15 hurricanes over the last 19

8   years, every storm we have is different.  No one comes in the

9   same way.  No one affects our system the same way.  So one

10   thing that we do every single year is review our major storm

11   restoration plan.  We do have a full document, written

12   document.  Employee assignments are contained in that, and it

13   even goes so far as to include sample press releases and things

14   for member communication after a storm.

15             Once a storm does hit, the first thing we do is a

16   full system damage assessment.  Before we start work we set our

17   plan then on how best to attack the problem.  We always start

18   with transmission first.  If we should have problems with a

19   transmission system, we work our way from there at the

20   substations, figuring we need the main backbone on.  We then

21   work down the main feeders before we get out into the

22   neighborhoods throwing fuses in and things along those lines.

23             And very critical that I've found over the years is

24   this next item, the post-storm critique.  As I mentioned, every

25   storm is different, every one has different challenges to it.

FLORIDA PUBLIC SERVICE COMMISSION

80

1   So immediately after a storm once we've got everybody back in

2   service we all sit down and talk about what went right, what

3   went wrong, and try and adjust our plan right then and there

4   for the next one.

5             We're also concerned with ensuring the safety of the

6   public and FKEC staff.  One of the concerns that we have is,

7   you know, being in the Keys with one road in, one road out, we,

8   before we will allow our line crews to work, we need to be sure

9   that there is emergency personnel available to take care of

10   them should they become injured.  So we won't let the linemen

11   even start working until we have that there.

12             Adequate material, a lot of folks have talked about

13   that.  We do keep lots of stock on hand, I guess.  We do stock

14   up prior to hurricane season as well for transformer poles and

15   that sort of thing.  We actually have a truck stock, boxes for

16   every truck, a specific storm box.  If a storm hits, that's

17   loaded on and gone.  So we have all that in place before a

18   storm even gets there.

19             Coordination with Monroe County EOC, we are on

20   conference calls with them three, four, five times a day every

21   day prior to arrival.  We do our best to staff the EOCs with

22   them, if we can cut loose a person to stay there.  But we do

23   work closely with them before, during and after the storms.

24             Redundant communication systems, we did find, I

25   believe it was with Hurricane Andrew, that we couldn't call

FLORIDA PUBLIC SERVICE COMMISSION

81

1   out.  The Keys at that point in time were essentially

2   untouched, but a lot of folks thought that we were gone because

3   they couldn't hear from us.  So we have done what we can to

4   have multiple communication devices in place from truck radios

5   to cell phones to satellite telephones with Internet capability

6   in them so that we can, we can get word out and in and talk

7   back and forth between our areas as well.

8             We're working to complete our GIS/OMS systems for

9   storm damage evaluation.  We intend to have that pretty much in

10   place by July 1st.  We do send all of our data out of state for

11   CIS, GIS.  All that is backed up and sent to St. Louis,

12   Missouri, prior to a storm so that we can get back into

13   business as soon as possible.

14             When we're doing our pole change outs, the line

15   contractors are on-site during hurricane season.  We, we look

16   at all the poles prior to and start restoring and changing

17   those poles out during hurricane season primarily to have on

18   hand two or three or four contract crews that can be there to

19   help us in the event we do get hit with a storm.  Also,

20   Statewide is always available to us and our mutual aid

21   assistance request there.

22             Finally, to finish up, we didn't have it in our

23   presentation, but a question has been asked, concerns and

24   vulnerabilities.  I've kind of hinted at that already.  We are

25   geographically isolated.  We're hanging off the end of the

FLORIDA PUBLIC SERVICE COMMISSION

82

1   world down there, and that primarily is our main concern.  We

2   can plan all we want to, but we are served with one highway and

3   that highway contains multiple bridges.  One bridge going out

4   presents a huge challenge for us, so that is probably our

5   primary concern.

6             Second to that is we are often affected with

7   mandatory evacuations.  We do not require our employees to stay

8   once the county evacuation order has been issued.  For us to

9   start restoration efforts we need those employees back.  So

10   we're always requesting to leave when you're supposed to leave

11   but return as soon as you possibly can.

12             We are a low-lying area.  Storm surge is always a

13   problem.  We've kind of addressed some of that too with our

14   headquarters and warehouse facilities.  The warehouse portions

15   of those facilities have been designed so our bucket trucks can

16   all be stored within the warehouse, within the storm hardened

17   facilities, and the slabs at those warehouses are elevated

18   12 feet.  We figure it does no good to have all kind of

19   material on hand if you don't have any equipment to get it out

20   into the field, so we've taken those steps as well.

21             And I believe that concludes what I had.  I'd be

22   happy to take any questions.

23             CHAIRMAN CARTER:  Thank you, Scott.  We're always

24   pleased to see our friends from the Conch Republic come up

25   here.

FLORIDA PUBLIC SERVICE COMMISSION

83

1             MR. NEWBERRY:  Well, we appreciate it.  Thank you.

2             CHAIRMAN CARTER:  Welcome to Tallahassee.  This

3   probably -- since everything is kind of tied into the road,

4   were you guys able to have the road four-laned all the way

5   through yet?

6             MR. NEWBERRY:  No, and never will.

7             CHAIRMAN CARTER:  Never will?

8             MR. NEWBERRY:  That will never happen, I don't think.

9   No.  They are right now finishing up reconstruction of Jewfish

10   Creek Bridge, the drawbridge into the Keys.  A 65-foot concrete

11   bridge is going to be opening next month, I believe, which

12   should help getting folks back into the Keys after a storm.

13   But it's primarily two-laned from Key Largo, the south end of

14   Key Largo down to Key West, primarily two-lane there.

15             CHAIRMAN CARTER:  Wow.  Sorry for thinking aloud.

16             Commissioners, any further questions?  Staff?

17             Thank you very much, Scott.

18             MR. NEWBERRY:  Thank you.

19             CHAIRMAN CARTER:  Next, Commissioners, we'll have

20   up -- will be from the Peace River Cooperative, we have

21   Mr. Jerry Twiggs; right?

22             MR. TWIGGS:  Yes.  And I also have Mr. Miles Green

23   here.  We appreciate the Commissioners giving us the

24   opportunity today for Peace River to come up and share with you

25   our information and our experience.  You see from our first

FLORIDA PUBLIC SERVICE COMMISSION

84

1   slide here we have experience in planning, so with that I will

2   begin.

3             We'll talk for a little bit about, for your

4   information, Peace River's service territory.  We currently are

5   in ten counties.  Obviously, Manatee County is primarily our

6   growth area.  Of course, we've had a little down, housing

7   downturn and that has slowed down.  But we serve the primary of

8   Lake Wood Ranch and other areas that -- also we go into the

9   Hardee, DeSoto, Osceola, Indian River, and we cover a wide band

10   of area.  And if you started from our west end in the morning

11   and went to our east end, it's about a three and a half to four

12   hour drive from one end of our service area to the other.

13             With that, I mentioned earlier hurricane experience,

14   and the reason why I asked that, my counterpart at Peace River,

15   Miles Green, has been with Peace River Electric Cooperative for

16   over 44 years.  He has a lot of hurricane experience, has been

17   in the trenches.  And as you'll see from the next slide, we

18   have had in the year 2004 multiple hurricanes, which some of

19   the prior presenters have been concerned about multiple

20   hurricanes.  Well, Peace River has experienced that.  And as

21   with anything, it's always good to have a lot of experience

22   with you on hurricanes.  And with that, I'll turn it over to

23   you, Miles.

24             MR. GREEN:  Good morning, ladies and gentlemen.  One

25   thing you'll notice that I guess 2004 for us was pretty much an

FLORIDA PUBLIC SERVICE COMMISSION

85

1   accelerated learning experience.  We started out with Charley.

2   We had met with the EOC about three days before Charley came

3   through, and actually during that time period we were having to

4   send people out to get ready for the eminent strike of Charley.

5   I didn't want to have any more meetings with the EOC after that

6   because the exact replica that we did in that meeting is what

7   happened on August 13th.  It came right up through the center

8   of our territory.  We experienced Charley, Frances, Jeanne and

9   Wilma in just over a year time, which I couldn't hardly

10   remember Wilma because Charley and Frances and Jeanne was,

11   stayed pretty heavy in my memory.

12             In Charley we had $9 million worth of damage.

13   Initially we had out -- you saw we had 32,000.  We had out

14   23,645 of our customers.  We had just a little over 1,500 poles

15   down.  And the average poles were 20 years old and 35-foot

16   high.  It came right through the center of our territory, if

17   you'll notice by that diagram.  Like the eye wasn't that far

18   from our headquarters, probably within probably less than a

19   mile.

20             When we replace the poles, we use 40-foot poles to

21   strengthen them more.  We replaced over 600,000 feet of

22   conductor and we were able to do the majority of that in

23   14 days.  That was -- that surprised me even at that.  But that

24   was -- thank goodness for Statewide because they helped us with

25   a lot of help.

FLORIDA PUBLIC SERVICE COMMISSION

86

1             Frances -- Charley, we were just trying to calm down

2   a little bit from it and looked over our shoulders and Frances

3   was on the way.  So it was about a million dollars worth of

4   damage.  We had 19,184 people out.  We had less than 50 poles

5   down.  And I heard mention that you had to look at each storm

6   to know the exact damage that it did.  And it was surprising to

7   me, that's one thing that really surprised me in this.  Charley

8   was devastating, it just put everything on the ground, but

9   Frances tore down trees.  We had more back taps and not main

10   lines that we had trouble with in that.  And you see there the

11   conductor was 15,000 feet, and the majority of it was restored

12   in two days.

13             That wasn't enough.  Jeanne came in the Atlantic out

14   there.  And we had sent help to some of the co-ops up in West

15   Florida for Ivan.  We had to turn around and ask them to come

16   back.  So the day we were supposed to swap crews, we just

17   pulled them all out and brought them back because we were

18   having to prepare for Jeanne.  We had 10,415 out, 400 poles

19   down.  And you see the average; the sizes are about the same.

20   The conductor, we replaced over 200,000 feet, and we were able

21   to do that in about six days.

22             If you look at the next diagram, you'll see that

23   that's the tracks of all three hurricanes.  And they weren't

24   over 50 miles apart with the eye when they came through our

25   territory.  So that was in a 45-day period.

FLORIDA PUBLIC SERVICE COMMISSION

87

1             Wilma I almost forgot after 2004, but Wilma did, we

2   got a bunch of it.  Some of our neighbors to the south got a

3   lot more.  But Wilma was basically a, just a rain event for us.

4   And we had 4,000 people out, and in two days we had the

5   majority of that back on.

6             MR. TWIGGS:  We have quite a few employees at Peace

7   River that have 40-plus years of experience.  With that and

8   with their hurricane experience it's really given us a great

9   opportunity to develop a hurricane plan.  And with that, we

10   have -- one of the requirements we have from RUS is that we

11   have an emergency response plan.  And one of the sections in

12   that is a hurricane plan, and I will outline that to you, is we

13   repair with it.  And I think we're meeting with all ten of the

14   EOCs in our area on May the 21st at 9:00 a.m.  So that's been a

15   very productive meeting that we've had annually.  We share with

16   them our maps, you know, where our poles, where our wires are

17   located and that.  So that helps us a tremendous part with them

18   in the exchange of information and it takes place there.

19             In the preparation, it takes a lot of parts.  You've

20   heard a lot of this today about GIS information, where our

21   poles and wires are, where the OMS is, our outage management

22   system, which handles during hurricanes a lot of calls in a lot

23   of areas, and it helps us to quantify that information.  Also

24   the IVR is able to handle a lot of calls.  That ties into the

25   OMS.  And also the Customer Information System.

FLORIDA PUBLIC SERVICE COMMISSION

88

1             So in addition to that, prior to hurricane season we

2   verify the data, that it's correct, the placement and sizing of

3   our stations in light of what Miles has just shared with you.

4   Obviously we integrate into our engineering design, which is my

5   primary function at Peace River, anticipation of hurricanes,

6   whether it's pole, substation locations and other things.

7   Particularly we have to use a lot of back feed capability and

8   there are some situations that come up -- we try to pick up as

9   many customers as we can from some unusual ways that take place

10   that test your system during hurricane season.  Also, as you've

11   heard today, all the utilities in Florida are looking at

12   improved materials to withstand the higher winds that we

13   experience with hurricanes.

14             We have our hurricane maps.  You know, this time of

15   year you can see around the electric cooperative everybody is

16   talking about hurricane season.  We're starting to implement

17   our plan, we're collecting the information.  We have annually a

18   meeting of all the key employees at the cooperative.  We sit

19   down and spend a day checking have we fully prepared ourselves

20   in accordance with the plan and try to anticipate as many

21   things as we can see forward in the future.  And we always,

22   like all of us, read in the paper the prognosticators or the

23   predictors of what they think this hurricane season is, and I

24   hope they're again wrong this year.  Anyway, again, as I said

25   earlier, we have an OMS and IVR and other things.

FLORIDA PUBLIC SERVICE COMMISSION

89

1             Just it is -- the scope of our plan is to as best we

2   can orderly prepare for a hurricane.  And as is mentioned

3   earlier about the others, we want to do this very safely.

4   Peace River has been very fortunate in all the hurricanes we

5   shared with you earlier.  I think we had, what, one person that

6   had poison ivy.  So we have been very fortunate at Peace River

7   that people have been safe and the only thing we've experienced

8   is poison ivy.

9             Phase 1, we break our hurricane plan into phases.

10   Phase 1 is, well, like all of us, we have access to

11   information.  We see where the weather people are projecting

12   where the proposed route is.  You know, we experienced Charley

13   or Miles experienced Charley.  I know they had predicted

14   earlier that it was going to go into the Tampa Bay area.  It

15   took a right turn and went right through Wauchula and part of

16   our service area.  So it's -- they have a very good planning

17   tool, but sometimes hurricanes take unpredictable routes.

18             We do as other utilities do, we look at our fuel, our

19   supplies, our vendors, our hotels, our restaurants.  We work

20   very good with our brethren investor-owneds that are in our

21   area and some of our transmission providers, Progress Energy

22   and FP&L.  We have communication links with them and they have

23   communication links with us and our control center.  So we

24   share information in our preparation of that.

25             Obviously we work with Michelle and Statewide.  And

FLORIDA PUBLIC SERVICE COMMISSION

90

1   that's one of the very good things about the cooperative

2   program, it's not just in the State of Florida but nationwide.

3   We help our brethren out in other states and our brethren in

4   other states help us out.  And I think Miles will share with

5   you we had, what, 47 different cooperatives from other states

6   when we had Charley.  So that speaks very well.

7             Again, we monitor and assess the storm's progress and

8   projected path.  And I mentioned about Statewide, and we do our

9   damage assessment teams that's been mentioned earlier.

10             Phase III is mobilization of our staging areas.

11   That's something we work very well particularly with Manatee

12   County.  They have designated, the EOC in Manatee County has

13   designated some staging areas.  We work with them, we work with

14   FP&L and come up with something to provide benefit to all of

15   us.

16             Of course, you have to clean up afterwards.  You

17   know, we have contractors, outside workers, minor repairs.  And

18   this is a picture, right, of Charley, Miles?  You can see in

19   the -- this is in the Wal-Mart parking lot in Wauchula right

20   across -- so the parking lot was full of pole trucks, bucket

21   trucks and linemen.

22             Fieldwork, daylight hours, communications will

23   distribute all information to the media.  Obviously

24   communication is critical in a hurricane.  We lost a lot of our

25   landlines, we lost the cell phones.  And satellite phones

FLORIDA PUBLIC SERVICE COMMISSION

91

1   really were the last resort, and they were busy at times.  But

2   communication is critical with this.  Again, we communicate

3   with our emergency management operations in our counties.  We

4   give them updates, we update with our investor-owneds.  And

5   this is an example of one of our updates that we provide to our

6   EOCs.

7             And as one -- here's our website to update the media

8   and also to update our customers on the best information we

9   have available at that time as far as what's taking place as

10   far as restoration impact to our system.

11             MR. GREEN:  These are -- we track our reliability

12   numbers.  And as you can see, they were fairly high in 2003,

13   and in 2004 they went off the scale.  But the one thing that we

14   are happy about, because of the increased right-of-way and the

15   increased pole inspections these numbers are coming down.  So

16   that's both the SAIFI, SAIDI and the CAIDI numbers.

17             We are trying to harden the system.  And you'll see

18   in this particular graph that as we cut more right-of-way, that

19   directly relates to the number of outages and the time of the

20   outages.  So we're aware of that and we're trying our best to

21   do it.

22             Since 2004 we had a great idea, we thought.  We were

23   going to go out and do the chemical growth retardant after all

24   of the right-of-way we trimmed with the storms and it just

25   didn't seem to pan out as well as we thought it was.  So what

FLORIDA PUBLIC SERVICE COMMISSION

92

1   we basically started doing, we have focused totally, not

2   totally but mostly on mechanical trimming and mowing.

3             We're planning on using concrete poles for all major

4   feeders, whether it be triple circuits, double circuits,

5   because we're building quite a few of those now and in the

6   future in Manatee County.  We've increased our standard pole to

7   a 40 Class 4, which is a stronger, a stronger pole.

8             The fiberglass crossarms, I was a little reluctant to

9   that to start off with because you know how bad the UV is on

10   that, the sun is.  But we found out that we got some pretty

11   good benefits out of it.  Not only were we able to have the

12   basic insulation level brought up on our lines, but also we

13   were able to have a raptor line built that the birds were not

14   near as apt to get killed on.  And then, of course, when the

15   storms come, we found out that the fiberglass was tougher.

16   Some of the wood crossarms just didn't stand up as well as

17   those fiberglass arms did.  So we're kind of happy with that.

18             We have started a -- we have a total spec on it from

19   engineering that we wrap every pole that's put back in an area

20   where woodpeckers are with small square mesh wire.  Because if

21   they ever get a nest in one, they just, it's just forever.  And

22   then, of course, the pole rots and the wind blows it down.

23             We've accelerated our pole inspection since that

24   time.  We've changed out a number of poles.  And we're trying

25   our best to catch all the dead trees that are out of the

FLORIDA PUBLIC SERVICE COMMISSION

93

1   right-of-way.  If they're dead and there's a danger of it

2   falling on the line, we'll even -- we won't put back a

3   full-grown tree but we will provide a tree from a nursery for

4   the people as long as they'll put it somewhere besides under

5   the line.

6             So this is a picture -- well, okay.  This is a

7   picture of some of the equipment that we're using to trim

8   right-of-way.  I was totally amazed at what some of these

9   operators can do with this type of machinery.  They can walk up

10   to a two-foot oak tree and basically tell where it's going to

11   fall just as well as you can with a chainsaw.

12             Which if you'll look at the next picture, we're

13   working with, we're working with both the state, Manatee County

14   and the property owners.  And this is a picture of the

15   right-of-way that we've just successfully done over Highway

16   70 just before you get into Bradenton and that's what's left of

17   it after that machinery goes through there.  And the state is

18   real happy with that, so.  They weren't real sure to start off

19   with whether they were or not and then they decided that was

20   the best thing.  No stumps left, nothing.  It's just shredded.

21             The next picture is our service area.  And we're

22   trying our best to get an eight to ten years inspection, and

23   right now it looks like it's about to be eight years for

24   reinspection with 12.5 percent done each year.  Any questions?

25             CHAIRMAN CARTER:  Commissioners, any questions?

FLORIDA PUBLIC SERVICE COMMISSION

94

1   Staff?

2             Thank you very kindly.  Thank you.

3             Commissioners, if you feel ambitious, we can plod on.

4             Okay.  Let's hear from AT&T.  Is it plod on or trod

5   on?

6             COMMISSIONER EDGAR:  Mr. Chairman, if I could, just a

7   brief comment since we're kind of switching gears and going

8   into a different subject area.

9             CHAIRMAN CARTER:  Okay.  You're recognized.

10             COMMISSIONER EDGAR:  Thank you very much.

11             I'd just like to, of course, say thank you to all of

12   our presenters, but in particular to those from the

13   municipalities and from the co-ops.  I really appreciate their

14   participation in this initiative.

15             CHAIRMAN CARTER:  Thank you so kindly.  Thank you so

16   kindly, Commissioner.  And all of us here sincerely appreciate

17   our colleagues from the co-ops and the munis, particularly our

18   friends that came all the way up from the Conch Republic.  That

19   was very interesting.  A lot of good ideas, a lot of great

20   ideas, and we're really pleased to have that participation.

21             Okay.  You are recognized, sir.  Good morning, or I

22   guess it's afternoon now.  Good afternoon.

23             MR. SMITH:  Yes, sir.  Thank you.

24             We appreciate the opportunity to come here again.  My

25   name is Kirk Smith.  I'm a Manager on the southeast, AT&T

FLORIDA PUBLIC SERVICE COMMISSION

95

1   Southeast Regional Construction and Engineering staff.  I have

2   with us today as well Ms. Janice Doherty, and she's from the

3   AT&T Global Network Operation Center.

4             We understand the importance of storm preparation.

5   We hope that the history of our performance bears that out.  We

6   know that it's not a last-minute endeavor at all.  It's

7   something that we practice every day, not only for hurricane

8   preparation or hurricane events but other events as well.

9             Our Florida team's long-standing dedication to

10   comprehensive storm preparation coupled with the increased

11   resource available to AT&T post-merger puts us in a much better

12   position to respond to these type of events.  Last year we

13   talked very briefly about some of the resource that we saw was

14   available as a benefit of the merger.  We'll go into more

15   detail with that today.

16             We'll focus our presentation today on four different

17   areas:  Our pole inspection program, pole replacements, our

18   coordination with other utilities on storm hardening

19   activities; our increased generator inventory; an overview of

20   AT&T Florida's preparation of restoration processes; and what

21   we see now as a different, possibly new to everybody hierarchy

22   of support within the new AT&T, which includes our Global

23   Network Operations Center.

24             In our Florida inventory we have 461,789 poles.  We

25   are inspecting these poles on an eight-year cycle.  For joint

FLORIDA PUBLIC SERVICE COMMISSION

96

1   use poles we have prioritized the areas where we're doing these

2   inspections in concert with our major power company partners.

3   We have looked at as a first priority of inspection the coastal

4   environments and, again, in connection with our power company

5   partners those areas that they would consider and take us and

6   guide us to as critical infrastructure.

7             At the workshop last year we had focused our areas

8   primarily in the South Florida area.  Through the course of

9   this past year we have expanded our pole inspection efforts and

10   now have an active presence on pole inspections in each of the

11   coastal environments we have up to and including the Florida

12   Panhandle.

13             We have inspected greater than 86,000 poles through

14   year end 2007, have inspected 19,000 poles already in 2008, and

15   are on track to inspect a minimum of an additional 38,000 poles

16   in 2008.  Through the course of the past several years we have

17   replaced greater than 3,900 poles as part of the pole

18   inspection program and with the storm hardening activities

19   jointly with our power company partners.  We are on track with

20   our eight-year program; actually ahead of schedule somewhat and

21   fully intend that we will make the commitment of inspecting our

22   entire pole inventory in this eight-year cycle.

23             We have added a significant number of portable

24   generators to our generator pool arsenal.  These support our

25   digital loop carrier sites.  From lessons learned in our

FLORIDA PUBLIC SERVICE COMMISSION

97

1   analysis of the 2004 season, we have also established what we

2   call a seasonal generator pool in Hialeah, Florida.  And we now

3   have greater than 700 critical digital loop carrier sites with

4   permanent natural gas generators supporting these that will be

5   completely independent of battery backup or commercial power.

6             The following are pictures of the additional

7   generators that we have added to our fleet.  Traditionally

8   we've used 10 kilowatt portable diesel generators for our

9   digital loop carrier sites.  What we'll be adding going forward

10   are larger generators that support some of the more complex

11   electronics that we now use.  These are 25 kilowatt generators

12   and, again, these will be the standard for our additions going

13   forward.

14             The next slide gives you a representation of our

15   regional generator pools across the nine states.  The red

16   numbers indicate where we have added the larger generators

17   through the past year since the last workshop we were here with

18   everybody last year.  These regional pools we draw on to

19   support the State of Florida in the event of a hurricane.  We

20   will actually load generators on a proactive basis as far away

21   as Nashville, Jackson, Mississippi, or Columbus, South

22   Carolina.  The generators are loaded on 18-wheelers.  They're

23   brought down to staging areas and prepositioned out of harm's

24   way but be able to respond very, very quickly after landfall.

25             The seasonal generator pool actually draws primarily

FLORIDA PUBLIC SERVICE COMMISSION

98

1   from the Atlanta pool and the Nashville pool where proactively

2   we'll load the generators up sometime during the month of May

3   and bring them down to a staging area in Hialeah, Florida.  As

4   I mentioned, a lesson we learned from 2004 is that major

5   thoroughfares can quite often prevent you from getting north,

6   south, east or west.  And we had generators that we had

7   pre-staged close to the South Florida area in 2004 and found

8   that we could not move the generators.  So what we're doing,

9   we're moving those closer to South Florida where in essence

10   going forward we'll have two generator pools for the State of

11   Florida and hopefully we'll cut our response time tremendously.

12             These are pictures of some of the permanent

13   generators that we've added to support our digital loop carrier

14   sites that are powered by natural gas.  The bottom picture

15   shows you a terminal wrap for our remote digital loop carrier

16   sites.  We dispatch technicians just prior to the storm, put

17   these wraps on to prevent from water intrusion and wind and

18   driving rain and sand.

19             All of these things that we're looking at are of

20   absolutely no use whatsoever if we don't have our employee body

21   to put their hands on the tools and the equipment.  Our

22   greatest asset is, in fact, our people.  We work very, very

23   diligently to prepare and support our employees so they can

24   concentrate on service continuity.  We have annual awareness

25   meetings where we go through each one of our business units,

FLORIDA PUBLIC SERVICE COMMISSION

99

1   look at personal storm preparation activities for the

2   employees, what the needs of our business are.  We have numbers

3   that they can call in to give us an indication of what their

4   status is from a personal standpoint, where they can monitor

5   storm event activity.  And, again, like several of the folks

6   had mentioned in prior conversations or presentations,

7   communication is extremely key.

8             We've gone so far in many cases as to provide

9   localized care for our employees as the, as the events dictate.

10   You've probably seen or possibly remember a presentation last

11   year where we have available our tent cities, provide clothing,

12   provide food and up to and including counseling, if necessary.

13             Each business unit within AT&T has an emergency plan

14   that supports our corporate directives, which obviously are

15   focused on service continuity.  As I mentioned earlier, the

16   meetings are held annually.  We go through periodic exercises

17   internally to test our emergency plans and are very active in

18   participating with county EOC and IOU and other industry

19   exercises.

20             We are prepared to mobilize restoration teams within

21   hours of any emergency that we may have.  Our supply chain

22   management is partnered with suppliers to ensure that we have

23   adequate supplies and equipment available for restoration

24   activities.  Lessons learned again:  Cable, poles, gasoline,

25   diesel fuel, water and sandbags.  We've got those on retainer

FLORIDA PUBLIC SERVICE COMMISSION

100

1   now.

2             We have staging areas that are identified to stage

3   the supplies and equipment, again, responsive to whatever

4   landfall the storm may be making.  And we have sweep teams that

5   are dispatched as soon as possible after landfall to identify

6   what the, what the immediate restoration needs are.

7             We, too, have partnered with local businesses to

8   house and feed out-of-town crews and have retainer contracts in

9   place for both unleaded gasoline and diesel.

10             We are prepared to address emergency operations that

11   are what I would term scalable.  What we're going to try to

12   educate you on here is post-merger, kind of the hierarchy of

13   support that AT&T would have.  We have what's termed our local

14   response teams, and there's three of those local response teams

15   within the State of Florida in the north, central and south

16   parts of the state.  These are ad hoc teams that are pulled

17   together as events are identified that have been identified by

18   name, skill sets and ready to respond to whatever the need is.

19   As the event is diagnosed as large, catastrophic, whatever the

20   case may be, again, it's scalable that we can roll up and

21   activate our regional local response centers.  We have the

22   capability of activating a regional local response center both

23   within the State of Florida, and in many case when we have

24   multiple state events such as we had in 2004, 2005, we can

25   activate a second level of local response center in Atlanta,

FLORIDA PUBLIC SERVICE COMMISSION

101

1   Georgia.  And after that we have our Global Network Operation

2   Centers.

3             Each one of our LRTs or LRCs are multidimensional and

4   represented by every department within our operations.  It goes

5   from consumer to small business to large business, residence,

6   construction, engineering, installation, maintenance, special

7   services.  You name it, we have a representative that can

8   handle their particular part of the catastrophe.

9             Within the LRC some of the things that we've

10   developed over the last several years, and several of the other

11   folks here have mentioned GIS type capabilities, we've done the

12   same.  We've got maps now where we can graphically display

13   central offices, digital loop carrier sites, forecast storm

14   surge and give us an idea of possibly what to expect as

15   forecasts are refined.

16             We have our network reliability centers in both

17   Charlotte and Nashville that continually monitor the network.

18   They're looking at not only digital loop carrier sites, they're

19   looking at circuits from the DS-0 to DS-3 and SONET levels.

20             As you see here as well, we have several different

21   types of strike teams:  Our safety team, generator team, cell

22   strike team, E911 and damage prevention teams that are

23   activated, again, on an ad hoc basis disciplined specific to

24   handle problems that we've identified from previous storm,

25   previous storm events.

FLORIDA PUBLIC SERVICE COMMISSION

102

1             And should the event be large enough that the LRT or

2   LRC hierarchy needs to call in additional help, we now have the

3   Global Network Operations Center to call on.  And I'll hand it

4   off to Ms. Doherty to explain that.

5             MS. DOHERTY:  As mentioned, I'm Janice Doherty.  I'm

6   part of the Global Network Operations Center.  We call it the

7   GNOC.  The GNOC can provide additional resources to the local

8   response center, if necessary.

9             The Global Network Operations Center monitors AT&T's

10   network on a 24-by-7 basis and will take any corrective action

11   necessary if an anomaly is found in the network.  In the event

12   of a hurricane, the GNOC may activate AT&T's Network Disaster

13   Recovery Team and then would monitor its response.  The Network

14   Disaster Recovery Team is a group of employees put together to

15   form a team that has had special training to recover AT&T's

16   network.  Some of the team members have been trained to handle

17   hazardous materials, if that is necessary.

18             The network disaster recovery infrastructure also

19   with the -- as a result of the merger we now have access to

20   additional resources such as the large generators and the large

21   air-conditioning that can be used to support one of our central

22   offices should the need arise if one of them is destroyed or

23   damaged.

24             Also, the network disaster recovery will provide

25   emergency communication.  We've also got access to the

FLORIDA PUBLIC SERVICE COMMISSION

103

1   emergency communication vehicles called ECVs that will provide

2   broadband voice and data communication from the disaster site.

3             Also we've got two types of mobile towers that can

4   provide cell service.  One of them is the COW, which is the

5   cells on wheels, and the other is the COLT, the cells on light

6   trucks.  The disaster recovery team uses the satellite COLT to

7   provide connectivity to the AT&T network should that be

8   impacted.  So as you see, AT&T Florida is prepared for storms

9   this year.

10             CHAIRMAN CARTER:  Thank you.  I just -- on the, the

11   picture on number 21 you just left from, is that a COW or a

12   COLT?

13             MS. DOHERTY:  I didn't hear you.  I'm sorry.

14             CHAIRMAN CARTER:  Which one is that on your last

15   slide, just before you say "AT&T is prepared"?

16             MS. DOHERTY:  It's the COLT.

17             CHAIRMAN CARTER:  Oh, it's the COLT?

18             MS. DOHERTY:  Uh-huh.  Yes, sir.

19             CHAIRMAN CARTER:  Thank you.

20             Commissioners, any questions?  Staff?

21             MR. GARL:  Thank you, Mr. Chairman.  Just one

22   question.  You were talking about the pole inspections and the

23   joint use poles, doing joint inspections with the power

24   company.  How many joint use poles do you have on your system

25   and how, how are you doing as far as getting those inspected?

FLORIDA PUBLIC SERVICE COMMISSION

104

1             MR. SMITH:  I'll give you our approximate numbers.  I

2   don't have those with me.  We have 461,000 plus poles that we

3   own.  Attached as a joint user, be it a power company and/or a

4   cable TV or a CLEC, we have attached to -- approximately

5   360,000 of our 461,000 poles have another attachment.

6             We are, we are attached to approximately

7   700,000/800,000 poles as I recall where we are attached to

8   somebody else's pole.

9             MR. GARL:  Do you have any information on how the

10   progress is going on doing those joint inspections with the

11   pole owners or the other pole users?

12             MR. SMITH:  Each of the companies that we have

13   partnered with at this time -- and I would tell you I'm

14   obviously not speaking for them.  I know that we're on track

15   with our eight-year cycle.  I would tell you anecdotally

16   information, our anecdotal information should say they are as

17   well.  I don't, I don't see or know of anybody that indicates

18   that they're not anything but right on target.

19             MR. GARL:  Thank you, Mr. Smith.

20             CHAIRMAN CARTER:  Thank you very kindly.

21             Next we'll have Verizon.  Mr. Lewis.

22             MS. CLARK:  Good afternoon, Commissioners.

23             CHAIRMAN CARTER:  You're not Mr. Lewis.

24             MS. CLARK:  No.  I'm Demetria Clark with Verizon, and

25   I just wanted to introduce Mr. Lewis.  Mr. Lonnie Lewis is

FLORIDA PUBLIC SERVICE COMMISSION

105

1   Coordinator for our Emergency Operations Center.  And we also

2   have Chris Krier, Division Resource Center Supervisor, and also

3   Mr. Frank App, who is with the regulatory group.

4             CHAIRMAN CARTER:  Good to see you, Demetria.  Thank

5   you.

6             MR. LEWIS:  Good afternoon, Commissioners and staff.

7             I'd like to first just start off by saying Verizon --

8   well, former GTE which merges, now Verizon, we've been for

9   quite some time involved in emergency preparedness, especially

10   in 1992, I think, when Andrew came in down to Miami.  Right

11   after that our Director of Emergency Management went down

12   there, met with the county EOC, tried to find out what went

13   right, what went wrong, what didn't work, what did, and those

14   things came back.  And as a result of that, you're going to see

15   in the information I'm going to provide you some of the things

16   that we learned in '92 that we brought forward that we've been

17   using for some time now since then, as well as some other

18   things that we have implemented in the last year, I think, is

19   some of the information that you also wanted to know.

20             One of the things that we really believe in is you've

21   got to have a plan.  If you've got a plan, you know what you're

22   going to do, you know where your people are supposed to be,

23   you're going to be successful.  One of the things that we do is

24   each year, and we'll talk about this a little bit further in

25   the thing, we actually have to update our emergency plan each

FLORIDA PUBLIC SERVICE COMMISSION

106

1   year.  It has to be certified by our headquarters in New York.

2   Our EOC has to be -- we have actually a hot EOC that's up and

3   running year-round.  And the responsibility that it has is to

4   coordinate any emergency event that we may have, whether it be

5   a storm, terrorist event, whatever it might be, that EOC is

6   there to make sure that whatever we need to do, move manpower,

7   move people, relocate, whatever, happens.  It's also part of in

8   case we run into any work stoppages or, for example, a pandemic

9   flu, we've been preparing for that.  So that's one of the other

10   programs that we've been working on.  Again, the EOC is

11   involved in all of that even though it's headquarters driven.

12             And today what you see is we have a corporate EOC in

13   New York.  We are what's -- in the corporate environment we're

14   considered the Region Control Center, RCC.  But for you I added

15   on the EOC so you would understand it's the same thing as

16   Emergency Operation Center, but in Verizon it's called RCC.  So

17   we are the -- and we work this way with all the seven counties

18   that we're in as well.  We're part of the EOC.  We are the EOC

19   for Verizon and we work with the EOC for the different

20   counties.  And we are responsible, the EOC is, to make the

21   policy that we send people home, what time does the wind get

22   here at 40 miles an hour, do we go into our different phases

23   that we have for emergency preparedness, et cetera?

24             The next group is the Division Control Center.  Now

25   the Division Control Center is where really the rubber meets

FLORIDA PUBLIC SERVICE COMMISSION

107

1   the road.  That's where our engineers come together, our

2   outside plant people come together, the area managers, finance,

3   engineering, planning, all of them sit down and they decide to

4   come up with a plan on how we're going to do the restoration.

5             The DAG or the Damage Assessment Group, one of the

6   things that we're proud of about this group, in 2004 after the

7   first storm hit, within 24 hours we knew every pole, how many,

8   how many drops were down, how many cables were down, we had all

9   that information because we had an upfront system where the

10   technicians would go out and once the damage hit, we sent all

11   of our technicians to that area, they would fill out a form.

12   At that time it had to be entered into the system and we in the

13   EOC could see a live or as close to live as we could get update

14   on how many damages and what kind we had.  Since then we've

15   automated that that it can be put in by the technician's laptop

16   and we in the EOC, it's almost realtime, we know where the

17   damages are.

18             Our structure is designed so that the EOC is a

19   central point of contact.  It's where we're, we can see the big

20   picture.  We know if we need to move people from Hudson to Lake

21   Wales, this type of thing, where we don't leave those kind of

22   decisions up to the local manager because he's concerned about

23   his little area.  And we in the EOC as a central point of

24   contact, we can see the big picture.  We make those decisions.

25             The EOC consists of our region's executive staff

FLORIDA PUBLIC SERVICE COMMISSION

108

1   under the direction of the Emergency Control Officer.  Our

2   staff, our Executive Directors are in there, our Region

3   President is in there during -- actually they're there the

4   night -- if the storm is coming at night, they've been there

5   all night long.  Two reasons:  Number one, they don't know if

6   they're going to get back into the area, so they have to --

7   we've got to run the company and they're there -- that EOC

8   becomes where they're going to run the company from.  It

9   functions as the region's policy group.  Again, when we close

10   centers, we send people home.

11             We go into Phase 1, Phase 2, Phase 3, those type of

12   things.  And, again, similar to one of the power companies, our

13   different phases we do different things.

14             Phase 1, we get ready, we get on conference bridges,

15   we tell everybody we're watching something, we're not sure yet

16   exactly what it's going to do, but we want you to know we're

17   watching.  Phase -- and we'll have additional phone calls

18   throughout the day at what point we would get into a Phase 2,

19   which means we activate everything that's in our book that says

20   do this, fuel your fueling tanks on your generators up to

21   90 percent, send your noncritical personnel home so that they

22   can come back or send your critical personnel home where they

23   can come back and stay during the storm in locations that

24   they've been predetermined.

25             Our Division Control Center again consists of those

FLORIDA PUBLIC SERVICE COMMISSION

109

1   folks that I talked about earlier, the engineering and planning

2   and those folks.  The process that they're used to, that

3   they'll use in there is they're a central point of contact kind

4   of for checks and balances to make sure they've got the right

5   amount of people where they need them.  They also coordinate

6   the personnel related type services, time reporting, safety,

7   lodging, things like that.

8             They develop a service restoration plan under the

9   project management philosophy.  This is to improve resource

10   planning and performance physically.  Once they've got all the

11   information where the damage is, they actually will make a

12   decision -- we actually have -- once the damage comes in, a

13   damage assessment, they're put into grids, and we actually

14   dispatch by grids not by individual cases of trouble after a

15   storm.  We may send 20 people into one grid, two people into

16   another grid.  But our objective is where the mass of the

17   trouble is, that's where we're going to go first.

18             Again, the Damage Assessment Group, today our folks

19   have laptops.  And when they go do a damage assessment, they do

20   it on their laptop.  As soon as they hit the enter key, we can

21   see in the EOC and see where the damage is, we can see how many

22   poles are down, which gives us a little bit of a heads up to

23   our construction folks, get ready, this area looks like it's

24   going to be the worst, you need to start getting ready for

25   that.  They work under the direction of the local managers in

FLORIDA PUBLIC SERVICE COMMISSION

110

1   the field.  They're everybody from engineers that go out,

2   technicians.  It doesn't matter what, where you are, we could

3   be sending Clearwater people over to do a Winter Haven damage

4   assessment because they get assigned a grid that I mentioned

5   earlier.  They go inside that grid and they go street by

6   street, house by house and they look at everything that is

7   wrong.  And I will go back in a minute and share some other

8   things with you as how do we get in there when all the streets

9   are closed, et cetera?

10             This is our corporate structure.  In the red you'll

11   see that this is the Southeast Region Control Center or EOC.

12   And we are just one of -- in the scheme of Verizon there's

13   several of the different regions' RCCs.  When we open our RCC

14   or EOC, the Verizon EOC in New York opens up.  It supports us

15   from the time we open up until the time we close.  Every two

16   hours or three hours we're sending them information:  What do

17   we know, so forth and so on, how much trouble do we have, do

18   you need help, do you need -- you know, they're literally there

19   to support us.

20             To give you a little bit of probably information that

21   you really want to know right now, are we ready?  Yes, we are,

22   and here's why.  We have that dedicated EOC that I talked to

23   you about.  It's online every -- 12 months out of the year.  In

24   hurricane season it's manned full-time except at night, of

25   course.  We watch storms before they come off the coast of

FLORIDA PUBLIC SERVICE COMMISSION

111

1   Africa and we track them all the way across the, either the

2   Caribbean or the Atlantic.  We have a weatherman that's on

3   contract to us.  We listen to him.  He's very, very good.  He

4   told us Charley wasn't going to hit us.  You know, we were all

5   set for Charley to come up a little bit further and hit us.  He

6   told us, he said, "I don't think that's going to happen."  We

7   don't get all the hype and the news media and so forth.  We

8   listen to him.  He tells us what, not what we should do but

9   here's what we expect is going to happen.  So we follow him

10   pretty well.

11             Every year we have a region emergency exercise.  Now

12   what we do is we try to go inside with Hillsborough County

13   because that's our, where we are, the EOC is located in

14   Hillsborough County, and we use the State of Florida's plan.

15   If they have a hurricane hitting the east coast, we'll move it

16   over here to the west coast, as Hillsborough County will as

17   well, and it'll be coming into our area and damaging our area.

18   So we work with Hillsborough County.  We have people stationed

19   in every county EOC.  Two of our engineers are full-time, 24

20   hours a day when they operate.  When they open up, we're there.

21             And so our emergency exercise, we have one every

22   year, not just for hurricanes.  We also have to have them for

23   what if one of our major buildings catches fire, what do we do?

24   So we have to have an exercise for each one of the emergency

25   plans that we have.  And I'm just talking to you today about

FLORIDA PUBLIC SERVICE COMMISSION

112

1   the one dealing with storms.

2             We annually have to update our emergency plan.  It

3   has to be sent to corporate headquarters.  They -- we can't be

4   certified for this year being emergency preparedness if we

5   don't send, have our updates sent to them and if we don't have

6   our exercises.

7             Again, back with partnering with the seven county

8   emergency management teams, we really believe in this and I'll

9   tell you why.  One of the things back in '92 that we found out

10   about Andrew was much of the damage that occurred wasn't

11   because of Andrew but it was because of the road clearing teams

12   that went in there to open up the roads.  They destroyed DLCs,

13   they destroyed terminals, they went in there with the front-end

14   loaders and bulldozers clearing the roads and they destroyed so

15   much of the infrastructure.

16             So one of the things that we've been working very

17   closely with, and I'll tell you now is one of our concerns is

18   we have -- Hillsborough County is very good.  We're very up

19   tight with them.  We have people, probably about 25 people

20   dedicated to go out with them when they first start that push.

21   Our people have the instruction, you stand in front of that

22   bulldozer.  If there's a crossbox or a terminal there, you

23   don't let them run over it.  The county works very well with

24   that.

25             Pinellas County, we've been working with them for

FLORIDA PUBLIC SERVICE COMMISSION

113

1   about three years now and finally they've got a real good plan

2   established.  Some of the other counties we don't have that

3   plan established yet.  We're actually going with them, we're

4   spending the night with them where their crews are located, we

5   go out with them.  That's what we want.  We want to be part of

6   their team.  That means taking a lot of our employees and

7   putting them there.  But two things happen:  First of all, they

8   protect our infrastructure and, secondly, they're communicating

9   back to us any major damage that they see while they're out

10   there.

11             One of the other things that where we talk about

12   implement the best practices, we've been doing this for a long

13   time and we think we're pretty smart.  I mean, after '92 we

14   realized there was a fuel problem.  We went out and got six

15   2,500-gallon tanks, fuel tanks, part of it gas, part of it

16   diesel, and before a storm we preposition them.  We have a fuel

17   truck go fuel them.  And we felt pretty good about that.  In

18   2004 it worked fabulous.  As a matter of fact, when you work on

19   a plan for so many years and everything happens like it's

20   supposed to happen, in this storm it did, the plan worked

21   great.  But what if, you know?  Then you take a look at

22   Katrina, a whole other ball game.  But still fortunately we had

23   our gas tanks out where they needed to be.  Our guys could get

24   fuel because the power was down and no gas stations and all

25   were open in the southern part of our operating area.  So our

FLORIDA PUBLIC SERVICE COMMISSION

114

1   fuel tanks worked great.

2             But that's only 2,500 gallons for each and we have

3   six of them.  They're not all going to be in one location

4   because we don't want them all destroyed in one place.  So

5   during some of this past year's working with the county EOC,

6   they started prepositioning fuel tankers.  And now while we

7   have a good fuel plan, our fuel plan calls for our fuel vendor

8   to bring us fuel after the storm and to keep those tanks filled

9   and do what we need.  Well, we saw in 2005 with Rita some of

10   the fuel gets moved to where it doesn't need to go or not to

11   where Verizon wants it to go.  Let me put it that way.  The

12   police will stop it or the National Guard stops it and takes

13   the fuel somewhere else.  So by taking these tankers and

14   prepositioning them, they're like 9,000 gallons, and

15   preposition them at different places, that's one of the things

16   we found out the county was doing, so that's one of the things

17   that we implemented for this year is that fuel tank

18   prepositioning.

19             The other thing, and I'll just hit it briefly, is the

20   dedicated EOC.  We just put in brand new computer hardware in

21   there this year or last year.  We installed a new second SHARES

22   high frequency radio.  We're part of the sheriff's network for

23   the federal government.  And if all other communication fails,

24   we're able to communicate not only with Verizon but with other

25   agencies through the SHARES network, plus we have satellite

FLORIDA PUBLIC SERVICE COMMISSION

115

1   phones in our EOC, et cetera.

2             The annual region emergency exercise, again, I won't

3   dwell on that, but we have that.  Not only do we test our

4   people, but we also have our generators running in our EOC

5   full-time during this exercise to ensure that we don't have any

6   problems there.  Even though it's tested every month, we want

7   it to run the whole time that we're doing this exercise.

8             Each year, again I'll go back to our plan, it's

9   updated each year with different things like we just did,

10   talked about the fuel, and it has to go to our corporate

11   headquarters for us to be deemed that we are certified.  Again,

12   the emergency certification, corporate makes sure that we're

13   doing everything that we're supposed to do even though we

14   basically got corporate started on what they were doing.

15             Again, we partner with the seven counties.  We have

16   people inside of them to assist them 24 hours a day.  We have

17   people assigned to the first-end teams that go out with the

18   counties and their job is to protect our infrastructure.

19             We also -- the Hillsborough County Sheriff's

20   Department came to us and they said, "Can you help us?  We have

21   people out in search and rescue before the road clearing crews

22   ever come out.  We can't determine what's a power and what's a

23   telephone cable.  Can you at least give us a tech, let him come

24   out there with us?  And if he says that's power, we won't go

25   any further.  If he says it's telephone, then he can cut it or

FLORIDA PUBLIC SERVICE COMMISSION

116

1   move it or do what he needs to do."  We agreed to give them

2   people to do that.  So we work very closely with law

3   enforcement as well as the seven counties that we support.

4             Again, I talked about the tanks that we have and

5   about the tanker trucks, and that's part of this year's plan.

6             Verizon continues to be proactive.  In downtown Tampa

7   we installed a new 2 megawatt generator to back up or support

8   the generator that's already there.  Just in case we continue

9   to lose power for an extended period of time, we don't have to

10   worry about the potential for that generator to go bad.

11             Pole hardening, Verizon has inspected approximately

12   20 percent of its pole inventory program to date.  Poles that

13   fail inspection are replaced.  And I believe you got a letter

14   February, February 29th giving you the updated information on

15   how many poles, et cetera.

16             Our supply department each year in April and May

17   start beefing up their supplies by 10 percent for minor

18   material.  They put in stock, in case they have to go out and

19   replace poles, the different kind of hardware associated with

20   that, additional certain size gauge of cable that we might need

21   for that aerial cable.  Again, in the neighborhood of

22   90 percent, I think, of our facilities are buried anyway.  But

23   in those instances where you do have a piece of aerial cable

24   that comes down, we'll have extra cable to go out and take care

25   of that.

FLORIDA PUBLIC SERVICE COMMISSION

117

1             I can't stress enough the ability for us to make a

2   phone call to our corporate EOC.  We've done that.  In 2004, in

3   24 hours I had over 100 generators sitting here ready for us to

4   deploy.  I had generators from all up north, from Texas from

5   5kW to 60kW.  Again, they're, they're the ones that we look to

6   should we not be able to handle a situation here.

7             The southeast region also has the Carolinas.  We have

8   generators, we have people in the Carolinas that just a stroke

9   of the pen we have on a trip down here.  And in 2004 we ended

10   up having to move some people from New Jersey down here, line

11   crews down here to help us.  So we have that ability to grab

12   people and move them around.

13             But I go back to the most important thing, we think,

14   is the plan.  If you've got a good plan and it's functional,

15   you can get through this.  2004 was a tough year for all of us.

16   We in the emergency group, we were kind of happy about the fact

17   that what we've been working on for so many years worked so

18   well.

19             Any questions?

20             CHAIRMAN CARTER:  Commissioners, any questions?

21   Staff, any questions?

22             Thank you very kindly.

23             MR. LEWIS:  Thank you.

24             CHAIRMAN CARTER:  Ms. Khazraee.

25             MS. KHAZRAEE:  Good afternoon.

FLORIDA PUBLIC SERVICE COMMISSION

118

1             CHAIRMAN CARTER:  Good afternoon.

2             MS. KHAZRAEE:  And I do recognize I'm all that's left

3   standing between us and lunch, so I will try to be quick.

4             Okay.  My presentation is basically building on the

5   one last year.  For us, network hardening is an ongoing

6   process.  It's also business as usual.  And by that I don't

7   mean that it's not important, but just that it is what we take

8   very seriously in keeping our network up and running.

9             We began our pole inspection process in November of

10   2006.  We are on track.  We have only 39,900 poles in our

11   network.  94 percent of our network is underground.  Only

12   6 percent is aerial.  We have currently checked approximately

13   5,500 of our poles.  And this past year in the 5,000 that we

14   checked, we had 127 that had failed.  So we have replaced

15   those.  We are on track with that process.

16             As we go out and do these pole inspections, we are

17   also putting GIS tags on them so that we can relocate, we can

18   locate them in the event of a storm, hurricane, some kind of

19   event, a tornado, something that might take poles down.

20             Our engineering design, which is just business as

21   usual again, includes consideration of storm hardening

22   requirements.  Things we learned from the storms in 2004 and

23   2005 we put into effect in the engineering plans that we do

24   today.  So we make sure that we have any digital loop carriers

25   or cross-connect boxes that have a lot of cable pairs coming

FLORIDA PUBLIC SERVICE COMMISSION

119

1   into them that are in an area where we think might be

2   susceptible to storm surge or rising water, they are put up on

3   platforms.  They are put in low profile cabinets so that they

4   don't have as much exposure to high winds.  We also look at

5   raised platforms for the ones that are down in the coastal

6   areas.  And, you know, we have coastal areas:  The Fort

7   Walton/Destin area, the St. Marks area, Crystal River, and then

8   from Port Charlotte, Punta Gorda, all the way down to the

9   southern tip of the state.  So we do have a lot of coastal

10   areas, a lot of exposure, and in those areas we have put any

11   digital loop carriers that are close to the coast up on raised

12   platforms.

13             We also take our generator maintenance very serious.

14   For the stationary generators in our offices, the ones that are

15   there continuously, those are run every month in a test to make

16   sure that they operate appropriately, that we make sure that we

17   have them maintained, that we keep the fuel.  We also have a

18   very large contingent of portable generators.  They are

19   assigned by district and it's based on how many digital loop

20   carriers are in each area that might need the portable

21   generators brought to them in the case of a power outage.  We

22   keep track of those, we keep them in logs, we maintain them,

23   and then as we approach storm season we begin to look at where

24   those are stationed.

25             And that brings me to my next slide on disaster

FLORIDA PUBLIC SERVICE COMMISSION

120

1   preparedness plan and action.  We have disaster preparedness

2   plans.  Those are by district.  We have eight districts in the

3   State of Florida.  And we implement those plans in advance of a

4   forecasted storm.  So in Florida where we have hurricane

5   season, towards the end of May we have a kickoff call each

6   year.  And this is an interdepartmental call.  Anybody who

7   would be involved in part of this disaster preparedness plan is

8   included on that call and everything is verified that it's

9   ready for this hurricane season.  There's a checklist that they

10   go through, we have this plan in writing, everybody has a copy

11   of it, and we verify every little detail about what we might

12   need if we had to go into a mode after a hurricane for, for

13   coordinating, replacement, repair, restoration.

14             We also coordinate with other utilities and with the

15   local governments through our presence at the Emergency

16   Operation Centers.  We actually send employees to be in those

17   Emergency Operation Centers.  We find that that works much

18   better if they can get -- then if they have any questions about

19   the teleco facilities in their area, they have somebody right

20   there.  We also communicate regularly and frequently both

21   internally and externally.  We have for the employees who are

22   actually going to be part of the restoration group, they are

23   told ahead of time who they have to communicate with, how

24   often, what numbers to call; and we also have a group that

25   provides updates to the external media; and we keep it on our

FLORIDA PUBLIC SERVICE COMMISSION

121

1   website as well, not only for our employees to know what's

2   going on but for our customers as well because, of course, they

3   want to know when their phones are going to be restored.

4             So if we've had an event and we're into post-storm

5   recovery, the first thing we do is before the storm has hit,

6   we've implemented our disaster preparedness plan, we have

7   opened our Regional Operations Center, which is in Apopka, and

8   we have opened our command center in whichever specific parts

9   of the state are going to be affected.  So if Tallahassee was

10   the area that we were expecting the hurricane, then Tallahassee

11   is where we would open a command center over on Blairstone

12   Road.  We have a building there.

13             We do two things almost immediately.  As soon as we

14   have gotten the all clear that it is safe to let our employees

15   out on the street, we mobilize our area survey teams to canvass

16   the area.  These are teams of two people who go out.  They have

17   a kit that was already prepared for them that they take with

18   them, and they identify where we have damaged facilities,

19   outages, cable down, poles down, whatever.  They make notes of

20   it and they communicate this back to the command center every

21   30 minutes so that we keep really up-to-date on what is down,

22   what needs to be fixed and where do we have clear access to get

23   to it to begin work.

24             We also activate rapid response teams.  These are

25   teams of employees.  They're technicians, they are preselected,

FLORIDA PUBLIC SERVICE COMMISSION

122

1   prechosen based on their abilities and their excellent skills.

2   We have outside techs, we have central office techs and we have

3   business office techs.  And between these three groups they can

4   get any service back up and working, whether it's voice

5   service, high speed Internet, special service circuits or a PBX

6   voice mail system, something that has software associated with

7   it, these groups of techs can do that.  And they are sent out

8   basically to begin restoration immediately with prioritized

9   circuits restored first.  We keep a list of all the prioritized

10   circuits, and these would include electric companies because we

11   found that they need to be able to communicate in order to get

12   their plant back up and working.  It would include hospitals,

13   police, sheriffs, fire departments, you know, some municipal

14   government lines, sometimes some bank lines in order to keep

15   money flowing in order to let people go out and, you know,

16   purchase what they need to begin restoration.  So we have those

17   prioritized circuits identified.  We begin restoration with

18   that immediately.

19             And then we have instituted something new that if we

20   have a storm this year, which I'm hoping we don't, we would put

21   into effect, and that's collecting forensic data after the fact

22   that we would then be able to take back and analyze for lessons

23   learned for the future.

24             That is my presentation.  If you have any questions,

25   I'd be happy to answer them.

FLORIDA PUBLIC SERVICE COMMISSION

123

1             CHAIRMAN CARTER:  Thank you so kindly.

2             Commissioners?  Staff?

3             Okay.  Thank you so kindly.  Commissioners, before we

4   go further, let me just ask staff, did we have anyone to sign

5   up for comments?

6             MR. GARL:  No, Mr. Chairman, there was not.

7             CHAIRMAN CARTER:  I would -- if we had anyone from

8   the public that wanted to speak, we wanted to give them an

9   opportunity to do so.  But hearing none, Commissioners, we're

10   back on comments and questions by Commissioners.

11             Let me start with, Commissioner Edgar, I'll start

12   with you, and then I'll go with Commissioner McMurrian and

13   Commissioner Skop and I think I'll bring us home.  You're

14   recognized.

15             COMMISSIONER EDGAR:  All right.  Thank you.  Thank

16   you, Mr. Chairman.

17             I would just say again I really appreciate all of our

18   presenters.  A lot of excellent information.  Always

19   educational for me.  And, you know, as you stated in your

20   earlier comments and we all realize that because we have had a

21   couple of seasons without the same significant storm events

22   that we had a few years back, sometimes some of this

23   information seems not quite as germane, but I firmly believe

24   that it truly is and that the consumers of Florida will benefit

25   from the initiative that this Commission took a few years back

FLORIDA PUBLIC SERVICE COMMISSION

124

1   and from the work our utilities are continuing to do on this

2   issue.  Thank you.

3             CHAIRMAN CARTER:  Thank you, Commissioner.

4             Commissioner McMurrian.

5             COMMISSIONER McMURRIAN:  Thank you.  I can't say

6   anything better than the two of you already have.  I appreciate

7   everyone's input from all the companies and participants and

8   staff's continued hard work on this.  And I hope the

9   predictions are wrong as well, Chairman.  Thank you.

10             CHAIRMAN CARTER:  Thank you.

11             Commissioner Skop.

12             COMMISSIONER SKOP:  Thank you, Mr. Chairman.

13             Again, I'd like to thank all the utilities that

14   presented today; a very informative presentation.  It's

15   important to remain diligent and pursue these in light of the

16   fact and some of the comments that have been raised that we

17   were very fortunate, knock on wood, not to have any major storm

18   events last year.  But we must remain ever prepared, and I

19   greatly appreciate the hard work and effort that you guys are

20   doing on behalf of the consumers such that in the event that we

21   do have a storm or multiple storms, that service restoration

22   will go smoother than historically has been the case.  Thank

23   you again.

24             CHAIRMAN CARTER:  Thank you, Commissioners.

25             We heard today from the investor-owned utilities, we

FLORIDA PUBLIC SERVICE COMMISSION

125

1   heard from the municipals and the co-ops, we heard from the

2   ILECs and we heard from -- did we get everybody?  I want to

3   make sure that we heard from everyone.  Did I miss anyone?

4   Good.  And we heard from our staff.  And I think this is a

5   great opportunity for us to be proactive, and this is why my

6   comments earlier were to kind of talk about how we got to where

7   we are now so that we can be prepared for what the future may

8   hold.  I'm hopeful that the predictions at Colorado State were

9   wrong, but, but we need to be prepared and we need to be

10   diligent.  So thank you, staff.  Thank you to all the parties.

11             Commissioners, anything else for the good of the

12   order?  With that, this workshop is adjourned.

13             (Workshop adjourned at 1:08 p.m.)

14

15

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION

126

1   STATE OF FLORIDA    )

:         CERTIFICATE OF REPORTER

2   COUNTY OF LEON      )

3

4             I, LINDA BOLES, RPR, CRR, Official Commission

Reporter, do hereby certify that the foregoing proceeding was

5   heard at the time and place herein stated.

6             IT IS FURTHER CERTIFIED that I stenographically

reported the said proceedings; that the same has been

7   transcribed under my direct supervision; and that this

transcript constitutes a true transcription of my notes of said

8   proceedings.

9             I FURTHER CERTIFY that I am not a relative, employee,

attorney or counsel of any of the parties, nor am I a relative

10   or employee of any of the parties' attorneys or counsel

connected with the action, nor am I financially interested in

11   the action.

12              DATED THIS ________ day of May, 2008.

13

14                  ________________________________

LINDA BOLES, RPR, CRR

15                  FPSC Official Commission Reporter

(850) 413-6734

16

17

18

19

20

21

22

23

24

25

FLORIDA PUBLIC SERVICE COMMISSION