## F 1
Gallons of Water Pumped, Sold and Unaccounted For | [10 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [10 empty] | Page 1 of 1
Docket No.: 160101-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2015
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ |  | _ | _ | _ | _ | _ | _ | _
_ | _ | _ |  |  | _ |  | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
[12 empty] | Unaccounted |  | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water |  | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2) |  | (1)+(2)-(3)-(4) |  | For Water
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ |  | _
2015-01-01 |  | 4.188 |  | 4.1559 |  | 0 |  | 3.3566 |  | 0.00477 |  | 0.79452 |  | 19.12%
2015-02-01 |  | 3.956 |  | 3.9239 |  | 0 |  | 3.488 |  | 0.01294 |  | 0.42295 |  | 10.78%
2015-03-01 |  | 4.701 |  | 4.6689 |  | 0 |  | 3.2513 |  | 0.03958 |  | 1.378 |  | 29.51%
2015-04-01 |  | 5.036 |  | 5.0039 |  | 0 |  | 3.6311 |  | 0.077199 |  | 1.2956 |  | 25.89%
2015-05-01 |  | 6.007 |  | 5.9749 |  | 0 |  | 4.7024 |  | 0.16324 |  | 1.1092 |  | 18.56%
2015-06-01 |  | 5.504 |  | 5.4719 |  | 0 |  | 5.4469 |  | 0.07347 |  | -0.04844 |  | -0.8853%
2015-07-01 |  | 4.611 |  | 4.5789 |  | 0 |  | 4.8189 |  | 0.03297 |  | -0.27293 |  | -5.961%
2015-08-01 |  | 4.1 |  | 4.0679 |  | 0 |  | 4.5486 |  | 0.17059 |  | -0.65129 |  | -16.01%
2015-09-01 |  | 3.767 |  | 3.7349 |  | 0 |  | 3.3226 |  | 0.00921 |  | 0.40307 |  | 10.79%
2015-10-01 |  | 4.744 |  | 4.7119 |  | 0 |  | 3.1977 |  | 0.00674 |  | 1.5074 |  | 31.99%
2015-11-01 |  | 4.646 |  | 4.6139 |  | 0 |  | 4.1523 |  | 0.09623 |  | 0.36539 |  | 7.919%
2015-12-01 |  | 4.441 |  | 4.4089 |  | 0 |  | 4.3686 |  | 0.06324 |  | -0.02297 |  | -0.521%
|  | - |  |  |  | - |  | - |  | - |  | - |  | -
Total |  | 55.701 |  | 55.3158 |  | 0 |  | 48.2851 |  | 0.75018 |  | 6.2806 |  | 11.35%
|  | = |  |  |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing
Reconciliation of Gallons Sold shown in Schedules F-1, F-9 and E-2:
The total gallons sold for Marion County, as shown on Schedule F-1 and F-9 are the same.
The total gallons sold for per Schedule E-2 is 48.170 mg, a 0/239% difference.
This is most likely due to the fact that the amounts on F-1 and F-9 are the sums of actual readings whereas the amount
on E-2 is taken from the billing analysis which is rounded to the nearest 1,000 gallons.

## F 2
Gallons of Wastewater Treated | [10 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [10 empty] | Page 1 of 1
Docket No.: 160101-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2015
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | Crownwood |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2015-01-01 |  | 0.584 | [7 empty] | 0.584 |  | 0
2015-02-01 |  | 0.691 | [7 empty] | 0.691 |  | 0
2015-03-01 |  | 0.543 | [7 empty] | 0.543 |  | 0
2015-04-01 |  | 0.467 | [7 empty] | 0.467 |  | 0
2015-05-01 |  | 0.446 | [7 empty] | 0.446 |  | 0
2015-06-01 |  | 0.432 | [7 empty] | 0.432 |  | 0
2015-07-01 |  | 0.453 | [7 empty] | 0.453 |  | 0
2015-08-01 |  | 0.467 | [7 empty] | 0.467 |  | 0
2015-09-01 |  | 0.469 | [7 empty] | 0.469 |  | 0
2015-10-01 |  | 0.446 | [7 empty] | 0.446 |  | 0
2015-11-01 |  | 0.468 | [7 empty] | 0.468 |  | 0
2015-12-01 |  | 0.534 | [7 empty] | 0.534 |  | 0
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 6 |  | 0 | [5 empty] | 6 |  | 0
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)

## F 3
Water Treatment Plant Data | [9 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [9 empty] | Schedule F-3
Docket No.: 160101-WS | [9 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [9 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity |  |  |  | Max Design Day per Sanitary Survey |  |  |  |  | 636000
| The hydraulic rated capacity. If different from that shown | [5 empty] | (Max Day Per CUP) |  |  | 442000
on the DEP operating or construction permit, provide an explanation.
2 | Maximum Day
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2016-08-05 | 267000
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2015-05-23 | 232000
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2015-05-09 | 233000
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2015-05-21 | 236000
| these days. | [6 empty] | (4) | 2015-05-07 | 238000
[8 empty] | (5) | 2015-05-13 | 266000
[9 empty] | AVERAGE | 241000
[9 empty] | Max Month | 192738.7097
4 | Average Daily Flow | [7 empty] | Annual | 151550.137
5 | Required Fire Flow | [7 empty] | 500 gpm for 2 hours
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F 4
Wastewater Treatment Plant Data | [9 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [9 empty] | Schedule F-4
Docket No.: 160101-WS | [9 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [9 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
[9 empty] | _ |  | _
1. | Plant Capacity (Three Month Average Daily Flow (TMADF) | [9 empty] | 40000
The hydraulic rated capacity. If different from that shown
on the DER operating or construction permit, provide an explanation.
2. | Average Daily Flow Max Month (a) | [7 empty] | 2015-02-01 |  | 24678.5714
| Highest TMADF | [7 empty] | 2015-03-01 |  | 20344.47
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.

## F 5
Used and Useful Calculations | [6 empty] | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [6 empty] | Schedule F-5
Docket No.: 160101-WS | [6 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 740 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 290 | gpm
| Ground storage capacity, gal. |  |  |  | 0 | gallons
| Usable ground storage (90%), gal. |  |  |  | 0 | gallons
| Elevated Storage |  |  |  | 0 | gallons
| Usable ground storage (100%), gal. |  |  |  | 0 | gallons
| Hydropneumatic storage capacity, gal. |  |  |  | 10000 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 0 | gallons
| Maximum day demand, |  |  |  | 267000 | gpd
| Peak hour demand = 2x max day/1440 |  |  |  | 370.8333 | gpm
| Fire flow requirement |  |  |  | 500 | gpm
| Unaccounted for water |  | 11.35% | of water pumped | 11.9493 | gpm
| Acceptable unaccounted for |  | 10% |  | 10.5243 | gpm
| Excess unaccounted for |  |  |  | 1.425 | gpm
Used & Useful Analysis, in accordance with Rule 25-30.4325:
No Usable Storage
Water Treatment Plant, no usable storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand |  |  | 370.8333 | gpm
| B = | Property needed to serve five years after TY |  |  | 15.6974 | gpm
| C = | Fire flow demand |  |  | 500 | gpm
| D = | Excess Unaccounted for water |  |  | 1.425 | gpm
| E = | Firm Reliable Capacity |  |  | 290 | gpm
The above used and useful factor is applicable to all source of supply, pumping, storage and treatment accounts,
as well as the land and structures accounts.
Storage
Storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | #DIV/0!
| A = | Peak demand |  |  | 370.8333 | gallons
| B = | Property needed to serve five years after TY |  |  | 15.6974 | gallons
| C = | Fire flow demand |  |  | 500 | gallons
| D = | Excess Unaccounted for water |  |  | 1.425 | gallons
| E = | Firm Reliable Capacity |  |  | 0 | gallons
The above used and useful factor is applicable to the distribution reservoir accounts.

## F 6
Used and Useful Calculations |  |  |  |  | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) |  |  |  |  | Schedule F-6
Docket No.: 160101-WS |  |  |  |  | Page 1 of 2
Test Year Ended: December 31, 2015 |  |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
Line
No.
1 | (A) | Used and useful flow (000):
2 |  | 3MADF - year 2015 |  | 20344.47
3 | (B) | Property needed for post test year period (see F-8) |  | 1148.4555
4 | (C) | Permitted capacity (3MADF) |  | 40000
5 | (D) | Used and useful percentage |  | 53.73%
|  |  | Use: | 100%
6 | (E) | Non-used and useful percentage |  | 46.27%
|  |  | Use: | 0%
Used & useful was set at 68.65% in Docket No. 020071-WS and has been held at that level in every case since.
In doing so, the Commission has recognized that although the number of customers has been virtually unchanged since
2006, flows remained almost the same or decreased and the Utility should not be penalized for reduced flows due to
conservation or loss of customers by assigning a reduced level of used and useful. The Commission has also
recognized that none of the UIF systems are overbuilt and are all substantially built out. And in the last case,
Docket No. 120209-WS, Order No. PSC-14-0025-PAA-WS, the Commission found all systems to be 100%
used and useful. It should continue to do so.
The above used and useful factor is applicable to all treatment and disposal plant accounts.

## F 6 (2)
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [5 empty] | Schedule F-6
Docket No.: 160101-WS | [5 empty] | Page 2 of 2
Test Year Ended: December 31, 2015 | [5 empty] | Preparer: F. Seidman
A. Infiltration allowance, excluding service laterals
Allowance @ 500
| Main dia. | Main length |  | gpd/inch-dia./mile
| inches | feet | miles | gpd | gpy
1 | 6 | 0 | 0 | 0
2 | 8 | 2798 | 0.52992 | 2119.697
3 | 10 | 0 | 0 | 0
4 | Total | 2798 | 0.52992 | 2119.697 | 773689.3939
5 | Estimated Inflow @ 10% of flows (l.10) |  |  |  | 614464.3
6 | Allowable I&I |  |  |  | 1388153.6939
B. Actual Inflow & Infiltration (I&I)
7 | Wastewater treated |  |  |  | 6000000
Estimated
| Gallons Billed (not capped) to: |  |  | returned *
8 | SFR Residential WW cust. |  | 2021700 | 80% | 1617360
9 | All Other |  | 4122943 | 90% | 3710648.7
10 | Estimated flows returned |  | 6144643 |  | 5328008.7
11 | Estimated I&I (treated less returned) [l.7-l.10] |  |  |  | 671991.3
12 | Actual less allowable [l.11-l.6] |  |  |  | -716162.3939
13 | Excess, if any [l.11-l.6, if positive] |  |  |  | 0
14 | Excess as percent of wastewater treated |  |  |  | 0%

## F 7
Used and Useful Calculations | [7 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [7 empty] | Schedule F-7
Docket No.: 160101-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Water Distribution & Wastewater Collection Systems
Used & useful was last set for this system in Docket No. 120209-WS. The water distribution
and wastewater collection systems were found to be 100% used & useful. Circumstances have not
significantly changed. The systems should remain at 100% used and useful.

## F 8
Margin Reserve Calculations |  |  |  |  | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) |  |  |  |  | Schedule F-8
Docket No.: 160101-WS |  |  |  |  | Page 1 of 1
Test Year Ended: December 31, 2015 |  |  |  |  | Preparer: Seidman, F.
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5,F-6,F-7
Water Pumping, Treatment & Storage
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs | 4.8505 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. | 0.64725 | gpm/ERC *
| PN = | Property needed expressed in U units | 15.6974 | gpm
* Based on the 2015 Peak Hour Demand (Sch. F-5) divided by 2015 ERCs (Sch F-9).
Wastewater Treatment & Disposal
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs | 2.9167 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. * | 78.7494 | gpd/ERC
| PN = | Property needed expressed in U units | 1148.4555 | gpd
* Based on the 2015 TMADF (Sch. F-6) divided 2015 ERCs (Sch F-10).

## F 9
Equivalent Residential Connections - Water | [10 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [10 empty] | Schedule F-9
Docket No.: 160101-WS | [10 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [10 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2011 | 463 | 468 |  | 465.5 |  | 45390440 | 97509.0011 | 54058120 |  | 554.3911
2 | 2012 | 468 | 479 |  | 473.5 |  | 44637300 | 94270.9609 | 51953920 |  | 551.1127 | -0.5914%
3 | 2013 | 479 | 488 |  | 483.5 |  | 45773178 | 94670.4819 | 51365798 |  | 542.5746 | -1.549%
4 | 2014 | 488 | 489 |  | 488.5 |  | 39066907 | 79973.1975 | 44946767 |  | 562.0229 | 3.584%
5 | 2015 | 489 | 491 |  | 490 |  | 41295180 | 84275.8776 | 48285060 |  | 572.9405 | 1.943%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 0.8466%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 542.2056 |  | 1 | 554.3911
[6 empty] | X Coefficient: |  | 4.8009 |  | 2 | 551.1127
[6 empty] | R^2: |  | 0.43643 |  | 3 | 542.5746
[10 empty] | 4 | 562.0229
[10 empty] | 5 | 572.9405
[10 empty] | 10 | 590.2146
[7 empty] | Five year growth |  |  |  | 17.2742
[7 empty] | Annual average |  |  |  | 3.4548
The Coefficient of determination - R^2 is weak. Use simple average growth rate:
[6 empty] | Five year growth |  |  |  | 24.2526 | Ercs
[6 empty] | Annual average growth @ 0.85% |  |  |  | 4.8505 | Ercs

## F 10
Equivalent Residential Connections - Wastewater | [10 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood 252-(136/90) | [10 empty] | Schedule F-10
Docket No.: 160101-WS | [10 empty] | Page 1 of 1
Test Year Ended: December 31, 2015 | [10 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2011 | 81 | 81 |  | 81 |  | 2191760 | 27058.7654 | 7028424 |  | 259.7467
2 | 2012 | 81 | 79 |  | 80 |  | 2514260 | 31428.25 | 10398251.6 |  | 330.8568 | 27.38%
3 | 2013 | 79 | 85 |  | 82 |  | 2336130 | 28489.3902 | 8062121.6 |  | 282.9868 | -14.47%
4 | 2014 | 85 | 86 |  | 85.5 |  | 2280150 | 26668.4211 | 7759429 |  | 290.9594 | 2.817%
5 | 2015 | 86 | 84 |  | 85 |  | 2021700 | 23784.7059 | 6144643 |  | 258.3443 | -11.21%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 1.129%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 297.3895 |  | 1 | 259.7467
[6 empty] | X Coefficient: |  | -4.2702 |  | 2 | 330.8568
[6 empty] | R^2: |  | 0.052252 |  | 3 | 282.9868
[10 empty] | 4 | 290.9594
[10 empty] | 5 | 258.3443
[10 empty] | 10 | 254.6873
[7 empty] | Five year growth |  |  |  | -3.657
[7 empty] | Annual average |  |  |  | -0.7314
The Coefficient of determination - R^2 is very weak. Use simple average growth rate:
[6 empty] | Five year growth |  |  |  | 14.5837 | Ercs
[6 empty] | Annual average growth @ 1.13% |  |  |  | 2.9167 | Ercs

## W (hidden)
Marion County - Golden Hills 2015 Summary
PWS ID No. 6424076
CUP No. 20-5643-005 |  | Exp. 12/23/15
Permitted Max Day Capacity of Plant - .641 mgd
Other - Water is supplied to the Crownwood system
Hyper Links'!A1 |  |  |  | Total Water Used/Loss |  |  | Source Meter Adj. 11/15/13
| Total Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Flow Meter Adj. % | Flow Meter Pumped Adj. | Pumped + Source Mtr Error, Less Gals Loss/Use
January 2015 | 4.188 | 0.1351 | 0.202 | 0.00327 | 0.0015 | 0.00477 | -3.21% | -0.13443 | 4.0488
February | 3.956 | 0.14129 | 0.201 | 0.00094 | 0.012 | 0.01294 | -3.21% | -0.12699 | 3.8161
March | 4.701 | 0.15165 | 0.245 | 0.00958 | 0.03 | 0.03958 | -3.21% | -0.1509 | 4.5105
April | 5.036 | 0.16787 | 0.214 | 0.018199 | 0.059 | 0.077199 | -3.21% | -0.16166 | 4.7971
May | 6.007 | 0.19377 | 0.266 | 0.073241 | 0.09 | 0.16324 | -3.21% | -0.19282 | 5.6509
June | 5.504 | 0.18347 | 0.253 | 0.02847 | 0.045 | 0.07347 | -3.21% | -0.17668 | 5.2539
July | 4.611 | 0.14874 | 0.203 | 0.01997 | 0.013 | 0.03297 | -3.21% | -0.14801 | 4.43
August | 4.1 | 0.13226 | 0.267 | 0.01059 | 0.16 | 0.17059 | -3.21% | -0.13161 | 3.7978
September | 3.767 | 0.12557 | 0.209 | 0.00671 | 0.0025 | 0.00921 | -3.21% | -0.12092 | 3.6369
October | 4.744 | 0.15303 | 0.213 | 0.00674 | 0 | 0.00674 | -3.21% | -0.15228 | 4.585
November | 4.646 | 0.15487 | 0.223 | 0.09423 | 0.002 | 0.09623 | -3.21% | -0.14914 | 4.4006
December | 4.441 | 0.14326 | 0.216 | 0.01324 | 0.05 | 0.06324 | -3.21% | -0.14256 | 4.2352
YTD Total/Avg/Max | 55.701 | 0.15257 | 0.267 | 0.28518 | 0.465 | 0.75018 |  | -1.788 | 53.1628
| 0 | Proof to Daily Flow
Water Loss-Use'!A1 |  |  |  | Water Loss/Use Proof | 0
Note on B8: Picked up from Daily Flow. Total daily flow, Column AH
Note on C8: Picked up from Daily Flow AVG, Column AI
Note on D8: Picked up from Daily Flow MAX, Column AJ
Note on E8: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the used detail.
Note on F8: Click on the hyperlink at the top of this worksheet to access the Water Accountability Data Input Form for the loss detail.

## WFLOW (hidden)
Marion County - Golden Hills | [11 empty] | Hyper Links'!A1
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max
January 2015 | 0.168 | 0.14 | 0.155 | 0.122 | 0.123 | 0.113 | 0.158 | 0.118 | 0.202 | 0.153 | 0.13 | 0.129 | 0.159 | 0.101 | 0.104 | 0.138 | 0.111 | 0.111 | 0.15 | 0.138 | 0.127 | 0.132 | 0.185 | 0.123 | 0.116 | 0.116 | 0.112 | 0.12 | 0.13 | 0.169 | 0.135 |  | 4.188 | 0.1351 | 0.202
February | 0.135 | 0.147 | 0.103 | 0.135 | 0.113 | 0.157 | 0.138 | 0.155 | 0.154 | 0.091 | 0.201 | 0.131 | 0.141 | 0.156 | 0.156 | 0.154 | 0.128 | 0.144 | 0.127 | 0.158 | 0.14 | 0.155 | 0.155 | 0.137 | 0.15 | 0.107 | 0.156 | 0.132 |  |  |  |  | 3.956 | 0.14129 | 0.201
March | 0.2 | 0.062 | 0.143 | 0.156 | 0.136 | 0.195 | 0.155 | 0.144 | 0.144 | 0.18 | 0.131 | 0.147 | 0.186 | 0.191 | 0.179 | 0.18 | 0.11 | 0.156 | 0.245 | 0.163 | 0.207 | 0.158 | 0.159 | 0.129 | 0.14 | 0.127 | 0.111 | 0.12 | 0.12 | 0.12 | 0.107 |  | 4.701 | 0.15165 | 0.245
April | 0.196 | 0.214 | 0.144 | 0.193 | 0.194 | 0.123 | 0.156 | 0.175 | 0.174 | 0.213 | 0.188 | 0.147 | 0.148 | 0.12 | 0.197 | 0.188 | 0.2 | 0.186 | 0.2 | 0.2 | 0.095 | 0.192 | 0.152 | 0.187 | 0.209 | 0.132 | 0.132 | 0.092 | 0.143 | 0.146 |  |  | 5.036 | 0.16787 | 0.214
May | 0.192 | 0.176 | 0.176 | 0.176 | 0.139 | 0.223 | 0.238 | 0.187 | 0.233 | 0.222 | 0.222 | 0.209 | 0.266 | 0.17 | 0.143 | 0.18 | 0.178 | 0.178 | 0.138 | 0.22 | 0.236 | 0.183 | 0.232 | 0.2 | 0.2 | 0.172 | 0.153 | 0.18 | 0.216 | 0.184 | 0.185 |  | 6.007 | 0.19377 | 0.266
June | 0.181 | 0.122 | 0.158 | 0.201 | 0.194 | 0.172 | 0.114 | 0.114 | 0.166 | 0.185 | 0.148 | 0.191 | 0.206 | 0.183 | 0.184 | 0.189 | 0.244 | 0.223 | 0.17 | 0.238 | 0.195 | 0.195 | 0.251 | 0.151 | 0.155 | 0.193 | 0.194 | 0.167 | 0.167 | 0.253 |  |  | 5.504 | 0.18347 | 0.253
July | 0.101 | 0.189 | 0.139 | 0.151 | 0.152 | 0.183 | 0.164 | 0.198 | 0.203 | 0.152 | 0.167 | 0.139 | 0.14 | 0.133 | 0.182 | 0.155 | 0.181 | 0.148 | 0.113 | 0.113 | 0.158 | 0.16 | 0.17 | 0.138 | 0.105 | 0.106 | 0.109 | 0.117 | 0.161 | 0.109 | 0.175 |  | 4.611 | 0.14874 | 0.203
August | 0.126 | 0.162 | 0.163 | 0.148 | 0.267 | 0.204 | 0.187 | 0.12 | 0.117 | 0.117 | 0.14 | 0.143 | 0.136 | 0.15 | 0.089 | 0.089 | 0.104 | 0.114 | 0.099 | 0.114 | 0.124 | 0.126 | 0.125 | 0.125 | 0.106 | 0.14 | 0.126 | 0.144 | 0.104 | 0.103 | 0.088 |  | 4.1 | 0.13226 | 0.267
September | 0.088 | 0.128 | 0.209 | 0.183 | 0.115 | 0.112 | 0.113 | 0.105 | 0.121 | 0.132 | 0.125 | 0.136 | 0.083 | 0.084 | 0.141 | 0.156 | 0.071 | 0.121 | 0.117 | 0.109 | 0.109 | 0.094 | 0.178 | 0.118 | 0.147 | 0.18 | 0.119 | 0.119 | 0.119 | 0.135 |  |  | 3.767 | 0.12557 | 0.209
October | 0.106 | 0.125 | 0.119 | 0.119 | 0.144 | 0.123 | 0.158 | 0.141 | 0.168 | 0.167 | 0.109 | 0.109 | 0.137 | 0.129 | 0.189 | 0.178 | 0.174 | 0.149 | 0.149 | 0.19 | 0.166 | 0.158 | 0.213 | 0.185 | 0.162 | 0.162 | 0.152 | 0.157 | 0.134 | 0.199 | 0.173 |  | 4.744 | 0.15303 | 0.213
November | 0.173 | 0.123 | 0.197 | 0.175 | 0.153 | 0.223 | 0.138 | 0.16 | 0.158 | 0.124 | 0.155 | 0.17 | 0.198 | 0.172 | 0.165 | 0.165 | 0.167 | 0.211 | 0.087 | 0.154 | 0.114 | 0.114 | 0.128 | 0.138 | 0.141 | 0.126 | 0.181 | 0.143 | 0.143 | 0.15 |  |  | 4.646 | 0.15487 | 0.223
December | 0.158 | 0.165 | 0.161 | 0.216 | 0.147 | 0.147 | 0.157 | 0.158 | 0.131 | 0.16 | 0.177 | 0.143 | 0.144 | 0.158 | 0.119 | 0.142 | 0.1 | 0.131 | 0.121 | 0.118 | 0.118 | 0.12 | 0.116 | 0.171 | 0.112 | 0.17 | 0.124 | 0.124 | 0.135 | 0.142 | 0.156 |  | 4.441 | 0.14326 | 0.216
[32 empty] | Grand Total | 55.701
[33 empty] | 6.007 |  | 0.267
Max Mo | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
May | 0.192 | 0.176 | 0.176 | 0.176 | 0.139 | 0.223 | 0.238 | 0.187 | 0.233 | 0.222 | 0.222 | 0.209 | 0.266 | 0.17 | 0.143 | 0.18 | 0.178 | 0.178 | 0.138 | 0.22 | 0.236 | 0.183 | 0.232 | 0.2 | 0.2 | 0.172 | 0.153 | 0.18 | 0.216 | 0.184 | 0.185
Sort | 19 | 5 | 15 | 27 | 14 | 26 | 2 | 3 | 4 | 17 | 18 | 16 | 28 | 22 | 30 | 31 | 8 | 1 | 24 | 25 | 12 | 29 | 20 | 10 | 11 | 6 | 23 | 9 | 21 | 7 | 13
May | 0.138 | 0.139 | 0.143 | 0.153 | 0.17 | 0.172 | 0.176 | 0.176 | 0.176 | 0.178 | 0.178 | 0.18 | 0.18 | 0.183 | 0.184 | 0.185 | 0.187 | 0.192 | 0.2 | 0.2 | 0.209 | 0.216 | 0.22 | 0.222 | 0.222 | 0.223 | 0.232 | 0.233 | 0.236 | 0.238 | 0.266

## WW (hidden)
2015 Crownwood - DMR Flow Summary
[32 empty] | Total | Avg | Max
FLW-01 | [31 empty] | 0.496
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 0.518
January 2015 | 0.023 | 0.016 | 0.016 | 0.016 | 0.017 | 0.019 | 0.013 | 0.016 | 0.019 | 0.015 | 0.013 | 0.013 | 0.018 | 0.014 | 0.021 | 0.024 | 0.02 | 0.019 | 0.021 | 0.02 | 0.013 | 0.016 | 0.022 | 0.03 | 0.018 | 0.018 | 0.023 | 0.015 | 0.023 | 0.029 | 0.024 | 0.584 | 0.018839 | 0.03
February | 0.024 | 0.025 | 0.023 | 0.021 | 0.028 | 0.025 | 0.026 | 0.034 | 0.035 | 0.021 | 0.038 | 0.029 | 0.027 | 0.028 | 0.028 | 0.036 | 0.025 | 0.027 | 0.02 | 0.023 | 0.018 | 0.016 | 0.016 | 0.016 | 0.017 | 0.021 | 0.024 | 0.02 |  |  |  | 0.691 | 0.024679 | 0.038
March | 0.02 | 0.013 | 0.017 | 0.019 | 0.015 | 0.021 | 0.019 | 0.016 | 0.017 | 0.015 | 0.016 | 0.015 | 0.021 | 0.016 | 0.02 | 0.021 | 0.011 | 0.014 | 0.03 | 0.017 | 0.021 | 0.012 | 0.021 | 0.019 | 0.013 | 0.017 | 0.017 | 0.021 | 0.015 | 0.015 | 0.019 | 0.543 | 0.017516 | 0.03
April | 0.012 | 0.016 | 0.014 | 0.015 | 0.017 | 0.014 | 0.014 | 0.021 | 0.012 | 0.018 | 0.015 | 0.014 | 0.014 | 0.012 | 0.019 | 0.013 | 0.021 | 0.014 | 0.018 | 0.017 | 0.013 | 0.015 | 0.011 | 0.017 | 0.017 | 0.017 | 0.017 | 0.02 | 0.017 | 0.013 |  | 0.467 | 0.015567 | 0.021
May | 0.019 | 0.016 | 0.017 | 0.017 | 0.014 | 0.018 | 0.014 | 0.013 | 0.015 | 0.015 | 0.013 | 0.016 | 0.012 | 0.013 | 0.02 | 0.014 | 0.013 | 0.013 | 0.011 | 0.019 | 0.008 | 0.016 | 0.012 | 0.013 | 0.013 | 0.013 | 0.015 | 0.013 | 0.02 | 0.01 | 0.011 | 0.446 | 0.014387 | 0.02
June | 0.014 | 0.013 | 0.014 | 0.01 | 0.018 | 0.015 | 0.013 | 0.012 | 0.015 | 0.014 | 0.014 | 0.014 | 0.012 | 0.015 | 0.014 | 0.011 | 0.017 | 0.018 | 0.014 | 0.014 | 0.012 | 0.013 | 0.011 | 0.015 | 0.015 | 0.026 | 0.023 | 0.012 | 0.012 | 0.012 |  | 0.432 | 0.0144 | 0.026
July | 0.015 | 0.019 | 0.014 | 0.014 | 0.013 | 0.015 | 0.01 | 0.015 | 0.018 | 0.012 | 0.011 | 0.015 | 0.013 | 0.017 | 0.015 | 0.015 | 0.013 | 0.013 | 0.011 | 0.012 | 0.015 | 0.012 | 0.015 | 0.016 | 0.012 | 0.012 | 0.02 | 0.019 | 0.011 | 0.02 | 0.021 | 0.453 | 0.014613 | 0.021
August | 0.017 | 0.009 | 0.009 | 0.006 | 0.007 | 0.016 | 0.019 | 0.015 | 0.015 | 0.014 | 0.013 | 0.015 | 0.018 | 0.02 | 0.013 | 0.014 | 0.019 | 0.011 | 0.02 | 0.019 | 0.021 | 0.015 | 0.017 | 0.019 | 0.017 | 0.015 | 0.015 | 0.015 | 0.013 | 0.012 | 0.019 | 0.467 | 0.015065 | 0.021
September | 0.021 | 0.013 | 0.014 | 0.021 | 0.013 | 0.013 | 0.012 | 0.016 | 0.019 | 0.013 | 0.02 | 0.013 | 0.014 | 0.013 | 0.016 | 0.022 | 0.015 | 0.013 | 0.018 | 0.016 | 0.016 | 0.01 | 0.016 | 0.018 | 0.015 | 0.014 | 0.013 | 0.013 | 0.021 | 0.018 |  | 0.469 | 0.015633 | 0.022
October | 0.011 | 0.02 | 0.012 | 0.011 | 0.016 | 0.012 | 0.013 | 0.012 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.016 | 0.015 | 0.017 | 0.013 | 0.01 | 0.011 | 0.018 | 0.015 | 0.016 | 0.013 | 0.012 | 0.014 | 0.014 | 0.017 | 0.013 | 0.015 | 0.018 | 0.017 | 0.446 | 0.014387 | 0.02
November | 0.017 | 0.013 | 0.02 | 0.013 | 0.016 | 0.019 | 0.006 | 0.017 | 0.017 | 0.019 | 0.018 | 0.015 | 0.015 | 0.013 | 0.013 | 0.013 | 0.016 | 0.021 | 0.013 | 0.018 | 0.013 | 0.012 | 0.019 | 0.021 | 0.011 | 0.014 | 0.02 | 0.015 | 0.015 | 0.016 |  | 0.468 | 0.0156 | 0.021
December | 0.021 | 0.016 | 0.015 | 0.025 | 0.017 | 0.017 | 0.023 | 0.021 | 0.016 | 0.016 | 0.013 | 0.014 | 0.013 | 0.019 | 0.02 | 0.017 | 0.014 | 0.02 | 0.014 | 0.015 | 0.013 | 0.02 | 0.017 | 0.023 | 0.011 | 0.02 | 0.015 | 0.013 | 0.018 | 0.02 | 0.018 | 0.534 | 0.017226 | 0.025
6
0.691
[37 empty] | TRC | Total Nitrogen
[35 empty] | MoGeoMean | Max | Min
[35 empty] | #/100ml | #/100ml | mg/L | mg/L
[35 empty] | 400 | 800 | 0.5 | Qtrly
[35 empty] | <2.0 | <2.0 | 0.9 | MNR
[35 empty] | 48 | 4700 | 1.2 | MNR
[35 empty] | <1 | <1 | 1.1 | MNR
[35 empty] | 3 | 3 | 2 | 1.5
[35 empty] | <1.0 | <1.0 | <2.2 | MNR
[35 empty] | <2.0 | <2.0 | 0.9 | MNR
[35 empty] | <1.0 | <1.0 | 1.6 | 31
[35 empty] | <1.0 | <1.0 | 1.4 | MNR
[35 empty] | <2.0 | <2.0 | 1.3 | MNR
[35 empty] | <2.0 | <2.0 | 1 | 28
[35 empty] | <1.0 | <1.0 | 1 | MNR
[35 empty] | <1.0 | <1.0 | 1.1 | MNR
[35 empty] | 25.5 | 2351.5 | 1.2273 | 20.1667
[35 empty] | 3 | 3 | 0.9 | 1.5
[35 empty] | 48 | 4700 | 2 | 31

## Newsales (hidden)
UIF -Marion, 252-136,90 CCB 2015
Rate Schedule | Description | Rev Class | Mtr Sz | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total |  | Yr End Res Cust
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 2" | 345023 | 402760 | 385368 | 355903 | 348563 | 298960 | 281710 | 351961 | 315248 | 362631 | 316964 | 350472 | 4115563 | sub 90
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 5/8" | 930 | 60 | 40 | 260 | 220 | 250 | 760 | 2080 | 170 | 1410 | 650 | 550 | 7380
252SRMAR | 252 UI of FL Wastewater Residential-Marion | RES | 5/8" | 145000 | 170360 | 366930 | 170945 | 177295 | 155380 | 148380 | 158830 | 129810 | 131790 | 112300 | 154680 | 2021700
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1.5" | 27900 | 61800 | 59800 | 58200 | 65500 | 71600 | 68100 | 67400 | 57700 | 63700 | 71800 | 70300 | 743800
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 162390 | 87030 | 88330 | 108710 | 114580 | 132710 | 271660 | 232180 | 414430 | 145990 | 247000 | 194360 | 2199370
252WIGMR | 252 UI of FL Water Irrigation General Service-Marion | COML | 1" | 46990 | 35620 | 35730 | 59050 | 73060 | 68720 | 66610 | 67930 | 62270 | 58350 | 66030 | 61310 | 701670
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 145000 | 170360 | 366930 | 170945 | 177295 | 155380 | 148380 | 158830 | 129810 | 131790 | 112300 | 154680 | 2021700
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1" | 26150 | 32150 | 4530 | 9690 | 17760 | 32740 | 38330 | 50870 | 55730 | 60840 | 43210 | 73650 | 445650 | sub136
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1.5" | 84100 | 81880 | 82990 | 79390 | 92020 | 81530 | 80380 | 92350 | 79570 | 90070 | 78950 | 12130 | 935360
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 4" | 125800 | 148090 | 161290 | 184670 | 196720 | 219930 | 179340 | 164550 | 108050 | 97120 | 230720 | 36960 | 1853240
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 9590 | 9790 | 8580 | 8900 | 10980 | 9880 | 8540 | 10480 | 8790 | 9560 | 15700 |  | 110790
252WRMAR | 252 UI of FL Water Residential-Marion | COML | 1" | 0 | 0
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 1" | 2661590 | 2795620 | 2378020 | 2880022 | 3884688 | 4523130 | 3879504 | 3648886 | 2350600 | 2472310 | 3193260 | 3685500 | 38353130
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 67100 | 65670 | 65140 | 71510 | 69830 | 151250 | 78020 | 55120 | 55670 | 67990 | 93310 | 79740 | 920350
|  |  |  | 3847563 | 4061190 | 4003678 | 4158195 | 5228511 | 5901460 | 5249714 | 5061467 | 3767848 | 3693551 | 4582194 | 4874332 | 54429703
Water 090,136 |  |  |  | 3356610 | 3488010 | 3251340 | 3631087 | 4702433 | 5446870 | 4818864 | 4548596 | 3322620 | 3197720 | 4152280 | 4368630 | 48285060
Wastewater 090 |  |  |  | 490953 | 573180 | 752338 | 527108 | 526078 | 454590 | 430850 | 512871 | 445228 | 495831 | 429914 | 505702 | 6144643
Total |  |  |  | 3847563 | 4061190 | 4003678 | 4158195 | 5228511 | 5901460 | 5249714 | 5061467 | 3767848 | 3693551 | 4582194 | 4874332 | 54429703
Water Res |  |  |  | 2873690 | 3031650 | 2810090 | 3122477 | 4131813 | 4829760 | 4105904 | 3862836 | 2536080 | 2672090 | 3398870 | 3919920 | 41295180 |  | 491
Wastewater Res 090 |  |  |  | 145000 | 170360 | 366930 | 170945 | 177295 | 155380 | 148380 | 158830 | 129810 | 131790 | 112300 | 154680 | 2021700 |  | 84
UIF -Marion, 252-136,90 CCB 2014
Water 090 | [15 empty] | 5717320
Water 0136 | [15 empty] | 39229447
Total Water | [15 empty] | 44946767
Wastewater 090 | [15 empty] | 7759429
Water Res 090 | [15 empty] | 2280150 |  | 86
Water Res 0136 | [15 empty] | 36786757 |  | 403
Total Water Res | [15 empty] | 39066907 |  | 489
Wastewater 090 | [15 empty] | 2280150 |  | 86
UIF -Marion, 252-136,90 CCB 2013
Water 090 | [15 empty] | 4973490
Water 0136 | [15 empty] | 46392308
Total Water | [15 empty] | 51365798
Wastewater 090 | [15 empty] | 8062121.6
Water Res 090 | [15 empty] | 2336130 |  | 85
Water Res 0136 | [15 empty] | 43437048 |  | 403
Total Water Res | [15 empty] | 45773178 |  | 488
Wastewater 090 | [15 empty] | 2336130 |  | 85
UIF -Marion, 252-136,90 CCB 2012
Water 090 | [15 empty] | 6431890
Water 0136 | [15 empty] | 45522030
Total Water | [15 empty] | 51953920
Wastewater 090 | [15 empty] | 10398251.6
Water Res 090 | [15 empty] | 2514260 |  | 79
Water Res 0136 | [15 empty] | 42123040 |  | 400
Total Water Res | [15 empty] | 44637300 |  | 479
Wastewater 090 | [15 empty] | 2514260 |  | 79
UIF -Marion, 252-136,90 CCB 2011
Water 090 | [15 empty] | 7081960
Water 0136 | [15 empty] | 46976160
Total Water | [15 empty] | 54058120
Wastewater 090 | [15 empty] | 7028424
Water Res 090 | [15 empty] | 2191760 |  | 81 | 81
Water Res 0136 | [15 empty] | 43198680 |  | 387 | 382
Total Water Res | [15 empty] | 45390440 |  | 468 | 463
Wastewater 090 | [15 empty] | 2191760 |  | 81 | 81

## Plant (hidden)
UIF - Marion
Golden Hills/Crownwood
WATER
Max Day per CUP |  | 442000 | gpd
Max Day Design Capacity |  | 636000 | gpd | Sanitary Survey, 12/31/14
Well 1 |  | 290 | gpm
Well 2 |  | 450 | gpm
Storage | Hydropneumatic | 1000 | gal
WASTEWATER
WWTP |  | 0.04 | MGD 3MADF
Disposal - RIB Reuse system |  | 0.04 | MGD 3MDAF
|  | 23350 | sq. ft.