## F 1
Gallons of Water Pumped, Sold and Unaccounted For | [10 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [10 empty] | Page 1 of 1
Docket No.: 20200139-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2019 | [10 empty] | Revised: 8/10/2020
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ |  | _ | _ | _ | _ | _ | _ | _
_ | _ | _ |  |  | _ |  | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
[12 empty] | Unaccounted |  | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water |  | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2) |  | (1)+(2)-(3)-(4) |  | For Water (3)
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ |  | _
2019-01-01 |  | 3.678 |  | 3.6272 |  | 0 |  | 3.0688 |  | 0.02093 |  | 0.53751 |  | 14.82%
2019-02-01 |  | 3.708 |  | 3.6568 |  | 0 |  | 2.9187 |  | 0.23549 |  | 0.50265 |  | 13.75%
2019-03-01 |  | 4.834 |  | 4.7673 |  | 0 |  | 2.9773 |  | 0.01827 |  | 1.7717 |  | 37.16%
2019-04-01 |  | 4.499 |  | 4.4369 |  | 0 |  | 3.8918 |  | 0.05824 |  | 0.48688 |  | 10.97%
2019-05-01 |  | 5.751 |  | 5.6716 |  | 0 |  | 3.5514 |  | 0.02132 |  | 2.0989 |  | 37.01%
2019-06-01 |  | 6.27 |  | 6.1835 |  | 0 |  | 3.5996 |  | 0.35568 |  | 2.2282 |  | 36.03%
2019-07-01 |  | 4.227 |  | 4.1687 |  | 0 |  | 4.3138 |  | 0.20578 |  | -0.35088 |  | -8.417%
2019-08-01 |  | 3.87 |  | 3.817 |  | 0 |  | 3.6465 |  | 0.08026 |  | 0.090238 |  | 2.364%
2019-09-01 |  | 4.491 |  | 4.4452 |  | 0 |  | 2.926 |  | 0.02968 |  | 1.4895 |  | 33.51%
2019-10-01 |  | 4.735 |  | 4.6867 |  | 0 |  | 3.5788 |  | 0.06387 |  | 1.044 |  | 22.28%
2019-11-01 |  | 4.167 |  | 4.1245 |  | 0 |  | 4.0081 |  | 0.15288 |  | -0.036493 |  | -0.8848%
2019-12-01 |  | 3.929 |  | 3.8889 |  | 0 |  | 3.5567 |  | 0.14445 |  | 0.18774 |  | 4.828%
|  | - |  |  |  | - |  | - |  | - |  | - |  | -
Total |  | 54.159 |  | 53.4743 |  | 0 |  | 42.0376 |  | 1.3868 |  | 10.0499 |  | 18.79% | 52.0875
|  | = |  |  |  | = |  | = |  | = |  | = |  | = | 52.087
(Above data in millions of gallons)
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing
(3) 8.8% excess UAW - Most likely due to aged galvanized pipe at the end cul-ded-sacs where there may be leaks due to type of soil.
All galvnized service lines have already been replaced.

## F 2
Gallons of Wastewater Treated | [10 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [10 empty] | Page 1 of 1
Docket No.: 20200139-WS | [10 empty] | Preparer: Seidman, F.
Test Year Ended: December 31, 2019
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | Crownwood |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2019-01-01 |  | 0.875 | [7 empty] | 0.875 |  | 0
2019-02-01 |  | 0.675 | [7 empty] | 0.675 |  | 0
2019-03-01 |  | 0.71 | [7 empty] | 0.71 |  | 0
2019-04-01 |  | 0.785 | [7 empty] | 0.785 |  | 0
2019-05-01 |  | 0.696 | [7 empty] | 0.696 |  | 0
2019-06-01 |  | 0.439 | [7 empty] | 0.439 |  | 0
2019-07-01 |  | 0.588 | [7 empty] | 0.588 |  | 0
2019-08-01 |  | 0.762 | [7 empty] | 0.762 |  | 0
2019-09-01 |  | 0.528 | [7 empty] | 0.528 |  | 0
2019-10-01 |  | 0.515 | [7 empty] | 0.515 |  | 0
2019-11-01 |  | 0.494 | [7 empty] | 0.494 |  | 0
2019-12-01 |  | 0.564 | [7 empty] | 0.564 |  | 0
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 7.631 |  | 0 | [5 empty] | 7.631 |  | 0
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)

## F 3
Water Treatment Plant Data | [9 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [9 empty] | Schedule F-3
Docket No.: 20200139-WS | [9 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [9 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity |  |  |  | Max Design Day per Sanitary Survey |  |  |  |  | 636000
| The hydraulic rated capacity. If different from that shown | [5 empty] | (Max Day Per CUP) |  |  | 244900
on the DEP operating or construction permit, provide an explanation.
2 | Maximum Day
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2019-06-07 | 582000
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2019-06-06 | 380000
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2019-06-08 | 382000
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2019-06-04 | 395000
| these days. | [6 empty] | (4) | 2019-06-05 | 580000
[8 empty] | (5) | 2019-06-07 | 582000
[9 empty] | AVERAGE | 463800
[9 empty] | Max Month | 206115.8
4 | Average Daily Flow | [7 empty] | Annual | 146505.0592
5 | Required Fire Flow | [7 empty] | 500 gpm for 2 hours
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F 4
Wastewater Treatment Plant Data | [9 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [9 empty] | Schedule F-4
Docket No.: 20200139-WS | [9 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [9 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
[9 empty] | _ |  | _
1. | Plant Capacity (Three Month Average Daily Flow (TMADF) | [9 empty] | 40000
The hydraulic rated capacity. If different from that shown
on the DER operating or construction permit, provide an explanation.
2. | Average Daily Flow Max Month (a) | [7 empty] | 2019-02-01 |  | 24107.1429
| Highest TMADF | [7 empty] | 2019-03-01 |  | 26433.5637
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.

## F 5
Used and Useful Calculations | [6 empty] | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [6 empty] | Schedule F-5
Docket No.: 20200139-WS | [6 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 740 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 290 | gpm
| Ground storage capacity, gal. |  |  |  | 0 | gallons
| Usable ground storage (90%), gal. |  |  |  | 0 | gallons
| Elevated Storage |  |  |  | 0 | gallons
| Usable ground storage (100%), gal. |  |  |  | 0 | gallons
| Hydropneumatic storage capacity, gal. |  |  |  | 10000 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 0 | gallons
| Maximum day demand, |  |  |  | 582000 | gpd
| Peak hour demand = 2x max day/1440 |  |  |  | 808.3333 | gpm
| Fire flow requirement |  |  |  | 500 | gpm
| Unaccounted for water |  | 18.79% | of water pumped | 19.1209 | gpm
| Acceptable unaccounted for |  | 10% |  | 10.174 | gpm
| Excess unaccounted for |  |  |  | 8.9469 | gpm
Used & Useful Analysis, in accordance with Rule 25-30.4325:
No Usable Storage
Water Treatment Plant, no usable storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand |  |  | 808.3333 | gpm
| B = | Property needed to serve five years after TY |  |  | 5.1105 | gpm
| C = | Fire flow demand |  |  | 500 | gpm
| D = | Excess Unaccounted for water |  |  | 8.9469 | gpm
| E = | Firm Reliable Capacity |  |  | 290 | gpm
The above used and useful factor is applicable to all source of supply, pumping, storage and treatment accounts,
as well as the land and structures accounts.
Storage
Storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | #DIV/0!
| A = | Peak demand |  |  | 808.3333 | gallons
| B = | Property needed to serve five years after TY |  |  | 5.1105 | gallons
| C = | Fire flow demand |  |  | 500 | gallons
| D = | Excess Unaccounted for water |  |  | 8.9469 | gallons
| E = | Firm Reliable Capacity |  |  | 0 | gallons
The above used and useful factor is applicable to the distribution reservoir accounts.

## F 6
Used and Useful Calculations |  |  |  | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood |  |  |  | Schedule F-6
Docket No.: 20200139-WS |  |  |  | Page 1 of 2
Test Year Ended: December 31, 2019 |  |  |  | Preparer: Seidman, F.
REVISED FOR STAFF ROG 28
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
Line
No.
1 | (A) | Used and useful flow (000):
2 |  | 3MADF - year 2019 | 26433.5637
REVISED FOR STAFF ROG 28
3 | (B) | Property needed for post test year period (see F-8) | 3479.0892
4 | (C) | Permitted capacity (3MADF) | 40000
5 | (D) | Used and useful percentage | 74.78%
6 | (E) | Non-used and useful percentage | 25.22%
The above used and useful factor is applicable to all treatment and disposal plant accounts.

## F 6 (2)
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Wastewater Treatment Plant
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [5 empty] | Schedule F-6
Docket No.: 20200139-WS | [5 empty] | Page 2 of 2
Test Year Ended: December 31, 2019 | [5 empty] | Preparer: F. Seidman
A. Infiltration allowance, excluding service laterals
Allowance @ 500
| Main dia. | Main length |  | gpd/inch-dia./mile
| inches | feet | miles | gpd | gpy
1 | 6 | 0 | 0 | 0
2 | 8 | 3451 | 0.6536 | 2614.3939
3 | 10 | 0 | 0 | 0
4 | Total | 3451 | 0.6536 | 2614.3939 | 954253.7879
5 | Estimated Inflow @ 10% of flows (l.10) |  |  |  | 706916.8
6 | Allowable I&I |  |  |  | 1661170.5879
B. Actual Inflow & Infiltration (I&I)
7 | Wastewater treated |  |  |  | 7631000
Estimated
| Gallons Billed (not capped) to: |  |  | returned *
8 | SFR Residential WW cust. |  | 2053879 | 80% | 1643103.2
9 | All Other |  | 5015289 | 90% | 4513760.1
10 | Estimated flows returned |  | 7069168 |  | 6156863.3
11 | Estimated I&I (treated less returned) [l.7-l.10] |  |  |  | 1474136.7
12 | Actual less allowable [l.11-l.6] |  |  |  | -187033.8879
13 | Excess, if any [l.11-l.6, if positive] |  |  |  | 0
14 | Excess as percent of wastewater treated |  |  |  | 0%

## F 7
Used and Useful Calculations | [7 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [7 empty] | Schedule F-7
Docket No.: 20200139-WS | [7 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [7 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Water Distribution & Wastewater Collection Systems
Used & useful was last set for this system in Docket No. 20160101-WS The water distribution
and wastewater collection systems were found to be 100% used & useful. Circumstances have not
significantly changed. The systems should remain at 100% used and useful.

## F 8
Margin Reserve Calculations |  |  |  |  | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood |  |  |  |  | Schedule F-8
Docket No.: 20200139-WS |  |  |  |  | Page 1 of 1
Test Year Ended: December 31, 2019 |  |  |  |  | Preparer: Seidman, F.
REVISED FOR STAFF ROG 28
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5,F-6,F-7
Water Pumping, Treatment & Storage
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs | 0.66225 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. | 1.5434 | gpm/ERC *
| PN = | Property needed expressed in U units | 5.1105 | gpm
* Based on the 2019 Peak Hour Demand (Sch. F-5) divided by 2015 ERCs (Sch F-9).
Wastewater Treatment & Disposal
PN = EG x PT x U
| where: | REVISED FOR STAFF ROG 28
| EG = | Equivalent annual growth in ERCs | 7.6558 | ERCs/yr
| PT = | Post test year period per statute | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. * | 90.8878 | gpd/ERC
| PN = | Property needed expressed in U units | 3479.0892 | gpd
* Based on the 2019 TMADF (Sch. F-6) divided 2019 ERCs (Sch F-10).

## F 9
Equivalent Residential Connections - Water | [10 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [10 empty] | Schedule F-9
Docket No.: 20200139-WS | [10 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [10 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2015 | 488 | 491 |  | 489.5 |  | 41295220 | 84362.0429 | 43976890 |  | 521.2876
2 | 2016 | 491 | 490 |  | 490.5 |  | 46310680 | 94415.2497 | 50049450 |  | 530.0992 | 1.69%
3 | 2017 | 490 | 496 |  | 493 |  | 45580988 | 92456.3651 | 49322918 |  | 533.4724 | 0.6363%
4 | 2018 | 496 | 499 |  | 497.5 |  | 40364882 | 81135.4412 | 43347682 |  | 534.2632 | 0.1482%
5 | 2019 | 499 | 491 |  | 495 |  | 39730560 | 80263.7576 | 42037570 |  | 523.7429 | -1.969%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 0.1264%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 525.8507 |  | 1 | 521.2876
[6 empty] | X Coefficient: |  | 0.90744 |  | 2 | 530.0992
[6 empty] | R^2: |  | 0.060943 |  | 3 | 533.4724
[10 empty] | 4 | 534.2632
[10 empty] | 5 | 523.7429
[10 empty] | 10 | 534.9252
[7 empty] | Five year growth |  |  |  | 11.1823
[7 empty] | Annual average |  |  |  | 2.2365
The Coefficient of determination - R^2 is weak. Use simple average growth rate:
[6 empty] | Five year growth |  |  |  | 3.3113 | Ercs
[6 empty] | Annual average growth @ 0.85% |  |  |  | 0.66225 | Ercs

## F 10
Equivalent Residential Connections - Wastewater | [10 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - UIF - Marion -Golden Hills/Crownwood | [10 empty] | Schedule F-10
Docket No.: 20200139-WS | [10 empty] | Page 1 of 1
Test Year Ended: December 31, 2019 | [10 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) | in ERCs
1 | 2015 | 82 | 84 |  | 83 |  | 2021740 | 24358.3133 | 6144683 |  | 252.2623
2 | 2016 | 84 | 82 |  | 83 |  | 2258610 | 27212.1687 | 6656191 |  | 244.6035 | -3.036%
3 | 2017 | 82 | 86 |  | 84 |  | 2302780 | 27414.0476 | 6790304 |  | 247.6943 | 1.264%
4 | 2018 | 86 | 85 |  | 85.5 |  | 2273480 | 26590.4094 | 7068739 |  | 265.8379 | 7.325%
5 | 2019 | 85 | 84 |  | 84.5 |  | 2053879 | 24306.2604 | 7069168 |  | 290.8373 | 9.404%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  | 3.739%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y
[6 empty] | Constant: |  | 230.7317 |  | 1 | 252.2623
[6 empty] | X Coefficient: |  | 9.8385 |  | 2 | 244.6035
[6 empty] | R^2: |  | 0.67544 |  | 3 | 247.6943
[10 empty] | 4 | 265.8379
[10 empty] | 5 | 290.8373
[10 empty] | 10 | 329.1163
[7 empty] | Five year growth |  |  |  | 38.2789
[7 empty] | Annual average |  |  |  | 7.6558
The Coefficient of determination - R^2 is very weak. Use simple average growth rate:
[6 empty] | Five year growth |  |  |  | 54.3741 | Ercs
[6 empty] | Annual average growth @ 1.13% |  |  |  | 10.8748 | Ercs

## W2019 (hidden)
252/136 - Golden Hills
PWS ID No. 6424076
CUP No. 20-5643-005 |  | 1936-02-23
FDEP Permitted Max Day Capacity of Plant - .636 mgd
Other - Water is supplied to the Crownwood customers
Hyper Links'!A1 |  |  |  | Total Water Used/Loss |  |  | Source Meter Error Adj. 01/31/2019 -1.38% 08/30/19 -1.02%
| Total Pumped | Pumpgd Daily Avg. | Pumpgd Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Flow Mtr Adj. % | Flow Mtr Pumped Adj. | Pumped + Source Mtr Error, Less Gals Loss/Used | Golden Hills Billed Consumption | Crownwood Billed Consumption | Total Billed Consumption | Total AFW (Total Used/Loss + Billed) | AFW % plus source mtr. error | 2018 AFW %
January 2019 | 3.678 | 0.11862 | 0.148 | 0.02093 | 0 | 0.02093 | -1.38% | -0.050756 | 3.6063 | 2.6978 | 0.25809 | 2.9559 | 2.9768 | 82.07% | 90.96%
February | 3.708 | 0.1325 | 0.165 | 0.02649 | 0.209 | 0.23549 | -1.38% | -0.05117 | 3.4213 | 2.7192 | 0.18858 | 2.9078 | 3.1432 | 85.96% | 90.2%
March | 4.834 | 0.15631 | 0.242 | 0.01826 | 1e-05 | 0.01827 | -1.38% | -0.066709 | 4.749 | 3.7979 | 0.24328 | 4.0412 | 4.0595 | 85.15% | 88.21%
April | 4.499 | 0.14832 | 0.213 | 0.04994 | 0.0083 | 0.05824 | -1.38% | -0.062086 | 4.3787 | 3.5701 | 0.1883 | 3.7584 | 3.8166 | 86.02% | 92.96%
May | 5.751 | 0.18683 | 0.309 | 0.02132 | 0 | 0.02132 | -1.38% | -0.079364 | 5.6503 | 3.7888 | 0.15999 | 3.9488 | 3.9702 | 70% | 93.5%
June | 6.27 | 0.20293 | 0.582 | 0.00568 | 0.35 | 0.35568 | -1.38% | -0.086526 | 5.8278 | 3.8583 | 0.17556 | 4.0339 | 4.3895 | 70.99% | 85.83%
July | 4.227 | 0.13555 | 0.271 | 0.00578 | 0.2 | 0.20578 | -1.38% | -0.058333 | 3.9629 | 3.2547 | 0.16055 | 3.4152 | 3.621 | 86.86% | 87.65%
August | 3.87 | 0.12331 | 0.169 | 0.05026 | 0.03 | 0.08026 | -1.38% & -1.02% | -0.053024 | 3.7367 | 2.8594 | 0.19332 | 3.0527 | 3.133 | 82.08% | 86.67%
September | 4.491 | 0.15071 | 0.201 | 0.02168 | 0.008 | 0.02968 | -1.02% | -0.045808 | 4.4155 | 3.3447 | 0.20088 | 3.5456 | 3.5752 | 80.43% | 82.93%
October | 4.735 | 0.15069 | 0.231 | 0.02087 | 0.043 | 0.06387 | -1.02% | -0.048297 | 4.6228 | 3.8548 | 0.23984 | 4.0947 | 4.1585 | 88.73% | 81.57%
November | 4.167 | 0.13918 | 0.205 | 0.04988 | 0.103 | 0.15288 | -1.02% | -0.042503 | 3.9716 | 3.1628 | 0.20983 | 3.3726 | 3.5255 | 85.48% | 88.56%
December | 3.929 | 0.1259 | 0.172 | 0.06245 | 0.082 | 0.14445 | -1.02% | -0.040076 | 3.7445 | 3.2441 | 0.22601 | 3.4701 | 3.6146 | 92.95% | 89.05%
YTD Total/Avg/Max | 54.159 | 0.14757 | 0.582 | 0.35354 | 1.0333 | 1.3868 |  | -0.68465 | 52.0875 | 40.1526 | 2.4442 | 42.5968 | 43.9837
| 54.159 | [6 empty] | -0.68465 |  |  |  |  | 43.9837
| 0 | Proof to Daily Flow | [6 empty] | Proof to Total Billed | 0 | 0 | YTD AFW % Jan - Dec |  | 82.25%
Water Loss-Use'!A1 |  |  |  | Water Loss/Use Proof | 0 |  | Verified W/UIWtrMain WLU worksheet
[7 empty] | POE Mtr | Source Mtr Error Adjust
[7 empty] | Dates | Meter Adj. % | Pumped | Adjusted
[7 empty] | 08/01-08/30 | -1.38% | 3.764 | -0.051943
[7 empty] | 2019-08-31 | -1.02% | 0.106 | -0.0010812
-0.053024

## FLOW2019 (hidden)
252/136 - Golden Hills | [5 empty] | MWAF - Use P.O.E. Meter which is same as AH(x) | [5 empty] | Hyper Links'!A1
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0.147 | 0.091 | 0.137 | 0.139 | 0.101 | 0.094 | 0.093 | 0.099 | 0.148 | 0.086 | 0.14 | 0.125 | 0.119 | 0.118 | 0.106 | 0.125 | 0.129 | 0.108 | 0.136 | 0.137 | 0.121 | 0.134 | 0.13 | 0.118 | 0.135 | 0.125 | 0.099 | 0.098 | 0.104 | 0.126 | 0.11 |  | 3.678 | 0.11862 | 0.148 | 0
February | 0.139 | 0.124 | 0.117 | 0.117 | 0.084 | 0.117 | 0.121 | 0.165 | 0.131 | 0.129 | 0.129 | 0.077 | 0.16 | 0.124 | 0.111 | 0.136 | 0.136 | 0.161 | 0.133 | 0.155 | 0.138 | 0.146 | 0.162 | 0.162 | 0.154 | 0.152 | 0.116 | 0.112 |  |  |  |  | 3.708 | 0.1325 | 0.165 | 0
March | 0.147 | 0.154 | 0.125 | 0.125 | 0.09 | 0.129 | 0.168 | 0.135 | 0.17 | 0.169 | 0.153 | 0.15 | 0.09 | 0.145 | 0.231 | 0.15 | 0.151 | 0.152 | 0.133 | 0.146 | 0.144 | 0.24 | 0.153 | 0.159 | 0.159 | 0.242 | 0.149 | 0.137 | 0.208 | 0.135 | 0.195 |  | 4.834 | 0.15631 | 0.242 | 0
April | 0.196 | 0.15 | 0.126 | 0.192 | 0.148 | 0.141 | 0.141 | 0.164 | 0.107 | 0.124 | 0.181 | 0.199 | 0.164 | 0.164 | 0.162 | 0.108 | 0.141 | 0.187 | 0.144 | 0.122 | 0.121 | 0.15 | 0.094 | 0.182 | 0.213 | 0.129 | 0.11 | 0.167 | 0.167 | 0.105 |  |  | 4.499 | 0.14832 | 0.213 | 0
May | 0.173 | 0.16 | 0.201 | 0.148 | 0.145 | 0.144 | 0.096 | 0.12 | 0.184 | 0.188 | 0.156 | 0.157 | 0.164 | 0.111 | 0.16 | 0.142 | 0.194 | 0.185 | 0.185 | 0.202 | 0.204 | 0.217 | 0.217 | 0.213 | 0.236 | 0.236 | 0.246 | 0.235 | 0.17 | 0.253 | 0.309 |  | 5.751 | 0.18683 | 0.309 | 0
June | 0.294 | 0.294 | 0.233 | 0.395 | 0.58 | 0.38 | 0.582 | 0.382 | 0.178 | 0.135 | 0.102 | 0.137 | 0.14 | 0.115 | 0.141 | 0.145 | 0.145 | 0.117 | 0.117 | 0.071 | 0.149 | 0.186 | 0.155 | 0.155 | 0.107 | 0.209 | 0.136 | 0.203 | 0.144 | 0.143 |  |  | 6.27 | 0.20293 | 0.582 | 0
July | 0.18 | 0.116 | 0.174 | 0.156 | 0.12 | 0.142 | 0.271 | 0.082 | 0.104 | 0.204 | 0.109 | 0.15 | 0.11 | 0.11 | 0.163 | 0.099 | 0.166 | 0.177 | 0.149 | 0.144 | 0.144 | 0.092 | 0.126 | 0.124 | 0.096 | 0.14 | 0.103 | 0.132 | 0.132 | 0.073 | 0.139 |  | 4.227 | 0.13555 | 0.271 | 0
August | 0.137 | 0.157 | 0.152 | 0.156 | 0.157 | 0.086 | 0.127 | 0.099 | 0.168 | 0.151 | 0.151 | 0.084 | 0.11 | 0.148 | 0.169 | 0.069 | 0.109 | 0.109 | 0.106 | 0.093 | 0.127 | 0.108 | 0.141 | 0.151 | 0.151 | 0.118 | 0.076 | 0.133 | 0.103 | 0.118 | 0.106 |  | 3.87 | 0.12331 | 0.169 | 0
September | 0.136 | 0.135 | 0.073 | 0.113 | 0.112 | 0.121 | 0.148 | 0.149 | 0.157 | 0.107 | 0.198 | 0.15 | 0.127 | 0.143 | 0.142 | 0.141 | 0.132 | 0.177 | 0.167 | 0.144 | 0.191 | 0.16 | 0.16 | 0.15 | 0.142 | 0.177 | 0.144 | 0.201 | 0.201 | 0.193 |  |  | 4.491 | 0.15071 | 0.201 | 0
October | 0.188 | 0.177 | 0.186 | 0.231 | 0.19 | 0.188 | 0.187 | 0.076 | 0.16 | 0.158 | 0.163 | 0.174 | 0.173 | 0.19 | 0.131 | 0.201 | 0.134 | 0.138 | 0.146 | 0.146 | 0.08 | 0.091 | 0.138 | 0.146 | 0.121 | 0.134 | 0.123 | 0.123 | 0.166 | 0.14 | 0.136 |  | 4.735 | 0.15069 | 0.231 | 0
November | 0.128 | 0.142 | 0.142 | 0.16 | 0.092 | 0.18 | 0.144 | 0.17 | 0.121 | 0.121 | 0.145 | 0.137 | 0.169 | 0.181 | 0.138 | 0.087 | 0.116 | 0.116 | 0.104 | 0.139 | 0.153 | 0.122 | 0.205 | 0.141 | 0.141 | 0.111 | 0.13 | 0.195 | 0.116 | 0.121 |  |  | 4.167 | 0.13918 | 0.205 | 0
December | 0.139 | 0.139 | 0.114 | 0.172 | 0.126 | 0.168 | 0.13 | 0.151 | 0.151 | 0.096 | 0.171 | 0.15 | 0.159 | 0.122 | 0.122 | 0.121 | 0.121 | 0.121 | 0.124 | 0.082 | 0.114 | 0.138 | 0.127 | 0.053 | 0.121 | 0.106 | 0.102 | 0.133 | 0.137 | 0.138 | 0.081 |  | 3.929 | 0.1259 | 0.172 | 0
[32 empty] | Grand Total | 54.159
[33 empty] | 6.27 | MAX | 0.582
Day | 20 | 11 | 25 | 14 | 18 | 19 | 10 | 27 | 12 | 13 | 15 | 30 | 29 | 16 | 17 | 21 | 23 | 24 | 9 | 22 | 28 | 26 | 3 | 1 | 2 | 6 | 8 | 4 | 5 | 7
June | 0.071 | 0.102 | 0.107 | 0.115 | 0.117 | 0.117 | 0.135 | 0.136 | 0.137 | 0.14 | 0.141 | 0.143 | 0.144 | 0.145 | 0.145 | 0.149 | 0.155 | 0.155 | 0.178 | 0.186 | 0.203 | 0.209 | 0.233 | 0.294 | 0.294 | 0.38 | 0.382 | 0.395 | 0.58 | 0.582

## WW2019 (hidden)
2019 Crownwood - DMR Flow Summary | [5 empty] | Hyperlinks!A1
[33 empty] | Total | Avg | Max
FLW-01 | Note: See Word.doc file to copy the FLW-1 daily flows from. Copy/past to B21 then format the cells to number with 3 decimal places. Then copy/paste value/tranpose to the applicable month Row. | [31 empty] | 0.615 | 0.0205 |  | 3MADF
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | 0.836 | 0.026968
2019-01-01 | 0.039 | 0.026 | 0.029 | 0.029 | 0.024 | 0.026 | 0.024 | 0.026 | 0.026 | 0.028 | 0.036 | 0.024 | 0.027 | 0.026 | 0.016 | 0.019 | 0.024 | 0.02 | 0.025 | 0.024 | 0.037 | 0.032 | 0.03 | 0.032 | 0.038 | 0.03 | 0.031 | 0.033 | 0.038 | 0.027 | 0.029 |  | 0.875 | 0.028226 | 0.039 | 0.025231
February | 0.036 | 0.029 | 0.028 | 0.027 | 0.016 | 0.025 | 0.023 | 0.03 | 0.026 | 0.03 | 0.029 | 0.026 | 0.021 | 0.025 | 0.021 | 0.023 | 0.021 | 0.026 | 0.022 | 0.013 | 0.029 | 0.023 | 0.022 | 0.023 | 0.024 | 0.022 | 0.022 | 0.013 |  |  |  |  | 0.675 | 0.024107 | 0.036 | 0.026434
March | 0.011 | 0.033 | 0.033 | 0.024 | 0.012 | 0.022 | 0.021 | 0.024 | 0.025 | 0.024 | 0.029 | 0.02 | 0.019 | 0.023 | 0.022 | 0.02 | 0.019 | 0.028 | 0.012 | 0.03 | 0.024 | 0.035 | 0.02 | 0.022 | 0.022 | 0.03 | 0.018 | 0.022 | 0.027 | 0.012 | 0.027 |  | 0.71 | 0.022903 | 0.035 | 0.025079
April | 0.028 | 0.021 | 0.02 | 0.03 | 0.023 | 0.023 | 0.023 | 0.026 | 0.019 | 0.023 | 0.017 | 0.025 | 0.02 | 0.02 | 0.022 | 0.01 | 0.029 | 0.035 | 0.037 | 0.037 | 0.037 | 0.037 | 0.027 | 0.021 | 0.031 | 0.029 | 0.021 | 0.037 | 0.036 | 0.021 |  |  | 0.785 | 0.026167 | 0.037 | 0.024392
May | 0.034 | 0.028 | 0.038 | 0.028 | 0.03 | 0.028 | 0.014 | 0.027 | 0.028 | 0.036 | 0.029 | 0.029 | 0.032 | 0.035 | 0.025 | 0.014 | 0.016 | 0.016 | 0.015 | 0.016 | 0.01 | 0.021 | 0.017 | 0.021 | 0.016 | 0.015 | 0.018 | 0.015 | 0.014 | 0.01 | 0.021 |  | 0.696 | 0.022452 | 0.038 | 0.023841
June | 0.016 | 0.015 | 0.01 | 0.015 | 0.026 | 0.008 | 0.016 | 0.018 | 0.018 | 0.024 | 0.014 | 0.016 | 0.013 | 0.008 | 0.01 | 0.01 | 0.008 | 0.019 | 0.015 | 0.01 | 0.025 | 0.023 | 0.015 | 0.013 | 0.009 | 0.023 | 0.011 | 0.02 | 0.006 | 0.005 |  |  | 0.439 | 0.014633 | 0.026 | 0.021084
July | 0.005 | 0.015 | 0.019 | 0.019 | 0.014 | 0.018 | 0.015 | 0.014 | 0.015 | 0.018 | 0.01 | 0.024 | 0.018 | 0.018 | 0.018 | 0.013 | 0.017 | 0.019 | 0.018 | 0.018 | 0.018 | 0.01 | 0.023 | 0.018 | 0.027 | 0.036 | 0.032 | 0.03 | 0.03 | 0.018 | 0.021 |  | 0.588 | 0.018968 | 0.036 | 0.018684
August | 0.019 | 0.024 | 0.016 | 0.018 | 0.018 | 0.009 | 0.02 | 0.019 | 0.023 | 0.016 | 0.017 | 0.014 | 0.013 | 0.019 | 0.022 | 0.016 | 0.051 | 0.052 | 0.044 | 0.035 | 0.03 | 0.036 | 0.036 | 0.034 | 0.034 | 0.025 | 0.024 | 0.02 | 0.022 | 0.019 | 0.017 |  | 0.762 | 0.024581 | 0.052 | 0.019394
September | 0.026 | 0.025 | 0.014 | 0.025 | 0.019 | 0.026 | 0.018 | 0.019 | 0.018 | 0.01 | 0.017 | 0.022 | 0.016 | 0.018 | 0.017 | 0.015 | 0.017 | 0.017 | 0.01 | 0.024 | 0.017 | 0.016 | 0.016 | 0.014 | 0.011 | 0.014 | 0.017 | 0.016 | 0.016 | 0.018 |  |  | 0.528 | 0.0176 | 0.026 | 0.020383
October | 0.016 | 0.01 | 0.02 | 0.023 | 0.018 | 0.018 | 0.017 | 0.013 | 0.02 | 0.016 | 0.024 | 0.013 | 0.016 | 0.017 | 0.013 | 0.017 | 0.012 | 0.013 | 0.018 | 0.02 | 0.018 | 0.009 | 0.018 | 0.014 | 0.015 | 0.017 | 0.018 | 0.018 | 0.022 | 0.016 | 0.016 | 0 | 0.515 | 0.017 | 0 | 0.019727
November | 0.018 | 0.009 | 0.009 | 0.018 | 0.01 | 0.016 | 0.016 | 0.019 | 0.018 | 0.018 | 0.018 | 0.014 | 0.01 | 0.014 | 0.022 | 0.02 | 0.019 | 0.019 | 0.018 | 0.017 | 0.015 | 0.016 | 0.022 | 0.019 | 0.019 | 0.012 | 0.02 | 0.021 | 0.018 | 0.01 |  |  | 0.494 | 0.016467 | 0.022 | 0.017022
December | 0.018 | 0.018 | 0.027 | 0.014 | 0.012 | 0.02 | 0.023 | 0.017 | 0.016 | 0.016 | 0.011 | 0.019 | 0.01 | 0.019 | 0.019 | 0.018 | 0.018 | 0.018 | 0.018 | 0.004 | 0.019 | 0.026 | 0.024 | 0.016 | 0.019 | 0.022 | 0.02 | 0.019 | 0.022 | 0.023 | 0.019 |  | 0.564 | 0.018194 | 0.027 | 0.01722
7.631
0.026434
FLW-01
1 | 0.018
2 | 0.018
3 | 0.027
4 | 0.014
5 | 0.012
6 | 0.02
7 | 0.023
8 | 0.017
9 | 0.016
10 | 0.016
11 | 0.011
12 | 0.019
13 | 0.01
14 | 0.019
15 | 0.019
16 | 0.018
17 | 0.018
18 | 0.018
19 | 0.018
20 | 0.004
21 | 0.019
22 | 0.026
23 | 0.024
24 | 0.016
25 | 0.019
26 | 0.022
27 | 0.02
28 | 0.019
29 | 0.022
30 | 0.023
31 | 0.019

## Sales2019 (hidden)
Marion (Golden Hills, Crownwood) - 2019
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust. |  | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 2" | 4943599 |  |  | 614857 | 549058 | 467643 | 421012 | 362106 | 294351 | 294111 | 356929 | 570445 | 377389 | 282878 | 352820 | 4943599
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 5/8" | 71690 |  |  | 700 | 950 | 360 | 30850 | 24460 | 690 | 760 | 630 | 10660 | 540 | 230 | 860 | 71690
252SRMAR | 252 UI of FL Wastewater Residential-Marion | RES | 5/8" | 2053879 |  |  | 203411 | 249308 | 188670 | 190490 | 158530 | 137265 | 143693 | 148472 | 141550 | 148750 | 176550 | 167190 | 2053879
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 371290 |  |  | 7690 | 9540 | 7740 | 34330 | 36130 | 13080 | 34870 | 12740 | 51400 | 51310 | 54670 | 57790 | 371290
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 2053879 |  |  | 203411 | 249308 | 188670 | 190490 | 158530 | 137265 | 143693 | 148472 | 141550 | 148750 | 176550 | 167190 | 2053879
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1" | 810170 |  |  | 39230 | 35770 | 39930 | 92270 | 143340 | 131060 | 85290 | 94690 | 11400 | 55900 | 56350 | 24940 | 810170
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 2" | 545400 |  |  | 33400 | 1800 | 15100 | 91787 | 129213 | 71200 | 52900 | 1600 | 1900 | 25300 | 59000 | 62200 | 545400
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 4" | 125450 |  |  | 51640 | 46110 | 2600 | 1300 | 1600 | 1900 | 2600 | 2100 | 3400 | 5700 | 4800 | 1700 | 125450
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 454700 |  |  | 37250 | 29010 | 77470 | 63600 | 37760 | 36780 | 41960 | 35760 | 17220 | 16320 | 25040 | 36530 | 454700
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 1" | 36788821 |  |  | 2636218 | 2455367 | 2545250 | 3332610 | 2972050 | 3141910 | 3862184 | 3261856 | 2643400 | 3218300 | 3566780 | 3152896 | 36788821
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 887860 |  |  | 59960 | 91780 | 100550 | 85410 | 72820 | 66430 | 90270 | 89260 | 55730 | 57240 | 64920 | 53490 | 887860
|  |  |  | 49106738 |  |  | 3887767 | 3718001 | 3633983 | 4534149 | 4096539 | 4031931 | 4752331 | 4152509 | 3648655 | 4105499 | 4467768 | 4077606 | 49106738
Water |  |  |  | 42037570 |  |  | 3068799 | 2918685 | 2977310 | 3891797 | 3551443 | 3599625 | 4313767 | 3646478 | 2926000 | 3578820 | 4008110 | 3556736 | 42037570
Wastewater |  |  |  | 7069168 |  |  | 818968 | 799316 | 656673 | 642352 | 545096 | 432306 | 438564 | 506031 | 722655 | 526679 | 459658 | 520870 | 7069168
Total |  |  |  | 49106738 |  |  | 3887767 | 3718001 | 3633983 | 4534149 | 4096539 | 4031931 | 4752331 | 4152509 | 3648655 | 4105499 | 4467768 | 4077606 | 49106738
Water Res |  |  |  | 39730560 | 491 |  | 2899589 | 2796455 | 2834470 | 3608510 | 3203400 | 3345605 | 4096147 | 3499588 | 2840680 | 3424290 | 3808250 | 3373576 | 39730560
Wastewater Res |  |  |  | 2053879 | 84 |  | 203411 | 249308 | 188670 | 190490 | 158530 | 137265 | 143693 | 148472 | 141550 | 148750 | 176550 | 167190 | 2053879
Marion (Golden Hills, Crownwood) - 2018
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust.
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 2" | 4774169
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 5/8" | 21090
252SRMAR | 252 UI of FL Wastewater Residential-Marion | RES | 5/8" | 2273480
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 147580
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 2273480
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1" | 532150
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 2" | 635400
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 4" | 1230300
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 437370
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 1" | 37296022
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 795380
50416421
Water |  |  |  | 43347682
Wastewater |  |  |  | 7068739
Total |  |  |  | 50416421
Water Res |  |  |  | 40364882 | 499
Wastewater Res |  |  |  | 2273480 | 85
Marion (Golden Hills, Crownwood) - 2017
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust.
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 2" | 4471934
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 5/8" | 15590
252SRMAR | 252 UI of FL Wastewater Residential-Marion | RES | 5/8" | 2302780
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 106690
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 2302780
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1" | 1312940
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 2" | 922300
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 4" | 1064450
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 335550
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 1" | 42285668
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 992540
56113222
Water |  |  |  | 49322918
Wastewater |  |  |  | 6790304
Total |  |  |  | 56113222
Water Res |  |  |  | 45580988 | 496
Wastewater Res |  |  |  | 2302780 | 86
Marion (Golden Hills, Crownwood) - 2016
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust.
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 2" | 4312851
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 5/8" | 84730
252SRMAR | 252 UI of FL Wastewater Residential-Marion | RES | 5/8" | 2258610
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 294810
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 2258610
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1" | 920300
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 2" | 577600
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 4" | 1476970
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 469090
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 1" | 42903800
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 1148270
56705641
Water |  |  |  | 50049450
Wastewater |  |  |  | 6656191
Total |  |  |  | 56705641
Water Res |  |  |  | 46310680 | 490
Wastewater Res |  |  |  | 2258610 | 82
Marion (Golden Hills, Crownwood) - 2015
Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust.
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 2" | 4115563
252SGMAR | 252 UI of FL Wastewater Gen Serv-Marion | COML | 5/8" | 7380
252SRMAR | 252 UI of FL Wastewater Residential-Marion | RES | 5/8" | 2021740
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 232580
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 2021740
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 1" | 445650
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 2" | 935360
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 4" | 1853240
252WGMAR | 252 UI of FL Water General Service-Marion | COML | 5/8" | 110790
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 1" | 0
252WRMAR | 252 UI of FL Water Residential-Marion | RES | 5/8" | 38377530
895950
Water |  |  |  | 43976890
Wastewater |  |  |  | 6144683
Total |  |  |  | 50121573
Water Res |  |  |  | 41295220 | 491 | 488
Wastewater Res |  |  |  | 2021740 | 84 | 82
2021740

## Plant (hidden)
UIF - Marion - 2019
Golden Hills/Crownwood
WATER
Max Day per CUP |  | 244900 | gpd | per CUP, 2/23/2016
Annual Average |  | 188400
Max Day Design Capacity |  | 636000 | gpd | Sanitary Survey, 7/20/2017
Well 1 |  | 290 | gpm
Well 2 |  | 450 | gpm
Storage | Hydropneumatic | 10000 | gal
WASTEWATER
WWTP |  | 0.04 | MGD 3MADF |  | per Permit, 7/15/2013
Disposal - RIB Reuse system |  | 0.04 | MGD 3MDAF
|  | 23350 | sq. ft.