## F-1
Gallons of Water Pumped, Sold and Unaccounted For | [9 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [9 empty] | Page 1 of 3
Docket No.: 20200139-WS | [9 empty] | Preparer: Seidman, F.
Historical Year Ended: December 31, 2019
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) | (6)
[12 empty] | Unaccounted | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2) |  | (1)+(2)-(3)-(4) | For Water
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ | _
2019-01-01 |  | 118.825 |  | 118.7037 |  | 0 |  | 106.8906 |  | 0.18771 |  | 11.6254 | 9.794%
2019-02-01 |  | 108.616 |  | 108.4783 |  | 0 |  | 105.0035 |  | 0.27303 |  | 3.2018 | 2.952%
2019-03-01 |  | 141.2925 |  | 141.8872 |  | 0 |  | 103.073 |  | 0.17565 |  | 38.6386 | 27.23%
2019-04-01 |  | 139.3045 |  | 139.5912 |  | 0 |  | 133.0564 |  | 0.19672 |  | 6.3381 | 4.54%
2019-05-01 |  | 165.55 |  | 165.7984 |  | 0 |  | 129.1669 |  | 0.14329 |  | 36.4881 | 22.01%
2019-06-01 |  | 149.0145 |  | 149.4998 |  | 0 |  | 156.7046 |  | 1.2699 |  | -8.4747 | -5.669%
2019-07-01 |  | 136.2423 |  | 137.2511 |  | 0 |  | 138.1328 |  | 0.22139 |  | -1.103 | -0.8037%
2019-08-01 |  | 128.327 |  | 129.3597 |  | 0 |  | 113.8262 |  | 2.4459 |  | 13.0876 | 10.12%
2019-09-01 |  | 153.219 |  | 154.3697 |  | 0 |  | 132.9666 |  | 0.39805 |  | 21.005 | 13.61%
2019-10-01 |  | 158.832 |  | 159.8854 |  | 0 |  | 143.1053 |  | 0.3555 |  | 16.4246 | 10.27%
2019-11-01 |  | 141.717 |  | 142.6843 |  | 0 |  | 137.3602 |  | 0.32222 |  | 5.0019 | 3.506%
2019-12-01 |  | 124.562 |  | 125.407 |  | 0 |  | 133.2784 |  | 0.30325 |  | -8.1746 | -6.518%
|  | - |  |  |  | - |  | - |  | - |  | - | -
Total |  | 1665.5018 |  | 1672.9157 |  | 0 |  | 1532.5645 |  | 6.2926 |  | 134.0587 | 8.013% | 1666.6231
|  | = |  |  |  | = |  | = |  | = |  | = | = | 1666.151
(Above data in millions of gallons)
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing

## F-1 (2)
Gallons of Water Pumped, Sold and Unaccounted For | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida - Lake Utilities Services - Four Lakes | [8 empty] | Page 2 of 3
Docket No.: 20200139-WS | [8 empty] | Preparer: Seidman, F.
Historical Year Ended: June 30, 2010
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) | (6)
[12 empty] | Unaccounted | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2) |  | (1)+(2)-(3)-(4) | For Water (3)
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ | _
2019-01-01 |  | 0.48813 |  | 0.48486 |  | 0 |  | 0.37484 |  | 0.00601 |  | 0.10401 | 21.45%
2019-02-01 |  | 0.44534 |  | 0.44236 |  | 0 |  | 0.38909 |  | 0.0054 |  | 0.047865 | 10.82%
2019-03-01 |  | 0.68594 |  | 0.68023 |  | 0 |  | 0.38595 |  | 0.00607 |  | 0.28821 | 42.37%
2019-04-01 |  | 0.5145 |  | 0.50544 |  | 0 |  | 0.61413 |  | 0.020939 |  | -0.12963 | -25.65%
2019-05-01 |  | 0.72708 |  | 0.71428 |  | 0 |  | 0.44024 |  | 0.00327 |  | 0.27077 | 37.91%
2019-06-01 |  | 0.58576 |  | 0.57545 |  | 0 |  | 0.61589 |  | 0.00427 |  | -0.044708 | -7.769%
2019-07-01 |  | 0.5067 |  | 0.49778 |  | 0 |  | 0.5401 |  | 0.005574 |  | -0.047894 | -9.621%
2019-08-01 |  | 0.42576 |  | 0.41827 |  | 0 |  | 0.40246 |  | 0.00493 |  | 0.010881 | 2.601%
2019-09-01 |  | 0.54411 |  | 0.53453 |  | 0 |  | 0.38649 |  | 0.00497 |  | 0.14307 | 26.77%
2019-10-01 |  | 0.53295 |  | 0.52357 |  | 0 |  | 0.43349 |  | 0.01318 |  | 0.076898 | 14.69%
2019-11-01 |  | 0.49053 |  | 0.4819 |  | 0 |  | 0.43411 |  | 0.01026 |  | 0.037525 | 7.787%
2019-12-01 |  | 0.45496 |  | 0.44695 |  | 0 |  | 0.44136 |  | 0.00916 |  | -0.0035623 | -0.797%
|  | - |  |  |  | - |  | - |  | - |  | - | -
Total |  | 6.4018 |  | 6.3056 |  | 0 |  | 5.4581 |  | 0.094033 |  | 0.75344 | 11.95% | 6.2116
|  | = |  |  |  | = |  | = |  | = |  | = | = | 6.212
(Above data in millions of gallons)
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing

## F-1 (3)
Gallons of Water Pumped, Sold and Unaccounted For | [8 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-1
Company: Utilities, Inc. of Florida - Lake Utilities Services - Lake Saunders | [8 empty] | Page 3 of 3
Docket No.: 20200139-WS | [8 empty] | Preparer: Seidman, F.
Historical Year Ended: June 30, 2010
Explanation: Provide a schedule of gallons of water pumped, sold and unaccounted for each month of the test
year. The gallons pumped should match the flows shown on the monthly operating reports sent to DEP. The other
uses may include plant use, flushing of hydrants and water and sewer lines, line breakages and fire flows.
Provide all calculations to substantiate the other uses. If unaccounted for water is greater than 10%, pro-
vide an explanation as to the reasons why; if less than 10%, then Columns 4 & 5 may be omitted.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  |  |  | (2) |  | (3) |  | (4) |  | (5) | (6)
[12 empty] | Unaccounted | %
Month/ |  | Total Gallons |  | Total Gallons |  | Gallons |  | Gallons |  | Other |  | For Water | Unaccounted
Year |  | Pumped |  | Corrected for |  | Purchased |  | Sold |  | Uses (2) |  | (1)+(2)-(3)-(4) | For Water
_ |  | Per MORs |  | Meter Error (1) |  |  |  | _ |  | _ |  | _ | _
2019-01-01 |  | 0.2532 |  | 0.26059 |  | 0 |  | 0.1767 |  | 0.07542 |  | 0.0084734 | 3.252%
2019-02-01 |  | 0.26132 |  | 0.26895 |  | 0 |  | 0.15091 |  | 0.10874 |  | 0.0093005 | 3.458%
2019-03-01 |  | 0.40711 |  | 0.41607 |  | 0 |  | 0.17076 |  | 0.09417 |  | 0.15114 | 36.33%
2019-04-01 |  | 0.39963 |  | 0.39695 |  | 0 |  | 0.28663 |  | 0.14984 |  | -0.039518 | -9.955%
2019-05-01 |  | 0.35343 |  | 0.35106 |  | 0 |  | 0.23125 |  | 0.06714 |  | 0.052672 | 15%
2019-06-01 |  | 0.40025 |  | 0.39757 |  | 0 |  | 0.24656 |  | 0.08163 |  | 0.069378 | 17.45%
2019-07-01 |  | 0.28439 |  | 0.28248 |  | 0 |  | 0.30039 |  | 0.05243 |  | -0.070335 | -24.9%
2019-08-01 |  | 0.26959 |  | 0.26778 |  | 0 |  | 0.20064 |  | 0.05321 |  | 0.013929 | 5.202%
2019-09-01 |  | 0.3393 |  | 0.33702 |  | 0 |  | 0.16507 |  | 0.06014 |  | 0.11181 | 33.18%
2019-10-01 |  | 0.36481 |  | 0.36237 |  | 0 |  | 0.28692 |  | 0.07276 |  | 0.0026858 | 0.7412%
2019-11-01 |  | 0.30236 |  | 0.30034 |  | 0 |  | 0.25505 |  | 0.05913 |  | -0.013841 | -4.608%
2019-12-01 |  | 0.28431 |  | 0.28241 |  | 0 |  | 0.22818 |  | 0.05911 |  | -0.0048849 | -1.73%
|  | - |  |  |  | - |  | - |  | - |  | - | -
Total |  | 3.9197 |  | 3.9236 |  | 0 |  | 2.6991 |  | 0.93372 |  | 0.29082 | 7.412% | 2.9899
|  | = |  |  |  | = |  | = |  | = |  | = | = | 2.989
(Above data in millions of gallons)
(1) The Utility does an annual flow meter calibration. A correction factor is calculated that reflects the difference between our flow meter and a strap-on meter positioned directly adjacent to our meter to give highest confidence of meter accuracy. Meters are not necessarily repaired or modified after a calibration test. Instead, it is assumed that the measured error will be present consistently thereafter or until a subsequent flow test indicates otherwise. The corrected gallons = the gallons reported in the MOR + the percent correction determined in the most recent calibration.
(2) Other Uses includes such uses as line breaks, flushing and water quality testing

## F-2
Gallons of Wastewater Treated | [9 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [9 empty] | Page 1 of 2
Docket No.: 20200139-WS | [9 empty] | Preparer: Seidman, F.
Historical Year Ended: December 31, 2019
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | Lake Groves |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment | ADF/Mo
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2019-01-01 |  | 16.55 | [7 empty] | 16.55 |  | 0 | 0.53387
2019-02-01 |  | 15.188 | [7 empty] | 15.188 |  | 0 | 0.48994
2019-03-01 |  | 16.609 | [7 empty] | 16.609 |  | 0 | 0.55363
2019-04-01 |  | 16.271 | [7 empty] | 16.271 |  | 0 | 0.52487
2019-05-01 |  | 16.266 | [7 empty] | 16.266 |  | 0 | 0.5422
2019-06-01 |  | 16.097 | [7 empty] | 16.097 |  | 0 | 0.51926
2019-07-01 |  | 17.527 | [7 empty] | 17.527 |  | 0 | 0.56539
2019-08-01 |  | 17.323 | [7 empty] | 17.323 |  | 0 | 0.61868
2019-09-01 |  | 16.109 | [7 empty] | 16.109 |  | 0 | 0.51965
2019-10-01 |  | 17.033 | [7 empty] | 17.033 |  | 0 | 0.56777
2019-11-01 |  | 16.826 | [7 empty] | 16.826 |  | 0 | 0.54277
2019-12-01 |  | 17.864 | [7 empty] | 17.864 |  | 0 | 0.59547
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 199.663 |  | 0 |  | 0 |  | 0 |  | 199.663 |  | 0 | 0.54702
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)
MMADF
0.61868
AADF
0.54702

## F-2 (2)
Gallons of Wastewater Treated | [9 empty] | Florida Public Service Commission
In Thousands of Gallons
Schedule F-2
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [9 empty] | Page 2 of 2
Docket No.: 20200139-WS | [9 empty] | Preparer: Seidman, F.
Historical Year Ended: December 31, 2019
Explanation: Provide a schedule of gallons of wastewater treated by individual plant for each month of the
historical test year. Flow data should match the monthly operating reports sent to DEP.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
|  | (1) |  | (2) |  | (3) |  | (4) |  | (5) |  | (6)
|  |  |  | Individual Plant Flows | [7 empty] | Total Purch.
Month/ |  | _ | _ | _ | _ | _ | _ | _ |  | Total Plant |  | Sewage
Year |  | Barrington (1) |  | (Name) |  | (Name) |  | (Name) |  | Flows |  | Treatment
_ |  |  |  | _ |  | _ |  | _ |  | _ |  | _
2019-01-01 |  | 0.72 | [7 empty] | 0.72 |  | 0
2019-02-01 |  | 0.648 | [7 empty] | 0.648 |  | 0
2019-03-01 |  | 0.711 | [7 empty] | 0.711 |  | 0
2019-04-01 |  | 0.716 | [7 empty] | 0.716 |  | 0
2019-05-01 |  | 0.746 | [7 empty] | 0.746 |  | 0
2019-06-01 |  | 0.704 | [7 empty] | 0.704 |  | 0
2019-07-01 |  | 0.666 | [7 empty] | 0.666 |  | 0
2019-08-01 |  | 0.749 | [7 empty] | 0.749 |  | 0
2019-09-01 |  | 0.687 | [7 empty] | 0.687 |  | 0
2019-10-01 |  | 0.697 | [7 empty] | 0.697 |  | 0
2019-11-01 |  | 0.683 | [7 empty] | 0.683 |  | 0
2019-12-01 |  | 0.74 | [7 empty] | 0.74 |  | 0
|  | - |  | - |  | - |  | - |  | - |  | -
Total |  | 8.467 |  | 0 |  | 0 |  | 0 |  | 8.467 |  | 0
|  | = |  | = |  | = |  | = |  | = |  | =
(Above data in millions of gallons)
(1) - Not conneccted to Lake Groves plant
0.749

## F-3
Water Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [8 empty] | Schedule F-3
Docket No.: 20200139-WS | [8 empty] | Page 1 of 3
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [5 empty] | Combined Max Day Design Capacity |  |  | 13776000
on the DEP operating or construction permit, provide an explanation.
| [Cumulative design capacity of all well systems in LUSI] | [5 empty] | Combined Ann. Avg. Day per CUP |  |  | 5316000
2 | Maximum Day (see Sch. F-1)
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2019-05-30 | 8120000
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year (see Sch. F-1)
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2019-05-29 | 6580000
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2019-05-26 | 6994000
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2019-05-27 | 7030000
| these days. | [6 empty] | (4) | 2019-05-31 | 7556000
[8 empty] | (5) | 2019-05-30 | 8120000
[9 empty] | AVERAGE | 7256000
[9 empty] | Max Month | 5348334.0516
4 | Average Daily Flow | [7 empty] | Annual | 4583330.7591
5 | Required Fire Flow [Lake County Code] | [8 empty] | 500 gpm x 2 hrs
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F-3 (2)
Water Treatment Plant Data | [6 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Lake Utilities Services - Four Lakes | [6 empty] | Schedule F-3
Docket No.: 20200139-WS | [6 empty] | Page 2 of 3
Historical Year Ended: December 31, 2019 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [8 empty] | 151200
on the DEP operating or construction permit, provide an explanation.
[Limited by Water Use Permit peak month withdrawal]
2 | Maximum Day (see Sch. F-1, page 2)
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2019-05-27 | 43980
Explain, on a separate sheet of paper if fire flow, line breaks,
or other unusual occurrences affected the flow this day.
3 | Five Day Max. Year (see Sch. F-1, page 2)
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2019-05-30 | 29441
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2019-05-20 | 31815
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2019-05-25 | 36815.5
| these days. | [6 empty] | (4) | 2019-05-26 | 36815.5
[8 empty] | (5) | 2019-05-27 | 43980
[9 empty] | AVERAGE | 35773.4
[9 empty] | Max Month | 23041.3681
4 | Average Daily Flow | [7 empty] | Annual | 17275.6885
5 | Required Fire Flow [Lake County Code] | [8 empty] | 1200 gpm x 2 hrs
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F-3 (3)
Water Treatment Plant Data | [6 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Lake Utilities Services - Lake Saunders | [6 empty] | Schedule F-3
Docket No.: 20200139-WS | [6 empty] | Page 3 of 3
Historical Year Ended: December 31, 2019 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each water treatment plant. If the system has water plants that
are interconnected, the data for these plants may be combined. All flow data must be obtained from the monthly oper-
ating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | Date | GPD
1 | Plant Capacity
| The hydraulic rated capacity. If different from that shown | [8 empty] | 432000
on the DEP operating or construction permit, provide an explanation.
| [Limited by Water Use Permit peak month withdrawal] | [6 empty] | per CUP, Ann. Avg Day |  | 12328.7671
2 | Maximum Day (see Sch. F-1, page 2)
| The single day with the highest pumpage rate for the test year. | [7 empty] | 2019-04-23 | 65030
| Explain, on a separate sheet of paper if fire flow, line breaks, | [7 empty] | PRV Testing
| or other unusual occurrences affected the flow this day. | [6 empty] | Peak Day w/o unusual occurrence | 2019-06-18 | 31320
3 | Five Day Max. Year (see Sch. F-1, page 2)
| The five days with the highest pumpage rate from any one month | [6 empty] | (1) | 2019-03-24 | 16960
| in the test year. Provide an explanation if fire flow, line | [6 empty] | (2) | 2019-03-27 | 18930
| breaks or other unusual occurrences affected the flows on | [6 empty] | (3) | 2019-03-30 | 19105
| these days. | [6 empty] | (4) | 2019-03-31 | 19105
[8 empty] | (5) | 2019-03-11 | 19770
[9 empty] | AVERAGE | 18774
[9 empty] | Max Month | 13421.7276
4 | Average Daily Flow | [7 empty] | Annual | 10749.5767
5 | Required Fire Flow [Lake County Code] | [8 empty] | 1200 gpm x 2 hrs
The standards will be those as set by the Insurance Service
Organization or by a governmental agency ordinance. Provide
documents to support this calculation.

## F-4
Wastewater Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [8 empty] | Schedule F-4
Docket No.: 20200139-WS | [8 empty] | Page 1 of 2
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
[9 empty] | _ |  | _
1. | Plant Capacity (Lake Groves) |  |  |  |  | (AADF) |  |  |  |  | 999000
The hydraulic rated capacity. If different from that shown
on the DEP operating or construction permit, provide an explanation.
Note: Although the plant was expanded to 1 mgd, the permit allows operation
at .499 mgd as long as the AADF remains below .500 mgd.
2. | Average Daily Flow Max Month (a) | [7 empty] | Dec, 2019 |  | 576258.0645
| Annual Average Daily Flow | [9 empty] | 547021.9178
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.

## F-4 (2)
Wastewater Treatment Plant Data | [8 empty] | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [8 empty] | Schedule F-4
Docket No.: 20200139-WS | [8 empty] | Page 2 of 2
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information for each wastewater treatment plant. All flow data must be obtained
from the monthly operating reports (MORs) sent to the Department of Environmental Protection.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _ | _
[9 empty] | MONTH |  | GPD
[9 empty] | _ |  | _
1. | Plant Capacity (Barrington) |  |  |  |  | (AADF) |  |  |  |  | 49000
The hydraulic rated capacity. If different from that shown
on the DEP operating or construction permit, provide an explanation.
Note: Although the plant was expanded to 1 mgd, the permit allows operation
at .499 mgd as long as the AADF remains below .500 mgd.
2. | Average Daily Flow Max Month (a) | [7 empty] | Aug, 2019 |  | 24966.6667
| Annual Average Daily Flow | [9 empty] | 23197.2603
An average of the daily flows during the peak usage month
during the test year. Explain, on a separate page, if this
peak-month was influenced by abnormal infiltration due to
rainfall periods.

## F-5
Used and Useful Calculations | [5 empty] | Florida Public Service Commission
Water Treatment Plant
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [5 empty] | Schedule F-5
Docket No.: 20200139-WS | [5 empty] | Page 1 of 4
Historical Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 12455 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 9455 | gpm
| Ground storage capacity, gal. |  |  |  | 2624685 | gallons
| Usable ground storage (90%), gal. |  |  |  | 2362216.5 | gallons
Elevated Storage
Usable elevated storage (100%)
| Hydropneumatic storage capacity, gal. |  |  |  | 810400 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 2362216.5 | gallons
| Maximum day demand, |  |  |  | 8120000 | gpd
| Peak hour demand = 2 x max day/1440 |  |  |  | 11277.7778 | gpd
| Fire flow requirement |  | 500 gpm for x 2 hours |  | 60000 | gpd
| Unaccounted for water |  | 8.013% | of water pumped | 367284.0221 | gpd, avg
| Acceptable unaccounted for |  | 10% |  | 458333.0759 | gpd, avg
| Excess unaccounted for |  |  |  | 0 | gpd, avg
Used & Useful Analysis, inaccordance with Rule 25-30.4325;
Water Treatment Facilities, usable storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand (Max Day) |  |  | 8120000 | gpd
| B = | Property needed to serve five years after TY |  |  | 1486930.5345 | gpd
| C = | Fire flow demand |  |  | 60000 | gpd
| D = | Excess Unaccounted for water |  |  | 0 | gpd
| E = | Firm Reliable Capacity (16 hours) |  |  | 9076800 | gpd
The above used and useful factor is applicable to all source of supply, pumping and treatment accounts.
Storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand (Max Day) |  |  | 8120000 | gpd
| B = | Property needed to serve five years after TY |  |  | 1486930.5345 | gpd
| C = | Fire flow demand |  |  | 60000 | gpd
| D = | Excess Unaccounted for water |  |  | 0 | gpd
| E = | Firm Reliable Capacity (Usable Capacity) |  |  | 2362216.5 | gallons
The above used and useful factor is applicable to the distribution reservoir account.

## F-5 (2)
Used and Useful Calculations |  |  |  |  | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida - Lake Utilities Services - Four Lakes |  |  |  |  | Schedule F-5
Docket No.: 20200139-WS |  |  |  |  | Page 2 of 4
Historical Year Ended: December 31, 2019 |  |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 180 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 90 | gpm
| Ground storage capacity, gal. |  |  |  | 0 | gallons
| Usable ground storage (90%), gal. |  |  |  | 0 | gallons
Elevated Storage
Usable elevated storage (100%)
| Hydropneumatic storage capacity, gal. |  |  |  | 2000 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 0 | gallons
| Maximum day demand, |  |  |  | 43980 | gpd
| Peak hour demand = 2 x max day/1440 |  |  |  | 61.0833 | gpm
| Fire flow requirement |  | 500 gpm for x 2 hours |  | 500 | gpm
| Unaccounted for water |  | 11.95% | of water pumped | 1.4335 | gpm
| Acceptable unaccounted for |  | 10% |  | 1.1997 | gpm
| Excess unaccounted for |  |  |  | 0.23379 | gpm
Used & Useful Analysis, inaccordance with Rule 25-30.4325;
Water Treatment Facilities, no usable storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand (Max Day) - Peak hour |  |  | 61.0833 | gpm
| B = | Property needed to serve five years after TY |  |  | 0 | gpm
| C = | Fire flow demand |  |  | 500 | gpm
| D = | Excess Unaccounted for water |  |  | 0.23379 | gpm
| E = | Firm Reliable Capacity |  |  | 90 | gpm
The above used and useful factor is applicable to all source of supply, pumping and treatment accounts,
as well as the land, structures and distribution reservoir accounts.
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | #DIV/0!
| A = | Peak demand (Max Day) |  |  | 61.0833 | gpd
| B = | Property needed to serve five years after TY |  |  | 0 | gpd
| C = | Fire flow demand |  |  | 500 | gpd
| D = | Excess Unaccounted for water |  |  | 0.23379 | gpd
| E = | Firm Reliable Capacity (Usable Capacity) |  |  | 0 | gallons
The above used and useful factor is applicable to the distribution reservoir account.

## F-5 (3)
Used and Useful Calculations |  |  |  |  | Florida Public Service Commission
Water Treatment Plant
Company: Utilities, Inc. of Florida - Lake Utilities Services - Lake Saunders |  |  |  |  | Schedule F-5
Docket No.: 20200139-WS |  |  |  |  | Page 3 of 4
Historical Year Ended: December 31, 2019 |  |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water treatment plant(s) for the historical test year and
the projected test year (if applicable).
Recap Schedules: A-5,A-9,B-13
INPUT INFORMATION:
| Total well pumping capacity, gpm |  |  |  | 600 | gpm
| Firm Reliable well pumping capacity (largest well out), gpm |  |  |  | 300 | gpm
| Ground storage capacity, gal. |  |  |  | 0 | gallons
| Usable ground storage (90%), gal. |  |  |  | 0 | gallons
Elevated Storage
Usable elevated storage (100%)
| Hydropneumatic storage capacity, gal. |  |  |  | 5000 | gallons
| Usable hydropneumatic storage capacity (0.00%), gal. |  |  |  | 0 | gallons
| Total usable storage, gal. |  |  |  | 0 | gallons
| Maximum day demand, |  |  |  | 31320 | gpd
| Peak hour demand = 2 x max day/1440 |  |  |  | 43.5 | gpm
| Fire flow requirement |  | 500 gpm for x 2 hours |  | 500 | gpm
| Unaccounted for water |  | 7.412% | of water pumped | 0.5533 | gpm
| Acceptable unaccounted for |  | 10% |  | 0.7465 | gpm
| Excess unaccounted for |  |  |  | 0 | gpm
Used & Useful Analysis, inaccordance with Rule 25-30.4325;
Water Treatment Facilities, no usable storage
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | 100%
| A = | Peak demand (Max Day) - Peak hour |  |  | 43.5 | gpm
| B = | Property needed to serve five years after TY |  |  | 0 | gpm
| C = | Fire flow demand |  |  | 500 | gpm
| D = | Excess Unaccounted for water |  |  | 0 | gpm
| E = | Firm Reliable Capacity |  |  | 300 | gpm
The above used and useful factor is applicable to all source of supply, pumping and treatment accounts,
as well as the land, structures and distribution reservoir accounts.
| Percent Used & Useful = (A + B + C - D)/E x 100%, where: |  |  |  | #DIV/0!
| A = | Peak demand (Max Day) |  |  | 43.5 | gpd
| B = | Property needed to serve five years after TY |  |  | 0 | gpd
| C = | Fire flow demand |  |  | 500 | gpd
| D = | Excess Unaccounted for water |  |  | 0 | gpd
| E = | Firm Reliable Capacity (Usable Capacity) |  |  | 0 | gallons
The above used and useful factor is applicable to the distribution reservoir account.

## F-5 (4)
Used and Useful Calculations - Inventory of Components | [5 empty] | Florida Public Service Commission
Water Treatment Plant
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [5 empty] | Schedule F-5
Docket No.: 20200139-WS | [5 empty] | Page 4 of 4
Historical Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
The LUSI Combined system covers an extended area and is composed of multiple wells and storage facilities. These facilities are interconnected
and serve the service area as a whole. As such, the system is analyzed for used & useful as a single system. The capacities and
descriptions of the components are shown below.
Wells
Pump
Name |  |  |  |  | Capacity | Max Day | Storage
LUSI North | PWS ID # | Location | Well No. | Yr Drilled | gpm | Design, gpd | MG | Type | Source
Lake Louisa WTP | 3354883-02 | Vistas | 1/AAH6658 | 1988 | 1000 | 2520000 | 1 | G | Sanitary Survey 6/21/2018
|  | Vistas | 3/AAH2778 | 2003 | 625 |  | incl.
Vistas | 3354883-03 | Vistas | 2/AAH6686 | 1993 | 750 | 822000 | 0.1 | G | Sanitary Survey 6/21/2018
[7 empty] | 0.015 | H
Lake Ridge Club | 3354883-05 | L. Ridge Club | 1/Unknown | 1990 | 650 | 468000 | 0.007 | H | Sanitary Survey 6/21/2018
Amber Hill | 3354883-06 | Amber Hill | 1/Unknown | 1985 | 500 | 396000 | 0.0075 | H | Sanitary Survey 6/21/2018
Clermont #1 | 3354883-07 | Four Winds | 1/AAH6674 | 1940 | 236 | 115000 | 0.001 | H | Sanitary Survey 6/21/2018
|  |  | 2/AAH6675 | 1980 | 54 |  | 0.0009 | H
Clermont #2 | 3354883-08 | Carr Water System | 1/AAH6677 | 1939 | 45 | 71000 | 0.0035 | H | Sanitary Survey 6/21/2018
|  |  | 2/AAH6676 | 1963 | 75
Crescent Bay | 3354883-09 | Crescent Bay | 2/AAH6683 | 1995 | 700 | 396000 | 0.01 | H | Sanitary Survey 6/21/2018
The Oranges | 3354883-10 | The Oranges | 1/AAH6684 | 1986 | 530 | 396000 | 0.0045 | H | Sanitary Survey 6/21/2018
C.R. 561 | 3354883-12 |  |  |  |  | 2592000 |  |  | Sanitary Survey 6/21/2018
|  | L. Crescent Hills | 2/AAH6681 | 1991 | 600 |  | 0.75 | G
|  | Crescent West | 3/Unknown* | 1987 | 690 |  | 0.001 | H
|  | Highland Point | 1/AAH4420* | 1986 | 600 |  | 0.01 | H
LUSI South | 3354881 | Greater Groves | AAH6688 | 1991 | 1200 | 6000000 | 0 | H | Sanitary Survey 6/21/2018
|  |  | AAH6687 | 1992 | 1200 |  | 0.5 | G
|  |  | AAI5838 | 2005 | 3000 |  | 1 | G
[7 empty] | 0.024685 | GC
Totals - LUSI North & South |  |  |  |  | 12455 | 13776000 | 2.6247 | G
[7 empty] | 0.8104 | H
Stand Alone Systems
[5 empty] | Capacity | Design, gpd | Gal | Type
| PWS ID # | Location | Well No. | Yr Drilled | gpm
Lake Saunders | 3354695 | L. Saunders | AAH6670 | 1984 | 300 | 432000 | 5000 | H | Sanitary Survey 5/18/2018
|  | L. Saunders | AAH6671 | 1984 | 300
[5 empty] | Pump | Max Day | Storage
[5 empty] | Capacity | Design, gpd | Gal | Type
| PWS ID # | Location | Well No. | Yr Drilled | gpm
Four Lakes | 3354647 | Four Lakes | AAH6673 | 1980 | 90 | 151200 | 2000 | H | Sanitary Survey 7/10/18
|  | Four Lakes | AAH6672 | 1980 | 90
Wastewater
WWTP | 0.999 | MGD, AADF
Land application | 0.5 | MGD, AADF RIBs | 2.27 | acres
Land application | 0.999 | MGD, AADF Reuse irrigation

## F-6(LG)1
Used and Useful Calculations |  |  |  | FPSC
Wastewater Treatment Plant
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders |  |  |  | Schedule F-6
Docket No.: 20200139-WS |  |  |  | Page 1 of 4
Historical Year Ended: December 31, 2019 |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
Line |  |  | LAKE GROVES
No.
1 | (A) | Used and useful flow, GPD
2 |  | AADF |  | 547021.9178
|  | Less: Excessive I&I (from Sch. F-6, page 2) |  | 0
|  | Net Used and useful flow, GPD |  | 547021.9178
3 | (B) | Property needed for post test year period ( See F-8) |  | 99889.2963
4 | (C) | Permitted capacity |  | 999000
5 | (D) | Used and useful percentage |  | 65 | %
6 | (D1) |  |  | 100 | %
7 | (E) | Non-used and useful percentage |  | 35 | %
8 | (E1) |  |  | 0 | %
The above used and useful percentage is applicable to Treatment and Disposal accounts except reuse accounts. All Reuse, Pumping, Intangible and General Plant is considered 100% Used & Useful.

## F-6(LG)2
Used and Useful Calculations | [5 empty] | FPSC
Wastewater Treatment Plant
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [5 empty] | Schedule F-6
Docket No.: 20200139-WS | [5 empty] | Page 2 of 4
Historical Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
LAKE GROVES
A. Infiltration allowance, excluding service laterals
Allowance @ 500
| Main dia. | Main length |  | gpd/inch-dia./mile
| inches | feet | miles | gpd | gpy
1 | 6 | 0 | 0 | 0
2 | 8 | 156126 | 29.5693 | 118277.2727
3 | 10 | 0 | 0 | 0
4 | Total | 156126 | 29.5693 | 118277.2727 | 43171204.5455
5 | Estimated Inflow @ 10% of flows (l.8) |  |  |  | 18628436.038
6 | Allowable I&I |  |  |  | 61799640.5835
B. Actual Inflow & Infiltration (I&I)
7 | Wastewater treated |  |  |  | 199663000
Estimated
| Water Gallons used by WW cust. |  |  | returned *
8 | Residential WW |  | 490222001 | 38% | 186284360.38
| Non Res WW |  | 24920390 | 90% | 22428351
9 | Estimated flows returned |  | 515142391 |  | 208712711.38
* Homes & common areas are heavily landscaped and the soil is very porous, like
sugar sand. From F-10, average water use is 10,370 per month per SFR, up from 8944 per month in the last case.
Assuming just 4,000 gallons per mo per SFR for basic water, 4,000/10,370 equates to a 38% return ro wasterwater.
In the last case it was 48% and the case before that, 30% return.
10 | Estimated I&I (treated less returned) [l.7-l.9] |  |  |  | -9049711.38
11 | Actual less allowable [l.10-l.6] |  |  |  | -70849351.9635
12 | Excess, if any [l.10-l.6, if positive] |  |  |  | 0
13 | Excess as percent of wastewater treated |  |  |  | 0%

## F-6(B)1
Used and Useful Calculations |  |  |  |  | FPSC
Wastewater Treatment Plant
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders |  |  |  |  | Schedule F-6
Docket No.: 20200139-WS |  |  |  |  | Page 3 of 4
Historical Year Ended: December 31, 2019 |  |  |  |  | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
Recap Schedules: A-6,A-10,B-14
Line |  |  | BARRINGTON
No.
1 | (A) | Used and useful flow, GPD
2 |  | AADF |  | 23197.2603
|  | Less: Excessive I&I (from Sch. F-6, page 2) |  | 0
|  | Net Used and useful flow, GPD |  | 23197.2603
3 | (B) | Property needed for post test year period ( See F-8) |  | 0
| (C) | Permitted capacity |  | 49000
4 | (C) | Usable Capacity |  | 23197.2603
The agreement to purchase Barrington included the right of the
trustee to use all the permitted capacity of the WWTP, rapid infiltration
basins and lift station, present & future, not needed to serve
Barrington Estates, which is utility service area. Therefore, the U&U of
the capacity utilized by the utility is always 100%.
5 | (D) | Used and useful percentage |  | 100 | %
6 | (D1) |  |  |  | %
7 | (E) | Non-used and useful percentage |  | 0 | %
8 | (E1) |  |  | 0 | %
The above used and useful percentage is applicable to Treatment and Disposal accounts except reuse accounts. All Reuse, Pumping, Intangible and General Plant is considered 100% Used & Useful.

## F-6(B)2
Used and Useful Calculations | [5 empty] | FPSC
Wastewater Treatment Plant
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [5 empty] | Schedule F-6
Docket No.: 20200139-WS | [5 empty] | Page 4 of 4
Historical Year Ended: December 31, 2019 | [5 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the wastewater treatment plant(s) for the historical test year
and the projected test year (if applicable).
BARRINGTON
A. Infiltration allowance, excluding service laterals
Allowance @ 500
| Main dia. | Main length |  | gpd/inch-dia./mile
| inches | feet | miles | gpd | gpy
1 | 6 |  | 0 | 0
2 | 8 | 8685 | 1.6449 | 6579.5455
3 | 10 |  | 0 | 0
4 | Total | 8685 | 1.6449 | 6579.5455 | 2401534.0909
5 | Estimated Inflow @ 10% of flows (l.8) |  |  |  | 1919460.48
6 | Allowable I&I |  |  |  | 4320994.5709
B. Actual Inflow & Infiltration (I&I)
7 | Wastewater treated |  |  |  | 8467000
Estimated
returned *
8 | Water Gallons used by WW cust. |  | 23993256 | 80% | 19194604.8
9 | Estimated flows returned |  |  |  | 19194604.8
10 | Estimated I&I (treated less returned) [l.7-l.9] |  |  |  | -10727604.8
11 | Actual less allowable [l.10-l.6] |  |  |  | -15048599.3709
12 | Excess, if any [l.10-l.6, if positive] |  |  |  | 0
13 | Excess as percent of wastewater treated |  |  |  | 0%

## F-7
Used and Useful Calculations | [6 empty] | Florida Public Service Commission
Water Distribution and Wastewater Collection Systems
Company: Utilities Inc. of Florida - Lake Utilities Services | [6 empty] | Schedule F-7
Docket No.: 20200139-WS | [6 empty] | Page 1 of 1
Historical Year Ended: December 31, 2019 | [6 empty] | Preparer: Seidman, F.
Explanation: Provide all calculations, analyses and governmental requirements used to determine
the used and useful percentages for the water distribution and wastewater collection systems for
the historical and the projected test year (if applicable). The capacity should be in terms of
ability to serve a designated number of connections. It should then be related to actual connected
density for historical year calculations. Explain all assumptions for projected calculations. If
the distribution and collection systems are entirely contributed or built-out, this schedule is
not required.
_ | _ | _ | _ | _ | _ | _ | _ | _ | _
Recap Schedules: A-5,A-6,A-9,A-10,B-13,B-14
Water Distribution & Wastewater Collection Systems
In Docke No. 100426-WS, the Commission found that all the water & wastewater distribution & collection mains are
contributed to the Utility in all service areas, including Four Lakes & Lake Saunders, and should be considered 100% used and useful.
In Docket No. 20160101-Ws that conclusion was reaffirmed.

## F-8
Margin Reserve Calculations - Historic |  |  |  | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services |  |  |  | Schedule F-8
Docket No.: 20200139-WS |  |  |  | Page 1 of 1
Historical Year Ended: December 31, 2019 |  |  |  | Preparer: Seidman, F.
Explanation: If a margin reserve is requested, provide all calculations and analyses used to
determine the amount of margin reserve for each portion of used and useful plant.
Recap Schedules: F-5,F-6,F-7
Water Source, Pumping, Treatment & Storage - Combined Excl. Four Lakes & Lake Saunders
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs (Sch. F-9) |  | 442.8565 | ERCs/yr
| PT = | Post test year period per statute |  | 5 | yrs
| U = | Unit of measure utilized in U&U calculations (Sch. F-3, F-9) |  | 671.518 | max day gpd/ERC
| PN = | Property needed expressed in U units |  | 1486930.5345 | gpd
NOTE: U = T/A, where:
T = TY Max Day gallons (from Sch. F-3)
A = TY Total ERCs (from Sch. F-9)
Water Source, Pumping, Treatment & Storage - Four Lakes & Lake Saunders
In Docket No. 100426-WS, the Commission found the Four Lakes and Lake Saunders
system to be built with no growth. There is no growth margin.
Wastewater Treatment & Disposal
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs (Sch. F-10) |  | 151.1889 | ERCs/yr
| PT = | Post test year period per statute |  | 5 | yrs
| U = | Unit of measure utilized in U&U calculations (Sch. F-2, F-10) |  | 132.1384 | avg day gpd/ERC
| PN = | Property needed expressed in U units |  | 99889.2963 | gpd
NOTE: U = T/A, where:
T = TY treated gallons (from Sch. F-2)
A = TY Total ERCs (from Sch. F-10)
Water Distribution System
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs |  | 239.1302 | ERCs/yr
| PT = | Post test year period per statute |  | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. |  | 1 | ERC
| PN = | Property needed expressed in U units |  | 1195.6512 | ERCs
Wastewater Collection System
PN = EG x PT x U
where:
| EG = | Equivalent annual growth in ERCs |  | 151.1889 | ERCs/yr
| PT = | Post test year period per statute |  | 5 | yrs
| U = | Unit of measure utilized in U&U calculations. |  | 1 | ERC
| PN = | Property needed expressed in U units |  | 755.9443 | ERCs
In addition, there are prepaid lots not served in 2019. New phases of development
| have opened up in the Lake Groves service area, of which 967 had not connected |  |  | 560.8899 | prepaid lots
| at the end of the 2019TY. During 2019, the average SFRs increased by |  | @ | 132.1384 | gpd/ERC
| 351 (from F-10.) LUSI indicates that they average 30 new taps per month |  |  | 74115.109 | gpd
in 2020, which is consistent with the past year growth.
At that rate, the prepaid connections will be connected within 3 years.
Regression analyses reflects a trend of only 151.19 ERCs
growth per year. To better reflect actual new growth
being experienced,adjust by (360-151.19) = 208.81 Ercs/yr
for 2.69 yrs = 560.89 prepaid lots in the 5 year period.

## F-9
Equivalent Residential Connections - Water | [8 empty] | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [8 empty] | Schedule F-9
Docket No.: 20200139-WS | [8 empty] | Page 1 of 3
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | 9601 | 9904 |  | 9752.5 |  | 1205523153 | 123611.705 | 1304373114 |  | 10552.1812
2 | 2016 | 9904 | 9996 |  | 9950 |  | 1293894884 | 130039.6868 | 1496336662 |  | 11506.7692 |  | 9.046%
3 | 2017 | 9996 | 10144 |  | 10070 |  | 1332731220 | 132346.6951 | 1415864120 |  | 10698.1449 |  | -7.027%
4 | 2018 | 10144 | 11099 |  | 10621.5 |  | 1323221560 | 124579.5377 | 1414229761 |  | 11352.0229 |  | 6.112%
5 | 2019 | 11099 | 11666 |  | 11382.5 |  | 1442640263 | 126741.9515 | 1532564469 |  | 12092.0062 |  | 6.519%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 3.662% |  | 2103.325
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y |  | Year
[6 empty] | Constant: |  | 10362.7538 |  | 1 | 10552.1812 |  | 2011 | Actual
[6 empty] | X Coefficient: |  | 292.4904 |  | 2 | 11506.7692 |  | 2012 | Actual
[6 empty] | R^2: |  | 0.54272 |  | 3 | 10698.1449 |  | 2013 | Actual
[10 empty] | 4 | 11352.0229 |  | 2014 | Actual
[10 empty] | 5 | 12092.0062 |  | 2015 | Actual
[10 empty] | 10 | 13287.6575 |  | Hist TY + 5 yrs
HISTORIC
|  |  |  | Five year growth per regression equation: | [6 empty] | 1195.6512 | ERCs
|  |  |  | Five year growth, simple average of 3.5% | [6 empty] | 2214.2824
As regression os poor fit, use simple average

## F-9 (2)
Equivalent Residential Connections - Water | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Lake Utilities Services - Four Lakes | [8 empty] | Schedule F-9
Docket No.: 20200139-WS | [8 empty] | Page 2 of 3
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | 67 | 68 |  | 67.5 |  | 5994400 | 88805.9259 | 5994400 |  | 67.5
2 | 2016 | 68 | 71 |  | 69.5 |  | 6128743 | 88183.3525 | 6128743 |  | 69.5 |  | 2.963%
3 | 2017 | 71 | 70 |  | 70.5 |  | 6495700 | 92137.5887 | 6495700 |  | 70.5 |  | 1.439%
4 | 2018 | 70 | 71 |  | 70.5 |  | 5631340 | 79877.1631 | 5631340 |  | 70.5 |  | 0%
5 | 2019 | 71 | 71 |  | 71 |  | 5458150 | 76875.3521 | 5458150 |  | 71 |  | 0.7092%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 1.278%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y |  | Year
[6 empty] | Constant: |  | 67.4 |  | 1 | 67.5 |  | 2011 | Actual
[6 empty] | X Coefficient: |  | 0.8 |  | 2 | 69.5 |  | 2012 | Actual
[6 empty] | R^2: |  | 0.82051 |  | 3 | 70.5 |  | 2013 | Actual
[10 empty] | 4 | 70.5 |  | 2014 | Actual
[10 empty] | 5 | 71 |  | 2015 | Actual
[10 empty] | 10 | 75.4 |  | Hist TY + 5 yrs
HISTORIC
|  |  |  | Five year growth per regression equation: | [6 empty] | 4.4 | ERCs

## F-9 (3)
Equivalent Residential Connections - Water | [8 empty] | Florida Public Service Commission
Company: Utilities, Inc. of Florida - Lake Utilities Services - Lake Saunders | [8 empty] | Schedule F-9
Docket No.: 20200139-WS | [8 empty] | Page 3 of 3
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | 40 | 39 |  | 39.5 |  | 2284430 | 57833.6709 | 2284430 |  | 39.5
2 | 2016 | 39 | 42 |  | 40.5 |  | 2572130 | 63509.3827 | 2572130 |  | 40.5 |  | 2.532%
3 | 2017 | 42 | 42 |  | 42 |  | 2252461 | 53630.0238 | 2252461 |  | 42 |  | 3.704%
4 | 2018 | 42 | 43 |  | 42.5 |  | 2322380 | 54644.2353 | 2322380 |  | 42.5 |  | 1.19%
5 | 2019 | 43 | 45 |  | 44 |  | 2699060 | 61342.2727 | 2699060 |  | 44 |  | 3.529%
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 2.739%
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y |  | Year
[6 empty] | Constant: |  | 38.4 |  | 1 | 39.5 |  | 2011 | Actual
[6 empty] | X Coefficient: |  | 1.1 |  | 2 | 40.5 |  | 2012 | Actual
[6 empty] | R^2: |  | 0.98374 |  | 3 | 42 |  | 2013 | Actual
[10 empty] | 4 | 42.5 |  | 2015 | Actual
[10 empty] | 5 | 44 |  | 2015 | Actual
[10 empty] | 10 | 49.4 |  | Hist TY + 5 yrs
HISTORIC
|  |  |  | Five year growth per regression equation: | [6 empty] | 5.4 | ERCs

## F-10
Equivalent Residential Connections - Wastewater | [8 empty] | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [8 empty] | Schedule F-10
Docket No.: 20200139-WS | [8 empty] | Page 1 of 2
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
LAKE GROVE PLANT
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | 3164 | 3325 |  | 3244.5 |  | 348872774 | 107527.4384 | 369110368 |  | 3432.7086 |  |  |  |  | 107527.4384 | 8960.6199
2 | 2016 | 3325 | 3328 |  | 3326.5 |  | 357534935 | 107480.8162 | 380237455 |  | 3537.7239 |  | 3.059%
3 | 2017 | 3328 | 3472 |  | 3400 |  | 374595333 | 110175.0979 | 397785893 |  | 3610.4882 |  | 2.057%
4 | 2018 | 3472 | 3706 |  | 3589 |  | 419172184 | 116793.5871 | 446164554 |  | 3820.1117 |  | 5.806%
5 | 2019 | 3706 | 4173 |  | 3939.5 |  | 490222001 | 124437.6192 | 515142391 |  | 4139.7641 |  | 8.368% |  | 199.548 | 340.925 | 28.4104 | 0.38573
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 4.822%
NOTE: The above history of gallons is the gallons used by wastewater customers, not the gallons billed (and capped). Gallons billed was not used because
there is not a history readily available. Also, gallons billed reflects an arbitrary cap and is not necessarily indicative of gallons treated.
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y |  | Year
[6 empty] | Constant: |  | 3199.2097 |  | 1 | 3432.7086 |  | 2011 | Actual
[6 empty] | X Coefficient: |  | 169.6499 |  | 2 | 3537.7239 |  | 2012 | Actual
[6 empty] | R^2: |  | 0.91871 |  | 3 | 3610.4882 |  | 2013 | Actual
[10 empty] | 4 | 3820.1117 |  | 2014 | Actual | 0.0567
[10 empty] | 5 | 4139.7641 |  | 2015 | Actual | 1.3175
[10 empty] | 10 | 4895.7085 |  | Hist TY + 5 yrs
HISTORIC
|  |  |  | Five year growth per regression equation: | [6 empty] | 755.9443 | ERCs |  | 1.3182
|  |  |  | Five year growth per 5% per year maximum | [6 empty] | 1143.7405 | ERCs

## F-10 (2)
Equivalent Residential Connections - Wastewater | [8 empty] | Florida Public Service Commission
Company: Utilities Inc. of Florida - Lake Utilities Services. Excl. Four Lakes & Lake Saunders | [8 empty] | Schedule F-10
Docket No.: 20200139-WS | [8 empty] | Page 2 of 2
Historical Year Ended: December 31, 2019 | [8 empty] | Preparer: Seidman, F.
BARRINGTON PLANT
Explanation: Provide the following information in order to calculate the average growth in ERCs for the last
five years, including the test year. If the utility does not have single-family residential (SFR) customers,
the largest customer class should be used as a substitute.
| (1) | (2) | (3) |  | (4) |  | (5) | (6) | (7) |  | (8) |  | (9)
|  | SFR Customers |  |  |  |  | SFR | Gallons/ | Total |  | Total |  | Annual
Line | [6 empty] | Gallons | SFR | Gallons |  | ERCs |  | % Incr.
No. | Year | Beginning | Ending |  | Average |  | Sold | (5)/(4) | Sold |  | (7)/(6) |  | in ERCs
1 | 2015 | N/A | N/A |  | N/A |  | N/A | N/A | N/A
2 | 2016 | N/A | N/A |  | N/A |  | N/A | N/A | N/A
3 | 2017 | N/A | N/A |  | N/A |  | N/A | N/A | N/A
4 | 2018 | N/A | N/A |  | N/A |  | N/A | N/A | N/A
5 | 2019 | 148 | 148 |  | 148 |  | 23993256 | 162116.5946 | 23993256 |  | 148 |  |  |  | 13509.75
[9 empty] | Average Growth Through 5-Year Period (Col. 8) |  |  |  | 0%
NOTE: LUSI took over operation in March, 2019. There is no data available for prior periods, however, this is a stable, residential
community. Gallons reflected are 8 months actual, then annualized.
Regression Analysis per Rule 25-30.431(2)(C)
[10 empty] | X | Y |  | Year
[6 empty] | Constant: |  | #DIV/0! |  | 1 | 0 |  | 2011 | Actual
[6 empty] | X Coefficient: |  | #DIV/0! |  | 2 | 0 |  | 2012 | Actual
[6 empty] | R^2: |  | #DIV/0! |  | 3 | 0 |  | 2013 | Actual
[10 empty] | 4 | 0 |  | 2014 | Actual
[10 empty] | 5 | 148 |  | 2015 | Actual
[10 empty] | 10 | #DIV/0! |  | Hist TY + 5 yrs
HISTORIC
|  |  |  | Five year growth per regression equation: | [6 empty] | N/A | ERCs
|  |  |  | Five year growth per 5% per year maximum | [6 empty] | N/A | ERCs

## WComb2019 (hidden)
Lake Utility Services North & South
251/066 (628-I, 628-II) 251/004 (631), 251/175 (632), 251/426 (633), 251/224 (634), 251/462 (636), 251/082 (661), 251/086 (662), 251/085 (665), 251/333 (666), 251/038 (667), 251/038 (668), 251/248 (675)
PWS ID No. Varies - see system headings
CUP No. 2700
FDEP Permitted Max Day Capacity of Plants:
Lake Louisa 2.520 MGD | Amber Hill 0.468 MGD |  | Lake Groves 6.0 MGD
The Vistas 0.822 MGD | Lake Ridge 0.396 MGD
CR 561 2.592 MGD | Clermont I 0.115 MGD
Crescent Bay 0.396 MGD | Clermont II 0.071 MGD
Hyper Links'!A1
Water Loss-Use'!A1
251/066 (628I & 628II) Clermont I & II LUSI North
PWS ID No. 3354883
Permitted Capacity of Plant: Clermont I - .115 mgd, Clermont II - .071
Total Water Used/Loss
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Billed Consumption | Pumped + Source Mtr Error (-) Gals Loss/Use
2019-01-01 | 0.335 | 0.010806 | 0.035 | 0.00062 | 0 | 0.00062 | 2.3463 | 0.33438
February | 0.283 | 0.010107 | 0.033 | 0.01556 | 0 | 0.01556 | 2.3162 | 0.26744
March | 0.879 | 0.028355 | 0.06 | 0.00062 | 0 | 0.00062 | 3.4536 | 0.87838
April | 0.906 | 0.0302 | 0.062 | 0.0021 | 0 | 0.0021 | 3.0217 | 0.9039
May | 1.709 | 0.055129 | 0.252 | 0.00692 | 0 | 0.00692 | 3.8883 | 1.7021
June | 1.063 | 0.035433 | 0.09325 | 0.00068 | 0.004194 | 0.004874 | 3.4333 | 1.0581
July | 0.5798 | 0.018703 | 0.11615 | 0.008204 | 0.0055 | 0.013704 | 2.8345 | 0.5661
August | 0.229 | 0.0073871 | 0.024 | 0.00206 | 0 | 0.00206 | 2.5624 | 0.22694
September | 0.908 | 0.030267 | 0.083 | 0.00294 | 0 | 0.00294 | 3.34 | 0.90506
October | 1.123 | 0.036226 | 0.0855 | 0.005712 | 0 | 0.005712 | 3.2467 | 1.1173
November | 0.992 | 0.033067 | 0.068 | 0.00224 | 0.006 | 0.00824 | 2.9019 | 0.98376
December | 0.501 | 0.0016452 | 0.104 | 0.00083 | 0 | 0.00083 | 2.7681 | 0.50017
YTD Total/Avg/Max | 9.5078 | 0.024777 | 0.252 | 0.048486 | 0.015694 | 0.06418 | 36.1129 | 9.4436
|  | Proof to Daily Flow |  |  |  | Water Loss/Use Proof
Clermont I LUSI North
PWS ID No. 3354883-7
Permitted Capacity of Plant: Clermont I - .115 mgd
|  |  |  | Total Water Used/Loss |  |  | Source Meter Error Adj. Clrmt I (04/19/17 +0.66%) (03/09/18 -0.67%) |  |  |  |  | Source Meter Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Meter Error % | Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  |  |  | Meter Error % | Pumped Meter Error
2019-01-01 | 0.31 | 0.01 | 0.029 | 0.00031 | 0 | 0.00031 | -0.67% | -0.002077 | 0.30761 |  |  | 03/01-03/26/19 | -0.67% | -0.0036984
February | 0.241 | 0.0086071 | 0.0265 | 0.00028 | 0 | 0.00028 | -0.67% | -0.0016147 | 0.23911 |  |  | 03/27-03/31/19 | 1.58% | 0.0028282
March | 0.731 | 0.023581 | 0.048 | 0.00031 | 0 | 0.00031 | -0.67% & 1.58% | -0.0008702 | 0.72982 |  |  |  |  | -0.0008702
April | 0.742 | 0.024733 | 0.047 | 0.0003 | 0 | 0.0003 | 1.58% | 0.011724 | 0.75342
May | 1.298 | 0.041871 | 0.122 | 0.00261 | 0 | 0.00261 | 1.58% | 0.020508 | 1.3159
June | 0.902 | 0.030067 | 0.075 | 0.00038 | 0.004194 | 0.004574 | 1.58% | 0.014252 | 0.91168
July | 0.421 | 0.013581 | 0.055 | 0.006894 | 0.005 | 0.011894 | 1.58% | 0.0066518 | 0.41576
August | 0.18 | 0.0058065 | 0.0175 | 0.00175 | 0 | 0.00175 | 1.58% | 0.002844 | 0.18109
September | 0.741 | 0.0247 | 0.061 | 0.00264 | 0 | 0.00264 | 1.58% | 0.011708 | 0.75007
October | 0.921 | 0.02971 | 0.0635 | 0.00146 | 0 | 0.00146 | 1.58% | 0.014552 | 0.93409
November | 0.871 | 0.029033 | 0.05 | 0.00194 | 0.006 | 0.00794 | 1.58% | 0.013762 | 0.87682
December | 0.45 |  | 0.086 | 0.00052 | 0 | 0.00052 | 1.58% | 0.00711 | 0.45659
YTD Total/Avg/Max | 7.808 | 0.021972 | 0.122 | 0.019394 | 0.015194 | 0.034588 |  | 0.098549
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
Clermont II LUSI North
PWS ID No. 3354883-8
Permitted Capacity of Plant: Clermont II - .071 mgd
|  |  |  | Total Water Used/Loss |  |  | Source Meter Error Adj. Clrmt II (04/19/17 +1.00%) (03/09/2019 -2.04%) |  |  |  |  | Source Meter Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Meter Error % | Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  |  |  | Meter Error % | Pumped Meter Error
2019-01-01 | 0.025 | 0.00080645 | 0.006 | 0.00031 | 0 | 0.00031 | -2.04% | -0.00051 | 0.02418 |  |  | 03/01-03/26/19 | -2.04% | -0.0021828
February | 0.042 | 0.0015 | 0.0065 | 0.01528 | 0 | 0.01528 | -2.04% | -0.0008568 | 0.025863 |  |  | 03/27-03/31/19 | 1.96% | 0.0008036
March | 0.148 | 0.0047742 | 0.012 | 0.00031 | 0 | 0.00031 | -2.04% & 1.96% | -0.0013792 | 0.14631 |  |  |  |  | -0.0013792
April | 0.164 | 0.0054667 | 0.015 | 0.0018 | 0 | 0.0018 | 1.96% | 0.0032144 | 0.16541
May | 0.411 | 0.013258 | 0.13 | 0.00431 | 0 | 0.00431 | 1.96% | 0.0080556 | 0.41475
June | 0.161 | 0.0053667 | 0.01825 | 0.0003 | 0 | 0.0003 | 1.96% | 0.0031556 | 0.16386
July | 0.1588 | 0.0051226 | 0.06115 | 0.00131 | 0.0005 | 0.00181 | 1.96% | 0.0031125 | 0.1601
August | 0.049 | 0.0015806 | 0.0065 | 0.00031 | 0 | 0.00031 | 1.96% | 0.0009604 | 0.04965
September | 0.167 | 0.0055667 | 0.022 | 0.0003 | 0 | 0.0003 | 1.96% | 0.0032732 | 0.16997
October | 0.202 | 0.0065161 | 0.022 | 0.004252 | 0 | 0.004252 | 1.96% | 0.0039592 | 0.20171
November | 0.121 | 0.0040333 | 0.018 | 0.0003 | 0 | 0.0003 | 1.96% | 0.0023716 | 0.12307
December | 0.051 | 0.0016452 | 0.018 | 0.00031 | 0 | 0.00031 | 1.96% | 0.0009996 | 0.05169
YTD Total/Avg/Max | 1.6998 | 0.0046364 | 0.13 | 0.029092 | 0.0005 | 0.029592 |  | 0.026356 | 1.6966
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
251/004 (631) Amber Hill LUSI North
PWS ID No. 3354883-6
Permitted Capacity of Plant: Amber Hill - .468 mgd
|  |  |  | Total Water Used/Loss |  |  |  | Source Meter Error Adj. (04/19/17+ 0.74%)(03/13/18 +2.25%) |  |  |  | Source Meter Error Adj.
| Total Pumped | Pumped Daily Avg. | Pumped Daily Max | Gallons Used | Gallons Loss | Total Used/ Loss | Billed Consumption | Meter Error % | Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  |  | Meter Error % | Pumped Meter Error
2019-01-01 | 0.069 | 0.0022258 | 0.034 | 0.00318 | 0 | 0.00318 | 10.0316 | 2.25% | 0.0015525 | 0.067373 |  | 03/01-03/26/19 | 2.25% | 0.0078975
February | 0.064 | 0.0022857 | 0.013 | 0.007468 | 0 | 0.007468 | 9.9754 | 2.25% | 0.00144 | 0.057972 |  | 03/27-03/31/19 | 1.96% | 0.00343
March | 0.526 | 0.016968 | 0.079 | 0.003286 | 0 | 0.003286 | 12.8232 | 2.25%&1.96% | 0.011328 | 0.53404 |  |  |  | 0.011328
April | 0.752 | 0.025067 | 0.083 | 0.00318 | 0 | 0.00318 | 12.7279 | 1.96% | 0.014739 | 0.76356
May | 1.018 | 0.032839 | 0.22 | 0.023286 | 0 | 0.023286 | 15.815 | 1.96% | 0.019953 | 1.0147
June | 1.1895 | 0.03965 | 0.13 | 0.00318 | 0 | 0.00318 | 14.0532 | 1.96% | 0.023314 | 1.2096
July | 1.0595 | 0.034177 | 0.209 | 0.003286 | 0.0001 | 0.003386 | 12.6175 | 1.96% | 0.020766 | 1.0769
August | 0.255 | 0.0082258 | 0.05 | 0.012054 | 0 | 0.012054 | 11.8334 | 1.96% | 0.004998 | 0.24794
September | 0.588 | 0.0196 | 0.079 | 0.00323 | 0 | 0.00323 | 14.0056 | 1.96% | 0.011525 | 0.59629
October | 0.511 | 0.016484 | 0.085 | 0.007536 | 0 | 0.007536 | 14.2751 | 1.96% | 0.010016 | 0.51348
November | 0.069 | 0.0023 | 0.036 | 0.00518 | 0 | 0.00518 | 12.6533 | 1.96% | 0.0013524 | 0.065172
December | 0.001 | 3.2258e-05 | 0.001 | 0.003306 | 0 | 0.003306 | 10.6817 | 1.96% | 1.96e-05 | -0.0022864
YTD Total/Avg/Max | 6.102 | 0.018166 | 0.22 | 0.078172 | 0.0001 | 0.078272 | 151.4929 |  | 0.121 | 6.1447
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
251/224 (634) Lake Ridge Club LUSI North
PWS ID No. 3354883-5
Permitted Capacity of Plant: Lake Ridge Club - .396 mgd
|  |  |  | Total Water Used/Loss |  |  |  | Source Meter Error Adj. (04/19/17 +0.66%)(03/13/18 +0.5%) |  |  |  | Source Meter Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Billed Consumption | Meter Error % | Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  |  | Meter Error % | Pumped Meter Error
2019-01-01 | 1.526 | 0.049226 | 0.17 | 0.00318 | 0.0017 | 0.00488 | 1.9358 | 0.5% | 0.00763 | 1.5288 |  | 03/01-03/26/19 | 0.5% | 0.01052
February | 1.265 | 0.045179 | 0.13 | 0.010468 | 0.0148 | 0.025268 | 1.8845 | 0.5% | 0.006325 | 1.2461 |  | 03/27-03/31/19 | -3.45% | -0.018509
March | 2.6405 | 0.085177 | 0.18 | 0.003286 | 0 | 0.003286 | 2.6965 | 0.50%&-3.45% | -0.0079892 | 2.6292 |  |  |  | -0.0079892
April | 2.7745 | 0.092483 | 0.194 | 0.00318 | 0.0011 | 0.00428 | 2.5495 | -3.45% | -0.09572 | 2.6745
May | 5.121 | 0.16519 | 0.389 | 0.003286 | 0 | 0.003286 | 3.1646 | -3.45% | -0.17667 | 4.941
June | 3.548 | 0.11827 | 0.275 | 0.00318 | 0.001 | 0.00418 | 2.8739 | -3.45% | -0.12241 | 3.4214
July | 2.53 | 0.081613 | 0.313 | 0.003286 | 0 | 0.003286 | 2.2986 | -3.45% | -0.087285 | 2.4394
August | 1.85 | 0.059677 | 0.118 | 0.005046 | 0 | 0.005046 | 2.0344 | -3.45% | -0.063825 | 1.7811
September | 2.806 | 0.093533 | 0.242 | 0.00318 | 0 | 0.00318 | 2.601 | -3.45% | -0.096807 | 2.706
October | 3.86 | 0.12452 | 0.238 | 0.007196 | 0 | 0.007196 | 2.6991 | -3.45% | -0.13317 | 3.7196
November | 3.872 | 0.12907 | 0.354 | 0.00318 | 0 | 0.00318 | 2.4861 | -3.45% | -0.13358 | 3.7352
December | 2.354 | 0.075935 | 0.214 | 0.003286 | 0 | 0.003286 | 2.0662 | -3.45% | -0.081213 | 2.2695
YTD Total/Avg/Max | 34.147 | 0.093322 | 0.389 | 0.051754 | 0.0186 | 0.070354 | 29.2903 |  | -0.98472 | 33.0919
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
251/462 (636) The Vistas LUSI North
PWS ID No. 3354883-3 |  | Well#2
Permitted Capacity of Plant: .822 mgd
|  |  |  | Total Water Used/Loss |  |  |  | Source Meter Error Adj. (04/19/17 +0.50%)(03/09/18 -1.52%) |  |  |  | Source Meter Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Billed Consumption | Meter Error % | Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  |  | Meter Error % | Pumped Meter Error
2019-01-01 | 2.969 | 0.095774 | 0.222 | 0.032398 | 0.003 | 0.035398 | 13.2512 | -1.52% | -0.045129 | 2.8885 |  | 03/01-03/26/19 | -1.52% | -0.082794
February | 5.572 | 0.199 | 0.637 | 0.008064 | 0.03 | 0.038064 | 11.8103 | -1.52% | -0.084694 | 5.4492 |  | 03/27-03/31/19 | -2.04% | -0.026377
March | 6.74 | 0.21742 | 0.568 | 0.008928 | 0 | 0.008928 | 14.6339 | -1.52%&-2.04% | -0.10917 | 6.6219 |  |  |  | -0.10917
April | 6.906 | 0.2302 | 0.609 | 0.00964 | 0 | 0.00964 | 14.3274 | -2.04% | -0.14088 | 6.7555
May | 6.952 | 0.22426 | 0.439 | 0.029428 | 0 | 0.029428 | 17.0265 | -2.04% | -0.14182 | 6.7808
June | 2.453 | 0.081767 | 0.248 | 0.00864 | 0 | 0.00864 | 14.9657 | -2.04% | -0.050041 | 2.3943
July | 2.967 | 0.09571 | 0.332 | 0.008928 | 0 | 0.008928 | 14.0828 | -2.04% | -0.060527 | 2.8975
August | 2.901 | 0.093581 | 0.23 | 0.034045 | 0 | 0.034045 | 13.2368 | -2.04% | -0.05918 | 2.8078
September | 4.785 | 0.1595 | 0.444 | 0.00879 | 0 | 0.00879 | 15.1714 | -2.04% | -0.097614 | 4.6786
October | 5.34 | 0.17226 | 0.374 | 0.009618 | 0 | 0.009618 | 15.2878 | -2.04% | -0.10894 | 5.2214
November | 3.283 | 0.10943 | 0.207 | 0.01479 | 0 | 0.01479 | 13.6335 | -2.04% | -0.066973 | 3.2012
December | 3.48 | 0.11226 | 0.254 | 0.008968 | 0 | 0.008968 | 12.3076 | -2.04% | -0.070992 | 3.4
YTD Total/Avg/Max | 54.348 | 0.15263 | 0.637 | 0.18224 | 0.033 | 0.21524 | 169.7349 |  | -1.036 | 53.0968
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
251/082 (661) Crescent Bay LUSI North
PWS ID No. 3354883-9
Permitted Capacity of Plant: Crescent Bay - .396 mgd
|  |  |  | Total Water Used/Loss |  |  |  | Source Meter Error Adj. (04/19/17 +2.21%)(03/09/18 +1.0%) |  |  |  | Source Meter Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Billed Consumption | Meter Error % | Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  |  | Meter Error % | Pumped Meter Error
2019-01-01 | 0.001 | 3.2258e-05 | 0.001 | 0.00714 | 0 | 0.00714 | 0.81922 | 1% | 1e-05 | -0.00613 |  | 03/01-03/26/19 | 1% | 0.00028
February | 0.007 | 0.00025 | 0.004 | 0.00705 | 0 | 0.00705 | 0.74374 | 1% | 7e-05 | 2e-05 |  | 03/27-03/31/19 | -3.45% | -0.000345
March | 0.038 | 0.0012258 | 0.005 | 0.01259 | 0 | 0.01259 | 0.9951 | 1%&-3.45% | -6.5e-05 | 0.025345 |  |  |  | -6.5e-05
April | 0.288 | 0.0096 | 0.041 | 0.01292 | 0 | 0.01292 | 1.0919 | -3.45% | -0.009936 | 0.26514
May | 1.032 | 0.03329 | 0.237 | 0.00723 | 0 | 0.00723 | 1.2344 | -3.45% | -0.035604 | 0.98917
June | 2.445 | 0.0815 | 0.265 | 0.00703 | 0 | 0.00703 | 1.0349 | -3.45% | -0.084352 | 2.3536
July | 0.727 | 0.023452 | 0.19 | 0.00727 | 0 | 0.00727 | 0.96182 | -3.45% | -0.025081 | 0.69465
August | 0.009 | 0.00029032 | 0.005 | 0.00846 | 0 | 0.00846 | 0.87444 | -3.45% | -0.0003105 | 0.0002295
September | 0.215 | 0.0071667 | 0.042 | 0.09353 | 0.1 | 0.19353 | 0.9722 | -3.45% | -0.0074175 | 0.014053
October | 0.221 | 0.007129 | 0.048 | 0.00731 | 0 | 0.00731 | 0.98269 | -3.45% | -0.0076245 | 0.20607
November | 0.079 | 0.0026333 | 0.018 | 0.00697 | 0 | 0.00697 | 0.94295 | -3.45% | -0.0027255 | 0.069305
December | 0.03 | 0.00096774 | 0.013 | 0.00719 | 0 | 0.00719 | 0.86217 | -3.45% | -0.001035 | 0.021775
YTD Total/Avg/Max | 5.092 | 0.015143 | 0.265 | 0.18469 | 0.1 | 0.28469 | 11.5156 |  | -0.17407
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
251/333 Preston Cove; 251/038 Sth Clermont West ; 251/038 Lake Louisa
Permitted Capacity of Plant: N/A
Preston Cove Billed Consumption
2019-01-01 | 1.0364
February | 1.0343
March | 1.4196
April | 1.5553
May | 1.8357
June | 1.0589
July | 0.9859
August | 1.1469
September | 1.5389
October | 1.5543
November | 1.2978
December | 1.0412
YTD Total | 15.505
251/248 - LUSI South
PWS ID No. 3354881
CUP No. 2879 | Exp. 3/9/15
Permitted Max Day Capacity - 6.00 MGD
|  |  |  | Total Water Used/Loss |  |  |  | Source Meter Error Adj. | [8 empty] | Source Meter Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Billed Consumption | LG 1 % (03/06/17 +2.31%) (03/07/18 -0.65% | LG 1 Pumped Meter Error Adj. | LG 2 % (03/06/17 +0.50%) (03/07/18 +0.40%) | LG 2 Pumped Meter Error Adj. | LG 3 % (03/06/17 -1.83%) (03/07/18 -0.43%) | LG 3 Pumped Meter Error Adj. | Total Pumped Meter Error | Pumped + Source Mtr Error (-) Gals Loss/Use |  | LG 1 (03/07/18 -0.65% ) 03/26/19 -0.26% | LG 1 Pumped Meter Error Adj. | LG 2 (03/07/18 +0.40%)03/26/19 0.60% | LG 2 Pumped Meter Error Adj. | LG 3 (03/07/18 -0.43%)03/26/19 0.99% | LG 3 Pumped Meter Error Adj.
2019-01-01 | 70.144 | 2.2627 | 2.783 | 0.10247 | 0 | 0.10247 | 38.1695 | -0.65% | -0.26521 | 0.4% | 0.11737 | -0.43% | 0 | -0.14785 | 69.8937 |  | 0.65% | 0.23735 | 0.4% | 0.10807 | -0.43% | -8.6e-05 | 03/01-03/26/19
February | 61.003 | 2.1787 | 2.871 | 0.13529 | 0.001 | 0.13629 | 35.9131 | -0.65% | -0.22926 | 0.4% | 0.10262 | -0.43% | -0.0003311 | -0.12697 | 60.7397 |  | -0.26% | -0.018723 | 0.6% | 0.031944 | 0.99% | 0 | 03/27-03/31/19
March | 76.078 | 2.4541 | 3.128 | 0.11231 | 0.0017 | 0.11401 | 43.5359 | 0.65%&-0.26% | 0.21862 | 0.40%&0.60% | 0.14002 | -0.43%&0.99% | -8.6e-05 | 0.35855 | 76.3225 |  |  | 0.21862 |  | 0.14002 |  | -8.6e-05
April | 72.561 | 2.4187 | 2.993 | 0.12107 | 0.012948 | 0.13401 | 43.7642 | -0.26% | -0.1085 | 0.6% | 0.18471 | 0.99% | 0.0004455 | 0.076655 | 72.5036
May | 87.861 | 2.8342 | 4.384 | 0.044113 | 0 | 0.044113 | 49.5694 | -0.26% | -0.13162 | 0.6% | 0.22324 | 0.99% | 0.0002871 | 0.091904 | 87.9088
June | 82.121 | 2.7374 | 4.532 | 1.2062 | 0 | 1.2062 | 48.0278 | -0.26% | -0.08528 | 0.6% | 0.14032 | 0.99% | 0.25676 | 0.31179 | 81.2266
July | 75.05 | 2.421 | 3.857 | 0.097288 | 0.0515 | 0.14879 | 44.1698 | -0.26% | -8.32e-05 | 0.6% | 0.000114 | 0.99% | 0.74249 | 0.74252 | 75.6437
August | 76.139 | 2.4561 | 3.107 | 2.2989 | 0.0485 | 2.3474 | 43.7825 | -0.26% | -4.68e-05 | 0.6% | 3.6e-05 | 0.99% | 0.75354 | 0.75353 | 74.5451
September | 87.636 | 2.9212 | 4.042 | 0.16159 | 0 | 0.16159 | 49.8645 | -0.26% | 0 | 0.6% | 0 | 0.99% | 0.8676 | 0.8676 | 88.342
October | 97.091 | 3.132 | 4.078 | 0.2953 | 0 | 0.2953 | 55.6774 | -0.26% | -0.0056706 | 0.6% | 0.0105 | 0.99% | 0.92228 | 0.92711 | 97.7228
November | 90.296 | 3.0099 | 3.733 | 0.25932 | 0 | 0.25932 | 48.4325 | -0.26% | -2.34e-05 | 0.6% | 3.6e-05 | 0.99% | 0.89378 | 0.89379 | 90.9305
December | 76.162 | 2.4568 | 3.594 | 0.23054 | 0 | 0.23054 | 44.0529 | -0.26% | -0.012392 | 0.6% | 0.020736 | 0.99% | 0.67261 | 0.68095 | 76.6124
YTD Total/Avg/Max | 952.142 | 2.6069 | 4.532 | 5.0644 | 0.11565 | 5.1801 | 544.9597 |  | -0.61947 |  | 0.93969 |  | 5.1094 | 5.4296 | 952.3915
| 0 | Proof to Daily Flow |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
251/038 (667) Sth Clermont West ; 251/038 (668) Lake Louisa
251/038 - Lake Louisa
PWS ID No. 3354883-2
Permitted Max Day Capacity - 2.520 MGD
|  |  |  | Total Water Used/Loss |  |  |  |  | Billing |  |  | Source Meter Error
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used Vistas 1 & 3 | Gallons Used The Orgs | Gallons Loss Vistas 1 & 3 | Gallons Loss The Orgs | Total Used/ Loss | Billed Consumption Vistas 1 & 3 | Billed Consumption The Orgs | Total Consumption Billed | Well 1 (Vistas 1) Meter Error(03/09/18 -1.04%) 03/26/19 1.96% | Vistas 1 Pumped Meter Error Adj. | Well 3 (Vistas 3) Meter Error (03/09/18 -0.45%) 03/26/19 0.99% | Vistas 3 Pumped Meter Error Adj. | Oranges Meter Error (03/09/18 +1.63%) 03/26/19 1.32% | Oranges Pumped Meter Error Adj. | Total Pumped Meter Error Adj. | Pumped + Source Mtr Error, Less Gals Loss/ Use |  |  | Vistas Well 1 % | Vistas Well 1 Pump Adj | Vistas Well 3 % | Vistas Well 3 Pump Adj. | Oranges % | Oranges % Pump Adj.
2019-01-01 | 10.086 | 0.32535 | 0.398 | 0.019338 | 0.003286 | 0.001 | 0 | 0.023624 | 36.4354 | 0.51121 | 36.9466 | -1.04% | -0.10403 | -0.45% | -0.0002925 | 1.63% | 0.0002934 | -0.10403 | 9.9583 |  | 03/01-03/26/19 | 1.55% | 0.14128 | -0.7% | -0.000399 | -0.5% | -5e-05
February | 8.9 | 0.31786 | 0.42 | 0.016944 | 0.002968 | 0.0075 | 0 | 0.027412 | 35.0952 | 0.55762 | 35.6528 | -1.04% | -0.091416 | -0.45% | -0.000432 | 1.63% | 0.0002282 | -0.09162 | 8.781 |  | 03/27-03/31/19 | -1.04% | -9.36e-05 | -0.45% | -4.05e-05 | 1.63% | 4.89e-05
March | 11.585 | 0.37371 | 0.733 | 0.021378 | 0.004486 | 0.0016 | 0.0036 | 0.031064 | 45.7102 | 0.69899 | 46.4092 | & | 0.14119 | & | -0.0004395 | & | -1.1e-06 | 0.14075 | 11.6947 |  |  |  | 0.14119 |  | -0.0004395 |  | -1.1e-06
April | 10.174 | 0.32819 | 0.45 | 0.025492 | 0.00568 | 0 | 0 | 0.031172 | 47.9823 | 0.81962 | 48.8019 | 1.96% | 0.19814 | 0.99% | 0.0004554 | 1.32% | 0.0002508 | 0.19884 | 10.3417
May | 11.391 | 0.36745 | 1.158 | 0.008998 | 0.003286 | 0 | 0 | 0.012284 | 56.5544 | 0.98789 | 57.5423 | 1.96% | 0.189 | 0.99% | 0.017087 | 1.32% | 0.0002904 | 0.20638 | 11.5851
June | 16.709 | 0.539 | 0.951 | 0.03611 | 0.00318 | 0 | 0 | 0.03929 | 48.064 | 0.80702 | 48.871 | 1.96% | 0.050215 | 0.99% | 0.14006 | 1.32% | 0 | 0.19027 | 16.86
July | 12.701 | 0.40971 | 1.097 | 0.10482 | 0.003286 | 0 | 0 | 0.1081 | 42.7258 | 0.7121 | 43.4379 | 1.96% | 0.15745 | 0.99% | 0.046154 | 1.32% | 7.92e-05 | 0.20368 | 12.7966
August | 10.702 | 0.34523 | 0.446 | 0.043858 | 0.00383 | 0.0005 | 0 | 0.048188 | 40.2366 | 0.68726 | 40.9239 | 1.96% | 0.20923 | 0.99% | 0.0001485 | 1.32% | 0.0001584 | 0.20954 | 10.8633
September | 12.271 | 0.40903 | 0.615 | 0.01686 | 0.00318 | 0 | 0 | 0.02004 | 48.2727 | 0.7325 | 49.0052 | 1.96% | 0.23561 | 0.99% | 0.0024354 | 1.32% | 5.28e-05 | 0.2381 | 12.4891
October | 6.594 | 0.21271 | 0.432 | 0.016638 | 0.003286 | 0 | 0 | 0.019924 | 48.4895 | 0.73644 | 49.226 | 1.96% | 0.12901 | 0.99% | 5.94e-05 | 1.32% | 7.92e-05 | 0.12915 | 6.7032
November | 3.163 | 0.10543 | 0.242 | 0.01556 | 0.00318 | 0 | 0 | 0.01874 | 42.8406 | 0.61411 | 43.4548 | 1.96% | 0.06176 | 0.99% | 1.98e-05 | 1.32% | 0.000132 | 0.061911 | 3.2062
December | 6.769 | 0.21835 | 0.482 | 0.015788 | 0.003286 | 0.024 | 0 | 0.043074 | 38.6657 | 0.53383 | 39.1995 | 1.96% | 0.13228 | 0.99% | 7.92e-05 | 1.32% | 0.0001584 | 0.13252 | 6.8584
YTD Total/Avg/Max | 121.045 | 0.32934 | 1.158 | 0.34178 | 0.042934 | 0.0346 | 0.0036 | 0.42292 | 531.0725 | 8.3986 | 539.4711 |  | 1.3084 |  | 0.20533 |  | 0.0017217 | 1.5155 | 122.1376
| 0 | Proof to Daily Flow |  |  |  |  | Orgs Water Loss/Use Proof | 0
[7 empty] | Vistas Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
CR 561 Highland Point 251/175, Crescent West 251/086, Lake Crescent Hills 251/085
PWS ID No. 3354883-11
Permitted Max Day Capacity - 2.592 MGD
|  |  |  | Total Water Used/Loss CR561 |  |  | Total Water Used/Loss Highland Point |  |  | Total Water Used/Loss Crescent West |  |  | Total Water Used/Loss Lake Crescent Hills |  |  |  | Billed Consumption |  |  |  | Source Meter Error Adjustments
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | CR561 Total Used/ Loss | Gallons Used | Gallons Loss | Highland Pt. Total Used/ Loss | Gallons Used | Gallons Loss | Crescent W. Total Used/ Loss | Gallons Used | Gallons Loss | Lk Crescent W. Total Used/ Loss | Total Water Use/ Loss | Highland Point | Crescent West | Lake Crescent Hills | Total Billed | HghlndPt Meter Adj. (03/09/18 -1.00% | HghlndPt Pumped Meter Adj. | HghlndPt Revised Pumped | CrsntWst Meter Adj. (03/09/18 +0.86%) | CrsntWst Pumped Meter Adj. Adj. | CrsntWst Revised Pumped | LkCrsntHls Meter Adj. (03/08/18 +1.50%) | LkCrsntHls Pumped Meter Adj. Adj. | LkCrsntHls Revised Pumped | Total Meter Adj. | Pumped + Source Mtr Error, Less Gals Loss/ Use |  | Highland Pt. % | Highland Pt Pumped Adj. | Crescent West % | Crescent West Pumped Adj. | Lake Crescent Hills % | Lake Crescent Hills Pumped Adj.
2019-01-01 | 33.695 | 1.0869 | 1.428 | 0.032278 | 0.00075 | 0.033028 | 0.00031 | 0 | 0.00031 | 0.02054 | 0 | 0.02054 | 0.00854 | 0 | 0.00854 | 0.062418 | 0.43754 | 0.89789 | 1.4337 | 2.7692 | -1% | -0.09729 | 9.6317 | 0.86% | 0.12511 | 14.6731 | 1.5% | 0.14127 | 9.5593 | 0.16909 | 33.8017 | 03/01-03/26/19 | -1% | -0.09959 | 0.86% | 0.1323 | 1.5% | 0.14628
February | 31.522 | 1.1258 | 1.463 | 0.028328 | 0.0075 | 0.035828 | 0.00028 | 0 | 0.00028 | 0.0006 | 0 | 0.0006 | 0.00028 | 0 | 0.00028 | 0.036988 | 0.43721 | 0.88005 | 1.3337 | 2.651 | -1% | -0.08979 | 8.8892 | 0.86% | 0.11841 | 13.8874 | 1.5% | 0.13161 | 8.9056 | 0.16023 | 31.6452 | 03/27-03/31/19 | 0.25% | 0.00548 | -0.67% | -0.022686 | 1.96% | 0.041807
March | 42.806 | 1.3808 | 2.316 | 0.031328 | 0 | 0.031328 | 0.00031 | 0 | 0.00031 | 0.00136 | 0.0025 | 0.00386 | 0.00127 | 0 | 0.00127 | 0.036768 | 0.58599 | 1.2882 | 1.7521 | 3.6263 | & | -0.09411 | 12.0569 | & | 0.10962 | 18.8796 | & | 0.18809 | 12.0731 | 0.20359 | 42.9728 |  |  | -0.09411 |  | 0.10962 |  | 0.18809
April | 44.943 | 1.4981 | 2.224 | 0.02984 | 0.00075 | 0.03059 | 0.0003 | 0.001 | 0.0013 | 0.00211 | 0 | 0.00211 | 0.00106 | 0 | 0.00106 | 0.03506 | 0.58569 | 1.4189 | 1.8717 | 3.8763 | -1% | -0.12785 | 12.6571 | 0.86% | 0.16994 | 19.9299 | 1.5% | 0.18597 | 12.584 | 0.22806 | 45.136
May | 50.466 | 1.6279 | 2.296 | 0.029028 | 0 | 0.029028 | 0.00031 | 0 | 0.00031 | 0.00253 | 0 | 0.00253 | 0.00087 | 0 | 0.00087 | 0.032738 | 0.69763 | 1.5433 | 2.2942 | 4.5352 | -1% | -0.14391 | 14.2471 | 0.86% | 0.19022 | 22.3092 | 1.5% | 0.20934 | 14.1653 | 0.25565 | 50.6889
June | 39.486 | 1.3162 | 2.477 | 0.03574 | 0 | 0.03574 | 0.0003 | 0 | 0.0003 | 0.0022 | 0 | 0.0022 | 0.00166 | 0 | 0.00166 | 0.0399 | 0.61579 | 1.3791 | 2.1192 | 4.1141 | -1% | -0.11296 | 11.183 | 0.86% | 0.14863 | 17.4306 | 1.5% | 0.16362 | 11.0716 | 0.19929 | 39.6454
July | 40.628 | 1.3106 | 1.705 | 0.036028 | 0 | 0.036028 | 0.00031 | 0 | 0.00031 | 0.002444 | 0 | 0.002444 | 0.003962 | 0 | 0.003962 | 0.042744 | 0.53837 | 1.1835 | 1.9113 | 3.6332 | -1% | -0.11634 | 11.5177 | 0.86% | 0.15263 | 17.9006 | 1.5% | 0.16869 | 11.4147 | 0.20498 | 40.7902
August | 36.242 | 1.1691 | 1.581 | 0.036328 | 0 | 0.036328 | 0.00031 | 0 | 0.00031 | 0.00409 | 0 | 0.00409 | 0.00561 | 0 | 0.00561 | 0.046338 | 0.52227 | 0.99923 | 1.6408 | 3.1623 | -1% | -0.10295 | 10.1921 | 0.86% | 0.13722 | 16.0932 | 1.5% | 0.14986 | 10.1409 | 0.18414 | 36.3798
September | 44.01 | 1.467 | 2.355 | 0.02479 | 0 | 0.02479 | 0.0003 | 0 | 0.0003 | 0.00229 | 0 | 0.00229 | 0.00133 | 0 | 0.00133 | 0.02871 | 0.68901 | 1.3606 | 2.0076 | 4.0572 | -1% | -0.12649 | 12.5225 | 0.86% | 0.16613 | 19.4831 | 1.5% | 0.18066 | 12.2247 | 0.2203 | 44.2016
October | 44.092 | 1.4223 | 2.533 | 0.022828 | 0 | 0.022828 | 0.00046 | 0 | 0.00046 | 0.00395 | 0 | 0.00395 | 0.00163 | 0 | 0.00163 | 0.028868 | 0.82781 | 1.623 | 2.017 | 4.4678 | -1% | -0.12795 | 12.667 | 0.86% | 0.16552 | 19.4125 | 1.5% | 0.18075 | 12.2308 | 0.21832 | 44.2815
November | 39.963 | 1.3321 | 1.854 | 0.02454 | 0 | 0.02454 | 0.0003 | 0 | 0.0003 | 0.00282 | 0 | 0.00282 | 0.00192 | 0 | 0.00192 | 0.02958 | 0.6716 | 1.3226 | 1.77 | 3.7643 | -1% | -0.11603 | 11.487 | 0.86% | 0.15046 | 17.6455 | 1.5% | 0.16298 | 11.028 | 0.1974 | 40.1308
December | 35.265 | 1.1376 | 1.563 | 0.025128 | 0 | 0.025128 | 0.00031 | 0 | 0.00031 | 0.00304 | 0 | 0.00304 | 0.00197 | 0 | 0.00197 | 0.030448 | 0.51453 | 0.7997 | 1.6059 | 2.9202 | -1% | -0.1012 | 10.0188 | 0.86% | 0.13348 | 15.6545 | 1.5% | 0.14436 | 9.7684 | 0.17664 | 35.4112
YTD Total/Avg/Max | 483.118 | 1.3229 | 2.533 | 0.35618 | 0.009 | 0.36518 | 0.0038 | 0.001 | 0.0048 | 0.047974 | 0.0025 | 0.050474 | 0.030102 | 0 | 0.030102 | 0.45056 | 7.1234 | 14.6961 | 21.7574 | 43.5769 |  | -1.3569 | 137.0701 |  | 1.7674 | 213.2994 |  | 2.0072 | 135.1662 | 2.4177 | 485.0851
| 0 | Proof to Daily Flow |  |  | CR561 WLU Proof | 0 |  | HP Water Loss/Use Proof | 0 |  | CW WLU Proof | 0 |  | LkCHls WLU Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input
COMBINED LUSI NORTH & SOUTH | [5 empty] | COMBINED LUSI NORTH & SOUTH
| Total Water Use/ Loss | Total Meter Adj. |  |  |  | Total Billed Consumption
2019-01-01 | 0.18771 | -0.12131 |  |  | 2019-01-01 | 104.9602
February | 0.27303 | -0.13769 |  |  | February | 99.6807
March | 0.17565 | 0.59475 |  |  | March | 126.1403
April | 0.19672 | 0.28669 |  |  | April | 128.6966
May | 0.14329 | 0.24836 |  |  | May | 150.7299
June | 1.2699 | 0.48527 |  |  | June | 135.0044
July | 0.22139 | 1.0088 |  |  | July | 122.2012
August | 2.4459 | 1.0327 |  |  | August | 116.9967
September | 0.39805 | 1.1507 |  |  | September | 137.219
October | 0.3555 | 1.0534 |  |  | October | 144.176
November | 0.32222 | 0.96731 |  |  | November | 126.6734
December | 0.30325 | 0.845 |  |  | December | 113.1322
YTD Total/Avg/Max | 6.2926 | 7.4139 |  |  | Total | 1505.6106

## FLOWCOMB2019 (hidden)
251/066 (660) - Lake Utility Services, Inc. | [9 empty] | Hyper Links'!A1
MWAF - link to AH(x)
251/066 (628I) Clermont I LUSI North | [9 empty] | Daily Max (mgd) |  | 0.115 | [18 empty] | 251/066 (628I) Clermont I LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0.029 | 0.015 | 0 | 0.0135 | 0.0135 | 0 | 0 | 0.012 | 0.009 | 0 | 0.027 | 0.027 | 0.017 | 0 | 0.025 | 0.012 | 0 | 0.0195 | 0.0195 | 0 | 0 | 0.013 | 0.009 | 0 | 0.015 | 0.015 | 0 | 0 | 0.012 | 0.007 |  | 0.31 | 0.01 | 0.029 | 0
February | 0 | 0.0175 | 0.0175 | 0 | 0 | 0.011 | 0.008 | 0 | 0.0185 | 0.0185 | 0 | 0 | 0.006 | 0.005 | 0 | 0.023 | 0.023 | 0 | 0.001 | 0.013 | 0.01 | 0 | 0.0265 | 0.0265 | 0.003 | 0 | 0.008 | 0.005 |  |  |  |  | 0.241 | 0.0086071 | 0.0265 | 0
March | 0 | 0.024 | 0.024 | 0 | 0 | 0.014 | 0.019 | 0.005 | 0.037 | 0.037 | 0.031 | 0 | 0.032 | 0.041 | 0.021 | 0.036 | 0.036 | 0.006 | 0.007 | 0.023 | 0.028 | 0.005 | 0.0385 | 0.0385 | 0.028 | 0.021 | 0.041 | 0.037 | 0.005 | 0.048 | 0.048 |  | 0.731 | 0.023581 | 0.048 | 0
April | 0 | 0.004 | 0.041 | 0.04 | 0.007 | 0.0265 | 0.0265 | 0.007 | 0.004 | 0.03 | 0.042 | 0.01 | 0.039 | 0.039 | 0.004 | 0.01 | 0.036 | 0.042 | 0.02 | 0.0245 | 0.0245 | 0.008 | 0.006 | 0.041 | 0.047 | 0.011 | 0.047 | 0.047 | 0.04 | 0.018 |  |  | 0.742 | 0.024733 | 0.047 | 0
May | 0.054 | 0.051 | 0.017 | 0.031 | 0.031 | 0.003 | 0.008 | 0.051 | 0.038 | 0.006 | 0.046 | 0.046 | 0.019 | 0.007 | 0.032 | 0.04 | 0.019 | 0.0505 | 0.0505 | 0.021 | 0.012 | 0.065 | 0.068 | 0.016 | 0.0705 | 0.0705 | 0.041 | 0.053 | 0.091 | 0.122 | 0.068 |  | 1.298 | 0.041871 | 0.122 | 0
June | 0.0735 | 0.0735 | 0.075 | 0.031 | 0.045 | 0.065 | 0.024 | 0.026 | 0.026 | 0.007 | 0.006 | 0.032 | 0 | 0 | 0.023 | 0.023 | 0 | 0 | 0.015 | 0.013 | 0 | 0.041 | 0.041 | 0.018 | 0.017 | 0.051 | 0.049 | 0.021 | 0.053 | 0.053 |  |  | 0.902 | 0.030067 | 0.075 | 0
July | 0.012 | 0.012 | 0.055 | 0.055 | 0 | 0.035 | 0.035 | 0 | 0.006 | 0.037 | 0 | 0 | 0 | 0 | 0.012 | 0.008 | 0.03 | 0.025 | 0 | 0.044 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011 |  | 0.421 | 0.013581 | 0.055 | 0
August | 0.013 | 0 | 0.004 | 0.004 | 0 | 0 | 0.006 | 0.001 | 0 | 0.0175 | 0.0175 | 0 | 0 | 0.012 | 0.01 | 0 | 0.0105 | 0.0105 | 0 | 0 | 0.011 | 0.014 | 0 | 0.0125 | 0.0125 | 0 | 0 | 0 | 0.01 | 0 | 0.014 |  | 0.18 | 0.0058065 | 0.0175 | 0
September | 0.014 | 0 | 0 | 0.006 | 0.015 | 0 | 0.0335 | 0.0335 | 0.015 | 0 | 0.03 | 0.032 | 0 | 0.0135 | 0.0135 | 0 | 0.009 | 0.043 | 0.047 | 0.016 | 0.0455 | 0.0455 | 0.03 | 0.018 | 0.056 | 0.061 | 0.022 | 0.061 | 0.061 | 0.02 |  |  | 0.741 | 0.0247 | 0.061 | 0
October | 0.017 | 0.054 | 0.051 | 0.025 | 0.0635 | 0.0635 | 0.04 | 0.006 | 0.032 | 0.045 | 0.008 | 0.052 | 0.052 | 0.02 | 0.015 | 0.044 | 0.045 | 0.016 | 0.0245 | 0.0245 | 0.004 | 0.006 | 0.045 | 0.045 | 0.005 | 0.015 | 0.015 | 0.003 | 0.017 | 0.034 | 0.034 |  | 0.921 | 0.02971 | 0.0635 | 0
November | 0.009 | 0.0375 | 0.0375 | 0.017 | 0.049 | 0.04 | 0.041 | 0.018 | 0.0245 | 0.0245 | 0.027 | 0.011 | 0.05 | 0.043 | 0.005 | 0.032 | 0.032 | 0.034 | 0.016 | 0.036 | 0.037 | 0.032 | 0.033 | 0.033 | 0.007 | 0.012 | 0.035 | 0.028 | 0.027 | 0.043 |  |  | 0.871 | 0.029033 | 0.05 | 0
December | 0.086 | 0.028 | 0.009 | 0.022 | 0.034 | 0.016 | 0.038 | 0.038 | 0.033 | 0.011 | 0.025 | 0.011 | 0.001 | 0.0085 | 0.0085 | 0 | 0 | 0.004 | 0.015 | 0 | 0.0115 | 0.0115 | 0 | 0 | 0.01 | 0.01 | 0 | 0.0095 | 0.0095 | 0 | 0 |  | 0.45 | 0.014516 | 0.086 | 0
[33 empty] | 7.808 | Grand Total
251/066 (628II) Clermont II LUSI North | [5 empty] | MWAF - link to AH(x) |  |  |  | Daily Max (mgd) |  | 0.071 | [18 empty] | 251/066 (628II) Clermont II LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0.006 | 0 | 0 | 0.0005 | 0.0005 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.005 | 0 | 0 | 0.004 | 0 | 0 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.025 | 0.00080645 | 0.006 | 0
February | 0 | 0.003 | 0.003 | 0 | 0.001 | 0 | 0 | 0 | 0.0035 | 0.0035 | 0 | 0 | 0.001 | 0 | 0 | 0.006 | 0.006 | 0 | 0.002 | 0 | 0 | 0 | 0.0065 | 0.0065 | 0 | 0 | 0 | 0 |  |  |  |  | 0.042 | 0.0015 | 0.0065 | 0
March | 0 | 0.0045 | 0.0045 | 0 | 0.001 | 0.002 | 0 | 0 | 0.009 | 0.009 | 0 | 0 | 0.011 | 0.012 | 0 | 0.0095 | 0.0095 | 0 | 0 | 0.004 | 0.006 | 0 | 0.0105 | 0.0105 | 0.004 | 0 | 0.012 | 0.006 | 0 | 0.0115 | 0.0115 |  | 0.148 | 0.0047742 | 0.012 | 0
April | 0 | 0.006 | 0.015 | 0.008 | 0 | 0.0045 | 0.0045 | 0.002 | 0.001 | 0.006 | 0.014 | 0 | 0.013 | 0.013 | 0 | 0 | 0.009 | 0.007 | 0 | 0.0045 | 0.0045 | 0 | 0.001 | 0.01 | 0.01 | 0.005 | 0.011 | 0.011 | 0.003 | 0.001 |  |  | 0.164 | 0.0054667 | 0.015 | 0
May | 0.015 | 0.012 | 0 | 0.0065 | 0.0065 | 0.001 | 0.006 | 0.001 | 0.009 | 0 | 0.0135 | 0.0135 | 0 | 0 | 0.01 | 0.007 | 0 | 0.0125 | 0.0125 | 0 | 0.001 | 0.014 | 0.028 | 0 | 0.0135 | 0.0135 | 0.006 | 0.005 | 0.03 | 0.044 | 0.13 |  | 0.411 | 0.013258 | 0.13 | 0
June | 0.01825 | 0.01825 | 0.0099 | 0 | 0.0143 | 0.0115 | 0.0005 | 0.00315 | 0.00315 | 0 | 0 | 0.0001 | 0.0056 | 0 | 0.0034 | 0.0034 | 0 | 0 | 0 | 0 | 0 | 0.0082 | 0.0082 | 0 | 0.0001 | 0.0169 | 0.0098 | 0 | 0.01315 | 0.01315 |  |  | 0.161 | 0.0053667 | 0.01825 | 0
July | 0 | 0 | 0.018 | 0.0112 | 0 | 0.06115 | 0.06115 | 0 | 0 | 0.0011 | 0.0008 | 0 | 0.00055 | 0.00055 | 0 | 0 | 0.0006 | 0.0003 | 0 | 0.0009 | 0.0009 | 0.0001 | 0 | 0.0006 | 0 | 0 | 0.0003 | 0.0003 | 0 | 0.0001 | 0.0002 |  | 0.1588 | 0.0051226 | 0.06115 | 0
August | 0 | 0 | 0 | 0 | 0.001 | 0 | 0.003 | 0 | 0 | 0.0025 | 0.0025 | 0 | 0 | 0.005 | 0.003 | 0 | 0.0015 | 0.0015 | 0 | 0 | 0.005 | 0.005 | 0 | 0.0065 | 0.0065 | 0 | 0 | 0 | 0.004 | 0 | 0.002 |  | 0.049 | 0.0015806 | 0.0065 | 0
September | 0.002 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0.006 | 0 | 0.002 | 0.006 | 0.007 | 0 | 0.005 | 0.005 | 0 | 0 | 0.01 | 0.01 | 0 | 0.012 | 0.012 | 0 | 0 | 0.022 | 0.019 | 0 | 0.0215 | 0.0215 | 0 |  |  | 0.167 | 0.0055667 | 0.022 | 0
October | 0 | 0.022 | 0.02 | 0 | 0.0205 | 0.0205 | 0 | 0 | 0.011 | 0.001 | 0 | 0.0135 | 0.0135 | 0 | 0 | 0.016 | 0 | 0.013 | 0.0055 | 0.0055 | 0 | 0.001 | 0.009 | 0.006 | 0 | 0 | 0 | 0 | 0.003 | 0.01 | 0.011 |  | 0.202 | 0.0065161 | 0.022 | 0
November | 0 | 0.0085 | 0.0085 | 0 | 0.018 | 0.018 | 0.009 | 0 | 0.002 | 0.002 | 0 | 0.001 | 0.014 | 0.005 | 0 | 0.002 | 0.002 | 0 | 0 | 0.006 | 0 | 0 | 0.005 | 0.005 | 0 | 0 | 0.006 | 0 | 0 | 0.009 |  |  | 0.121 | 0.0040333 | 0.018 | 0
December | 0.018 | 0 | 0 | 0.004 | 0.005 | 0 | 0.0075 | 0.0075 | 0 | 0.001 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 |  | 0.051 | 0.0016452 | 0.018 | 0
[33 empty] | 1.6998 | Grand Total
251/004 (631) Amber Hill - LUSI North | [5 empty] | MWAF - link to AH(x) |  |  |  | Daily Max (mgd) |  | 0.468 | [18 empty] | 251/004 (631) Amber Hill - LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.069 | 0.0022258 | 0.034 | 0
February | 0 | 0 | 0.006 | 0.006 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.013 | 0.013 | 0 | 0.002 | 0 |  |  |  |  | 0.064 | 0.0022857 | 0.013 | 0
March | 0 | 0 | 0.0005 | 0.0005 | 0 | 0 | 0 | 0 | 0.029 | 0.027 | 0.027 | 0 | 0.036 | 0.032 | 0 | 0.068 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.062 | 0.0335 | 0.0335 | 0 | 0.053 | 0.01 | 0.001 | 0.079 | 0.032 |  | 0.526 | 0.016968 | 0.079 | 0
April | 0.032 | 0 | 0.083 | 0.067 | 0 | 0.052 | 0 | 0 | 0 | 0.031 | 0.006 | 0 | 0.042 | 0.027 | 0.027 | 0 | 0.051 | 0.025 | 0 | 0.001 | 0.007 | 0.007 | 0 | 0.07 | 0.067 | 0.001 | 0.061 | 0.0475 | 0.0475 | 0 |  |  | 0.752 | 0.025067 | 0.083 | 0
May | 0.101 | 0.071 | 0 | 0.075 | 0 | 0 | 0 | 0.068 | 0.062 | 0 | 0.087 | 0.0375 | 0.0375 | 0 | 0 | 0.002 | 0.001 | 0.036 | 0.015 | 0.015 | 0 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.11 | 0.22 | 0.013 |  | 1.018 | 0.032839 | 0.22 | 0
June | 0.06 | 0.0695 | 0.0695 | 0 | 0.116 | 0.121 | 0 | 0.068 | 0 | 0 | 0 | 0.001 | 0.063 | 0 | 0 | 0.0155 | 0.0155 | 0 | 0 | 0 | 0.001 | 0.081 | 0.0485 | 0.0485 | 0 | 0.13 | 0.109 | 0 | 0.111 | 0.0615 |  |  | 1.1895 | 0.03965 | 0.13 | 0
July | 0.0615 | 0 | 0.047 | 0.209 | 0 | 0.107 | 0.016 | 0.016 | 0 | 0.093 | 0.072 | 0 | 0 | 0.037 | 0.037 | 0 | 0.068 | 0 | 0 | 0.093 | 0.0545 | 0.0545 | 0.001 | 0.049 | 0 | 0 | 0 | 0.022 | 0.022 | 0 | 0 |  | 1.0595 | 0.034177 | 0.209 | 0
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0.042 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.042 | 0.05 | 0 | 0.026 | 0.021 | 0.021 | 0 | 0 | 0.031 | 0 | 0.001 |  | 0.255 | 0.0082258 | 0.05 | 0
September | 0 | 0 | 0 | 0 | 0 | 0 | 0.053 | 0.031 | 0.031 | 0 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047 | 0.018 | 0 | 0.029 | 0.0135 | 0.0135 | 0 | 0.079 | 0.078 | 0 | 0.072 | 0.039 | 0.039 |  |  | 0.588 | 0.0196 | 0.079 | 0
October | 0 | 0.085 | 0.067 | 0 | 0.081 | 0.034 | 0.034 | 0 | 0 | 0 | 0 | 0.032 | 0.0185 | 0.0185 | 0 | 0.063 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.001 | 0 | 0 | 0.012 | 0.003 | 0.001 |  | 0.511 | 0.016484 | 0.085 | 0
November | 0 | 0.004 | 0.0005 | 0.0005 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 |  |  | 0.069 | 0.0023 | 0.036 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.001 | 3.2258e-05 | 0.001 | 0
[33 empty] | 6.102 | Grand Total
251/224 Lake Ridge Club - LUSI North | [5 empty] | MWAF - link to AH(x) |  |  |  | Daily Max (mgd) |  | 0.396 | [18 empty] | 251/224 Lake Ridge Club - LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0.17 | 0.078 | 0 | 0 | 0.068 | 0.068 | 0 | 0.093 | 0.08 | 0 | 0.138 | 0.067 | 0.067 | 0 | 0.021 | 0.126 | 0 | 0.142 | 0.0205 | 0.0205 | 0 | 0.1 | 0.015 | 0 | 0.125 | 0.038 | 0.038 | 0 | 0.051 | 0 |  | 1.526 | 0.049226 | 0.17 | 0
February | 0 | 0.114 | 0.0225 | 0.0225 | 0 | 0.121 | 0.051 | 0 | 0.084 | 0.0445 | 0.0445 | 0 | 0.016 | 0 | 0 | 0.092 | 0.0645 | 0.0645 | 0 | 0.127 | 0.074 | 0 | 0.13 | 0.0695 | 0.0695 | 0 | 0.053 | 0.001 |  |  |  |  | 1.265 | 0.045179 | 0.13 | 0
March | 0 | 0.131 | 0.067 | 0.067 | 0 | 0.094 | 0.134 | 0.003 | 0.149 | 0.0915 | 0.0915 | 0.024 | 0.174 | 0.171 | 0.013 | 0.18 | 0.054 | 0.054 | 0.014 | 0.107 | 0.142 | 0 | 0.159 | 0.092 | 0.092 | 0 | 0.139 | 0.136 | 0.002 | 0.172 | 0.0875 |  | 2.6405 | 0.085177 | 0.18 | 0
April | 0.0875 | 0.002 | 0.023 | 0.154 | 0.017 | 0.163 | 0.0525 | 0.0525 | 0.005 | 0.126 | 0.156 | 0.002 | 0.131 | 0.079 | 0.079 | 0.051 | 0.139 | 0.194 | 0.049 | 0.048 | 0.087 | 0.087 | 0.02 | 0.154 | 0.191 | 0.014 | 0.171 | 0.167 | 0.167 | 0.106 |  |  | 2.7745 | 0.092483 | 0.194 | 0
May | 0.183 | 0.207 | 0.015 | 0.177 | 0.0705 | 0.0705 | 0.081 | 0.176 | 0.233 | 0.02 | 0.176 | 0.125 | 0.125 | 0 | 0.052 | 0.158 | 0.063 | 0.18 | 0.196 | 0.196 | 0.109 | 0.194 | 0.389 | 0.291 | 0.3 | 0.28 | 0.28 | 0.273 | 0.337 | 0.095 | 0.069 |  | 5.121 | 0.16519 | 0.389 | 0
June | 0.083 | 0.144 | 0.144 | 0.197 | 0.173 | 0.275 | 0.16 | 0.133 | 0.06 | 0.06 | 0.016 | 0.097 | 0.127 | 0 | 0.135 | 0.062 | 0.062 | 0 | 0.115 | 0.076 | 0.078 | 0.077 | 0.105 | 0.105 | 0.104 | 0.211 | 0.233 | 0.172 | 0.177 | 0.167 |  |  | 3.548 | 0.11827 | 0.275 | 0
July | 0.167 | 0.076 | 0.115 | 0.313 | 0 | 0.171 | 0.051 | 0.051 | 0.002 | 0.133 | 0.136 | 0 | 0.114 | 0.085 | 0.085 | 0.056 | 0.106 | 0.132 | 0 | 0.137 | 0.0845 | 0.0845 | 0.001 | 0.103 | 0.042 | 0 | 0.064 | 0.0575 | 0.0575 | 0 | 0.106 |  | 2.53 | 0.081613 | 0.313 | 0
August | 0.09 | 0 | 0.072 | 0.0605 | 0.0605 | 0.001 | 0.108 | 0.103 | 0 | 0.099 | 0.0645 | 0.0645 | 0 | 0.093 | 0.108 | 0 | 0.112 | 0.0575 | 0.0575 | 0 | 0.106 | 0.118 | 0 | 0.096 | 0.0605 | 0.0605 | 0 | 0.093 | 0.08 | 0 | 0.085 |  | 1.85 | 0.059677 | 0.118 | 0
September | 0.0565 | 0.0565 | 0 | 0.002 | 0.091 | 0 | 0.091 | 0.0625 | 0.0625 | 0 | 0.125 | 0.125 | 0 | 0.112 | 0.069 | 0.069 | 0.013 | 0.169 | 0.19 | 0.017 | 0.139 | 0.1355 | 0.1355 | 0.013 | 0.219 | 0.242 | 0.059 | 0.211 | 0.1705 | 0.1705 |  |  | 2.806 | 0.093533 | 0.242 | 0
October | 0.112 | 0.198 | 0.238 | 0.097 | 0.195 | 0.1445 | 0.1445 | 0.068 | 0.136 | 0.148 | 0.001 | 0.157 | 0.1235 | 0.1235 | 0.091 | 0.171 | 0.157 | 0.126 | 0.112 | 0.0725 | 0.0725 | 0.009 | 0.222 | 0.204 | 0.003 | 0.132 | 0.065 | 0.065 | 0.024 | 0.226 | 0.222 |  | 3.86 | 0.12452 | 0.238 | 0
November | 0.011 | 0.223 | 0.13 | 0.13 | 0.354 | 0.263 | 0.229 | 0.025 | 0.172 | 0.12 | 0.12 | 0 | 0 | 0.212 | 0 | 0.176 | 0.12 | 0.12 | 0.038 | 0.207 | 0.203 | 0.013 | 0.221 | 0.0895 | 0.0895 | 0.001 | 0.199 | 0.19 | 0 | 0.216 |  |  | 3.872 | 0.12907 | 0.354 | 0
December | 0.122 | 0.122 | 0.02 | 0.193 | 0.21 | 0 | 0.214 | 0.1325 | 0.1325 | 0.028 | 0.195 | 0.162 | 0 | 0.12 | 0.0775 | 0.0775 | 0.001 | 0.018 | 0 | 0 | 0.15 | 0.069 | 0.069 | 0 | 0.019 | 0.04 | 0 | 0.129 | 0.0265 | 0.0265 | 0 |  | 2.354 | 0.075935 | 0.214 | 0
[33 empty] | 34.147 | Grand Total
251/462 The Vistas Well #2 - LUSI North | [5 empty] | MWAF - link to AH(x) |  |  |  | Daily Max (mgd) |  | 0.822 | [18 empty] | 251/462 The Vistas Well #2 - LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0 | 0.179 | 0 | 0.125 | 0.169 | 0.006 | 0 | 0.172 | 0.127 | 0.05 | 0.144 | 0.219 | 0.081 | 0 | 0.135 | 0.18 | 0 | 0.174 | 0.192 | 0.013 | 0 | 0.186 | 0.137 | 0 | 0.146 | 0.222 | 0.017 | 0 | 0.146 | 0.149 |  | 2.969 | 0.095774 | 0.222 | 0
February | 0 | 0.157 | 0.276 | 0 | 0 | 0.213 | 0.259 | 0 | 0.167 | 0.267 | 0.045 | 0 | 0.222 | 0.173 | 0.007 | 0.174 | 0.385 | 0.368 | 0.049 | 0.291 | 0.319 | 0.09 | 0.19 | 0.637 | 0.541 | 0.173 | 0.214 | 0.355 |  |  |  |  | 5.572 | 0.199 | 0.637 | 0
March | 0.072 | 0.191 | 0.499 | 0.265 | 0.186 | 0.239 | 0.076 | 0 | 0.407 | 0.324 | 0.421 | 0.072 | 0.198 | 0.314 | 0.095 | 0.222 | 0.22 | 0.059 | 0 | 0.116 | 0.331 | 0 | 0.127 | 0.354 | 0.568 | 0.091 | 0.13 | 0.368 | 0.142 | 0.151 | 0.502 |  | 6.74 | 0.21742 | 0.568 | 0
April | 0.414 | 0.081 | 0.252 | 0.335 | 0.353 | 0.125 | 0.298 | 0.131 | 0.036 | 0.154 | 0.235 | 0.251 | 0.265 | 0.222 | 0.168 | 0 | 0.247 | 0.247 | 0.061 | 0.129 | 0.205 | 0.208 | 0.136 | 0.201 | 0.464 | 0.35 | 0.163 | 0.609 | 0.376 | 0.19 |  |  | 6.906 | 0.2302 | 0.609 | 0
May | 0.43 | 0.304 | 0.129 | 0.258 | 0.179 | 0.061 | 0.003 | 0.283 | 0.216 | 0.271 | 0.327 | 0.439 | 0.162 | 0.031 | 0.183 | 0.268 | 0.01 | 0.206 | 0.334 | 0.286 | 0.25 | 0.379 | 0.346 | 0.164 | 0.237 | 0.263 | 0.061 | 0.069 | 0.157 | 0.346 | 0.3 |  | 6.952 | 0.22426 | 0.439 | 0
June | 0.131 | 0.248 | 0.247 | 0.044 | 0.145 | 0.108 | 0.039 | 0.093 | 0.075 | 0 | 0 | 0.04 | 0.087 | 0 | 0.076 | 0.078 | 0 | 0 | 0.051 | 0.014 | 0 | 0.097 | 0.095 | 0.029 | 0 | 0.156 | 0.212 | 0.066 | 0.158 | 0.164 |  |  | 2.453 | 0.081767 | 0.248 | 0
July | 0.022 | 0 | 0.019 | 0.27 | 0 | 0.138 | 0.096 | 0 | 0 | 0.136 | 0.109 | 0.058 | 0.111 | 0.262 | 0 | 0 | 0.248 | 0.151 | 0.019 | 0.134 | 0.332 | 0.022 | 0 | 0.249 | 0.113 | 0.024 | 0 | 0.271 | 0 | 0 | 0.183 |  | 2.967 | 0.09571 | 0.332 | 0
August | 0.112 | 0 | 0.081 | 0.166 | 0 | 0 | 0.2 | 0.128 | 0 | 0.163 | 0.156 | 0 | 0.001 | 0.123 | 0.149 | 0.02 | 0.145 | 0.109 | 0.052 | 0 | 0.178 | 0.174 | 0 | 0.206 | 0.23 | 0 | 0.046 | 0.088 | 0.198 | 0.034 | 0.142 |  | 2.901 | 0.093581 | 0.23 | 0
September | 0.179 | 0 | 0 | 0.105 | 0.096 | 0.025 | 0.193 | 0.212 | 0.103 | 0 | 0.176 | 0.222 | 0 | 0.201 | 0.18 | 0.007 | 0.006 | 0.19 | 0.204 | 0.004 | 0.108 | 0.312 | 0.101 | 0.155 | 0.307 | 0.404 | 0.374 | 0.262 | 0.215 | 0.444 |  |  | 4.785 | 0.1595 | 0.444 | 0
October | 0.115 | 0.212 | 0.231 | 0.275 | 0.374 | 0.315 | 0.196 | 0 | 0.131 | 0.141 | 0.107 | 0.188 | 0.245 | 0.189 | 0.087 | 0.303 | 0.254 | 0.159 | 0.14 | 0.14 | 0.233 | 0.064 | 0.201 | 0.165 | 0.135 | 0.129 | 0.133 | 0.082 | 0.089 | 0.121 | 0.186 |  | 5.34 | 0.17226 | 0.374 | 0
November | 0.196 | 0.158 | 0.207 | 0.15 | 0.004 | 0.177 | 0.196 | 0.101 | 0.129 | 0.122 | 0.037 | 0.082 | 0.169 | 0.118 | 0.061 | 0.128 | 0.12 | 0.025 | 0.003 | 0.146 | 0.152 | 0.004 | 0.14 | 0.188 | 0.017 | 0.035 | 0.136 | 0.15 | 0.01 | 0.122 |  |  | 3.283 | 0.10943 | 0.207 | 0
December | 0.143 | 0.042 | 0.019 | 0.145 | 0.14 | 0.034 | 0.176 | 0.125 | 0.135 | 0.044 | 0.118 | 0.202 | 0.05 | 0.178 | 0.157 | 0.254 | 0.082 | 0.11 | 0.209 | 0 | 0.207 | 0.166 | 0.042 | 0 | 0.13 | 0.186 | 0 | 0.158 | 0.199 | 0.029 | 0 |  | 3.48 | 0.11226 | 0.254 | 0
[33 empty] | 54.348 | Grand Total
251/082 Crescent Bay - LUSI North | [5 empty] | MWAF - link to AH(x) |  |  |  | Daily Max (mgd) |  | 0.396 | [18 empty] | 251/082 Crescent Bay - LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof
2019-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.001 | 3.2258e-05 | 0.001 | 0
February | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0.001 | 0 | 0 | 0 |  |  |  |  | 0.007 | 0.00025 | 0.004 | 0
March | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.003 | 0 | 0.003 | 0.004 | 0 | 0 | 0.005 | 0.002 | 0 | 0.005 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0.004 | 0.004 |  | 0.038 | 0.0012258 | 0.005 | 0
April | 0 | 0 | 0.007 | 0.024 | 0 | 0.019 | 0.006 | 0 | 0 | 0.012 | 0.025 | 0 | 0.006 | 0.035 | 0 | 0 | 0.007 | 0.011 | 0 | 0 | 0.006 | 0 | 0 | 0.01 | 0.041 | 0 | 0.039 | 0.04 | 0 | 0 |  |  | 0.288 | 0.0096 | 0.041 | 0
May | 0.058 | 0.031 | 0 | 0.044 | 0 | 0 | 0 | 0.007 | 0.035 | 0.002 | 0.004 | 0.024 | 0 | 0 | 0 | 0.015 | 0 | 0.042 | 0.039 | 0 | 0 | 0.031 | 0.061 | 0.008 | 0.025 | 0.065 | 0.021 | 0.031 | 0.041 | 0.237 | 0.211 |  | 1.032 | 0.03329 | 0.237 | 0
June | 0.045 | 0.185 | 0.237 | 0.025 | 0.073 | 0.232 | 0.096 | 0.108 | 0.085 | 0.016 | 0.02 | 0.098 | 0.004 | 0.001 | 0.005 | 0.12 | 0 | 0.011 | 0.081 | 0.047 | 0.003 | 0.058 | 0.119 | 0.109 | 0.032 | 0.095 | 0.265 | 0.041 | 0.16 | 0.074 |  |  | 2.445 | 0.0815 | 0.265 | 0
July | 0.043 | 0.19 | 0.055 | 0.018 | 0.104 | 0.037 | 0.014 | 0.011 | 0.003 | 0.077 | 0.001 | 0.001 | 0.044 | 0.008 | 0.013 | 0.008 | 0.006 | 0.003 | 0.006 | 0.03 | 0.017 | 0.01 | 0 | 0.024 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 |  | 0.727 | 0.023452 | 0.19 | 0
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.009 | 0.00029032 | 0.005 | 0
September | 0.001 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0.006 | 0 | 0 | 0.012 | 0.015 | 0 | 0.008 | 0.012 | 0 | 0 | 0.01 | 0.015 | 0 | 0.017 | 0.021 | 0 | 0 | 0.025 | 0 | 0 | 0.042 | 0.028 | 0.001 |  |  | 0.215 | 0.0071667 | 0.042 | 0
October | 0 | 0.025 | 0.048 | 0 | 0.008 | 0.043 | 0 | 0 | 0.008 | 0.006 | 0 | 0.013 | 0.015 | 0 | 0 | 0.024 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.006 |  | 0.221 | 0.007129 | 0.048 | 0
November | 0 | 0.009 | 0 | 0 | 0.011 | 0.018 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.001 | 0 | 0 | 0.005 | 0 | 0 | 0.003 | 0.002 | 0 | 0.013 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.011 |  |  | 0.079 | 0.0026333 | 0.018 | 0
December | 0.013 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0.011 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.03 | 0.00096774 | 0.013 | 0
[33 empty] | 5.092 | Grand Total
251/248 Lake Groves Utilities, Inc. - LUSI South
Lake Groves - Combined Wells 1, 2, 3
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Groves - Combined Wells 1, 2, 3
2019-01-01 | 2.085 | 2.783 | 2.612 | 2.366 | 1.912 | 2.256 | 2.328 | 1.865 | 2.332 | 2.356 | 2.27 | 1.972 | 2.729 | 2.321 | 1.966 | 2.544 | 2.28 | 2.502 | 2.46 | 2.393 | 2.104 | 2.203 | 2.37 | 2.338 | 2.161 | 2.275 | 2.299 | 1.883 | 1.802 | 2.227 | 2.15 |  | 70.144 | 2.2627 | 2.783
February | 1.739 | 2.333 | 2.556 | 1.977 | 2.099 | 2.593 | 2.301 | 2.219 | 2.871 | 2.18 | 1.644 | 2.139 | 1.95 | 1.672 | 1.979 | 2.324 | 2.605 | 2.102 | 2.007 | 2.48 | 2.318 | 2 | 2.432 | 2.377 | 2.01 | 1.989 | 2.099 | 2.008 |  |  |  |  | 61.003 | 2.1787 | 2.871
March | 1.981 | 2.456 | 2.49 | 2.408 | 2.009 | 2.082 | 2.14 | 2.311 | 2.707 | 2.847 | 2.202 | 2.629 | 2.283 | 2.98 | 2.325 | 3.085 | 2.653 | 2.285 | 1.951 | 2.229 | 2.342 | 2.159 | 2.8 | 3.128 | 2.58 | 2.491 | 2.216 | 2.272 | 2.152 | 2.791 | 3.094 |  | 76.078 | 2.4541 | 3.128
April | 2.379 | 2.248 | 2.498 | 2.993 | 2.422 | 2.211 | 2.734 | 2.048 | 1.916 | 2.31 | 2.184 | 2.306 | 2.7 | 2.517 | 2.192 | 2.055 | 2.397 | 2.644 | 2.351 | 1.886 | 2.69 | 2.135 | 2.09 | 2.562 | 2.94 | 2.364 | 2.614 | 2.825 | 2.743 | 2.607 |  |  | 72.561 | 2.4187 | 2.993
May | 2.547 | 3.074 | 2.174 | 2.556 | 2.532 | 1.887 | 2.055 | 2.478 | 2.857 | 2.442 | 2.573 | 3.005 | 2.442 | 1.927 | 2.124 | 2.273 | 2.402 | 2.518 | 3.537 | 2.178 | 2.65 | 2.777 | 3.267 | 3.197 | 3.602 | 3.61 | 4.027 | 3.309 | 3.796 | 4.384 | 3.661 |  | 87.861 | 2.8342 | 4.384
June | 3.064 | 4.018 | 3.363 | 2.647 | 2.691 | 3.438 | 3.08 | 2.63 | 3.355 | 2.412 | 1.761 | 2.23 | 2.364 | 2.583 | 2.361 | 2.868 | 1.831 | 1.422 | 2.698 | 1.941 | 2.347 | 2.388 | 3.213 | 2.75 | 2.76 | 2.053 | 2.442 | 4.532 | 3.552 | 3.327 |  |  | 82.121 | 2.7374 | 4.532
July | 2.089 | 2.257 | 2.864 | 3.857 | 2.277 | 2.58 | 2.285 | 1.751 | 1.763 | 2.173 | 2.857 | 2.362 | 2.764 | 3.108 | 1.957 | 2.114 | 2.422 | 2.663 | 2.295 | 2.864 | 2.772 | 1.875 | 2.223 | 2.26 | 2.698 | 1.854 | 2.755 | 2.094 | 2.486 | 2.219 | 2.512 |  | 75.05 | 2.421 | 3.857
August | 2.666 | 2.346 | 2.258 | 2.656 | 2.486 | 1.867 | 2.25 | 2.853 | 2.417 | 2.08 | 2.643 | 2.933 | 1.795 | 2.244 | 2.637 | 2.268 | 2.219 | 2.968 | 2.582 | 2.308 | 2.27 | 2.926 | 2.557 | 2.569 | 2.588 | 3.107 | 1.88 | 2.21 | 2.442 | 2.253 | 2.861 |  | 76.139 | 2.4561 | 3.107
September | 1.644 | 2.265 | 2.015 | 2.127 | 1.961 | 2.575 | 2.501 | 2.888 | 2.83 | 2.443 | 2.516 | 3.123 | 2.814 | 2.515 | 3.95 | 2.018 | 2.569 | 2.814 | 3.787 | 3.568 | 3.189 | 3.927 | 3.099 | 2.588 | 4.042 | 3.343 | 3.524 | 3.43 | 3.782 | 3.789 |  |  | 87.636 | 2.9212 | 4.042
October | 2.836 | 3.165 | 4.078 | 4.076 | 4.078 | 3.377 | 3.808 | 2.616 | 3.178 | 2.543 | 3.133 | 3.205 | 3.72 | 3.748 | 3.035 | 3.337 | 3.681 | 3.109 | 3.164 | 2.495 | 2.685 | 2.51 | 2.614 | 3.364 | 2.981 | 2.718 | 2.672 | 2.876 | 1.633 | 3.622 | 3.034 |  | 97.091 | 3.132 | 4.078
November | 2.771 | 2.887 | 3.661 | 3.66 | 2.903 | 2.533 | 3.016 | 3.258 | 2.957 | 2.957 | 3.024 | 2.708 | 3.092 | 2.933 | 3.297 | 3.205 | 2.38 | 2.747 | 2.828 | 2.682 | 3.216 | 2.913 | 2.857 | 3.733 | 2.405 | 2.331 | 3.37 | 3.318 | 3.275 | 3.379 |  |  | 90.296 | 3.0099 | 3.733
December | 2.341 | 3.145 | 2.229 | 3.121 | 2.667 | 2.857 | 3.07 | 3.594 | 2.78 | 2.389 | 2.586 | 2.664 | 2.793 | 2.473 | 2.273 | 2.458 | 2.076 | 2.312 | 2.26 | 2.36 | 2.653 | 2.024 | 1.932 | 1.745 | 2.997 | 2.378 | 1.499 | 2.749 | 1.733 | 1.89 | 2.114 |  | 76.162 | 2.4568 | 3.594
[33 empty] | 952.142 | Grand Total
Lake Groves - Well 1 |  |  |  |  | Well 1 | MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Groves - Well 1
January | 1.156 | 1.627 | 1.525 | 1.381 | 1.117 | 1.317 | 1.359 | 1.088 | 1.363 | 1.376 | 1.326 | 0.975 | 1.569 | 1.389 | 1.157 | 1.479 | 1.339 | 1.455 | 1.442 | 1.403 | 1.157 | 1.378 | 1.389 | 1.339 | 1.261 | 1.339 | 1.328 | 1.1 | 1.107 | 1.3 | 1.261 |  | 40.802 | 1.3162 | 1.627 | 0
February | 1.004 | 1.376 | 1.429 | 1.2 | 1.223 | 1.433 | 1.364 | 1.313 | 1.685 | 1.274 | 0.965 | 1.248 | 1.145 | 0.978 | 1.158 | 1.305 | 1.497 | 1.206 | 1.152 | 1.426 | 1.331 | 1.147 | 1.395 | 1.365 | 1.153 | 1.141 | 1.205 | 1.153 |  |  |  |  | 35.271 | 1.2597 | 1.685 | 0
March | 1.102 | 1.444 | 1.43 | 1.382 | 1.154 | 1.195 | 1.228 | 1.326 | 1.553 | 1.633 | 1.264 | 1.509 | 1.311 | 1.699 | 1.335 | 1.773 | 1.523 | 1.312 | 1.121 | 1.282 | 1.351 | 1.237 | 1.608 | 1.829 | 1.483 | 1.431 | 1.274 | 1.306 | 1.237 | 1.605 | 1.779 |  | 43.716 | 1.4102 | 1.829 | 0
April | 1.367 | 1.293 | 1.438 | 1.721 | 1.392 | 1.272 | 1.572 | 1.178 | 1.101 | 1.332 | 1.258 | 1.326 | 1.555 | 1.449 | 1.261 | 1.183 | 1.381 | 1.522 | 1.351 | 1.087 | 1.522 | 1.229 | 1.202 | 1.475 | 1.692 | 1.36 | 1.506 | 1.626 | 1.579 | 1.501 |  |  | 41.731 | 1.391 | 1.721 | 0
May | 1.468 | 1.77 | 1.252 | 1.472 | 1.458 | 1.086 | 1.184 | 1.427 | 1.645 | 1.406 | 1.482 | 1.73 | 1.407 | 1.11 | 1.21 | 1.309 | 1.385 | 1.451 | 2.04 | 1.256 | 1.527 | 1.603 | 1.883 | 1.843 | 2.076 | 2.081 | 2.322 | 1.908 | 2.193 | 2.529 | 2.112 |  | 50.625 | 1.6331 | 2.529 | 0
June | 1.769 | 2.32 | 1.942 | 1.53 | 1.559 | 1.987 | 1.781 | 0.796 | 2.35 | 1.23 | 1.017 | 0.895 | 0.123 | 0 | 0 | 0 | 0 | 0.743 | 1.56 | 0.806 | 1.041 | 1.699 | 1.85 | 1.586 | 1.262 | 1.188 | 1.616 | 0.15 | 0 | 0 |  |  | 32.8 | 1.0933 | 2.35 | 0
July | 0 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.032 | 0.0010323 | 0.023 | 0
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.018 | 0.00058065 | 0.018 | 0
September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.835 | 0.346 |  | 2.181 | 0.070355 | 1.835 | 0
November | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.009 | 0.0003 | 0.009 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 1.597 | 1.372 | 0.019 | 0 | 1.208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.766 | 0.15374 | 1.597 | 0
[33 empty] | 251.951 | Grand Total
Lake Groves - Well 2 |  |  |  |  | Well 2 | MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Groves - Well 2
January | 0.929 | 1.156 | 1.087 | 0.985 | 0.795 | 0.939 | 0.969 | 0.777 | 0.969 | 0.98 | 0.944 | 0.997 | 1.16 | 0.932 | 0.809 | 1.065 | 0.941 | 1.047 | 1.018 | 0.99 | 0.947 | 0.825 | 0.981 | 0.999 | 0.9 | 0.936 | 0.971 | 0.783 | 0.695 | 0.927 | 0.889 |  | 29.342 | 0.94652 | 1.16 | 0
February | 0.735 | 0.957 | 1.127 | 0.777 | 0.876 | 1.083 | 0.937 | 0.906 | 1.186 | 0.906 | 0.679 | 0.891 | 0.805 | 0.694 | 0.821 | 1.019 | 1.108 | 0.896 | 0.855 | 1.054 | 0.987 | 0.853 | 1.037 | 1.012 | 0.857 | 0.848 | 0.894 | 0.855 |  |  |  |  | 25.655 | 0.91625 | 1.186 | 0
March | 0.879 | 1.012 | 1.06 | 1.026 | 0.855 | 0.887 | 0.912 | 0.985 | 1.154 | 1.214 | 0.938 | 1.12 | 0.972 | 1.261 | 0.99 | 1.312 | 1.13 | 0.973 | 0.83 | 0.947 | 0.991 | 0.922 | 1.192 | 1.299 | 1.097 | 1.06 | 0.942 | 0.966 | 0.915 | 1.186 | 1.315 |  | 32.342 | 1.0433 | 1.315 | 0
April | 1.012 | 0.955 | 1.06 | 1.272 | 1.03 | 0.939 | 1.162 | 0.87 | 0.815 | 0.978 | 0.926 | 0.98 | 1.145 | 1.068 | 0.931 | 0.872 | 1.016 | 1.122 | 1 | 0.799 | 1.123 | 0.906 | 0.888 | 1.087 | 1.248 | 1.004 | 1.108 | 1.199 | 1.164 | 1.106 |  |  | 30.785 | 1.0262 | 1.272 | 0
May | 1.079 | 1.304 | 0.922 | 1.084 | 1.074 | 0.801 | 0.871 | 1.051 | 1.212 | 1.036 | 1.091 | 1.275 | 1.035 | 0.817 | 0.885 | 0.964 | 1.017 | 1.067 | 1.497 | 0.922 | 1.123 | 1.174 | 1.384 | 1.354 | 1.526 | 1.529 | 1.705 | 1.401 | 1.603 | 1.855 | 1.549 |  | 37.207 | 1.2002 | 1.855 | 0
June | 1.295 | 1.698 | 1.421 | 1.117 | 1.132 | 1.451 | 1.299 | 1.834 | 1.005 | 0.901 | 0.744 | 0.468 | 0.091 | 0 | 0 | 0 | 0 | 0.545 | 1.131 | 0.591 | 0.762 | 0.291 | 1.363 | 1.164 | 0.924 | 0.865 | 0.826 | 0.468 | 0 | 0 |  |  | 23.386 | 0.77953 | 1.834 | 0
July | 0 | 0 | 0 | 0 | 0 | 0 | 0.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.019 | 0.0006129 | 0.012 | 0
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.006 | 0.00019355 | 0.006 | 0
September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.495 | 0.255 |  | 1.75 | 0.056452 | 1.495 | 0
November | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.006 | 0.0002 | 0.006 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.356 | 1.183 | 1.017 | 0.008 | 0 | 0.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.456 | 0.11148 | 1.183 | 0
[33 empty] | 183.954 | Grand Total
Lake Groves - Well 3 |  |  |  |  | Well 3 | MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Groves - Well 3
January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
February | 0 | 0 | 0 | 0 | 0 | 0.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.077 | 0.00275 | 0.077 | 0
March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.02 | 0.00064516 | 0.02 | 0
April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.045 | 0.0015 | 0.045 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.029 | 0.00093548 | 0.029 | 0
June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.281 | 0 | 0.867 | 2.15 | 2.583 | 2.361 | 2.868 | 1.831 | 0.134 | 0.007 | 0.544 | 0.544 | 0.398 | 0 | 0 | 0.574 | 0 | 0 | 3.914 | 3.552 | 3.327 |  |  | 25.935 | 0.8645 | 3.914 | 0
July | 2.089 | 2.257 | 2.864 | 3.857 | 2.277 | 2.58 | 2.264 | 1.751 | 1.763 | 2.173 | 2.857 | 2.362 | 2.764 | 3.108 | 1.957 | 2.114 | 2.422 | 2.663 | 2.265 | 2.864 | 2.772 | 1.875 | 2.223 | 2.26 | 2.698 | 1.854 | 2.755 | 2.094 | 2.486 | 2.219 | 2.512 |  | 74.999 | 2.4193 | 3.857 | 0
August | 2.666 | 2.346 | 2.258 | 2.656 | 2.486 | 1.867 | 2.25 | 2.853 | 2.417 | 2.08 | 2.643 | 2.933 | 1.795 | 2.244 | 2.637 | 2.268 | 2.219 | 2.968 | 2.582 | 2.308 | 2.27 | 2.902 | 2.557 | 2.569 | 2.588 | 3.107 | 1.88 | 2.21 | 2.442 | 2.253 | 2.861 |  | 76.115 | 2.4553 | 3.107 | 0
September | 1.644 | 2.265 | 2.015 | 2.127 | 1.961 | 2.575 | 2.501 | 2.888 | 2.83 | 2.443 | 2.516 | 3.123 | 2.814 | 2.515 | 3.95 | 2.018 | 2.569 | 2.814 | 3.787 | 3.568 | 3.189 | 3.927 | 3.099 | 2.588 | 4.042 | 3.343 | 3.524 | 3.43 | 3.782 | 3.789 |  |  | 87.636 | 2.9212 | 4.042 | 0
October | 2.836 | 3.165 | 4.078 | 4.076 | 4.078 | 3.377 | 3.808 | 2.616 | 3.178 | 2.543 | 3.133 | 3.205 | 3.72 | 3.748 | 3.035 | 3.337 | 3.681 | 3.109 | 3.164 | 2.495 | 2.685 | 2.51 | 2.614 | 3.364 | 2.981 | 2.718 | 2.672 | 2.876 | 1.633 | 0.292 | 2.433 |  | 93.16 | 3.0052 | 4.078 | 0
November | 2.756 | 2.887 | 3.661 | 3.66 | 2.903 | 2.533 | 3.016 | 3.258 | 2.957 | 2.957 | 3.024 | 2.708 | 3.092 | 2.933 | 3.297 | 3.205 | 2.38 | 2.747 | 2.828 | 2.682 | 3.216 | 2.913 | 2.857 | 3.733 | 2.405 | 2.331 | 3.37 | 3.318 | 3.275 | 3.379 |  |  | 90.281 | 3.0094 | 3.733 | 0
December | 2.341 | 3.145 | 2.229 | 3.121 | 2.667 | 2.857 | 3.07 | 2.668 | 0 | 0 | 2.559 | 2.664 | 0.693 | 2.473 | 2.273 | 2.458 | 2.076 | 2.312 | 2.26 | 2.36 | 2.653 | 2.024 | 1.932 | 1.745 | 2.997 | 2.378 | 1.499 | 2.749 | 1.733 | 1.89 | 2.114 |  | 67.94 | 2.1916 | 3.145 | 0
[33 empty] | 516.237 | Grand Total
251/038 Lake Louisia Total - LUSI North |  |  |  |  | Well 1 diverted to The Vistas GST |  |  |  |  | Daily Max (mgd Jan-Feb) |  | 1.944 | Daily Max (mgd Mar-Dec) |  | 2.52
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | 251/038 Lake Louisia (Combined Wells)
January | 0.341 | 0.089 | 0.336 | 0.28 | 0.288 | 0.34 | 0.35 | 0.277 | 0.39 | 0.276 | 0.398 | 0.296 | 0.395 | 0.377 | 0.281 | 0.355 | 0.361 | 0.338 | 0.355 | 0.339 | 0.33 | 0.333 | 0.354 | 0.364 | 0.257 | 0.325 | 0.346 | 0.333 | 0.326 | 0.376 | 0.28 |  | 10.086 | 0.32535 | 0.398
February | 0.246 | 0.307 | 0.42 | 0.251 | 0.311 | 0.379 | 0.393 | 0.28 | 0.347 | 0.368 | 0.31 | 0.309 | 0.309 | 0.265 | 0.288 | 0.306 | 0.364 | 0.353 | 0.337 | 0.329 | 0.283 | 0.292 | 0.323 | 0.382 | 0.187 | 0.372 | 0.288 | 0.301 |  |  |  |  | 8.9 | 0.31786 | 0.42
March | 0.267 | 0.355 | 0.369 | 0.384 | 0.288 | 0.311 | 0.391 | 0.312 | 0.343 | 0.355 | 0.417 | 0.357 | 0.414 | 0.395 | 0.359 | 0.427 | 0.311 | 0.344 | 0.323 | 0.327 | 0.393 | 0.3 | 0.305 | 0.319 | 0.513 | 0.303 | 0.567 | 0.733 | 0.329 | 0.343 | 0.431 |  | 11.585 | 0.37371 | 0.733
April | 0.328 | 0.325 | 0.402 | 0.298 | 0.352 | 0.314 | 0.365 | 0.314 | 0.285 | 0.323 | 0.339 | 0.316 | 0.443 | 0.29 | 0.324 | 0.281 | 0.389 | 0.362 | 0.344 | 0.246 | 0.359 | 0.316 | 0.375 | 0.286 | 0.405 | 0.31 | 0.359 | 0.45 | 0.38 | 0.294 | 0 |  | 10.174 | 0.32819 | 0.45
May | 0.459 | 0.335 | 0.322 | 0.408 | 0.297 | 0.337 | 0.257 | 0.436 | 0.322 | 0.316 | 0.443 | 0.383 | 0.322 | 0.085 | 0.489 | 0.364 | 0.365 | 0.348 | 0.358 | 0.398 | 0.35 | 0.437 | 0.346 | 0.118 | 0.229 | 0.676 | 0.298 | 0.068 | 0.152 | 0.515 | 1.158 |  | 11.391 | 0.36745 | 1.158
June | 0.586 | 0.861 | 0.951 | 0.502 | 0.653 | 0.664 | 0.543 | 0.568 | 0.881 | 0.468 | 0.332 | 0.4 | 0.572 | 0.221 | 0.518 | 0.494 | 0.418 | 0.369 | 0.452 | 0.312 | 0.393 | 0.547 | 0.599 | 0.51 | 0.508 | 0.688 | 0.745 | 0.645 | 0.67 | 0.639 | 0 |  | 16.709 | 0.539 | 0.951
July | 0.603 | 0.402 | 0.379 | 1.097 | 0.385 | 0.569 | 0.558 | 0.422 | 0.279 | 0.55 | 0.349 | 0.31 | 0.356 | 0.486 | 0.3 | 0.409 | 0.363 | 0.31 | 0.341 | 0.291 | 0.493 | 0.345 | 0.328 | 0.363 | 0.285 | 0.348 | 0.27 | 0.431 | 0.358 | 0.357 | 0.364 |  | 12.701 | 0.40971 | 1.097
August | 0.328 | 0.273 | 0.291 | 0.407 | 0.41 | 0.202 | 0.364 | 0.406 | 0.302 | 0.396 | 0.349 | 0.385 | 0.254 | 0.391 | 0.334 | 0.293 | 0.376 | 0.316 | 0.446 | 0.229 | 0.367 | 0.402 | 0.314 | 0.38 | 0.445 | 0.381 | 0.27 | 0.316 | 0.372 | 0.42 | 0.283 |  | 10.702 | 0.34523 | 0.446
September | 0.462 | 0.35 | 0.197 | 0.352 | 0.338 | 0.304 | 0.381 | 0.463 | 0.361 | 0.351 | 0.384 | 0.432 | 0.343 | 0.366 | 0.39 | 0.359 | 0.368 | 0.447 | 0.398 | 0.425 | 0.299 | 0.615 | 0.515 | 0.379 | 0.441 | 0.488 | 0.544 | 0.465 | 0.474 | 0.58 |  |  | 12.271 | 0.40903 | 0.615
October | 0.432 | 0.379 | 0.218 | 0.245 | 0.348 | 0.354 | 0.191 | 0 | 0.132 | 0.149 | 0.091 | 0.165 | 0.247 | 0.166 | 0.081 | 0.294 | 0.247 | 0.133 | 0.139 | 0.309 | 0.401 | 0.273 | 0.398 | 0.136 | 0.092 | 0.189 | 0.187 | 0.084 | 0.045 | 0.149 | 0.32 |  | 6.594 | 0.21271 | 0.432
November | 0.242 | 0.163 | 0.173 | 0.139 | 0 | 0.151 | 0.18 | 0.202 | 0 | 0.135 | 0.027 | 0.087 | 0.171 | 0.125 | 0.06 | 0.102 | 0.133 | 0.025 | 0 | 0.132 | 0.155 | 0 | 0.128 | 0.2 | 0.001 | 0.036 | 0.132 | 0.133 | 0.006 | 0.125 |  |  | 3.163 | 0.10543 | 0.242
December | 0.155 | 0.038 | 0.008 | 0.112 | 0.113 | 0.049 | 0.152 | 0.124 | 0.482 | 0.329 | 0.192 | 0.198 | 0.051 | 0.157 | 0.158 | 0.202 | 0.08 | 0.088 | 0.388 | 0.316 | 0.289 | 0.316 | 0.319 | 0.235 | 0.338 | 0.343 | 0.361 | 0.26 | 0.33 | 0.304 | 0.282 |  | 6.769 | 0.21835 | 0.482
[33 empty] | 121.045 | Grand Total
Lake Louisa - Well 1 - (Vistas 1) LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Louisa - Well 1 (Vistas 1)
January | 0.34 | 0.089 | 0.336 | 0.28 | 0.288 | 0.34 | 0.35 | 0.277 | 0.377 | 0.276 | 0.398 | 0.284 | 0.395 | 0.377 | 0.281 | 0.35 | 0.361 | 0.338 | 0.355 | 0.338 | 0.329 | 0.333 | 0.354 | 0.342 | 0.257 | 0.325 | 0.346 | 0.312 | 0.319 | 0.376 | 0.28 |  | 10.003 | 0.32268 | 0.398 | 0
February | 0.246 | 0.307 | 0.42 | 0.248 | 0.311 | 0.379 | 0.393 | 0.279 | 0.347 | 0.368 | 0.264 | 0.306 | 0.308 | 0.259 | 0.288 | 0.306 | 0.364 | 0.323 | 0.334 | 0.328 | 0.283 | 0.292 | 0.323 | 0.382 | 0.187 | 0.359 | 0.286 | 0.3 |  |  |  |  | 8.79 | 0.31393 | 0.42 | 0
March | 0.267 | 0.355 | 0.369 | 0.384 | 0.288 | 0.307 | 0.391 | 0.312 | 0.343 | 0.355 | 0.417 | 0.357 | 0.414 | 0.38 | 0.358 | 0.427 | 0.311 | 0.344 | 0.318 | 0.327 | 0.393 | 0.299 | 0.305 | 0.319 | 0.472 | 0.303 | 0.558 | 0.73 | 0.329 | 0.343 | 0.431 |  | 11.506 | 0.37116 | 0.73 | 0
April | 0.319 | 0.325 | 0.402 | 0.298 | 0.352 | 0.314 | 0.365 | 0.314 | 0.261 | 0.323 | 0.339 | 0.316 | 0.443 | 0.29 | 0.316 | 0.281 | 0.379 | 0.362 | 0.332 | 0.245 | 0.359 | 0.316 | 0.375 | 0.286 | 0.405 | 0.31 | 0.358 | 0.45 | 0.38 | 0.294 |  |  | 10.109 | 0.33697 | 0.45 | 0
May | 0.459 | 0.334 | 0.322 | 0.408 | 0.297 | 0.337 | 0.255 | 0.414 | 0.321 | 0.315 | 0.443 | 0.383 | 0.322 | 0.083 | 0.488 | 0.363 | 0.365 | 0.346 | 0.358 | 0.397 | 0.35 | 0.437 | 0.346 | 0.116 | 0.229 | 0.249 | 0.056 | 0.068 | 0.152 | 0.3 | 0.33 |  | 9.643 | 0.31106 | 0.488 | 0
June | 0.139 | 0.237 | 0.236 | 0.049 | 0.139 | 0.113 | 0.033 | 0.089 | 0.232 | 0.006 | 0.008 | 0.047 | 0.089 | 0 | 0.067 | 0.076 | 0 | 0 | 0.054 | 0.008 | 0 | 0.102 | 0.106 | 0.011 | 0.01 | 0.149 | 0.194 | 0.051 | 0.184 | 0.133 |  |  | 2.562 | 0.0854 | 0.237 | 0
July | 0.029 | 0 | 0.018 | 0.281 | 0 | 0.132 | 0.071 | 0 | 0 | 0.13 | 0.28 | 0.31 | 0.354 | 0.486 | 0.298 | 0.409 | 0.363 | 0.31 | 0.339 | 0.29 | 0.493 | 0.345 | 0.326 | 0.36 | 0.285 | 0.348 | 0.27 | 0.43 | 0.358 | 0.356 | 0.362 |  | 8.033 | 0.25913 | 0.493 | 0
August | 0.324 | 0.273 | 0.29 | 0.407 | 0.41 | 0.202 | 0.362 | 0.406 | 0.301 | 0.396 | 0.349 | 0.385 | 0.251 | 0.384 | 0.334 | 0.293 | 0.376 | 0.316 | 0.446 | 0.229 | 0.367 | 0.398 | 0.314 | 0.38 | 0.445 | 0.381 | 0.27 | 0.315 | 0.372 | 0.419 | 0.28 |  | 10.675 | 0.34435 | 0.446 | 0
September | 0.462 | 0.35 | 0.196 | 0.352 | 0.336 | 0.069 | 0.381 | 0.463 | 0.361 | 0.351 | 0.384 | 0.432 | 0.343 | 0.364 | 0.39 | 0.359 | 0.368 | 0.445 | 0.398 | 0.424 | 0.296 | 0.615 | 0.515 | 0.379 | 0.439 | 0.488 | 0.544 | 0.465 | 0.472 | 0.58 |  |  | 12.021 | 0.4007 | 0.615 | 0
October | 0.432 | 0.377 | 0.218 | 0.245 | 0.348 | 0.354 | 0.191 | 0 | 0.132 | 0.149 | 0.088 | 0.165 | 0.247 | 0.166 | 0.081 | 0.294 | 0.247 | 0.133 | 0.139 | 0.309 | 0.401 | 0.272 | 0.398 | 0.132 | 0.091 | 0.189 | 0.187 | 0.084 | 0.045 | 0.149 | 0.319 |  | 6.582 | 0.21232 | 0.432 | 0
November | 0.242 | 0.163 | 0.173 | 0.139 | 0 | 0.148 | 0.18 | 0.202 | 0 | 0.135 | 0.027 | 0.087 | 0.17 | 0.124 | 0.059 | 0.102 | 0.133 | 0.025 | 0 | 0.132 | 0.152 | 0 | 0.128 | 0.2 | 0.001 | 0.036 | 0.132 | 0.13 | 0.006 | 0.125 |  |  | 3.151 | 0.10503 | 0.242 | 0
December | 0.155 | 0.038 | 0.008 | 0.112 | 0.113 | 0.049 | 0.152 | 0.124 | 0.479 | 0.328 | 0.192 | 0.198 | 0.048 | 0.157 | 0.158 | 0.202 | 0.08 | 0.088 | 0.388 | 0.313 | 0.289 | 0.316 | 0.319 | 0.235 | 0.338 | 0.341 | 0.358 | 0.258 | 0.33 | 0.304 | 0.279 |  | 6.749 | 0.21771 | 0.479 | 0
[33 empty] | 99.824 | Grand Total
Lake Louisa - Well 3 - (Vistas 3) LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Louisa - Well 3 (Vistas 3)
January | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0 | 0 | 0.022 | 0 | 0 | 0 | 0.021 | 0.001 | 0 | 0 |  | 0.065 | 0.0020968 | 0.022 | 0
February | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.046 | 0.003 | 0.001 | 0 | 0 | 0 | 0 | 0.026 | 0.003 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0.009 | 0.002 | 0.001 |  |  |  |  | 0.096 | 0.0034286 | 0.046 | 0
March | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.036 | 0 | 0.009 | 0 | 0 | 0 | 0 |  | 0.066 | 0.002129 | 0.036 | 0
April | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0 | 0 | 0 | 0.012 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 |  |  | 0.046 | 0.0015333 | 0.024 | 0
May | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0.001 | 0.001 | 0 | 0 | 0 | 0.002 | 0.001 | 0.001 | 0 | 0.002 | 0 | 0.001 | 0 | 0 | 0 | 0.002 | 0 | 0.427 | 0.242 | 0 | 0 | 0.215 | 0.828 |  | 1.726 | 0.055677 | 0.828 | 0
June | 0.447 | 0.624 | 0.715 | 0.453 | 0.514 | 0.551 | 0.51 | 0.479 | 0.649 | 0.462 | 0.324 | 0.353 | 0.483 | 0.221 | 0.451 | 0.418 | 0.418 | 0.369 | 0.398 | 0.304 | 0.393 | 0.445 | 0.493 | 0.499 | 0.498 | 0.539 | 0.551 | 0.594 | 0.486 | 0.506 |  |  | 14.147 | 0.47157 | 0.715 | 0
July | 0.574 | 0.402 | 0.361 | 0.816 | 0.385 | 0.437 | 0.487 | 0.422 | 0.279 | 0.417 | 0.069 | 0 | 0.002 | 0 | 0.002 | 0 | 0 | 0 | 0.002 | 0.001 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0.001 | 0.002 |  | 4.662 | 0.15039 | 0.816 | 0
August | 0.001 | 0 | 0.001 | 0 | 0 | 0 | 0.002 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0.001 | 0 |  | 0.015 | 0.00048387 | 0.007 | 0
September | 0 | 0 | 0.001 | 0 | 0.002 | 0.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0.002 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0.001 | 0 |  |  | 0.246 | 0.0082 | 0.235 | 0
October | 0 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0.001 |  | 0.006 | 0.00019355 | 0.002 | 0
November | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.002 | 6.6667e-05 | 0.001 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0.002 | 0 | 0 | 0.003 |  | 0.008 | 0.00025806 | 0.003 | 0
[33 empty] | 21.085 | Grand Total
Lake Louisa - The Oranges Well LUSI North
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | Lake Louisa - The Oranges
January | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 |  | 0.018 | 0.00058065 | 0.007 | 0
February | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.006 | 0 | 0 | 0 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0 | 0 |  |  |  |  | 0.014 | 0.0005 | 0.006 | 0
March | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0 | 0 | 0.003 | 0 | 0 | 0 |  | 0.013 | 0.00041935 | 0.005 | 0
April | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.019 | 0.00063333 | 0.01 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.022 | 0.00070968 | 0.022 | 0
June | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.006 | 0.00019355 | 0.003 | 0
August | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 |  | 0.012 | 0.0003871 | 0.003 | 0
September | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 |  |  | 0.004 | 0.00013333 | 0.003 | 0
October | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.006 | 0.00019355 | 0.003 | 0
November | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 |  |  | 0.01 | 0.00033333 | 0.003 | 0
December | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003 | 0 | 0 | 0 | 0 |  | 0.012 | 0.0003871 | 0.003 | 0
[33 empty] | 0.118 | Grand Total
CR 561 (Combined Wells) - LUSI North | [9 empty] | Daily Max (mgd) |  | 2.592
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Total | Avg. | Max | Proof | CR 561 (Combined Wells) - LUSI North
January | 0.81 | 1.428 | 1.356 | 0.784 | 1.037 | 1.167 | 0.989 | 0.934 | 1.253 | 1.137 | 1.015 | 1.274 | 1.318 | 1.162 | 1.03 | 1.221 | 1.355 | 0.886 | 1.385 | 1.161 | 0.978 | 0.802 | 1.127 | 1.233 | 0.941 | 1.149 | 1.166 | 0.742 | 0.879 | 1.026 | 0.95 |  | 33.695 | 1.0869 | 1.428
February | 0.904 | 1.093 | 1.299 | 0.996 | 0.918 | 1.288 | 1.13 | 1.098 | 1.306 | 1.273 | 0.709 | 1.036 | 0.962 | 0.97 | 0.774 | 1.288 | 1.463 | 0.941 | 1.205 | 1.357 | 1.299 | 0.91 | 1.357 | 1.44 | 1.158 | 0.956 | 1.303 | 1.089 |  |  |  |  | 31.522 | 1.1258 | 1.463
March | 0.78 | 1.506 | 1.516 | 1.14 | 1.236 | 1.272 | 0.975 | 1.304 | 1.224 | 1.676 | 1.786 | 1.33 | 1.472 | 1.284 | 1.837 | 1.102 | 1.811 | 1.18 | 1.039 | 1.21 | 1.408 | 0.956 | 1.3 | 1.299 | 2.316 | 1.136 | 1.411 | 1.406 | 1.563 | 1.243 | 2.088 |  | 42.806 | 1.3808 | 2.316
April | 1.888 | 0.878 | 1.738 | 1.626 | 1.401 | 1.387 | 1.495 | 1.409 | 0.852 | 1.518 | 1.518 | 1.429 | 1.552 | 2.035 | 1.417 | 1.14 | 1.255 | 1.806 | 1.531 | 1.273 | 1.509 | 1.276 | 1.381 | 1.389 | 1.843 | 1.625 | 1.284 | 1.794 | 2.224 | 1.47 |  |  | 44.943 | 1.4981 | 2.224
May | 1.957 | 1.551 | 1.351 | 1.627 | 1.367 | 1.073 | 1.111 | 1.468 | 1.664 | 1.514 | 1.345 | 1.604 | 1.724 | 0.967 | 1.352 | 1.552 | 1.21 | 1.502 | 1.732 | 1.85 | 1.419 | 1.592 | 1.955 | 2.02 | 1.654 | 2.016 | 2.296 | 2.024 | 1.866 | 2.157 | 1.946 |  | 50.466 | 1.6279 | 2.296
June | 1.272 | 1.307 | 2.477 | 1.27 | 1.492 | 1.508 | 1.242 | 1.4 | 1.272 | 1.094 | 0.84 | 1.141 | 1.355 | 1.061 | 0.979 | 1.438 | 0.917 | 0.978 | 1.092 | 1.038 | 1.017 | 1.295 | 1.509 | 1.401 | 1.376 | 1.437 | 1.95 | 1.377 | 1.499 | 1.452 |  |  | 39.486 | 1.3162 | 2.477
July | 1.385 | 1.483 | 1.705 | 1.366 | 1.478 | 1.619 | 1.206 | 1.369 | 1.018 | 1.378 | 1.445 | 1.013 | 1.151 | 1.245 | 1.539 | 1.228 | 1.406 | 1.311 | 1.033 | 1.51 | 1.373 | 1.576 | 0.937 | 1.558 | 1.171 | 0.888 | 1.119 | 1.298 | 1.405 | 1.086 | 1.329 |  | 40.628 | 1.3106 | 1.705
August | 1.03 | 1.099 | 1.035 | 1.152 | 1.373 | 0.947 | 1.119 | 1.232 | 1.149 | 1.168 | 1.103 | 1.308 | 1.016 | 1.103 | 1.13 | 0.992 | 1.308 | 1.241 | 1.221 | 0.9 | 1.227 | 1.339 | 1.217 | 1.355 | 1.355 | 1.581 | 0.986 | 1.121 | 1.294 | 1.006 | 1.135 |  | 36.242 | 1.1691 | 1.581
September | 1.06 | 1.282 | 0.75 | 1.101 | 1.069 | 1.001 | 1.493 | 1.332 | 1.797 | 0.917 | 1.547 | 1.474 | 1.176 | 1.012 | 1.422 | 1.493 | 1.183 | 1.633 | 1.5 | 1.504 | 1.489 | 1.891 | 1.903 | 1.381 | 1.405 | 2.299 | 2.123 | 1.342 | 2.076 | 2.355 |  |  | 44.01 | 1.467 | 2.355
October | 1.551 | 1.217 | 2.533 | 1.705 | 1.523 | 1.85 | 2.098 | 1.021 | 1.211 | 1.13 | 1.441 | 1.409 | 1.477 | 1.938 | 1.435 | 1.668 | 1.629 | 1.513 | 1.149 | 1.32 | 1.241 | 0.958 | 1.408 | 1.252 | 1.222 | 1.05 | 1.246 | 1.082 | 1.009 | 1.356 | 1.45 |  | 44.092 | 1.4223 | 2.533
November | 1.403 | 1.258 | 1.854 | 1.464 | 1.233 | 1.368 | 1.537 | 1.355 | 1.135 | 1.462 | 1.284 | 1.053 | 1.461 | 1.295 | 1.168 | 1.071 | 1.501 | 1.182 | 1.047 | 1.466 | 1.309 | 1.32 | 1.654 | 1.376 | 1.107 | 0.971 | 1.43 | 1.614 | 1.035 | 1.55 |  |  | 39.963 | 1.3321 | 1.854
December | 1.459 | 1.378 | 0.938 | 1.313 | 1.486 | 1.231 | 1.21 | 1.563 | 1.525 | 1.071 | 1.498 | 1.069 | 1.085 | 1.162 | 1.298 | 1.112 | 0.942 | 0.975 | 1.073 | 0.912 | 1.19 | 1.103 | 0.959 | 0.73 | 1.043 | 1.043 | 1.076 | 1.121 | 1.012 | 0.852 | 0.836 |  | 35.265 | 1.1376 | 1.563
[33 empty] | 483.118 | Grand Total
251/086 CR 561 (Well 1 - Crescent West ) - LUSI North | [6 empty] | Well 1 | MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | 251/086 CR 561 (Well 1 - Crescent West ) - LUSI North
January | 0.355 | 0.622 | 0.587 | 0.341 | 0.446 | 0.517 | 0.431 | 0.401 | 0.546 | 0.495 | 0.438 | 0.555 | 0.581 | 0.505 | 0.448 | 0.541 | 0.583 | 0.385 | 0.567 | 0.504 | 0.426 | 0.24 | 0.502 | 0.534 | 0.396 | 0.516 | 0.51 | 0.321 | 0.39 | 0.441 | 0.424 |  | 14.548 | 0.46929 | 0.622 | 0
February | 0.382 | 0.484 | 0.565 | 0.438 | 0.399 | 0.566 | 0.497 | 0.474 | 0.574 | 0.555 | 0.313 | 0.448 | 0.421 | 0.427 | 0.331 | 0.567 | 0.638 | 0.411 | 0.528 | 0.591 | 0.564 | 0.407 | 0.587 | 0.632 | 0.511 | 0.412 | 0.57 | 0.477 |  |  |  |  | 13.769 | 0.49175 | 0.638 | 0
March | 0.335 | 0.664 | 0.668 | 0.495 | 0.541 | 0.557 | 0.432 | 0.562 | 0.542 | 0.734 | 0.781 | 0.579 | 0.641 | 0.576 | 0.8 | 0.485 | 0.795 | 0.515 | 0.456 | 0.532 | 0.615 | 0.426 | 0.568 | 0.57 | 1.01 | 0.505 | 0.619 | 0.623 | 0.678 | 0.547 | 0.919 |  | 18.77 | 0.60548 | 1.01 | 0
April | 0.826 | 0.396 | 0.747 | 0.727 | 0.61 | 0.613 | 0.656 | 0.617 | 0.376 | 0.67 | 0.666 | 0.63 | 0.683 | 0.893 | 0.623 | 0.501 | 0.555 | 0.793 | 0.666 | 0.568 | 0.662 | 0.563 | 0.607 | 0.608 | 0.812 | 0.715 | 0.567 | 0.787 | 0.979 | 0.644 |  |  | 19.76 | 0.65867 | 0.979 | 0
May | 0.834 | 0.682 | 0.591 | 0.718 | 0.599 | 0.47 | 0.484 | 0.639 | 0.732 | 0.661 | 0.594 | 0.706 | 0.757 | 0.422 | 0.593 | 0.683 | 0.533 | 0.662 | 0.761 | 0.812 | 0.625 | 0.702 | 0.86 | 0.888 | 0.726 | 0.886 | 1.009 | 0.894 | 0.794 | 0.95 | 0.852 |  | 22.119 | 0.71352 | 1.009 | 0
June | 0.563 | 0.578 | 1.084 | 0.557 | 0.652 | 0.664 | 0.545 | 0.617 | 0.538 | 0.47 | 0.366 | 0.492 | 0.596 | 0.464 | 0.435 | 0.627 | 0.397 | 0.417 | 0.48 | 0.457 | 0.447 | 0.566 | 0.667 | 0.611 | 0.606 | 0.633 | 0.852 | 0.604 | 0.657 | 0.64 |  |  | 17.282 | 0.57607 | 1.084 | 0
July | 0.605 | 0.635 | 0.736 | 0.595 | 0.65 | 0.714 | 0.525 | 0.606 | 0.442 | 0.605 | 0.638 | 0.446 | 0.508 | 0.548 | 0.677 | 0.516 | 0.571 | 0.576 | 0.452 | 0.67 | 0.602 | 0.694 | 0.415 | 0.677 | 0.513 | 0.392 | 0.492 | 0.571 | 0.617 | 0.475 | 0.585 |  | 17.748 | 0.57252 | 0.736 | 0
August | 0.453 | 0.482 | 0.454 | 0.51 | 0.606 | 0.41 | 0.495 | 0.542 | 0.506 | 0.515 | 0.489 | 0.572 | 0.437 | 0.484 | 0.501 | 0.435 | 0.579 | 0.543 | 0.537 | 0.416 | 0.55 | 0.589 | 0.533 | 0.601 | 0.593 | 0.692 | 0.432 | 0.494 | 0.568 | 0.443 | 0.495 |  | 15.956 | 0.51471 | 0.692 | 0
September | 0.469 | 0.558 | 0.329 | 0.484 | 0.471 | 0.436 | 0.657 | 0.59 | 0.785 | 0.401 | 0.676 | 0.642 | 0.515 | 0.449 | 0.622 | 0.651 | 0.519 | 0.719 | 0.658 | 0.657 | 0.659 | 0.826 | 0.838 | 0.606 | 0.615 | 1.01 | 0.932 | 0.595 | 0.912 | 1.036 |  |  | 19.317 | 0.6439 | 1.036 | 0
October | 0.679 | 0.54 | 1.105 | 0.741 | 0.671 | 0.811 | 0.92 | 0.445 | 0.536 | 0.496 | 0.637 | 0.632 | 0.637 | 0.848 | 0.633 | 0.731 | 0.717 | 0.678 | 0.47 | 0.599 | 0.541 | 0.42 | 0.623 | 0.561 | 0.419 | 0.461 | 0.541 | 0.477 | 0.443 | 0.6 | 0.635 |  | 19.247 | 0.62087 | 1.105 | 0
November | 0.617 | 0.553 | 0.813 | 0.641 | 0.541 | 0.604 | 0.675 | 0.593 | 0.501 | 0.638 | 0.565 | 0.462 | 0.642 | 0.573 | 0.494 | 0.475 | 0.658 | 0.516 | 0.459 | 0.652 | 0.518 | 0.578 | 0.728 | 0.608 | 0.483 | 0.429 | 0.631 | 0.707 | 0.456 | 0.685 |  |  | 17.495 | 0.58317 | 0.813 | 0
December | 0.64 | 0.605 | 0.41 | 0.583 | 0.65 | 0.482 | 0.553 | 0.732 | 0.668 | 0.47 | 0.66 | 0.474 | 0.473 | 0.512 | 0.571 | 0.489 | 0.413 | 0.432 | 0.473 | 0.403 | 0.52 | 0.491 | 0.418 | 0.32 | 0.459 | 0.459 | 0.477 | 0.492 | 0.446 | 0.375 | 0.371 |  | 15.521 | 0.50068 | 0.732 | 0
[33 empty] | 211.532 | Grand Total
251/085 CR 561 (Well 2 - Lake Crescent Hills ) - LUSI North | [6 empty] | Well 2 | MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | 251/085 CR 561 (Well 2 - Lake Crescent Hills ) - LUSI North
2019-01-01 | 0.227 | 0.397 | 0.378 | 0.22 | 0.29 | 0.324 | 0.278 | 0.261 | 0.349 | 0.317 | 0.286 | 0.354 | 0.366 | 0.324 | 0.288 | 0.338 | 0.378 | 0.248 | 0.36 | 0.321 | 0.273 | 0.279 | 0.311 | 0.343 | 0.262 | 0.317 | 0.323 | 0.206 | 0.244 | 0.286 | 0.27 |  | 9.418 | 0.30381 | 0.397 | 0
February | 0.244 | 0.306 | 0.36 | 0.279 | 0.256 | 0.358 | 0.314 | 0.306 | 0.363 | 0.355 | 0.198 | 0.29 | 0.268 | 0.272 | 0.216 | 0.358 | 0.408 | 0.263 | 0.338 | 0.379 | 0.36 | 0.253 | 0.378 | 0.399 | 0.322 | 0.266 | 0.362 | 0.303 |  |  |  |  | 8.774 | 0.31336 | 0.408 | 0
March | 0.218 | 0.418 | 0.42 | 0.318 | 0.344 | 0.353 | 0.272 | 0.364 | 0.34 | 0.464 | 0.496 | 0.37 | 0.403 | 0.363 | 0.51 | 0.307 | 0.501 | 0.33 | 0.29 | 0.335 | 0.392 | 0.264 | 0.363 | 0.36 | 0.641 | 0.316 | 0.391 | 0.385 | 0.437 | 0.345 | 0.575 |  | 11.885 | 0.38339 | 0.641 | 0
April | 0.521 | 0.25 | 0.473 | 0.448 | 0.389 | 0.383 | 0.413 | 0.39 | 0.241 | 0.417 | 0.419 | 0.393 | 0.429 | 0.56 | 0.391 | 0.316 | 0.346 | 0.497 | 0.423 | 0.35 | 0.415 | 0.352 | 0.382 | 0.386 | 0.507 | 0.45 | 0.352 | 0.492 | 0.611 | 0.402 |  |  | 12.398 | 0.41327 | 0.611 | 0
May | 0.575 | 0.426 | 0.374 | 0.448 | 0.377 | 0.297 | 0.311 | 0.416 | 0.457 | 0.419 | 0.371 | 0.44 | 0.476 | 0.268 | 0.373 | 0.429 | 0.335 | 0.413 | 0.476 | 0.509 | 0.392 | 0.438 | 0.536 | 0.554 | 0.455 | 0.553 | 0.628 | 0.554 | 0.534 | 0.59 | 0.532 |  | 13.956 | 0.45019 | 0.628 | 0
June | 0.349 | 0.361 | 0.676 | 0.348 | 0.411 | 0.415 | 0.343 | 0.386 | 0.365 | 0.316 | 0.232 | 0.323 | 0.372 | 0.293 | 0.269 | 0.396 | 0.254 | 0.283 | 0.301 | 0.286 | 0.281 | 0.353 | 0.414 | 0.384 | 0.377 | 0.396 | 0.534 | 0.379 | 0.41 | 0.401 |  |  | 10.908 | 0.3636 | 0.676 | 0
July | 0.382 | 0.424 | 0.483 | 0.372 | 0.407 | 0.444 | 0.334 | 0.375 | 0.279 | 0.378 | 0.396 | 0.279 | 0.312 | 0.347 | 0.42 | 0.365 | 0.431 | 0.359 | 0.282 | 0.413 | 0.374 | 0.431 | 0.257 | 0.431 | 0.32 | 0.243 | 0.305 | 0.356 | 0.385 | 0.297 | 0.365 |  | 11.246 | 0.36277 | 0.483 | 0
August | 0.28 | 0.303 | 0.283 | 0.316 | 0.377 | 0.264 | 0.307 | 0.336 | 0.316 | 0.319 | 0.303 | 0.359 | 0.292 | 0.303 | 0.309 | 0.274 | 0.359 | 0.339 | 0.336 | 0.264 | 0.345 | 0.367 | 0.336 | 0.374 | 0.37 | 0.434 | 0.273 | 0.307 | 0.358 | 0.277 | 0.311 |  | 9.991 | 0.32229 | 0.434 | 0
September | 0.291 | 0.354 | 0.207 | 0.303 | 0.293 | 0.277 | 0.41 | 0.362 | 0.494 | 0.252 | 0.431 | 0.405 | 0.324 | 0.277 | 0.392 | 0.409 | 0.325 | 0.447 | 0.411 | 0.411 | 0.41 | 0.515 | 0.519 | 0.378 | 0.383 | 0.626 | 0.575 | 0.364 | 0.563 | 0.636 |  |  | 12.044 | 0.40147 | 0.636 | 0
October | 0.42 | 0.337 | 0.68 | 0.47 | 0.413 | 0.502 | 0.569 | 0.278 | 0.329 | 0.307 | 0.399 | 0.379 | 0.405 | 0.526 | 0.391 | 0.453 | 0.441 | 0.422 | 0.291 | 0.369 | 0.338 | 0.262 | 0.381 | 0.334 | 0.392 | 0.286 | 0.341 | 0.295 | 0.276 | 0.369 | 0.395 |  | 12.05 | 0.38871 | 0.68 | 0
November | 0.384 | 0.343 | 0.503 | 0.399 | 0.337 | 0.373 | 0.418 | 0.369 | 0.309 | 0.398 | 0.353 | 0.289 | 0.398 | 0.354 | 0.311 | 0.292 | 0.411 | 0.323 | 0.287 | 0.403 | 0.323 | 0.358 | 0.451 | 0.375 | 0.302 | 0.267 | 0.389 | 0.44 | 0.284 | 0.422 |  |  | 10.865 | 0.36217 | 0.503 | 0
December | 0.398 | 0.377 | 0.257 | 0.357 | 0.405 | 0.338 | 0.302 | 0.453 | 0.415 | 0.293 | 0.408 | 0.292 | 0.296 | 0.317 | 0.353 | 0.304 | 0.258 | 0.266 | 0.292 | 0.249 | 0.324 | 0.299 | 0.264 | 0.2 | 0.284 | 0.284 | 0.295 | 0.306 | 0.275 | 0.234 | 0.229 |  | 9.624 | 0.31045 | 0.453 | 0
[33 empty] | 133.159 | Grand Total
251/175 CR 561 (Well 3 - Highland Point ) - LUSI North | [6 empty] | Well 3 | MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max | Proof | 251/175 CR 561 (Well 3 - Highland Point ) - LUSI North
2019-01-01 | 0.228 | 0.409 | 0.391 | 0.223 | 0.301 | 0.326 | 0.28 | 0.272 | 0.358 | 0.325 | 0.291 | 0.365 | 0.371 | 0.333 | 0.294 | 0.342 | 0.394 | 0.253 | 0.458 | 0.336 | 0.279 | 0.283 | 0.314 | 0.356 | 0.283 | 0.316 | 0.333 | 0.215 | 0.245 | 0.299 | 0.256 |  | 9.729 | 0.31384 | 0.458 | 0
February | 0.278 | 0.303 | 0.374 | 0.279 | 0.263 | 0.364 | 0.319 | 0.318 | 0.369 | 0.363 | 0.198 | 0.298 | 0.273 | 0.271 | 0.227 | 0.363 | 0.417 | 0.267 | 0.339 | 0.387 | 0.375 | 0.25 | 0.392 | 0.409 | 0.325 | 0.278 | 0.371 | 0.309 |  |  |  |  | 8.979 | 0.32068 | 0.417 | 0
March | 0.227 | 0.424 | 0.428 | 0.327 | 0.351 | 0.362 | 0.271 | 0.378 | 0.342 | 0.478 | 0.509 | 0.381 | 0.428 | 0.345 | 0.527 | 0.31 | 0.515 | 0.335 | 0.293 | 0.343 | 0.401 | 0.266 | 0.369 | 0.369 | 0.665 | 0.315 | 0.401 | 0.398 | 0.448 | 0.351 | 0.594 |  | 12.151 | 0.39197 | 0.665 | 0
April | 0.541 | 0.232 | 0.518 | 0.451 | 0.402 | 0.391 | 0.426 | 0.402 | 0.235 | 0.431 | 0.433 | 0.406 | 0.44 | 0.582 | 0.403 | 0.323 | 0.354 | 0.516 | 0.442 | 0.355 | 0.432 | 0.361 | 0.392 | 0.395 | 0.524 | 0.46 | 0.365 | 0.515 | 0.634 | 0.424 |  |  | 12.785 | 0.42617 | 0.634 | 0
May | 0.548 | 0.443 | 0.386 | 0.461 | 0.391 | 0.306 | 0.316 | 0.413 | 0.475 | 0.434 | 0.38 | 0.458 | 0.491 | 0.277 | 0.386 | 0.44 | 0.342 | 0.427 | 0.495 | 0.529 | 0.402 | 0.452 | 0.559 | 0.578 | 0.473 | 0.577 | 0.659 | 0.576 | 0.538 | 0.617 | 0.562 |  | 14.391 | 0.46423 | 0.659 | 0
June | 0.36 | 0.368 | 0.717 | 0.365 | 0.429 | 0.429 | 0.354 | 0.397 | 0.369 | 0.308 | 0.242 | 0.326 | 0.387 | 0.304 | 0.275 | 0.415 | 0.266 | 0.278 | 0.311 | 0.295 | 0.289 | 0.376 | 0.428 | 0.406 | 0.393 | 0.408 | 0.564 | 0.394 | 0.432 | 0.411 |  |  | 11.296 | 0.37653 | 0.717 | 0
July | 0.398 | 0.424 | 0.486 | 0.399 | 0.421 | 0.461 | 0.347 | 0.388 | 0.297 | 0.395 | 0.411 | 0.288 | 0.331 | 0.35 | 0.442 | 0.347 | 0.404 | 0.376 | 0.299 | 0.427 | 0.397 | 0.451 | 0.265 | 0.45 | 0.338 | 0.253 | 0.322 | 0.371 | 0.403 | 0.314 | 0.379 |  | 11.634 | 0.37529 | 0.486 | 0
August | 0.297 | 0.314 | 0.298 | 0.326 | 0.39 | 0.273 | 0.317 | 0.354 | 0.327 | 0.334 | 0.311 | 0.377 | 0.287 | 0.316 | 0.32 | 0.283 | 0.37 | 0.359 | 0.348 | 0.22 | 0.332 | 0.383 | 0.348 | 0.38 | 0.392 | 0.455 | 0.281 | 0.32 | 0.368 | 0.286 | 0.329 |  | 10.295 | 0.3321 | 0.455 | 0
September | 0.3 | 0.37 | 0.214 | 0.314 | 0.305 | 0.288 | 0.426 | 0.38 | 0.518 | 0.264 | 0.44 | 0.427 | 0.337 | 0.286 | 0.408 | 0.433 | 0.339 | 0.467 | 0.431 | 0.436 | 0.42 | 0.55 | 0.546 | 0.397 | 0.407 | 0.663 | 0.616 | 0.383 | 0.601 | 0.683 |  |  | 12.649 | 0.42163 | 0.683 | 0
October | 0.452 | 0.34 | 0.748 | 0.494 | 0.439 | 0.537 | 0.609 | 0.298 | 0.346 | 0.327 | 0.405 | 0.398 | 0.435 | 0.564 | 0.411 | 0.484 | 0.471 | 0.413 | 0.388 | 0.352 | 0.362 | 0.276 | 0.404 | 0.357 | 0.411 | 0.303 | 0.364 | 0.31 | 0.29 | 0.387 | 0.42 |  | 12.795 | 0.41274 | 0.748 | 0
November | 0.402 | 0.362 | 0.538 | 0.424 | 0.355 | 0.391 | 0.444 | 0.393 | 0.325 | 0.426 | 0.366 | 0.302 | 0.421 | 0.368 | 0.363 | 0.304 | 0.432 | 0.343 | 0.301 | 0.411 | 0.468 | 0.384 | 0.475 | 0.393 | 0.322 | 0.275 | 0.41 | 0.467 | 0.295 | 0.443 |  |  | 11.603 | 0.38677 | 0.538 | 0
December | 0.421 | 0.396 | 0.271 | 0.373 | 0.431 | 0.411 | 0.355 | 0.378 | 0.442 | 0.308 | 0.43 | 0.303 | 0.316 | 0.333 | 0.374 | 0.319 | 0.271 | 0.277 | 0.308 | 0.26 | 0.346 | 0.313 | 0.277 | 0.21 | 0.3 | 0.3 | 0.304 | 0.323 | 0.291 | 0.243 | 0.236 |  | 10.12 | 0.32645 | 0.442 | 0
[33 empty] | 128.698 | Grand Total
LUSI COMBINED - ALL AREAS IN LUSI NORTH & SOUTH
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Total | Avg. | Max
2019-01-01 | 3.236 | 4.538 | 4.576 | 3.43 | 3.376 | 4.014 | 3.741 | 3.076 | 4.252 | 3.986 | 3.733 | 3.856 | 4.761 | 4.026 | 3.277 | 4.339 | 4.314 | 3.726 | 4.5375 | 4.127 | 3.4455 | 3.338 | 4.15 | 4.096 | 3.359 | 4.035 | 4.086 | 3.013 | 3.007 | 3.838 | 3.536 |  | 118.825 |  | 4.761
February | 2.889 | 4.0245 | 4.6 | 3.2525 | 3.329 | 4.605 | 4.143 | 3.597 | 4.801 | 4.1545 | 2.7525 | 3.494 | 3.467 | 3.085 | 3.048 | 4.222 | 4.9105 | 3.8285 | 3.602 | 4.597 | 4.303 | 3.296 | 4.465 | 4.9515 | 3.9825 | 3.49 | 3.967 | 3.759 | 0 | 0 | 0 |  | 108.616 |  | 4.9515
March | 3.1 | 4.6675 | 4.97 | 4.2655 | 3.72 | 4.014 | 3.738 | 3.935 | 4.908 | 5.3705 | 4.9755 | 4.412 | 4.625 | 5.231 | 4.65 | 5.1345 | 5.0945 | 3.928 | 3.334 | 4.019 | 4.65 | 3.42 | 4.806 | 5.2745 | 6.1345 | 4.042 | 4.571 | 4.968 | 4.194 | 4.8425 | 6.298 |  | 141.2925 |  | 6.298
April | 5.1285 | 3.544 | 5.059 | 5.545 | 4.552 | 4.302 | 4.9815 | 3.9635 | 3.099 | 4.51 | 4.519 | 4.314 | 5.191 | 5.257 | 4.211 | 3.537 | 4.53 | 5.338 | 4.356 | 3.612 | 4.892 | 4.037 | 4.009 | 4.723 | 6.008 | 4.68 | 4.749 | 5.9905 | 5.9805 | 4.686 | 0 |  | 139.3045 |  | 6.008
May | 5.804 | 5.636 | 4.008 | 5.1825 | 4.483 | 3.4325 | 3.521 | 4.968 | 5.436 | 4.571 | 5.0145 | 5.677 | 4.8315 | 3.017 | 4.242 | 4.679 | 4.07 | 4.895 | 6.274 | 4.944 | 4.791 | 5.555 | 6.46 | 5.814 | 6.131 | 6.994 | 7.03 | 5.833 | 6.58 | 8.12 | 7.556 |  | 165.55 |  | 8.12
June | 5.3327 | 6.9242 | 7.5734 | 4.716 | 5.4023 | 6.4225 | 5.1845 | 5.0291 | 5.7572 | 4.057 | 2.975 | 4.0391 | 4.5776 | 3.866 | 4.1004 | 5.1019 | 3.2435 | 2.78 | 4.504 | 3.441 | 3.839 | 4.5922 | 5.7377 | 4.9705 | 4.7971 | 4.8379 | 6.0148 | 6.854 | 6.3932 | 5.9507 | 0 |  | 149.0145 |  | 7.5734
July | 4.3825 | 4.42 | 5.257 | 7.1962 | 4.244 | 5.3171 | 4.3221 | 3.62 | 3.071 | 4.5781 | 4.9698 | 3.744 | 4.5405 | 5.2316 | 3.943 | 3.823 | 4.6496 | 4.5953 | 3.694 | 5.1039 | 5.1709 | 3.9671 | 3.49 | 4.6066 | 4.309 | 3.114 | 4.2083 | 4.1778 | 4.3285 | 3.6621 | 4.5052 |  | 136.2423 |  | 7.1962
August | 4.239 | 3.718 | 3.741 | 4.4455 | 4.3305 | 3.017 | 4.05 | 4.723 | 3.868 | 3.947 | 4.3355 | 4.6905 | 3.067 | 4.013 | 4.371 | 3.574 | 4.172 | 4.7045 | 4.3585 | 3.437 | 4.206 | 5.028 | 4.089 | 4.651 | 4.7235 | 5.1505 | 3.182 | 3.828 | 4.431 | 3.713 | 4.523 |  | 128.327 |  | 5.1505
September | 3.4185 | 3.9535 | 2.962 | 3.693 | 3.57 | 3.905 | 4.7535 | 5.034 | 5.1995 | 3.713 | 4.841 | 5.43 | 4.333 | 4.2325 | 6.0415 | 3.946 | 4.148 | 5.363 | 6.169 | 5.534 | 5.3275 | 6.9725 | 5.797 | 4.534 | 6.596 | 6.934 | 6.646 | 5.9065 | 6.867 | 7.3985 | 0 |  | 153.219 |  | 7.3985
October | 5.063 | 5.357 | 7.484 | 6.423 | 6.691 | 6.2015 | 6.5115 | 3.711 | 4.839 | 4.163 | 4.781 | 5.2345 | 5.9115 | 6.203 | 4.744 | 5.92 | 6.082 | 5.069 | 4.734 | 4.3665 | 4.6365 | 3.821 | 4.904 | 5.172 | 4.438 | 4.234 | 4.318 | 4.192 | 2.832 | 5.531 | 5.264 |  | 158.832 |  | 7.484
November | 4.632 | 4.748 | 6.0715 | 5.5605 | 4.608 | 4.568 | 5.209 | 4.959 | 4.4195 | 4.8225 | 4.519 | 3.942 | 4.988 | 4.732 | 4.591 | 4.716 | 4.293 | 4.133 | 3.932 | 4.678 | 5.074 | 4.282 | 5.051 | 5.6245 | 3.6265 | 3.386 | 5.31 | 5.433 | 4.353 | 5.455 | 0 |  | 141.717 |  | 6.0715
December | 4.337 | 4.753 | 3.223 | 4.912 | 4.655 | 4.187 | 4.8675 | 5.595 | 5.0875 | 3.873 | 4.625 | 4.306 | 3.98 | 4.0995 | 3.972 | 4.1035 | 3.181 | 3.507 | 3.945 | 3.588 | 4.5005 | 3.6895 | 3.321 | 2.71 | 4.537 | 4 | 2.937 | 4.4265 | 3.31 | 3.1015 | 3.232 |  | 124.562 |  | 5.595
Totals | 51.5622 | 56.2837 | 59.5249 | 58.6217 | 52.9608 | 53.9856 | 55.0226 | 52.2107 | 54.7377 | 51.7456 | 52.0408 | 53.1391 | 54.2732 | 52.9935 | 51.1909 | 53.0959 | 52.6881 | 51.8673 | 53.44 | 51.4474 | 54.8359 | 51.9983 | 56.2797 | 57.1276 | 58.6421 | 54.8974 | 57.0191 | 58.3813 | 52.2762 | 56.2983 | 34.9142 | 0 | 1665.5018 |  | 59.5249
[31 empty] | ck |  | 165.55 | MAX | 8.12
Peak Days
Day | 14 | 6 | 7 | 3 | 17 | 15 | 5 | 10 | 16 | 21 | 13 | 18 | 20 | 8 | 11 | 4 | 9 | 22 | 2 | 12 | 1 | 24 | 28 | 25 | 19 | 23 | 29 | 26 | 27 | 31 | 30
May | 3.017 | 3.4325 | 3.521 | 4.008 | 4.07 | 4.242 | 4.483 | 4.571 | 4.679 | 4.791 | 4.8315 | 4.895 | 4.944 | 4.968 | 5.0145 | 5.1825 | 5.436 | 5.555 | 5.636 | 5.677 | 5.804 | 5.814 | 5.833 | 6.131 | 6.274 | 6.46 | 6.58 | 6.994 | 7.03 | 7.556 | 8.12

## W4lk2019 (hidden)
251/127 - Four Lakes
PWS ID No. 3354647
CUP No. N/A |  | Exp. N/A
FDEP Permitted Max Day Capacity of Plant - .088 mgd
Hyper Links'!A1 |  |  |  | Total Water Used/Loss |  |  |  |  | Source Mtr Error Adj. (04/20/17 -2.00%)(03/13/2019 -0.67%)
| Pumped | Pumped Daily Avg. | Pumped Daily Max. | Gallons Used | Gallons Loss | Total Used/ Loss | Pumped, Less Gallons Loss/ Used | Billed Consumption | Meter Adj. % | Pumped Meter Adj. | Pumped (-) Gals Loss/ Use (+) Source Mtr Error | Total AFW (Total Used/Loss + Billed) | AFW % plus source mtr. error | 2018 AFW % | Source Meter Error Adj.
January 2019 | 0.48813 | 0.015746 | 0.023704 | 0.00601 | 0 | 0.00601 | 0.48212 | 0.41131 | -0.67% | -0.0032705 | 0.47885 | 0.41732 | 86.07% | 88.75% |  | Meter Error % | Pumped Meter Error
February | 0.44534 | 0.015905 | 0.026685 | 0.0054 | 0 | 0.0054 | 0.43994 | 0.38474 | -0.67% | -0.0029838 | 0.43696 | 0.39014 | 88.2% | 96.51% | 03/01-03/26/19 | -0.67% | -0.0039085
March | 0.68594 | 0.022127 | 0.034115 | 0.00607 | 0 | 0.00607 | 0.67987 | 0.60371 | -0.67%&-1.76% | -0.0057141 | 0.67416 | 0.60978 | 89.64% | 91.7% | 03/27-03/31/19 | -1.76% | -0.0018056
April | 0.5145 | 0.01715 | 0.040683 | 0.020939 | 0 | 0.020939 | 0.49356 | 0.44672 | -1.76% | -0.0090552 | 0.4845 | 0.46766 | 92.52% | 94.61% |  |  | -0.0057141
May | 0.72708 | 0.023454 | 0.04398 | 0.00327 | 0 | 0.00327 | 0.72381 | 0.63874 | -1.76% | -0.012797 | 0.71101 | 0.64201 | 89.88% | 84.82%
June | 0.58576 | 0.019525 | 0.031717 | 0.00427 | 0 | 0.00427 | 0.58149 | 0.49993 | -1.76% | -0.010309 | 0.57118 | 0.5042 | 87.62% | 100.9%
July | 0.5067 | 0.016345 | 0.024404 | 0.005574 | 0 | 0.005574 | 0.50112 | 0.42408 | -1.76% | -0.0089179 | 0.49221 | 0.42966 | 86.32% | 87.96%
August | 0.42576 | 0.013734 | 0.018426 | 0.00493 | 0 | 0.00493 | 0.42083 | 0.35402 | -1.76% | -0.0074934 | 0.41334 | 0.35895 | 85.82% | 88.72%
September | 0.54411 | 0.018137 | 0.033991 | 0.00497 | 0 | 0.00497 | 0.53914 | 0.46255 | -1.76% | -0.0095763 | 0.52956 | 0.46752 | 87.46% | 91.7%
October | 0.53295 | 0.017192 | 0.03225 | 0.01318 | 0 | 0.01318 | 0.51977 | 0.4363 | -1.76% | -0.0093799 | 0.51039 | 0.44948 | 85.85% | 86.11%
November | 0.49053 | 0.016351 | 0.025311 | 0.01026 | 0 | 0.01026 | 0.48027 | 0.4151 | -1.76% | -0.0086333 | 0.47164 | 0.42536 | 88.27% | 87.27%
December | 0.45496 | 0.014676 | 0.0342 | 0.00916 | 0 | 0.00916 | 0.4458 | 0.37389 | -1.76% | -0.0080073 | 0.43779 | 0.38305 | 85.7% | 84.32%
YTD Total/Avg/Max | 6.4018 | 0.017529 | 0.04398 | 0.094033 | 0 | 0.094033 | 6.3077 | 5.4511 |  | -0.096138 | 6.2116 | 5.5451
| 6.4018 | [8 empty] | -0.08813 |  | 5.5451
| 0 | Proof to Daily Flow |  |  |  |  | Proof to Total Billed | 0 |  |  |  | YTD AFW % Jan - Dec | 87.83%
Water Loss-Use'!A1
[5 empty] | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input

## WLS2019 (hidden)
251/226 (664) - Lake Saunders | [9 empty] | Hyper Links'!A1
PWS ID No. 3354695
CUP No. 50094 |  | Exp. 05/05/2038
FDEP Permitted Max Day Capacity of Plant - .432 mgd
Hyper Links'!A1
|  |  |  | Total Water Used/Loss |  |  |  |  | Source Mtr Error Adj.
| Pumped | Pumped Daily Avg. | Pumped Daily Max | Gallons Used | Gallons Loss | Total Used/ Loss | Pumped, Less Gallons Loss/ Used | Billed Consumption | Meter Adj. % | Pumped Meter Adj. | Pumped + Source Mtr Error, Less Gals Loss/ Use | Total AFW (Total Used/Loss + Billed) | AFW % plus source mtr. error | 2018 AFW % | Source Meter Error Adj.
January 2019 | 0.2532 | 0.0081677 | 0.013905 | 0.07542 | 0 | 0.07542 |  | 0.16359 | 2.92% | 0.0073934 | 0.18517 | 0.23901 | 91.72% | 91.49% |  | Meter Error % | Pumped Meter Error
February | 0.26132 | 0.0093329 | 0.02151 | 0.09394 | 0.0148 | 0.10874 |  | 0.16927 | 2.92% | 0.0076305 | 0.16021 | 0.27801 | 103.4% | 87.06% | 03/01-03/26/19 | 2.92% | 0.0095093
March | 0.40711 | 0.013133 | 0.01977 | 0.09417 | 0 | 0.09417 |  | 0.28298 | 2.92%&-0.67% | 0.0089636 | 0.3219 | 0.37715 | 90.65% | 91.39% | 03/27-03/31/19 | -0.67% | -0.00054572
April | 0.39963 | 0.013321 | 0.06503 | 0.14984 | 0 | 0.14984 |  | 0.23284 | -0.67% | -0.0026775 | 0.24711 | 0.38268 | 96.4% | 94.98% |  |  | 0.0089636
May | 0.35343 | 0.011401 | 0.02073 | 0.06714 | 0 | 0.06714 |  | 0.2565 | -0.67% | -0.002368 | 0.28392 | 0.32364 | 92.19% | 96.54%
June | 0.40025 | 0.013342 | 0.03132 | 0.08163 | 0 | 0.08163 |  | 0.28401 | -0.67% | -0.0026817 | 0.31594 | 0.36564 | 91.97% | 70.48%
July | 0.28439 | 0.0091739 | 0.0148 | 0.05243 | 0 | 0.05243 |  | 0.20669 | -0.67% | -0.0019054 | 0.23005 | 0.25912 | 91.73% | 92.11%
August | 0.26959 | 0.0086963 | 0.01412 | 0.05321 | 0 | 0.05321 |  | 0.15379 | -0.67% | -0.0018062 | 0.21457 | 0.207 | 77.3% | 73.54%
September | 0.3393 | 0.01131 | 0.02002 | 0.06014 | 0 | 0.06014 |  | 0.29303 | -0.67% | -0.0022733 | 0.27688 | 0.35317 | 104.8% | 115.3%
October | 0.36481 | 0.011768 | 0.02182 | 0.07276 | 0 | 0.07276 |  | 0.25939 | -0.67% | -0.0024442 | 0.28961 | 0.33215 | 91.66% | 90.32%
November | 0.30236 | 0.010079 | 0.015 | 0.05913 | 0 | 0.05913 |  | 0.21528 | -0.67% | -0.0020258 | 0.24121 | 0.27441 | 91.37% | 91.37%
December | 0.28431 | 0.0091713 | 0.02551 | 0.05911 | 0 | 0.05911 |  | 0.19118 | -0.67% | -0.0019049 | 0.2233 | 0.25029 | 88.63% | 92.61%
YTD Total/Avg/Max | 3.9197 | 0.010741 | 0.06503 | 0.91892 | 0.0148 | 0.93372 |  | 2.7086 |  | 0.0039005 | 2.9899 | 3.6423
| 3.9197 | [8 empty] | 0.0039005 |  | 3.6423
| 0 | Proof to Daily Flow |  |  |  | Proof to Total Billed |  | 0 |  |  |  | YTD AFW% Jan-Dec | 92.83%
Water Loss-Use'!A1 |  |  |  |  | Water Loss/Use Proof | 0
Verif. W/UIWtrMn WLU wrksht & WAF Input

## FLOW4LK19 (hidden)
251/127- Four Lakes | [9 empty] | Hyper Links'!A1
MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0.012649 | 0.021765 | 0.011587 | 0.013906 | 0.016717 | 0.016717 | 0.013423 | 0.009032 | 0.021765 | 0.021288 | 0.014912 | 0.018846 | 0.018846 | 0.01085 | 0.012967 | 0.021461 | 0.014308 | 0.014528 | 0.020327 | 0.020327 | 0.015805 | 0.009062 | 0.023704 | 0.013892 | 0.009516 | 0.017417 | 0.017417 | 0.009577 | 0.012758 | 0.020262 | 0.012499 | 0.48813 | 0.015746 | 0.023704 | 0
February | 0.011499 | 0.020567 | 0.020567 | 0.013997 | 0.01438 | 0.019387 | 0.012829 | 0.012771 | 0.017701 | 0.017701 | 0.011272 | 0.011795 | 0.015355 | 0.012275 | 0.011256 | 0.018628 | 0.018628 | 0.017022 | 0.013665 | 0.026685 | 0.011096 | 0.015102 | 0.021816 | 0.021816 | 0.014851 | 0.015947 | 0.014811 | 0.011923 |  |  |  | 0.44534 | 0.015905 | 0.026685 | 0
March | 0.014747 | 0.025786 | 0.025786 | 0.015359 | 0.011063 | 0.0222 | 0.022302 | 0.014087 | 0.032202 | 0.032202 | 0.021696 | 0.022358 | 0.034115 | 0.017988 | 0.02343 | 0.032383 | 0.032383 | 0.020536 | 0.022773 | 0.026376 | 0.01552 | 0.016191 | 0.021816 | 0.021816 | 0.019585 | 0.018653 | 0.026447 | 0.012244 | 0.01331 | 0.025295 | 0.025295 | 0.68594 | 0.022127 | 0.034115 | 0
April | 0.016691 | 0.009955 | 0.015414 | 0.019755 | 0.01477 | 0.02071 | 0.02071 | 0.009998 | 0.013029 | 0.024816 | 0.015692 | 0.016763 | 0.020726 | 0.020726 | 0.01139 | 0.010378 | 0.020444 | 0.015388 | 0.012493 | 0.015352 | 0.015352 | 0.010855 | 0.011617 | 0.040683 | 0.016639 | 0.014107 | 0.024826 | 0.024826 | 0.012877 | 0.017515 |  | 0.5145 | 0.01715 | 0.040683 | 0
May | 0.023161 | 0.023354 | 0.014352 | 0.02191 | 0.02191 | 0.009803 | 0.011843 | 0.018202 | 0.02341 | 0.012513 | 0.024502 | 0.024502 | 0.016312 | 0.016277 | 0.020213 | 0.012903 | 0.020997 | 0.02914 | 0.02914 | 0.031815 | 0.018219 | 0.026253 | 0.025904 | 0.022661 | 0.036816 | 0.036816 | 0.04398 | 0.026801 | 0.02744 | 0.029441 | 0.026487 | 0.72708 | 0.023454 | 0.04398 | 0
June | 0.027143 | 0.027143 | 0.018933 | 0.019231 | 0.031717 | 0.018925 | 0.024809 | 0.021508 | 0.021508 | 0.012746 | 0.013287 | 0.020102 | 0.011677 | 0.015671 | 0.018426 | 0.018426 | 0.011628 | 0.012035 | 0.018354 | 0.021646 | 0.01341 | 0.023443 | 0.023443 | 0.015065 | 0.017726 | 0.02862 | 0.016392 | 0.020776 | 0.020986 | 0.020986 |  | 0.58576 | 0.019525 | 0.031717 | 0
July | 0.011794 | 0.016332 | 0.023404 | 0.021895 | 0.017747 | 0.018759 | 0.018759 | 0.013102 | 0.013685 | 0.024404 | 0.017132 | 0.01921 | 0.017725 | 0.017725 | 0.010284 | 0.014855 | 0.017551 | 0.017355 | 0.011758 | 0.017611 | 0.017611 | 0.017203 | 0.01448 | 0.017194 | 0.010829 | 0.012878 | 0.016095 | 0.016095 | 0.011848 | 0.013137 | 0.01824 | 0.5067 | 0.016345 | 0.024404 | 0
August | 0.014893 | 0.010481 | 0.016053 | 0.016053 | 0.008969 | 0.010983 | 0.015997 | 0.011732 | 0.012116 | 0.017421 | 0.017421 | 0.013941 | 0.013002 | 0.016431 | 0.016228 | 0.010637 | 0.012779 | 0.012779 | 0.010485 | 0.011953 | 0.016858 | 0.011628 | 0.013069 | 0.016088 | 0.016088 | 0.010243 | 0.013699 | 0.018426 | 0.010302 | 0.014005 | 0.015005 | 0.42576 | 0.013734 | 0.018426 | 0
September | 0.015005 | 0.008607 | 0.010128 | 0.01892 | 0.01091 | 0.010929 | 0.016011 | 0.016011 | 0.015128 | 0.015386 | 0.016968 | 0.020132 | 0.013606 | 0.018177 | 0.018177 | 0.010355 | 0.012334 | 0.026686 | 0.01156 | 0.015512 | 0.020159 | 0.020159 | 0.015696 | 0.017925 | 0.033991 | 0.024886 | 0.027153 | 0.028451 | 0.028451 | 0.0267 |  | 0.54411 | 0.018137 | 0.033991 | 0
October | 0.018856 | 0.024475 | 0.020274 | 0.03225 | 0.027675 | 0.027675 | 0.011757 | 0.01588 | 0.015548 | 0.015381 | 0.010193 | 0.017414 | 0.017414 | 0.015268 | 0.012944 | 0.022658 | 0.017376 | 0.011918 | 0.016178 | 0.016178 | 0.012388 | 0.011229 | 0.020346 | 0.014243 | 0.012493 | 0.014878 | 0.014878 | 0.010531 | 0.012388 | 0.024288 | 0.017973 | 0.53295 | 0.017192 | 0.03225 | 0
November | 0.015212 | 0.023057 | 0.023057 | 0.013847 | 0.011996 | 0.020707 | 0.012946 | 0.012962 | 0.017559 | 0.017559 | 0.014864 | 0.015805 | 0.025311 | 0.010921 | 0.014175 | 0.018909 | 0.018909 | 0.009435 | 0.01476 | 0.020881 | 0.015148 | 0.012709 | 0.020675 | 0.020675 | 0.011347 | 0.010381 | 0.018888 | 0.011958 | 0.018756 | 0.01712 |  | 0.49053 | 0.016351 | 0.025311 | 0
December | 0.0342 | 0.011023 | 0.011429 | 0.01909 | 0.012543 | 0.014649 | 0.018658 | 0.018658 | 0.01312 | 0.013232 | 0.015216 | 0.014898 | 0.009897 | 0.016043 | 0.016043 | 0.011824 | 0.013395 | 0.015703 | 0.01281 | 0.014735 | 0.016501 | 0.016501 | 0.010635 | 0.015814 | 0.016701 | 0.014037 | 0.008423 | 0.01494 | 0.01494 | 0.011727 | 0.007577 | 0.45496 | 0.014676 | 0.0342 | 0
[32 empty] | 6.4018 | Grand Total
[32 empty] | 0.72708 | MAX | 0.04398
Peak Days
Day | 6 | 7 | 10 | 16 | 3 | 14 | 13 | 8 | 21 | 15 | 17 | 4 | 5 | 24 | 1 | 2 | 9 | 11 | 12 | 23 | 22 | 31 | 28 | 29 | 18 | 19 | 30 | 20 | 25 | 26 | 27
May | 0.009803 | 0.011843 | 0.012513 | 0.012903 | 0.014352 | 0.016277 | 0.016312 | 0.018202 | 0.018219 | 0.020213 | 0.020997 | 0.02191 | 0.02191 | 0.022661 | 0.023161 | 0.023354 | 0.02341 | 0.024502 | 0.024502 | 0.025904 | 0.026253 | 0.026487 | 0.026801 | 0.02744 | 0.02914 | 0.02914 | 0.029441 | 0.031815 | 0.036816 | 0.036816 | 0.04398

## FLOWLS19 (hidden)
251/226 - Lake Saunders | [9 empty] | Hyper Links'!A1
MWAF - link to AH(x)
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg. | Max | Proof
2019-01-01 | 0.00495 | 0.01144 | 0.00672 | 0.00408 | 0.008615 | 0.008615 | 0.0054 | 0.00807 | 0.0089 | 0.00908 | 0.00788 | 0.013905 | 0.013905 | 0.00944 | 0.00368 | 0.00903 | 0.00917 | 0.00594 | 0.00973 | 0.00973 | 0.00559 | 0.00546 | 0.01036 | 0.00693 | 0.00503 | 0.010095 | 0.010095 | 0.0058 | 0.00791 | 0.0102 | 0.00745 | 0.2532 | 0.0081677 | 0.013905 | 0
February | 0.00781 | 0.01039 | 0.01039 | 0.00947 | 0.00691 | 0.00876 | 0.00932 | 0.00801 | 0.01052 | 0.01052 | 0.00716 | 0.00528 | 0.02151 | 0.00801 | 0.00567 | 0.01477 | 0.01477 | 0.00857 | 0.00665 | 0.00817 | 0.00795 | 0.00627 | 0.01213 | 0.01213 | 0.00526 | 0.00836 | 0.0092 | 0.00736 |  |  |  | 0.26132 | 0.0093329 | 0.02151 | 0
March | 0.00824 | 0.00969 | 0.00969 | 0.00877 | 0.00713 | 0.01275 | 0.00748 | 0.00985 | 0.01652 | 0.01652 | 0.01977 | 0.01102 | 0.01154 | 0.01465 | 0.01229 | 0.01529 | 0.01529 | 0.00457 | 0.01553 | 0.01538 | 0.01067 | 0.01463 | 0.01696 | 0.01696 | 0.01075 | 0.01372 | 0.01893 | 0.00905 | 0.01526 | 0.019105 | 0.019105 | 0.40711 | 0.013133 | 0.01977 | 0
April | 0.00972 | 0.0072 | 0.00966 | 0.00629 | 0.01053 | 0.01673 | 0.01673 | 0.00794 | 0.01404 | 0.013 | 0.01299 | 0.01139 | 0.01654 | 0.01654 | 0.00838 | 0.00813 | 0.01179 | 0.0119 | 0.01065 | 0.00845 | 0.00845 | 0.00735 | 0.06503 | 0.01353 | 0.01274 | 0.0132 | 0.014995 | 0.014995 | 0.00867 | 0.01207 |  | 0.39963 | 0.013321 | 0.06503 | 0
May | 0.01447 | 0.01311 | 0.0074 | 0.014715 | 0.014715 | 0.00382 | 0.00868 | 0.0156 | 0.01007 | 0.0085 | 0.013055 | 0.013055 | 0.00341 | 0.00978 | 0.01188 | 0.01652 | 0.00811 | 0.007795 | 0.007795 | 0.00892 | 0.00564 | 0.00783 | 0.00814 | 0.01138 | 0.01478 | 0.01478 | 0.01218 | 0.00895 | 0.01811 | 0.01951 | 0.02073 | 0.35343 | 0.011401 | 0.02073 | 0
June | 0.015175 | 0.015175 | 0.00972 | 0.01407 | 0.01501 | 0.01395 | 0.01226 | 0.01261 | 0.01261 | 0.00522 | 0.01215 | 0.02638 | 0.01284 | 0.00601 | 0.01209 | 0.01209 | 0.00639 | 0.03132 | 0.0078 | 0.00862 | 0.01341 | 0.014215 | 0.014215 | 0.01015 | 0.01337 | 0.02033 | 0.01307 | 0.0114 | 0.0143 | 0.0143 |  | 0.40025 | 0.013342 | 0.03132 | 0
July | 0.01102 | 0.01195 | 0.01328 | 0.0148 | 0.01202 | 0.011085 | 0.011085 | 0.00475 | 0.01025 | 0.00961 | 0.00872 | 0.00518 | 0.009605 | 0.009605 | 0.00479 | 0.00736 | 0.01121 | 0.01004 | 0.00427 | 0.0093 | 0.0093 | 0.00446 | 0.01042 | 0.00616 | 0.00708 | 0.00764 | 0.012555 | 0.012555 | 0.00344 | 0.00813 | 0.01272 | 0.28439 | 0.0091739 | 0.0148 | 0
August | 0.00984 | 0.0072 | 0.01043 | 0.01043 | 0.00446 | 0.00992 | 0.00581 | 0.00666 | 0.00982 | 0.008615 | 0.008615 | 0.00736 | 0.00613 | 0.00946 | 0.01412 | 0.00462 | 0.00979 | 0.00979 | 0.00412 | 0.00853 | 0.01116 | 0.00819 | 0.00994 | 0.01129 | 0.01129 | 0.00554 | 0.00953 | 0.0065 | 0.00984 | 0.00969 | 0.010895 | 0.26959 | 0.0086963 | 0.01412 | 0
September | 0.010895 | 0.00457 | 0.00591 | 0.00847 | 0.00501 | 0.00591 | 0.005985 | 0.005985 | 0.01499 | 0.01243 | 0.01054 | 0.00978 | 0.00762 | 0.011455 | 0.011455 | 0.00769 | 0.00785 | 0.01186 | 0.01189 | 0.0137 | 0.016475 | 0.016475 | 0.00775 | 0.01816 | 0.02002 | 0.00936 | 0.01715 | 0.019725 | 0.019725 | 0.01046 |  | 0.3393 | 0.01131 | 0.02002 | 0
October | 0.02182 | 0.01184 | 0.01112 | 0.01698 | 0.0195 | 0.0195 | 0.00823 | 0.00659 | 0.00668 | 0.01514 | 0.0117 | 0.01769 | 0.01769 | 0.01691 | 0.00513 | 0.0096 | 0.01139 | 0.00705 | 0.01061 | 0.01061 | 0.00456 | 0.00585 | 0.01273 | 0.01164 | 0.00771 | 0.01353 | 0.01353 | 0.00523 | 0.01065 | 0.00991 | 0.01369 | 0.36481 | 0.011768 | 0.02182 | 0
November | 0.00916 | 0.015 | 0.015 | 0.00725 | 0.0045 | 0.01369 | 0.00862 | 0.00849 | 0.0106 | 0.0106 | 0.00469 | 0.0145 | 0.00885 | 0.0089 | 0.0091 | 0.009215 | 0.009215 | 0.00586 | 0.00984 | 0.0093 | 0.01361 | 0.0076 | 0.014435 | 0.014435 | 0.00406 | 0.00772 | 0.01344 | 0.01304 | 0.00889 | 0.012755 |  | 0.30236 | 0.010079 | 0.015 | 0
December | 0.02551 | 0.00484 | 0.00794 | 0.00989 | 0.01237 | 0.00973 | 0.012075 | 0.012075 | 0.00661 | 0.007 | 0.01023 | 0.01091 | 0.00438 | 0.010125 | 0.010125 | 0.00476 | 0.00892 | 0.00748 | 0.00752 | 0.00875 | 0.009915 | 0.009915 | 0.00657 | 0.01044 | 0.00759 | 0.00796 | 0.00636 | 0.010435 | 0.010435 | 0.00782 | 0.00563 | 0.28431 | 0.0091713 | 0.02551 | 0
[32 empty] | 3.9197 | Grand Total
[32 empty] | 0.40711 | MAX | 0.06503
Peak Days
Day | 18 | 5 | 7 | 1 | 4 | 28 | 2 | 3 | 8 | 21 | 25 | 12 | 13 | 15 | 6 | 26 | 22 | 14 | 29 | 16 | 17 | 20 | 19 | 9 | 10 | 23 | 24 | 27 | 30 | 31 | 11
March | 0.00457 | 0.00713 | 0.00748 | 0.00824 | 0.00877 | 0.00905 | 0.00969 | 0.00969 | 0.00985 | 0.01067 | 0.01075 | 0.01102 | 0.01154 | 0.01229 | 0.01275 | 0.01372 | 0.01463 | 0.01465 | 0.01526 | 0.01529 | 0.01529 | 0.01538 | 0.01553 | 0.01652 | 0.01652 | 0.01696 | 0.01696 | 0.01893 | 0.019105 | 0.019105 | 0.01977

## WW 2019 Lake Grove (hidden)
2019 Lake Groves DMR Flow Summary
Hyperlinks!A1
Note: Operator to send the Lake Groves WWTP Log (Excel) which contains the daily flows that can be Copy/Paste Special/Transpose to this worksheet by FLW.
FLW-02 | Reuse
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0.193 | 0.379 | 0.349 | 0.228 | 0.315 | 0.366 | 0.219 | 0.21 | 0.361 | 0.356 | 0.226 | 0.436 | 0.295 | 0.339 | 0.239 | 0.392 | 0.351 | 0.23 | 0.446 | 0.354 | 0.212 | 0.221 | 0.38 | 0.33 | 0.179 | 0.399 | 0.377 | 0.159 | 0.164 | 0.233 | 0.309 | 9.247 | 0.29829 | 0.446
February | 0.343 | 0.183 | 0.567 | 0.225 | 0.279 | 0.213 | 0.503 | 0.241 | 0.245 | 0.482 | 0.302 | 0.196 | 0.252 | 0.26 | 0.267 | 0.21 | 0.368 | 0.458 | 0.405 | 0.216 | 0.562 | 0.314 | 0.204 | 0.438 | 0.349 | 0.261 | 0.255 | 0.347 |  |  |  | 8.945 | 0.31946 | 0.567
March | 0.208 | 0.336 | 0.344 | 0.235 | 0.24 | 0.334 | 0.315 | 0.232 | 0.355 | 0.367 | 0.289 | 0.268 | 0.379 | 0.381 | 0.297 | 0.399 | 0.402 | 0.291 | 0.282 | 0.327 | 0.335 | 0.269 | 0.377 | 0.415 | 0.306 | 0.297 | 0.402 | 0.32 | 0.246 | 0.378 | 0.375 | 10.001 | 0.32261 | 0.415
April | 0.301 | 0.236 | 0.355 | 0.467 | 0.316 | 0.425 | 0.427 | 0.246 | 0.202 | 0.383 | 0.39 | 0.277 | 0.49 | 0.434 | 0.232 | 0.259 | 0.463 | 0.423 | 0.276 | 0.333 | 0.444 | 0.277 | 0.29 | 0.481 | 0.471 | 0.298 | 0.477 | 0.497 | 0.372 | 0.344 |  | 10.886 | 0.36287 | 0.497
May | 0.583 | 0.479 | 0.327 | 0.544 | 0.436 | 0.22 | 0.282 | 0.503 | 0.485 | 0.348 | 0.607 | 0.626 | 0.414 | 0.27 | 0.425 | 0.439 | 0.287 | 0.487 | 0.61 | 0.309 | 0.333 | 0.608 | 0.571 | 0.395 | 0.634 | 0.634 | 0.492 | 0.228 | 0.763 | 0.662 | 0.49 | 14.491 | 0.46745 | 0.763
June | 0.616 | 0.783 | 0.42 | 0.209 | 0.598 | 0.585 | 0.253 | 0.595 | 0.508 | 0.264 | 0.31 | 0.407 | 0.453 | 0.261 | 0.407 | 0.489 | 0.248 | 0.25 | 0.341 | 0.321 | 0.276 | 0.476 | 0.552 | 0.383 | 0.383 | 0.649 | 0.504 | 0.578 | 0.547 | 0.582 |  | 13.248 | 0.4416 | 0.783
July | 0.378 | 0.415 | 0.619 | 0.444 | 0.392 | 0.413 | 0.404 | 0.251 | 0.245 | 0.468 | 0.491 | 0.289 | 0.337 | 0.456 | 0.322 | 0.237 | 0.45 | 0.444 | 0.258 | 0.335 | 0.473 | 0.256 | 0.282 | 0.43 | 0.443 | 0.229 | 0.348 | 0.411 | 0.297 | 0.231 | 0.429 | 11.477 | 0.37023 | 0.619
August | 0.471 | 0.272 | 0.329 | 0.429 | 0.179 | 0.22 | 0.335 | 0.219 | 0.295 | 0.334 | 0.395 | 0.191 | 0.193 | 0.327 | 0.358 | 0.159 | 0.317 | 0.366 | 0.224 | 0.241 | 0.366 | 0.379 | 0.167 | 0.323 | 0.359 | 0.21 | 0.176 | 0.276 | 0.337 | 0.164 | 0.235 | 8.846 | 0.28535 | 0.471
September | 0.262 | 0.115 | 0.142 | 0.216 | 0.243 | 0.161 | 0.392 | 0.369 | 0.235 | 0.232 | 0.454 | 0.415 | 0.238 | 0.464 | 0.37 | 0.23 | 0.275 | 0.506 | 0.447 | 0.282 | 0.527 | 0.46 | 0.338 | 0.289 | 0.574 | 0.567 | 0.354 | 0.578 | 0.54 | 0.333 |  | 10.608 | 0.3536 | 0.578
October | 0.333 | 0.533 | 0.49 | 0.134 | 0.62 | 0.559 | 0.325 | 0.202 | 0.314 | 0.333 | 0.253 | 0.451 | 0.46 | 0.267 | 0.275 | 0.464 | 0.454 | 0.273 | 0.32 | 0.357 | 0.247 | 0.19 | 0.441 | 0.403 | 0.236 | 0.338 | 0.346 | 0.219 | 0.103 | 0.402 | 0.392 | 10.734 | 0.34626 | 0.62
November | 0.256 | 0.405 | 0.449 | 0.253 | 0.236 | 0.411 | 0.377 | 0.241 | 0.308 | 0.377 | 0.234 | 0.221 | 0.408 | 0.354 | 0.536 | 0 | 0.355 | 0.219 | 0.191 | 0.36 | 0.379 | 0.204 | 0.389 | 0.336 | 0.211 | 0.196 | 0.395 | 0.355 | 0.212 | 0.354 |  | 9.222 | 0.3074 | 0.536
December | 0.381 | 0.197 | 0.171 | 0.38 | 0.332 | 0.204 | 0.36 | 0.365 | 0.264 | 0.214 | 0.38 | 0.347 | 0.193 | 0.279 | 0.327 | 0.193 | 0.193 | 0.254 | 0.291 | 0.216 | 0.321 | 0.268 | 0.157 | 0.131 | 0.262 | 0.254 | 0.186 | 0.275 | 0.219 | 0.138 | 0.135 | 7.887 | 0.25442 | 0.381
FLW-03 | Total Plant Flow
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0.638 | 0.565 | 0.638 | 0.568 | 0.517 | 0.539 | 0.629 | 0.508 | 0.489 | 0.555 | 0.447 | 0.5 | 0.557 | 0.553 | 0.541 | 0.483 | 0.543 | 0.492 | 0.457 | 0.566 | 0.56 | 0.493 | 0.472 | 0.64 | 0.468 | 0.457 | 0.534 | 0.593 | 0.518 | 0.501 | 0.529 | 16.55 | 0.53387 | 0.64
February | 0.482 | 0.491 | 0.569 | 0.589 | 0.532 | 0.519 | 0.496 | 0.505 | 0.509 | 0.608 | 0.586 | 0.539 | 0.532 | 0.519 | 0.486 | 0.583 | 0.575 | 0.557 | 0.571 | 0.492 | 0.562 | 0.547 | 0.601 | 0.561 | 0.607 | 0.492 | 0.509 | 0.569 |  |  |  | 15.188 | 0.54243 | 0.608
March | 0.55 | 0.473 | 0.578 | 0.557 | 0.575 | 0.593 | 0.487 | 0.556 | 0.519 | 0.522 | 0.635 | 0.499 | 0.525 | 0.599 | 0.456 | 0.561 | 0.542 | 0.524 | 0.487 | 0.51 | 0.52 | 0.52 | 0.539 | 0.548 | 0.598 | 0.501 | 0.524 | 0.544 | 0.489 | 0.502 | 0.576 | 16.609 | 0.53577 | 0.635
April | 0.549 | 0.531 | 0.558 | 0.586 | 0.513 | 0.485 | 0.591 | 0.548 | 0.557 | 0.598 | 0.444 | 0.578 | 0.527 | 0.5 | 0.614 | 0.526 | 0.529 | 0.598 | 0.491 | 0.546 | 0.603 | 0.575 | 0.552 | 0.516 | 0.541 | 0.473 | 0.503 | 0.588 | 0.553 | 0.498 |  | 16.271 | 0.54237 | 0.614
May | 0.497 | 0.501 | 0.544 | 0.474 | 0.584 | 0.584 | 0.51 | 0.495 | 0.563 | 0.491 | 0.508 | 0.511 | 0.572 | 0.506 | 0.709 | 0.538 | 0.536 | 0.509 | 0.576 | 0.494 | 0.5 | 0.487 | 0.5 | 0.468 | 0.538 | 0.505 | 0.607 | 0.487 | 0.496 | 0.486 | 0.49 | 16.266 | 0.52471 | 0.709
June | 0.502 | 0.563 | 0.485 | 0.485 | 0.491 | 0.561 | 0.475 | 0.553 | 0.577 | 0.52 | 0.503 | 0.55 | 0.504 | 0.6 | 0.479 | 0.591 | 0.555 | 0.523 | 0.605 | 0.627 | 0.496 | 0.49 | 0.63 | 0.534 | 0.614 | 0.504 | 0.523 | 0.478 | 0.575 | 0.504 |  | 16.097 | 0.53657 | 0.63
July | 0.59 | 0.516 | 0.531 | 0.582 | 0.504 | 0.616 | 0.646 | 0.546 | 0.581 | 0.584 | 0.571 | 0.542 | 0.648 | 0.592 | 0.52 | 0.557 | 0.523 | 0.59 | 0.447 | 0.575 | 0.64 | 0.499 | 0.565 | 0.532 | 0.514 | 0.623 | 0.564 | 0.601 | 0.585 | 0.553 | 0.59 | 17.527 | 0.56539 | 0.648
August | 0.56 | 0.512 | 0.502 | 0.618 | 0.53 | 0.573 | 0.521 | 0.568 | 0.528 | 0.529 | 0.606 | 0.522 | 0.545 | 0.537 | 0.57 | 0.501 | 0.563 | 0.654 | 0.548 | 0.547 | 0.589 | 0.573 | 0.557 | 0.557 | 0.589 | 0.587 | 0.575 | 0.546 | 0.567 | 0.526 | 0.623 | 17.323 | 0.55881 | 0.654
September | 0.569 | 0.523 | 0.618 | 0.619 | 0.475 | 0.529 | 0.531 | 0.529 | 0.543 | 0.564 | 0.502 | 0.55 | 0.439 | 0.525 | 0.552 | 0.612 | 0.528 | 0.513 | 0.542 | 0.503 | 0.489 | 0.576 | 0.609 | 0.507 | 0.508 | 0.534 | 0.47 | 0.514 | 0.576 | 0.56 |  | 16.109 | 0.53697 | 0.619
October | 0.557 | 0.504 | 0.512 | 0.574 | 0.492 | 0.557 | 0.595 | 0.581 | 0.572 | 0.493 | 0.466 | 0.555 | 0.554 | 0.558 | 0.552 | 0.535 | 0.56 | 0.508 | 0.583 | 0.632 | 0.585 | 0.524 | 0.544 | 0.486 | 0.533 | 0.574 | 0.605 | 0.573 | 0.559 | 0.52 | 0.59 | 17.033 | 0.54945 | 0.632
November | 0.548 | 0.544 | 0.616 | 0.514 | 0.61 | 0.566 | 0.502 | 0.524 | 0.566 | 0.624 | 0.51 | 0.598 | 0.536 | 0.543 | 0.609 | 0.559 | 0.558 | 0.618 | 0.55 | 0.526 | 0.523 | 0.566 | 0.503 | 0.628 | 0.518 | 0.533 | 0.582 | 0.599 | 0.621 | 0.532 |  | 16.826 | 0.56087 | 0.628
December | 0.546 | 0.619 | 0.521 | 0.511 | 0.557 | 0.55 | 0.522 | 0.514 | 0.55 | 0.567 | 0.517 | 0.502 | 0.591 | 0.55 | 0.564 | 0.569 | 0.529 | 0.55 | 0.555 | 0.548 | 0.652 | 0.562 | 0.667 | 0.569 | 0.739 | 0.583 | 0.616 | 0.651 | 0.594 | 0.687 | 0.612 | 17.864 | 0.57626 | 0.739
199.663
FLW-04 | RIBS
Day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | Total | Avg | Max
2019-01-01 | 0.37 | 0.358 | 0.227 | 0.117 | 0.357 | 0.143 | 0.273 | 0.304 | 0.253 | 0.094 | 0.137 | 0.3 | 0 | 0.183 | 0.316 | 0.205 | 0.062 | 0.189 | 0.247 | 0 | 0.21 | 0.285 | 0.254 | 0.117 | 0.215 | 0.276 | 0 | 0.308 | 0.332 | 0.336 | 0.25 | 6.718 | 0.21671 | 0.37
February | 0.181 | 0.275 | 0 | 0.362 | 0.26 | 0.299 | 0 | 0.262 | 0.266 | 0.124 | 0.285 | 0.342 | 0.281 | 0.259 | 0.218 | 0.372 | 0.205 | 0.102 | 0.167 | 0.276 | 0 | 0.242 | 0.387 | 0.12 | 0.262 | 0.231 | 0.253 | 0.224 |  |  |  | 6.255 | 0.22339 | 0.387
March | 0.288 | 0.248 | 0.171 | 0.193 | 0.296 | 0.648 | 0.124 | 0.244 | 0.272 | 0.075 | 0.235 | 0.182 | 0.262 | 0.084 | 0.084 | 0.289 | 0 | 0.164 | 0.201 | 0.221 | 0.155 | 0.172 | 0.276 | 0 | 0.246 | 0.148 | 0.204 | 0.064 | 0.229 | 0.218 | 0.067 | 6.06 | 0.19548 | 0.648
April | 0.179 | 0.235 | 0.309 | 0.059 | 0 | 0.309 | 0 | 0.15 | 0.3 | 0.447 | 0 | 0 | 0.262 | 0 | 0.023 | 0.346 | 0.223 | 0 | 0.042 | 0.289 | 0.205 | 0.043 | 0.243 | 0.173 | 0 | 0.085 | 0 | 0 | 0 | 0 |  | 3.922 | 0.13073 | 0.447
May | 0 | 0 | 0.111 | 0.03 | 0.025 | 0 | 0.116 | 0.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.253 | 0 | 0 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0.052 | 0 | 0 | 0.023 | 0 | 0.796 | 0.025677 | 0.253
June | 0.01 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073 | 0 | 0 | 0.337 | 0.013 | 0.113 | 0.26 | 0.32 | 0.188 | 0.19 | 0.162 | 0 | 0 | 0.146 | 0 | 0.027 | 0.028 | 0.026 | 0.004 |  | 1.901 | 0.063367 | 0.337
July | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.164 | 0.305 | 0 | 0 | 0.367 | 0.243 | 0.085 | 0.05 | 0.255 | 0.047 | 0.025 | 0.177 | 0.133 | 0 | 0.306 | 0.162 | 0 | 0.082 | 0.368 | 0.204 | 0.011 | 0.553 | 0.25 | 3.787 | 0.12216 | 0.553
August | 0.204 | 0.196 | 0.178 | 0.201 | 0 | 0.218 | 0.167 | 0.228 | 0.259 | 0.194 | 0.219 | 0.001 | 0.293 | 0 | 0.025 | 0.128 | 0.289 | 0.239 | 0.102 | 0.227 | 0.321 | 0.57 | 0.177 | 0.213 | 0.032 | 0.035 | 0.36 | 0.108 | 0.14 | 0.141 | 0.437 | 5.902 | 0.19039 | 0.57
September | 0.248 | 0.214 | 0.469 | 0.366 | 0.232 | 0.216 | 0.32 | 0.238 | 0.002 | 0.273 | 0.082 | 0 | 0 | 0.253 | 0.107 | 0.105 | 0.23 | 0.149 | 0 | 0 | 0 | 0.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026 | 0 |  | 3.825 | 0.1275 | 0.469
October | 0 | 0 | 0.095 | 0.044 | 0 | 0 | 0 | 0 | 0 | 0.126 | 0.088 | 0.281 | 0 | 0.044 | 0.269 | 0.201 | 0 | 0 | 0.302 | 0.214 | 0.241 | 0.234 | 0.299 | 0.013 | 0 | 0.283 | 0.203 | 0.228 | 0.348 | 0.28 | 0.341 | 4.134 | 0.13335 | 0.348
November | 0.035 | 0.054 | 0 | 0.123 | 0.325 | 0.249 | 0 | 0 | 0.378 | 0.27 | 0.054 | 0.378 | 0.26 | 0.079 | 0.237 | 0.281 | 0.208 | 0.252 | 0.315 | 0.292 | 0.051 | 0.167 | 0.28 | 0.137 | 0.242 | 0.326 | 0.31 | 0.089 | 0.273 | 0.312 |  | 5.977 | 0.19923 | 0.378
December | 0.06 | 0.276 | 0.322 | 0.304 | 0.129 | 0.156 | 0.272 | 0.101 | 0.153 | 0.305 | 0.189 | 0.122 | 0.165 | 0.336 | 0.253 | 0.248 | 0.342 | 0.325 | 0.245 | 0.188 | 0.524 | 0.117 | 0.427 | 0.409 | 0.538 | 0.384 | 0.28 | 0.399 | 0.285 | 0.484 | 0.468 | 8.806 | 0.28406 | 0.538
Calculated with Decimal
|  | FLW2 | FLW3 | FLW4 | FLW2 | FLW3 | FLW4
| 1 |  |  |  | 0 | 0 | 0
| 2 |  |  |  | 0 | 0 | 0
| 3 |  |  |  | 0 | 0 | 0
| 4 |  |  |  | 0 | 0 | 0
| 5 |  |  |  | 0 | 0 | 0
| 6 |  |  |  | 0 | 0 | 0
| 7 |  |  |  | 0 | 0 | 0
| 8 |  |  |  | 0 | 0 | 0
| 9 |  |  |  | 0 | 0 | 0
| 10 |  |  |  | 0 | 0 | 0
| 11 |  |  |  | 0 | 0 | 0
| 12 |  |  |  | 0 | 0 | 0
| 13 |  |  |  | 0 | 0 | 0
| 14 |  |  |  | 0 | 0 | 0
| 15 |  |  |  | 0 | 0 | 0
| 16 |  |  |  | 0 | 0 | 0
| 17 |  |  |  | 0 | 0 | 0
| 18 |  |  |  | 0 | 0 | 0
| 19 |  |  |  | 0 | 0 | 0
| 20 |  |  |  | 0 | 0 | 0
| 21 |  |  |  | 0 | 0 | 0
| 22 |  |  |  | 0 | 0 | 0
| 23 |  |  |  | 0 | 0 | 0
| 24 |  |  |  | 0 | 0 | 0
| 25 |  |  |  | 0 | 0 | 0
| 26 |  |  |  | 0 | 0 | 0
| 27 |  |  |  | 0 | 0 | 0
| 28 |  |  |  | 0 | 0 | 0
| 29 |  |  |  | 0 | 0 | 0
| 30 |  |  |  | 0 | 0 | 0
| 31 |  |  |  | 0 | 0 | 0
[5 empty] | 0 | 0 | 0

## WW 2019 Barrington (hidden)
Barrington WWTP
Monthly WW Flows (MG) from DMRs - 2019
Month
1 | 0.72
2 | 0.648
3 | 0.711
4 | 0.716
5 | 0.746
6 | 0.704
7 | 0.666
8 | 0.749
9 | 0.687
10 | 0.697
11 | 0.683
12 | 0.74
Total | 8.467

## Sales2019 (hidden)
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2019 | [20 empty] | Four Lakes 127 - 2019 | [20 empty] | Lake Saunders 226 - 2019
Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust |  | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust |  | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust |  | January | February | March | April | May | June | July | August | September | October | November | December | Grand Total
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 962670 |  |  | 101120 | 98180 | 86580 | 95100 | 99550 | 109110 | 117370 | 87600 | 103890 | 34570 | 16350 | 13250 | 962670 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 108690 |  |  | 3690 | 3690 | 3630 | 14120 | 13910 | 12530 | 12260 | 9790 | 3910 | 9690 | 10920 | 10550 | 108690 | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 24330 |  |  | 1670 | 2010 | 1880 | 2090 | 2260 | 2380 | 2160 | 2030 | 2060 | 1760 | 2010 | 2020 | 24330
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1012000 |  |  | 105100 | 62600 | 69000 | 107600 | 112700 | 77000 | 53400 | 105700 | 151800 | 139500 | 27600 |  | 1012000 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 5349460 |  |  | 371150 | 385400 | 382320 | 600010 | 426330 | 603360 | 527840 | 392670 | 382580 | 423800 | 423193 | 430807 | 5349460 | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 2674730 |  |  | 175030 | 148900 | 168880 | 284540 | 228990 | 244180 | 298230 | 198610 | 163010 | 285160 | 253040 | 226160 | 2674730
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 4151100 |  |  | 203400 | 170700 | 250800 | 293400 | 303100 | 213800 | 431000 | 778700 | 667700 | 333000 | 268000 | 237500 | 4151100 | Total W & Res |  |  |  |  | 5458150 | 71 |  | 374840 | 389090 | 385950 | 614130 | 440240 | 615890 | 540100 | 402460 | 386490 | 433490 | 434113 | 441357 | 5458150 | Total W & Res |  |  |  |  | 2699060 | 45 |  | 176700 | 150910 | 170760 | 286630 | 231250 | 246560 | 300390 | 200640 | 165070 | 286920 | 255050 | 228180 | 2699060
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 2309680 |  |  | 164460 | 139060 | 134760 | 144000 | 155920 | 186662 | 238255 | 195563 | 260520 | 216560 | 144010 | 329910 | 2309680
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1549470 |  |  | 111300 | 88530 | 86440 | 112640 | 129810 | 140060 | 147141 | 157846 | 202503 | 109790 | 107200 | 156210 | 1549470 | Four Lakes 127 - 2018 | [20 empty] | Lake Saunders 226 - 2018
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 805900 |  |  | 15750 | 69570 | 64150 | 68230 | 68920 | 76410 | 86940 | 75680 | 77633 | 59337 | 77940 | 65340 | 805900
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 1128400 |  |  | 177900 | 57019 | 35314 | 134847 | 109720 | 94408 | 95305 | 98887 | 55700 | 81900 | 89800 | 97600 | 1128400 | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust | [14 empty] | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 2000540 |  |  | 91030 | 137970 | 136160 | 118890 | 177210 | 167520 | 102750 | 96770 | 406720 | 223450 | 235390 | 106680 | 2000540 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 83510 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 25020
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 3837152 |  |  | 394850 | 345690 | 224630 | 267110 | 274090 | 395020 | 463210 | 350290 | 343330 | 267350 | 275610 | 235972 | 3837152 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 5547830 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 2297360
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1019090 |  |  | 77590 | 142020 | 56430 | 105710 | 90330 | 90010 | 47130 | 94170 | 87090 | 109860 | 59710 | 59040 | 1019090 | Total W & Res |  |  |  |  | 5631340 | 71 | [14 empty] | Total W & Res |  |  |  |  | 2322380 | 43
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1079000 |  |  | 63800 | 53600 | 57100 | 55100 | 64800 | 63300 | 62900 | 78100 | 139900 | 105100 | 158700 | 176600 | 1079000
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 963980 |  |  | 36040 | 156700 | 43094 | 328776 | 48330 | 59390 | 85570 | 52750 | 41770 | 29620 | 30210 | 51730 | 963980 | Four Lakes 127 - 2017 | [20 empty] | Lake Saunders 226 - 2017
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 46140 |  |  | 5370 | 5970 | 5790 | 6840 | 6320 | 6800 | 6840 | 1630 | 180 | 60 | 120 | 220 | 46140
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | [16 empty] | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust | [14 empty] | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 296380 |  |  | 20650 | 24100 | 16670 | 21250 | 19050 | 27190 | 29850 | 31150 | 35450 | 19650 | 28230 | 23140 | 296380 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 96170 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 38100
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 410300 |  |  | 23900 | 15000 | 15500 | 23400 | 38600 | 45900 | 46800 | 96400 | 37300 | 22830 | 21570 | 23100 | 410300 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6399530 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 2214361
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 364890 |  |  | 14120 | 18940 | 22980 | 33490 | 31430 | 33690 | 36880 | 31670 | 38130 | 36470 | 26350 | 40740 | 364890 | Total W & Res |  |  |  |  | 6495700 | 70 | [14 empty] | Total W & Res |  |  |  |  | 2252461 | 42
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1" | 20 |  |  |  |  | 20 | [9 empty] | 20
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1393500 |  |  | 57300 | 76800 | 79500 | 100400 | 345900 | 58000 | 137100 | 99500 | 118700 | 115700 | 112100 | 92500 | 1393500 | Four Lakes 127 - 2016 | [20 empty] | Lake Saunders 226 - 2016
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 1028980 |  |  | 73310 | 71110 | 53460 | 76520 | 82150 | 72360 | 90820 | 5510 | 375040 | 48800 | 36700 | 43200 | 1028980
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 7816399 |  |  | 1062870 | 833580 | 864280 | 698790 | 421207 | 474913 | 425390 | 239290 | 970210 | 601670 | 611940 | 612259 | 7816399 | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust | [14 empty] | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 2881590 |  |  | 216200 | 223800 | 186700 | 200900 | 195100 | 187700 | 241500 | 239000 | 212800 | 217800 | 239500 | 520590 | 2881590 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 115250 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 27340
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 14988700 |  |  | 1252320 | 1032270 | 1237430 | 1549360 | 1363090 | 1240760 | 1311310 | 1144460 | 1137440 | 1254340 | 1275080 | 1190840 | 14988700 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6013493 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 2544790
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 7669670 |  |  | 90620 | 272110 | 309110 | 263120 | 262150 | 228650 | 871650 | 1053275 | 1440015 | 1459090 | 510931 | 908949 | 7669670 | Total W & Res |  |  |  |  | 6128743 | 71 | [14 empty] | Total W & Res |  |  |  |  | 2572130 | 42
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 3943100 |  |  | 293900 | 361000 | 218800 | 427700 | 347400 | 357200 | 466500 | 272100 | 260100 | 247600 | 389300 | 301500 | 3943100
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 3398929 |  |  | 191484 | 159114 | 224840 | 373822 | 202639 | 282460 | 311330 | 283070 | 250150 | 316220 | 325890 | 477910 | 3398929 | Four Lakes 127 - 2015 | [20 empty] | Lake Saunders 226 - 2015
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4016086 |  |  | 526920 | 489850 | 368286 | 573934 | 519227 | 211903 | 312640 | 98260 | 248700 | 362366 | 162200 | 141800 | 4016086
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 11500 |  |  | 900 | 2200 | 1700 | 3500 | 2300 | 500 | 100 | 300 |  |  |  |  | 11500 | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust | [14 empty] | Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Yr End Res Cust
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 301800 |  |  | 31180 | 28920 | 28530 | 25100 | 15140 | 18290 | 26590 | 27020 | 28800 | 14300 | 44290 | 13640 | 301800 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 72670 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 37040
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2712674 |  |  | 183810 | 161010 | 149370 | 163980 | 146215 | 205345 | 269710 | 135160 | 393500 | 256080 | 287700 | 360794 | 2712674 | 127 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 5921730 | [15 empty] | 226 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 2247390
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 168600 |  |  | 2800 | 3800 | 2800 | 1400 | 1300 | 7600 | 36700 | 40100 | 4900 | 23500 | 43500 | 200 | 168600 | Total W & Res |  |  |  |  | 5994400 | 68 | 67 | [13 empty] | Total W & Res |  |  |  |  | 2284430 | 39 | 40
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 14988700 |  |  | 1252320 | 1032270 | 1237430 | 1549360 | 1363090 | 1240760 | 1311310 | 1144460 | 1137440 | 1254340 | 1275080 | 1190840 | 14988700
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1093190 |  |  | 89750 | 79980 | 78210 | 95120 | 91840 | 80970 | 106940 | 90540 | 96760 | 92760 | 93870 | 96450 | 1093190
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1941140 |  |  | 135070 | 103200 | 172730 | 152240 | 134340 | 183960 | 196870 | 185420 | 124270 | 206970 | 198080 | 147990 | 1941140
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4016086 |  |  | 526920 | 489850 | 368286 | 573934 | 519227 | 211903 | 312640 | 98260 | 248700 | 362366 | 162200 | 141800 | 4016086
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 105440 |  |  | 60 |  | 8490 | 8410 | 4910 | 12050 | 27710 | 9780 | 8010 | 3270 | 11270 | 11480 | 105440
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2478290 |  |  | 211430 | 196440 | 186770 | 192900 | 219590 | 204030 | 239490 | 204450 | 224870 | 162550 | 224770 | 211000 | 2478290
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1036680 |  |  | 77990 | 67370 | 69421 | 97729 | 74520 | 70890 | 87040 | 87240 | 112120 | 77330 | 111530 | 103500 | 1036680
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2412900 |  |  | 1912600 | 9500 | 45700 | 43000 | 47700 | 47400 | 48600 | 48900 | 49600 | 50300 | 57400 | 52200 | 2412900
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 7307600 |  |  | 534600 | 989600 | 502200 | 677700 | 628800 | 901200 | 522500 | 407800 | 500400 | 557200 | 555800 | 529800 | 7307600
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 427900 |  |  | 21950 | 30890 | 50100 | 45450 | 31600 | 43110 | 57990 | 41860 | 31340 | 31650 | 41160 | 800 | 427900
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 453330 |  |  | 41200 | 31350 | 32700 | 33380 | 36940 | 31580 | 40600 | 33820 | 44690 | 38490 | 44720 | 43860 | 453330
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 799160 |  |  | 46210 | 30590 | 45510 | 135600 | 86150 | 133540 | 53500 | 20740 | 36820 | 109210 | 63740 | 37550 | 799160
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 141483574 |  |  | 9524117 | 9392229 | 9482411 | 11677399 | 11976390 | 15233542 | 13342584 | 10833086 | 12063346 | 12228663 | 12617245 | 13112562 | 141483574
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 8737600 |  |  | 771100 | 734400 | 735000 | 712900 | 721800 | 680900 | 730800 | 700700 | 767000 | 655700 | 805200 | 722100 | 8737600
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 3640560 |  |  | 223430 | 288790 | 250860 | 298590 | 322150 | 421410 | 303630 | 287120 | 306150 | 331120 | 318310 | 289000 | 3640560
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 324800 |  |  | 25800 | 20800 | 23500 | 23600 | 25500 | 47300 | 33200 | 26600 | 33000 | 18300 | 26600 | 20600 | 324800
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 832300 |  |  | 48100 | 66300 | 59000 | 71600 | 62700 | 75700 | 61700 |  | 155200 | 72900 | 73800 | 85300 | 832300
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 490896180 |  |  | 32596048 | 35809899 | 33318380 | 45327152 | 42627590 | 52601198 | 43753052 | 34884650 | 42557662 | 44419086 | 41611595 | 41389868 | 490896180
038 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 16153604 | [6 empty] | 2261030 | 2542942 | 2099712 | 1735388 | 1723279 | 1996356 | 1950640 | 1844257 | 16153604
038 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 15995504 | [6 empty] | 2261030 | 2542250 | 2098524 | 1645278 | 1698889 | 1954636 | 1950640 | 1844257 | 15995504
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 2418990 |  |  | 185474 | 114586 | 100590 | 177340 | 177790 | 271120 | 285720 | 241630 | 184110 | 286420 | 209320 | 184890 | 2418990
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 30322257 |  |  | 1996709 | 1874208 | 2032953 | 2736057 | 2603590 | 3392450 | 2934320 | 2357144 | 2387556 | 2638070 | 2758577 | 2610623 | 30322257
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 223700 |  |  | 18220 | 15720 | 15540 | 20560 | 17460 | 23030 | 19580 | 20790 | 17820 | 16720 | 15260 | 23000 | 223700
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 11276500 |  |  | 730590 | 796510 | 724610 | 1044630 | 1059400 | 1189470 | 1065500 | 870920 | 921130 | 1008620 | 909140 | 955980 | 11276500
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 21712700 |  |  | 1366490 | 1510520 | 1210630 | 1917500 | 1829540 | 2503690 | 2090206 | 1637100 | 1815514 | 2099490 | 1856100 | 1875920 | 21712700
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 72340 |  |  | 3850 | 5540 | 5170 | 6580 | 6960 | 14380 | 6020 | 4990 | 4630 | 5190 | 4320 | 4710 | 72340
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 14706860 |  |  | 758930 | 1001230 | 834370 | 1375050 | 1427420 | 1616010 | 1306310 | 1123250 | 943740 | 1480830 | 1712150 | 1127570 | 14706860
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6874280 |  |  | 422950 | 441790 | 438440 | 564380 | 560112 | 739368 | 548530 | 426820 | 579300 | 655800 | 673390 | 823400 | 6874280
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 28786140 |  |  | 2018810 | 1784280 | 1796580 | 2691870 | 2333610 | 3138140 | 2950040 | 1910500 | 2412220 | 2420310 | 2581720 | 2748060 | 28786140
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 115360426 |  |  | 7879210 | 7500632 | 7591388 | 9868706 | 11474430 | 12662370 | 11449065 | 9181705 | 8976490 | 11384130 | 8945990 | 8446310 | 115360426
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 490307591 |  |  | 34839563 | 31702946 | 34095432 | 41731427 | 39120677 | 47104206 | 42838963 | 36723177 | 42640627 | 49388348 | 46650701 | 43471524 | 490307591
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 490222001 |  |  | 34836873 | 31695316 | 34083632 | 41724117 | 39110967 | 47092506 | 42831393 | 36720427 | 42635847 | 49377248 | 46647721 | 43465954 | 490222001
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 16050984 |  |  | 917830 | 1062430 | 1043750 | 1531060 | 1499320 | 1880440 | 1414360 | 1062380 | 1273030 | 1619244 | 1397990 | 1349150 | 16050984
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 8331720 |  |  | 505330 | 502080 | 557140 | 676860 | 807960 | 1023620 | 862430 | 496770 | 868670 | 633490 | 611290 | 786080 | 8331720
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 110590 |  |  | 5640 | 9480 | 28130 | 5800 | 3120 | 2870 | 1260 | 17200 | 11240 | 19850 | 4000 | 2000 | 110590
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 157315433 |  |  | 11812770 | 11525507 | 10634550 | 13199260 | 13534485 | 15970402 | 14389053 | 11921682 | 13095688 | 13818375 | 14336571 | 13077090 | 157315433
[5 empty] | 2181485290 |  |  | 151927928 | 146217446 | 146889827 | 187362170 | 184697436 | 221062658 | 196973823 | 163172528 | 188777129 | 208181845 | 197113811 | 189108689 | 2181485290
Total Water |  |  |  |  | 1532564469 |  |  | 106890565 | 105003478 | 103073001 | 133056393 | 129166947 | 156704634 | 138132751 | 113826168 | 132966593 | 143105315 | 137360230 | 133278394 | 1532564469
Total Res Water |  |  |  |  | 1442640263 | 11666 |  | 98817961 | 98689835 | 97432546 | 125925215 | 123064754 | 150605728 | 131090470 | 107302637 | 124797732 | 135922092 | 131187659 | 126541234 | 1451377863
Barrington Sewer |  |  |  |  | 15995504 | 148 |  | 0 | 0 | 0 | 0 | 2261030 | 2542250 | 2098524 | 1645278 | 1698889 | 1954636 | 1950640 | 1844257 | 15995504
L. Groves Total Sewer |  |  |  |  | 515142391 |  |  | 37027543 | 33565426 | 36092458 | 44260151 | 41366979 | 49023044 | 45065563 | 38414367 | 44641417 | 51573264 | 48708151 | 45404028 | 515142391
L. Groves Res Sewer |  |  |  |  | 490222001 | 4173 |  | 34836873 | 31695316 | 34083632 | 41724117 | 39110967 | 47092506 | 42831393 | 36720427 | 42635847 | 49377248 | 46647721 | 43465954 | 490222001
Reuse |  |  |  |  | 117782926 |  |  | 8009820 | 7648542 | 7724368 | 10045626 | 11902480 | 12792730 | 11676985 | 9286715 | 9470230 | 11548630 | 9094790 | 8582010 | 117782926
[5 empty] | 2181485290 |  |  | 151927928 | 146217446 | 146889827 | 187362170 | 184697436 | 221062658 | 196973823 | 163172528 | 188777129 | 208181845 | 197113811 | 189108689 | 2181485290
0
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2018
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1170980
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 928900
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 6424500
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1860120
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1167470
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 378650
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 2237400
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 1823900
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4185760
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1253600
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1392200
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 333040
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 30820
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1"
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 324760
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 848800
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 500360
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1"
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1017100
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 608960
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 11629180
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1679900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 14291900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 928810
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 7569400
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 4097451
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4862180
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 45250
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 353610
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 3928620
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 72700
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 14291900
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 924000
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 2825320
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4862180
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8"
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2433930
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1251340
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 439800
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 5914000
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 417120
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1178420
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 801789
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 137239396
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 8967000
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 4012420
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 284400
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 629950
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 475200802
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 2069130
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 28872653
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 199630
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 11166530
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 20060490
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 72320
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13545840
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6578830
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 27187750
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 119436888
248 | 251WMLG | 251 Lake Utility Serv-Lake Groves-Water Multi-Residential | RES | 5/8" | 87650
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 420323134
248 | 251WWMLG | 251 Lake Utility Services-Lake Groves-Wastewater Multi-Res | RES | 5/8" | 87650
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 419172184
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 15574830
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 7453220
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 64820
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 151883626
1981457263
Total Water |  |  |  |  | 1414229761
Total Res Water |  |  |  |  | 1323221560 | 11099
Barrington Sewer |  |  |  |  | 0 | 0
L. Groves Total Sewer |  |  |  |  | 446164554
L. Groves Res Sewer |  |  |  |  | 419172184 | 3706
Reuse |  |  |  |  | 121062948
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2017
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1536540
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2160100
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 4127600
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1730530
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 802500
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 260120
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 1917614
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 2005990
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4013220
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1154300
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 519400
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 353910
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 66850
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 10
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 598250
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1073900
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 471560
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1" | 721210
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1149100
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 992220
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 5704720
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1789700
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 13476600
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 1093090
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 5742200
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 3400576
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4377350
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 27850
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 470040
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2720460
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 85100
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 13476600
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1092640
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1438410
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4377350
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 13900
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2414590
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 2277560
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 614900
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 8458500
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 462400
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1424230
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 979970
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 141706647
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 8592300
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 4882770
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 281400
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 379550
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 507634525
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1880120
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 30400710
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 209110
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13175461
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 21315460
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 69700
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 14575990
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6984320
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 29064870
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 128516341
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 374685013
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 374595333
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 15843840
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 8056050
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 70870
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 160534844
1945028884
Total Water |  |  |  |  | 1415864120
Total Res Water |  |  |  |  | 1332731220 | 10144
Barrington Sewer |  |  |  |  | 0 | 0
L. Groves Total Sewer |  |  |  |  | 397785893
L. Groves Res Sewer |  |  |  |  | 374595333 | 3472
Reuse |  |  |  |  | 131378871
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2016
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 2191040
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2170600
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 5995990
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1313670
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 732360
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1098500
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 1474500
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 2349140
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4161180
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 811640
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 438800
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 208640
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 68550
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1"
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 450870
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1140400
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 486620
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1" | 1388330
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1179000
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 552360
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 5265110
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1848900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 14431900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 1074880
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 2028300
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 2562387
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 3467400
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 59100
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 438130
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2502630
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 54600
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 14431900
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1074270
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1171720
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 3467400
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 41870
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2189200
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1504540
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 721200
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 8697000
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 631300
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 840720
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1237400
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 142681667
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 9047600
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 3835450
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 232700
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 80600
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 487383771
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1877133
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 29906094
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 152031
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13688681
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 21435121
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 64190
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13435080
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 7208742
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 29207182
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 127755653
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 357611595
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 357534935
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 16016574
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 8344896
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 74380
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 159421597
1884949719
Total Water |  |  |  |  | 1496336662
Total Res Water |  |  |  |  | 1293894884 | 9996
Barrington Sewer |  |  |  |  | 0 | 0
L. Groves Total Sewer |  |  |  |  | 380237455
L. Groves Res Sewer |  |  |  |  | 357534935 | 3328
Reuse |  |  |  |  | 8375602
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2015
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 2221160
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 14333230
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 6140900
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1307080
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1060940
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2340680
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 643600
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 1945650
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4173590
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 8" | 0
038 | 251WRES | 251 Lake Utility Services Water Residential | COML | 5/8" | 93770
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 785130
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 355300
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 254150
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 57290
066 | 251WRES | 251 Lake Utility Services Water Residential | COML | 5/8" | 12140
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 13040
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1023710
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1431100
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 653640
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 668800
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 698818
248 | 251RRUSE | 251 LUSI Reuse Residential | COML | 1" | 1415480
248 | 251RRUSE | 251 LUSI Reuse Residential | COML | 2" | 201800
248 | 251RRUSE | 251 LUSI Reuse Residential | COML | 5/8" | 61270
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 4836940
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1354000
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 10848200
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 1223850
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 3550400
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 2273207
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4464100
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 21200
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 224400
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2107660
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 98000
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 10848200
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1087050
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1109510
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4464100
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 13160
426 | 251WRES | 251 Lake Utility Services Water Residential | COML | 5/8" | 0
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 1803600
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1524180
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 733200
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 4822000
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 1308890
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 778720
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 765830
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 136332532
038 | 251WGENS | 251 Lake Utility Services Water General Service | RES | 1" | 0
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 3825200
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 3186370
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 231300
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 227800
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 449142947
066 | 251WGENS | 251 Lake Utility Services Water General Service | RES | 1" | 0
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1738880
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 27779720
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 165880
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 12887200
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 19700740
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 39040
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 12943940
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6428050
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 25748570
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 102865210
248 | 251WMLG | 251 Lake Utility Serv-Lake Groves-Water Multi-Residential | RES | 5/8" | 523074
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 348963914
248 | 251WWMLG | 251 Lake Utility Services-Lake Groves-Wastewater Multi-Res | RES | 5/8" | 523074
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 348872774
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13931060
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 7573440
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 62700
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 153548780
1779394860
Total Water |  |  |  |  | 1304373114
Total Res Water |  |  |  |  | 1205523153 | 9904 | 9601
Barrington Sewer |  |  |  |  | 0 | 0 | 0
L. Groves Total Sewer |  |  |  |  | 369110368
L. Groves Res Sewer |  |  |  |  | 348872774 | 3325 | 3164
Reuse |  |  |  |  | 105911378

## CUP (hidden)
LUSI CUP DATA - 2019
| Max Comb. | Ann. Avg
LUSI- North | 5.316 | 2.91 | gpd | CUP, 9/16/2014
LUSI- South |  | 2.406
5.316
Lake Saunders |  | 12328.7671 | gpd | CUP, 5/3/2018

## Sales2019 (2) (hidden)
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2019
Sub | Rate Schedule | Description | Rev Class | Mtr Size |  | Sub | Rate Schedule | Description | Rev Class | Mtr Size
[6 empty] | 004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 962670
[6 empty] | 004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1012000
[6 empty] | 004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 4151100
[6 empty] | 004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 2309680
[6 empty] | 038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1549470
[6 empty] | 038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 805900
[6 empty] | 038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 1128400
[6 empty] | 038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 2000540
[6 empty] | 038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 3837152
[6 empty] | 066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1019090
[6 empty] | 066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1079000
[6 empty] | 066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 963980
[6 empty] | 066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 46140
[6 empty] | 175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1"
[6 empty] | 175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 296380
[6 empty] | 224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 410300
[6 empty] | 224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 364890
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1" | 20 | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 7816399
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1393500 | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 2881590
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 1028980 | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 14988700
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 115360426 | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 7669670
[5 empty] | 117782926 | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 3943100
[6 empty] | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 3398929
[6 empty] | 248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4016086
[6 empty] | 248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 11500
[6 empty] | 248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 301800
[6 empty] | 426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 105440
[6 empty] | 462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2478290
[6 empty] | 462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1036680
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2712674 | 462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2412900
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 168600 | 462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 7307600
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 14988700 | 462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 427900
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1093190 | 462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 453330
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1941140 | 038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 8737600
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4016086 | [5 empty] | 89924206
24920390
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 490222001
515142391
038 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 15995504
[6 empty] | 004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 799160
[6 empty] | 004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 141483574
[6 empty] | 038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 3640560
[6 empty] | 038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 324800
[6 empty] | 038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 832300
[6 empty] | 038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 490896180
[6 empty] | 038 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 16153604
[6 empty] | 066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 2418990
[6 empty] | 066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 30322257
[6 empty] | 082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 223700
[6 empty] | 082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 11276500
[6 empty] | 085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 21712700
[6 empty] | 086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 72340
[6 empty] | 086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 14706860
[6 empty] | 175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6874280
[6 empty] | 224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 28786140
[6 empty] | 248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 490307591
[6 empty] | 333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 16050984
[6 empty] | 426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 8331720
[6 empty] | 462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 110590
[6 empty] | 462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 157315433
1442640263
1532564469
2181485290
Total Water |  |  |  |  | 789201637
Total Res Water |  |  |  |  | -490222001
Barrington Sewer |  |  |  |  | 15995504
L. Groves Total Sewer |  |  |  |  | 515142391
L. Groves Res Sewer |  |  |  |  | 490222001
Reuse |  |  |  |  | 117782926
1438122458
-743362832
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2018
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1170980
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 928900
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 6424500
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1860120
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1167470
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 378650
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 2237400
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 1823900
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4185760
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1253600
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1392200
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 333040
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 30820
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1"
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 324760
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 848800
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 500360
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1"
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1017100
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 608960
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 11629180
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1679900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 14291900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 928810
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 7569400
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 4097451
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4862180
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 45250
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 353610
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 3928620
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 72700
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 14291900
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 924000
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 2825320
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4862180
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8"
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2433930
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1251340
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 439800
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 5914000
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 417120
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1178420
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 801789
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 137239396
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 8967000
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 4012420
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 284400
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 629950
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 475200802
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 2069130
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 28872653
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 199630
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 11166530
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 20060490
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 72320
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13545840
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6578830
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 27187750
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 119436888
248 | 251WMLG | 251 Lake Utility Serv-Lake Groves-Water Multi-Residential | RES | 5/8" | 87650
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 420323134
248 | 251WWMLG | 251 Lake Utility Services-Lake Groves-Wastewater Multi-Res | RES | 5/8" | 87650
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 419172184
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 15574830
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 7453220
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 64820
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 151883626
1981457263
Total Water |  |  |  |  | 1414229761
Total Res Water |  |  |  |  | 1323221560
Barrington Sewer |  |  |  |  | 0
L. Groves Total Sewer |  |  |  |  | 446164554
L. Groves Res Sewer |  |  |  |  | 419172184
Reuse |  |  |  |  | 121062948
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2017
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1536540
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2160100
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 4127600
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1730530
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 802500
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 260120
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 1917614
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 2005990
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4013220
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1154300
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 519400
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 353910
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 66850
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 10
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 598250
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1073900
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 471560
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1" | 721210
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1149100
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 992220
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 5704720
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1789700
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 13476600
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 1093090
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 5742200
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 3400576
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4377350
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 27850
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 470040
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2720460
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 85100
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 13476600
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1092640
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1438410
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4377350
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 13900
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2414590
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 2277560
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 614900
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 8458500
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 462400
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1424230
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 979970
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 141706647
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 8592300
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 4882770
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 281400
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 379550
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 507634525
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1880120
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 30400710
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 209110
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13175461
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 21315460
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 69700
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 14575990
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6984320
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 29064870
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 128516341
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 374685013
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 374595333
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 15843840
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 8056050
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 70870
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 160534844
1945028884
Total Water |  |  |  |  | 1415864120
Total Res Water |  |  |  |  | 1332731220
Barrington Sewer |  |  |  |  | 0
L. Groves Total Sewer |  |  |  |  | 397785893
L. Groves Res Sewer |  |  |  |  | 374595333
Reuse |  |  |  |  | 131378871
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2016
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 2191040
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2170600
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 5995990
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1313670
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 732360
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1098500
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 1474500
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 2349140
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4161180
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 811640
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 438800
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 208640
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 68550
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1"
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 450870
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1140400
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 486620
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 1" | 1388330
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 1179000
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 552360
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 5265110
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1848900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 14431900
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 1074880
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 2028300
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 2562387
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 3467400
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 59100
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 438130
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2502630
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 54600
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 14431900
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1074270
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1171720
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 3467400
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 41870
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 2189200
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1504540
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 721200
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 8697000
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 631300
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 840720
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1237400
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 142681667
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 9047600
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 3835450
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 232700
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 80600
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 487383771
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1877133
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 29906094
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 152031
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13688681
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 21435121
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 64190
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13435080
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 7208742
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 29207182
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 127755653
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 357611595
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 357534935
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 16016574
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 8344896
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 74380
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 159421597
1884949719
Total Water |  |  |  |  | 1496336662
Total Res Water |  |  |  |  | 1293894884
Barrington Sewer |  |  |  |  | 0
L. Groves Total Sewer |  |  |  |  | 380237455
L. Groves Res Sewer |  |  |  |  | 357534935
Reuse |  |  |  |  | 8375602
LUSI, 251-66,excl. Four Lakes 127 and Lake Saunders 226 - 2015
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 2221160
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 14333230
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 6140900
004 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1307080
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1060940
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 2340680
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 643600
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 3" | 1945650
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 4173590
038 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 8" | 0
038 | 251WRES | 251 Lake Utility Services Water Residential | COML | 5/8" | 93770
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 785130
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 355300
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 254150
066 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 57290
066 | 251WRES | 251 Lake Utility Services Water Residential | COML | 5/8" | 12140
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 13040
175 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 1023710
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 1431100
224 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 653640
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 2" | 668800
248 | 251GRUSE | 251 LUSI Reuse General Service | COML | 5/8" | 698818
248 | 251RRUSE | 251 LUSI Reuse Residential | COML | 1" | 1415480
248 | 251RRUSE | 251 LUSI Reuse Residential | COML | 2" | 201800
248 | 251RRUSE | 251 LUSI Reuse Residential | COML | 5/8" | 61270
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1" | 4836940
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 1.5" | 1354000
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 10" | 10848200
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 2" | 1223850
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 4" | 3550400
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 5/8" | 2273207
248 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 8" | 4464100
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 21200
248 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 224400
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1" | 2107660
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 1.5" | 98000
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 10" | 10848200
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 2" | 1087050
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 5/8" | 1109510
248 | 251WWCLG | 251 Lake Utility Services-Lake Groves-Wastewater General Ser | COML | 8" | 4464100
426 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 13160
426 | 251WRES | 251 Lake Utility Services Water Residential | COML | 5/8" | 0
462 | 251WCLG | 251 Lake Utility Serv-Lake Groves-Water General Serv | COML | 3" | 1803600
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1" | 1524180
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 1.5" | 733200
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 2" | 4822000
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 4" | 1308890
462 | 251WGENS | 251 Lake Utility Services Water General Service | COML | 5/8" | 778720
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 765830
004 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 136332532
038 | 251WGENS | 251 Lake Utility Services Water General Service | RES | 1" | 0
038 | 251WMR | 251 LUSI Multi Res Water Service | RES | 8" | 3825200
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 3186370
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1.5" | 231300
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 2" | 227800
038 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 449142947
066 | 251WGENS | 251 Lake Utility Services Water General Service | RES | 1" | 0
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 1738880
066 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 27779720
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 165880
082 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 12887200
085 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 19700740
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 39040
086 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 12943940
175 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 6428050
224 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 25748570
248 | 251RRUSE | 251 LUSI Reuse Residential | RES | 5/8" | 102865210
248 | 251WMLG | 251 Lake Utility Serv-Lake Groves-Water Multi-Residential | RES | 5/8" | 523074
248 | 251WRLG | 251 Lake Utility Serv-Lake Groves-Water Residential | RES | 5/8" | 348963914
248 | 251WWMLG | 251 Lake Utility Services-Lake Groves-Wastewater Multi-Res | RES | 5/8" | 523074
248 | 251WWRLG | 251 Lake Utility Serv-Lake Groves-Wastewater Residential | RES | 5/8" | 348872774
333 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 13931060
426 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 7573440
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 1" | 62700
462 | 251WRES | 251 Lake Utility Services Water Residential | RES | 5/8" | 153548780
1779394860
Total Water |  |  |  |  | 1304373114
Total Res Water |  |  |  |  | 1205523153
Barrington Sewer |  |  |  |  | 0
L. Groves Total Sewer |  |  |  |  | 369110368
L. Groves Res Sewer |  |  |  |  | 348872774
Reuse |  |  |  |  | 105911378