## Appendix A
FPUC's 2022-2031 Estimated Storm Protection Plan Costs by Program (in Millions)
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | Total
Distribution - OH Feeder Hardening | Capital | 0.28942 | 2.9229 | 2.9769 | 1.2837 | 2.4922 | 1.4691 | 1.4644 | 1.4219 | 1.4252 | 1.3094 | 17.0551
| O&M | 0.0089513 | 0.0904 | 0.092068 | 0.039701 | 0.077078 | 0.045436 | 0.04529 | 0.043976 | 0.044078 | 0.040497 | 0.52748
| Total | 0.29838 | 3.0133 | 3.0689 | 1.3234 | 2.5693 | 1.5145 | 1.5097 | 1.4659 | 1.4693 | 1.3499 | 17.5825
Distribution - OH Lateral Hardening | Capital | 0.056013 | 0.56013 | 0.97525 | 4.4068 | 1.7979 | 2.9865 | 3.1723 | 4.7119 | 3.4619 | 2.6188 | 24.7475
| O&M | 0.0017324 | 0.017324 | 0.030162 | 0.13629 | 0.055605 | 0.092367 | 0.098112 | 0.14573 | 0.10707 | 0.080993 | 0.76539
| Total | 0.057745 | 0.57745 | 1.0054 | 4.5431 | 1.8535 | 3.0789 | 3.2704 | 4.8576 | 3.569 | 2.6998 | 25.5129
Distribution - OH Lateral Underground | Capital | 0.10891 | 1.0891 | 1.6209 | 6.2275 | 4.9998 | 8.5242 | 8.0634 | 6.4431 | 13.1343 | 13.1343 | 63.3455
| O&M | 0.0033684 | 0.033684 | 0.050132 | 0.1926 | 0.15463 | 0.26363 | 0.24938 | 0.19927 | 0.40621 | 0.40621 | 1.9591
| Total | 0.11228 | 1.1228 | 1.6711 | 6.4201 | 5.1544 | 8.7878 | 8.3128 | 6.6424 | 13.5405 | 13.5405 | 65.3046
Distribution - Pole Insp. & Replace | Capital | 1.0699 | 1.3327 | 1.4203 | 1.508 | 1.5956 | 1.4309 | 1.0699 | 1.0699 | 1.0699 | 1.0699 | 12.6369
| O&M | 0.1512 | 0.18834 | 0.20073 | 0.21311 | 0.22549 | 0.20221 | 0.1512 | 0.1512 | 0.1512 | 0.1512 | 1.7859
| Total | 1.2211 | 1.5211 | 1.6211 | 1.7211 | 1.8211 | 1.6331 | 1.2211 | 1.2211 | 1.2211 | 1.2211 | 14.4227
T&D - Vegetation Management | Capital | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O&M | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 12
| Total | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 12
Future T&D Enhancements | Capital | 0 | 0 | 0 | 1.5 | 3 | 4.5 | 4.8 | 5.1 | 5.1 | 6 | 30
| O&M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total | 0 | 0 | 0 | 1.5 | 3 | 4.5 | 4.8 | 5.1 | 5.1 | 6 | 30
Transmission / Substation Resiliency | Capital | 0 | 0 | 9.0695 | 38.4993 | 38.4993 | 0 | 0 | 0 | 0 | 0 | 86.0681
| O&M | 0 | 0 | 0.2805 | 1.1907 | 1.1907 | 0 | 0 | 0 | 0 | 0 | 2.6619
| Total | 0 | 0 | 9.35 | 39.69 | 39.69 | 0 | 0 | 0 | 0 | 0 | 88.73
Transmission - Inspection and Hardening | Capital | 0.59952 | 0.59952 | 0.59952 | 0.59952 | 0.59952 | 0.81814 | 0.81814 | 0.81814 | 0.81814 | 0.81814 | 7.0883
| O&M | 0.017482 | 0.017482 | 0.017482 | 0.017482 | 0.017482 | 0.023857 | 0.023857 | 0.023857 | 0.023857 | 0.023857 | 0.20669
| Total | 0.617 | 0.617 | 0.617 | 0.617 | 0.617 | 0.842 | 0.842 | 0.842 | 0.842 | 0.842 | 7.295
SPP Program Management | Capital | 0.19 | 0.1957 | 0.20157 | 0.20762 | 0.21385 | 0.22026 | 0.22687 | 0.23368 | 0.24069 | 0.24791 | 2.1781
| O&M | 0.01 | 0.0103 | 0.010609 | 0.010927 | 0.011255 | 0.011593 | 0.011941 | 0.012299 | 0.012668 | 0.013048 | 0.11464
| Total | 0.2 | 0.206 | 0.21218 | 0.21855 | 0.2251 | 0.23185 | 0.23881 | 0.24597 | 0.25335 | 0.26095 | 2.2928
Totals | Capital | 2.3137 | 6.7001 | 16.864 | 54.2324 | 53.1981 | 19.9491 | 19.6149 | 19.7986 | 25.2501 | 25.1984 | 243.1194
| O&M | 1.3927 | 1.5575 | 1.8817 | 3.0008 | 2.9322 | 1.8391 | 1.7798 | 1.7763 | 1.9451 | 1.9158 | 20.0211
| Total | 3.7065 | 8.2577 | 18.7457 | 57.2332 | 56.1304 | 21.7882 | 21.3947 | 21.5749 | 27.1951 | 27.1142 | 263.1405

## Calculations
Ramp up Rates by Program
| O&M % of costs | % of annual Invest | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | total | Dist Pole Insp & Repl. |  |  | Trans Ins. & Repair |  | Trans/Sub Resiliency |  | SPP Plan Develop
Feeder Hardening | 3% | 16.22% | 1.697% | 17.14% | 17.45% | 7.527% | 14.61% | 8.614% | 8.586% | 8.337% | 8.356% | 7.677% | 100% | Poles in System | 31700 |  | Inspection Costs | 102000 | Substation | 2570000 | FTE | 100000
Lateral Hardening | 3% | 23.54% | 0.2263% | 2.263% | 3.941% | 17.81% | 7.265% | 12.07% | 12.82% | 19.04% | 13.99% | 10.58% | 100% | Cycle | 8 |  | Cycle | 6 | 69kV Hardening | 1750000 | Loaders | 100000
Lateral UG | 3% | 60.24% | 0.1719% | 1.719% | 2.559% | 9.831% | 7.893% | 13.46% | 12.73% | 10.17% | 20.73% | 20.73% | 100% | Inspections/Year | 3962.5 |  | Avg cost/year | 17000 | Eng Cost Sub/69 | 1010000 | Utilization Rate | 95%
Pole Insp & Repl | 12.38% | 100% | 8.466% | 10.55% | 11.24% | 11.93% | 12.63% | 11.32% | 8.466% | 8.466% | 8.466% | 8.466% | 100% | Blended Cost / Insp | 38.157 |  | 69kV wood | 95 | 138kV Line | 83400000 | Escalation | 3%
T&D VM | 100% | 100% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 100% | Failure Rate | 4.5% |  | Repl cost/pole | 75000 | Total Costs | 88730000 | Years in plan | 10
Future T&D Enhance | 0% | 100% | 0% | 0% | 0% | 5% | 10% | 15% | 16% | 17% | 17% | 20% | 100% | Failed Poles/ Yr | 178.3125 |  | Backlog 69Kv | 15 | Eng Costs 138 | 8340000 | Total cost | 2292775.8623
Trans/Sub Resiliency | 3% | 100% | Ramp up Rates by Program 2024: 10.54%; Ramp up Rates by Program 2025: 44.73%; Ramp up Rates by Program 2026: 44.73% | 100% | Blended Cost/Pole Repl | 6000 |  | 2027 Extra | 3
Trans Insp. & Hard | 2.833% | 100% | 8.419% | 8.419% | 8.419% | 8.419% | 8.419% | 11.49% | 11.49% | 11.49% | 11.49% | 11.49% | 99.54% | Annual Insp Cost | 151197.2018 |  | 2028 Extra | 3
SPP Plan Develop | 5% | 100% | 8.723% | 8.985% | 9.254% | 9.532% | 9.818% | 10.11% | 10.42% | 10.73% | 11.05% | 11.38% | 100% | Annual Repl Cost | 1069875 |  | 2029 Extra | 3
[14 empty] | Osmose Data |  |  | 2030 Extra | 3
| 10yr ($M) | [12 empty] | 2019 Inspections | 6858 |  | 2031 Extra | 3
Total Investment New SPP | 108.4 | [12 empty] | 2020 Inspections | 4292 |  | 2024 Insp Cost | 102000
Trans/Sub Resiliency | 88.73 |  | Ramp up Rates by Program 2027: 2022; Ramp up Rates by Program 2028: 2023; Ramp up Rates by Program 2029: 2024 |  | 2021 Inspections | 2825 |  | 2030 Insp Cost | 102000
Future Placeholder | 30 |  | Ramp up Rates by Program 2026: VM Programs; Ramp up Rates by Program 2027: 1.2; Ramp up Rates by Program 2028: 1.2; Ramp up Rates by Program 2029: 1.2 |  | 2019 Rejects | 509 |  | Annual Hard Cost | 600000
Dist Poles | 14.4227 |  | Ramp up Rates by Program 2026: Transmission Programs; Ramp up Rates by Program 2027: 0.617; Ramp up Rates by Program 2028: 0.617; Ramp up Rates by Program 2029: 9.967 |  | 2020 Rejects | 283 |  | Total Program | 7329000
T&D VM | 12 |  | Ramp up Rates by Program 2026: Other Distribution Programs; Ramp up Rates by Program 2027: 1.2211; Ramp up Rates by Program 2028: 1.5211; Ramp up Rates by Program 2029: 1.6211 |  | 2021 Rejects | 109
Trans Insp. & Hard | 7.329 |  | Ramp up Rates by Program 2026: SPP Program Management; Ramp up Rates by Program 2027: 0.2; Ramp up Rates by Program 2028: 0.206; Ramp up Rates by Program 2029: 0.21218 |  | 2019 Costs | 278586.83
SPP Plan Develop | 2.2928 |  | Ramp up Rates by Program 2026: Total of Other SPP Programs; Ramp up Rates by Program 2027: 3.2381; Ramp up Rates by Program 2028: 3.5441; Ramp up Rates by Program 2029: 13.0003 |  | 2020 Costs | 159704.99
[14 empty] | 2021 Costs | 94952.57
[14 empty] | Blended Cost/Pole | 38.157
[14 empty] | Blended Reject Rate | 6.447%
[14 empty] | Adjusted Reject Rate | 4.5% | Reflects downward trend and higher failure rate post Michael
Pole Backlog
[14 empty] | Current Count | 553
[14 empty] | 2023 Extra | 75
[14 empty] | 2024 Extra | 100
[14 empty] | 2025 Extra | 125
[14 empty] | 2026 Extra | 150
[14 empty] | 2027 Extra | 103
[14 empty] | Backlog Cost/Pole | 4000 | Mostly Single phase