## ModelResults
Original System Inputs
|  |  | Probability |  |  | Response |  |  | Impact
# | Substation | Feeder ID | Wind Probability | Flood/Storm Surge | Past Performance | Accessibility | Contingency | Vegetation Exposure | Critical Load | Customers Served | ICE | Risk
16 | BLOUNTSTOWN | BRISTOL (9882) | 120mph | 1 to 2 | 100-200 | >50% Accessible | Radial | 31-40% | Tier 1 | 1001-1500 | >$10M | 66.85
29 | MARIANNA | SOUTH STREET (9854) | 120mph | 1 to 2 | 200-400 | >75% Accessible | Looped | 31-40% | Tier 1 | 1500-2000 | $1-$5M | 65.25
25 | MARIANNA | COTTONDALE (9866) | 120mph | 1 to 2 | 200-400 | >75% Accessible | Radial | 31-40% | Tier 1 | 1001-1500 | $1-$5M | 64.65
8 | JL TERRY | JASMINE STREET (211) | 130mph | 9 | 50-100 | Fully Accessible | Looped | 11-20% | Tier 1 | 1500-2000 | $5-$10M | 57.9
12 | STEPDOWN | BAILEY (311) | 130mph | 3 to 4 | 50-100 | >75% Accessible | Looped | 21-30% | Tier 2 | >2000 | >$10M | 54.575
27 | MARIANNA | HOSPITAL (9872) | 120mph | 1 to 2 | 50-100 | >50% Accessible | Looped | 41-50% | Tier 1 | 501-1000 | $0-$150k | 54.35
14 | ALTHA | ALTHA (9952) | 120mph | 1 to 2 | 100-200 | >75% Accessible | Looped | 21-30% | Tier 1 | 501-1000 | $1-$5M | 51.7
7 | JL TERRY | FIFTEENTH STREET (209) | 130mph | 9 | 0-25 | Fully Accessible | Looped | 11-20% | Tier 1 | 1500-2000 | $1-$5M | 51.05
10 | JL TERRY | SADLER NECTARINE SO.14TH (215) | 130mph | 9 | 0-25 | Fully Accessible | Looped | 11-20% | Tier 1 | 1500-2000 | $1-$5M | 51.05
28 | MARIANNA | RAILROAD (9512) | 120mph | 1 to 2 | 50-100 | Fully Accessible | Looped | 31-40% | Tier 1 | 501-1000 | $1-$5M | 50.3
21 | CHIPOLA | COLLEGE (9982) | 120mph | 1 to 2 | 100-200 | >75% Accessible | Looped | 31-40% | Tier 2 | 1001-1500 | $5-$10M | 50.125
22 | CHIPOLA | HWY 90E (9942) | 120mph | 1 to 2 | 100-200 | >75% Accessible | Looped | 21-30% | Tier 1 | 501-1000 | $0-$150k | 47.65
23 | CHIPOLA | HWY 90W (9992) | 120mph | 1 to 2 | 50-100 | Fully Accessible | Looped | 31-40% | Tier 1 | 501-1000 | $151-$500k | 47.6
9 | JL TERRY | NECTARINE (210) | 130mph | 9 | 25-50 | Fully Accessible | Looped | 11-20% | Tier 1 | 501-1000 | $500k-$1M | 45.25
24 | CHIPOLA | INDIAN SPRINGS (9932) | 120mph | 1 to 2 | 100-200 | >50% Accessible | Radial | 41-50% | Tier 3 | 501-1000 | $500k-$1M | 42.55
18 | CAVERNS ROAD | GREENWOOD (9742) | 120mph | 1 to 2 | 100-200 | >75% Accessible | Radial | 31-40% | Tier 3 | 1001-1500 | $500k-$1M | 40.3
11 | STEPDOWN | AMELIA ISLAND PARKWAY (312) | 130mph | 3 to 4 | 0-25 | Fully Accessible | Looped | 11-20% | Tier 1 | 501-1000 | $1-$5M | 39.85
20 | CAVERNS ROAD | PRISON (9732) | 120mph | 1 to 2 | 0-25 | >50% Accessible | Looped | 31-40% | Tier 1 | 1-250 | $0-$150k | 38.05
4 | AIP | SOUTH FLETCHER (102) | 130mph | 5 to 6 | 50-100 | >75% Accessible | Looped | 11-20% | Tier 3 | 1500-2000 | $5-$10M | 36.9
15 | ALTHA | BLOUNTSTOWN (9972) | 120mph | 1 to 2 | 0-25 | >75% Accessible | Looped | 21-30% | Tier 1 | 1-250 | $1-$5M | 36.25
6 | JL TERRY | ELEVEN STREET (212) | 130mph | 9 | 25-50 | >50% Accessible | Looped | 21-30% | Tier 3 | 501-1000 | $1-$5M | 34.45
26 | MARIANNA | FAMILY DOLLAR (9782) | 120mph | 1 to 2 | 0-25 | >25% Accessible | Looped | 31-40% | Tier 2 | 1-250 | $0-$150k | 30.175
13 | STEPDOWN | BONNIEVIEW (310) | 130mph | 3 to 4 | 25-50 | Fully Accessible | Looped | 0-10% | Tier 2 | 501-1000 | $1-$5M | 28.875
5 | JL TERRY | CLINCH DRIVE (214) | 130mph | 9 | 25-50 | Fully Accessible | Looped | 11-20% | Tier 3 | 501-1000 | $1-$5M | 26.35
2 | AIP | PLANTATION FIELDSIDE (111) | 130mph | 5 to 6 | 0-25 | Fully Accessible | Looped | 11-20% | Tier 3 | 1001-1500 | $1-$5M | 24.2
17 | CAVERNS ROAD | DOGWOOD HEIGHTS (9722) | 120mph | 1 to 2 | 25-50 | >75% Accessible | Looped | 31-40% | Tier 3 | 251-500 | $151-$500k | 23.25
1 | AIP | PARKWAY SOUTH (104) | 130mph | 5 to 6 | 0-25 | Fully Accessible | Looped | 11-20% | Tier 3 | 1001-1500 | $0-$150k | 20.15
3 | AIP | PLANTATION ROADSIDE (110) | 130mph | 5 to 6 | 0-25 | Fully Accessible | Looped | 11-20% | Tier 3 | 1001-1500 | $0-$150k | 20.15
19 | CAVERNS ROAD | INDUSTRIAL PARK (9752) | 120mph | 1 to 2 | 0-25 | Fully Accessible | Looped | 0-10% | Tier 2 | 1-250 | $0-$150k | 12.625
[11 empty] | Avg | 41.8078
[11 empty] | StdDev | 14.2427
[11 empty] | Threshold | 56.0505

## Strategy
Strategy #1 - Harden entire feeder |  | Strategy #2 - Harden Fdr/Lats by Risk |  | Strategy #3 - Harden Feeder & key Laterals on Feeder
| Prioritize feeders leveraging Risk Resiliency Model |  | Prioritize feeders leveraging Risk Resiliency Model |  | Prioritize feeders leveraging Risk Resiliency Model
| Focus on feeder with highest risk score |  | Prioritize laterals leveraging Risk Resiliency Model |  | Focus on feeders with highest risk score
| Harden the feeder backbone |  | Harden the feeder backbone with highest risk |  | Harden the feeder backbone
| Harden the laterals on that feeder |  | Harden the laterals with highest risk |  | Harden all multiphase OH and UG worst 16% (approx 1stdDev) single phase laterals on that feeder (based on ID count)
| Move to next feeder |  | Move to next feeder and lateral in order |  | Move to next feeder
Pros |  | Pros |  | Pros
| Simple to administer and keep track of |  | Focuses on sections of system with highest risk |  | Administration is simple if can identify all fuses with phasing and distance
Balances cost with performance
Cons |  | Cons |  | Cons
| Laterals of higher importance in other feeders may be deferred |  | Administrative burden to know when done with feeder |  | Laterals of higher importance in other feeders may be deferred
| Costly to harden 100% of system |  | Inefficient mobilization of resources |  | May have to harden (UG) additional laterals if performance degrades over time
|  |  | Data intentisive process to feed model with lateral information |  | Must keep track of un-hardened laterals that remain
May cause re-work of poles as you circle back to next ranked lateral

## FeederData
[29 empty] | 2020-12-31 |  |  | 2019 data
Cust Count | Outages | 2016 | 2017 | 2018 | 2019 | 2020 | Average | CMI | 2016 | 2017 | 2018 | 2019 | 2020 | Average | CI | 2016 | 2017 | 2018 | 2019 | 2020 | Average | Avg SAIDI | Avg CAIDI | Avg SAIFI | Res Cust | CI Cust | ICE | Feeder | 1PhOH | 2PhOH | 3PhOH | BB | Lat | UG | Lat | Fdr
1009 | PARKWAY SOUTH (104) | 1 | 3 | 2 | 1 | 1 | 1.6 | PARKWAY SOUTH (104) | 949 | 1887771 | 161 | 34 | 131 | 377809.2 | PARKWAY SOUTH (104) | 1 | 905 | 2 | 1 | 1 | 182 | 374.4392 | 2075.8747 | 0.18038 | 807.2 | 201.8 | 6894 | PARKWAY SOUTH (104) | 0.17 | 0 | 0.25 | 0.25 | 0.17 | 0.17 | 0 | 0.25
1414 | PLANTATION FIELDSIDE (111) | 16 | 24 | 12 | 8 | 12 | 14.4 | PLANTATION FIELDSIDE (111) | 172408 | 5325572 | 30561 | 236682 | 20970 | 1157238.6 | PLANTATION FIELDSIDE (111) | 2072 | 1548 | 329 | 2226 | 222 | 1279.4 | 818.4149 | 904.5166 | 0.90481 | 1131.2 | 282.8 | 3656475 | PLANTATION FIELDSIDE (111) | 1.32 | 0.26 | 2.08 | 1.96 | 1.7 | 1.32 | 0.38 | 1.96
1363 | PLANTATION ROADSIDE (110) | 6 | 11 | 14 | 9 | 15 | 11 | PLANTATION ROADSIDE (110) | 3333 | 4941054 | 9245 | 6270 | 99474 | 1011875.2 | PLANTATION ROADSIDE (110) | 28 | 1790 | 122 | 58 | 336 | 466.8 | 742.3883 | 2167.6847 | 0.34248 | 1090.4 | 272.6 | 2460 | PLANTATION ROADSIDE (110) | 0.77 | 0 | 2.6 | 1.95 | 1.43 | 0.77 | 0.65 | 1.95
1862 | SOUTH FLETCHER (102) | 89 | 70 | 50 | 43 | 63 | 63 | SOUTH FLETCHER (102) | 1022707 | 5844283 | 972029 | 129005 | 174407 | 1628486.2 | SOUTH FLETCHER (102) | 7505 | 3498 | 7254 | 639 | 2804 | 4340 | 874.5898 | 375.2272 | 2.3308 | 1489.6 | 372.4 | 5131749 | SOUTH FLETCHER (102) | 4.97 | 1.07 | 4.28 | 3.65 | 6.67 | 4.97 | 1.7 | 3.65
556 | CLINCH DRIVE (214) | 37 | 34 | 30 | 19 | 34 | 30.8 | CLINCH DRIVE (214) | 784337 | 1512055 | 107943 | 43686 | 71429 | 503890 | CLINCH DRIVE (214) | 1559 | 1924 | 1184 | 666 | 766 | 1219.8 | 906.277 | 413.0923 | 2.1939 | 444.8 | 111.2 | 1605944 | CLINCH DRIVE (214) | 3.71 | 0.23 | 3.71 | 2.83 | 4.82 | 3.71 | 1.11 | 2.83
979 | ELEVEN STREET (212) | 61 | 37 | 26 | 23 | 45 | 38.4 | ELEVEN STREET (212) | 2014629 | 2085530 | 152395 | 49550 | 304662 | 921353.2 | ELEVEN STREET (212) | 4552 | 2085 | 1209 | 237 | 2614 | 2139.4 | 941.1166 | 430.6596 | 2.1853 | 783.2 | 195.8 | 3011729 | ELEVEN STREET (212) | 6.92 | 1.76 | 6.4 | 3.31 | 11.78 | 6.92 | 4.85 | 3.31
1546 | FIFTEENTH STREET (209) | 47 | 27 | 10 | 17 | 23 | 24.8 | FIFTEENTH STREET (209) | 504395 | 1628085 | 85733 | 8688 | 12895 | 447959.2 | FIFTEENTH STREET (209) | 4909 | 2527 | 1585 | 106 | 134 | 1852.2 | 289.7537 | 241.8525 | 1.1981 | 1236.8 | 309.2 | 1315756 | FIFTEENTH STREET (209) | 2.04 | 1.07 | 5.74 | 4.81 | 4.03 | 2.04 | 2 | 4.81
1891 | JASMINE STREET (211) | 85 | 102 | 59 | 46 | 70 | 72.4 | JASMINE STREET (211) | 4277150 | 5199262 | 228950 | 107326 | 930615 | 2148660.6 | JASMINE STREET (211) | 6065 | 9835 | 3717 | 1534 | 10964 | 6423 | 1136.2563 | 334.526 | 3.3966 | 1512.8 | 378.2 | 6600059 | JASMINE STREET (211) | 5.27 | 3.37 | 5.56 | 2.65 | 11.55 | 5.27 | 6.28 | 2.65
646 | NECTARINE (210) | 40 | 23 | 28 | 20 | 17 | 25.6 | NECTARINE (210) | 482328 | 573416 | 155499 | 59643 | 24023 | 258981.8 | NECTARINE (210) | 3675 | 1540 | 959 | 282 | 331 | 1357.4 | 400.9006 | 190.7925 | 2.1012 | 516.8 | 129.2 | 755716 | NECTARINE (210) | 1.63 | 0.23 | 3.75 | 1.89 | 3.73 | 1.63 | 2.09 | 1.89
1898 | SADLER NECTARINE SO.14TH (215) | 22 | 9 | 12 | 13 | 18 | 14.8 | SADLER NECTARINE SO.14TH (215) | 162589 | 2648111 | 393458 | 173092 | 27247 | 680899.4 | SADLER NECTARINE SO.14TH (215) | 640 | 1897 | 2283 | 3398 | 282 | 1700 | 358.7457 | 400.5291 | 0.89568 | 1518.4 | 379.6 | 2181550 | SADLER NECTARINE SO.14TH (215) | 3.92 | 0.26 | 4.31 | 2.13 | 6.36 | 3.92 | 2.44 | 2.13
597 | AMELIA ISLAND PARKWAY (312) | 25 | 4 | 1 | 11 | 17 | 11.6 | AMELIA ISLAND PARKWAY (312) | 56012 | 1484492 | 3418 | 102944 | 126889 | 354751 | AMELIA ISLAND PARKWAY (312) | 263 | 1249 | 50 | 834 | 1209 | 721 | 594.2228 | 492.0264 | 1.2077 | 477.6 | 119.4 | 1191589 | AMELIA ISLAND PARKWAY (312) | 0.24 | 0.05 | 1.03 | 1.03 | 0.29 | 0.24 | 0.05 | 1.03
2530 | BAILEY (311) | 92 | 87 | 39 | 44 | 61 | 64.6 | BAILEY (311) | 6664971 | 10043803 | 96448 | 745313 | 267456 | 3563598.2 | BAILEY (311) | 20208 | 10030 | 3587 | 8058 | 7180 | 9812.6 | 1408.5368 | 363.1655 | 3.8785 | 2024 | 506 | 11138129 | BAILEY (311) | 6.38 | 0.21 | 7.34 | 5.24 | 8.69 | 6.38 | 2.31 | 5.24
530 | BONNIEVIEW (310) | 49 | 40 | 30 | 21 | 23 | 32.6 | BONNIEVIEW (310) | 1705341 | 2613818 | 42433 | 230609 | 63524 | 931145 | BONNIEVIEW (310) | 2554 | 3007 | 770 | 2717 | 626 | 1934.8 | 1756.8774 | 481.2616 | 3.6506 | 424 | 106 | 3085011 | BONNIEVIEW (310) | 2.97 | 1.12 | 2.99 | 3.05 | 4.03 | 2.97 | 1.06 | 3.05
886 | ALTHA (9952) | 78 | 65 | 208 | 135 | 86 | 114.4 | ALTHA (9952) | 244999 | 656167 | 32600595 | 329483 | 627763 | 6891801.4 | ALTHA (9952) | 2461 | 3805 | 6914 | 3365 | 4047 | 4118.4 | 7778.5569 | 1673.4172 | 4.6483 | 708.8 | 177.2 | 2284298 | ALTHA (9952) | 59.97 | 0.5 | 19.75 | 4.6 | 75.61 | 59.97 | 15.65 | 4.6
174 | BLOUNTSTOWN (9972) | 15 | 12 | 56 | 20 | 16 | 23.8 | BLOUNTSTOWN (9972) | 92109 | 94254 | 1710771 | 32513 | 21199 | 390169.2 | BLOUNTSTOWN (9972) | 517 | 560 | 828 | 518 | 348 | 554.2 | 2242.3517 | 704.0224 | 3.1851 | 139.2 | 34.8 | 1371888 | BLOUNTSTOWN (9972) | 6.02 | 0.19 | 7.71 | 6.24 | 7.68 | 6.02 | 1.66 | 6.24
1022 | BRISTOL (9882) | 78 | 73 | 209 | 80 | 75 | 103 | BRISTOL (9882) | 276497 | 319323 | 23872099 | 538287 | 575929 | 5116427 | BRISTOL (9882) | 3109 | 2317 | 5128 | 5907 | 4921 | 4276.4 | 5006.2886 | 1196.4332 | 4.1843 | 817.6 | 204.4 | 10566490 | BRISTOL (9882) | 34.41 | 3.39 | 16.14 | 11.36 | 42.57 | 34.41 | 8.17 | 11.36
290 | DOGWOOD HEIGHTS (9722) | 25 | 41 | 74 | 29 | 26 | 39 | DOGWOOD HEIGHTS (9722) | 29639 | 40943 | 8891995 | 58329 | 100114 | 1824204 | DOGWOOD HEIGHTS (9722) | 504 | 890 | 2415 | 539 | 842 | 1038 | 6290.3586 | 1757.422 | 3.5793 | 232 | 58 | 435536 | DOGWOOD HEIGHTS (9722) | 10.09 | 0 | 3.4 | 4.26 | 9.23 | 10.09 | -0.86 | 4.26
1103 | GREENWOOD (9742) | 135 | 104 | 315 | 100 | 84 | 147.6 | GREENWOOD (9742) | 252980 | 590458 | 49189503 | 776565 | 553701 | 10272641.4 | GREENWOOD (9742) | 2120 | 4816 | 8938 | 5935 | 5097 | 5381.2 | 9313.3648 | 1908.9871 | 4.8787 | 882.4 | 220.6 | 823885 | GREENWOOD (9742) | 33.84 | 1.63 | 24.62 | 6.79 | 53.31 | 33.84 | 19.46 | 6.79
47 | INDUSTRIAL PARK (9752) | 4 | 2 | 8 | 10 | 8 | 6.4 | INDUSTRIAL PARK (9752) | 22406 | 11252 | 579917 | 8022 | 1436 | 124606.6 | INDUSTRIAL PARK (9752) | 92 | 94 | 95 | 88 | 8 | 75.4 | 2651.2043 | 1652.6074 | 1.6043 | 37.6 | 9.4 | 49283 | INDUSTRIAL PARK (9752) | 0.28 | 0 | 3.94 | 3.53 | 0.69 | 0.28 | 0.41 | 3.53
55 | PRISON (9732) | 11 | 5 | 17 | 8 | 11 | 10.4 | PRISON (9732) | 9346 | 521 | 1108865 | 2247 | 75208 | 239237.4 | PRISON (9732) | 67 | 9 | 196 | 22 | 184 | 95.6 | 4349.7709 | 2502.4833 | 1.7382 | 44 | 11 | 427 | PRISON (9732) | 0.49 | 0 | 5.7 | 3.21 | 2.98 | 0.49 | 2.49 | 3.21
1184 | COLLEGE (9982) | 143 | 157 | 408 | 125 | 110 | 188.6 | COLLEGE (9982) | 364730 | 483027 | 37758721 | 298948 | 1327924 | 8046670 | COLLEGE (9982) | 3274 | 3733 | 8525 | 3319 | 7654 | 5301 | 6796.174 | 1517.9532 | 4.4772 | 947.2 | 236.8 | 6373238 | COLLEGE (9982) | 24.65 | 6.4 | 21.71 | 13.44 | 39.32 | 24.65 | 14.67 | 13.44
768 | HWY 90E (9942) | 78 | 130 | 426 | 53 | 68 | 151 | HWY 90E (9942) | 161724 | 283912 | 41172225 | 118737 | 255790 | 8398477.6 | HWY 90E (9942) | 970 | 1887 | 6473 | 1104 | 1896 | 2466 | 10935.5177 | 3405.7087 | 3.2109 | 614.4 | 153.6 | 62 | HWY 90E (9942) | 20.69 | 2.44 | 11.03 | 11.26 | 22.9 | 20.69 | 2.21 | 11.26
923 | HWY 90W (9992) | 71 | 50 | 215 | 53 | 46 | 87 | HWY 90W (9992) | 594546 | 183932 | 30570084 | 109128 | 523925 | 6396323 | HWY 90W (9992) | 3544 | 886 | 5483 | 1813 | 3773 | 3099.8 | 6929.9274 | 2063.4631 | 3.3584 | 738.4 | 184.6 | 161229 | HWY 90W (9992) | 6.07 | 0.96 | 8.55 | 2.86 | 12.72 | 6.07 | 6.65 | 2.86
926 | INDIAN SPRINGS (9932) | 68 | 134 | 243 | 80 | 75 | 120 | INDIAN SPRINGS (9932) | 167477 | 453453 | 36313678 | 145905 | 1078328 | 7631768.2 | INDIAN SPRINGS (9932) | 1842 | 4395 | 8251 | 1578 | 3793 | 3971.8 | 8241.6503 | 1921.4885 | 4.2892 | 740.8 | 185.2 | 535052 | INDIAN SPRINGS (9932) | 18.72 | 2.87 | 10.81 | 5.7 | 26.7 | 18.72 | 7.98 | 5.7
1429 | COTTONDALE (9866) | 143 | 157 | 401 | 160 | 141 | 200.4 | COTTONDALE (9866) | 294839 | 532321 | 48650838 | 370885 | 1952971 | 10360370.8 | COTTONDALE (9866) | 4041 | 6013 | 6613 | 3665 | 10163 | 6099 | 7250.0845 | 1698.6999 | 4.268 | 1143.2 | 285.8 | 3532713 | COTTONDALE (9866) | 53.99 | 2.89 | 22.57 | 11.72 | 67.73 | 53.99 | 13.74 | 11.72
25 | FAMILY DOLLAR (9782) | 4 | 3 | 9 | 4 | 2 | 4.4 | FAMILY DOLLAR (9782) | 11470 | 2296 | 476278 | 10027 | 2005 | 100415.2 | FAMILY DOLLAR (9782) | 51 | 9 | 57 | 72 | 26 | 43 | 4016.608 | 2335.2372 | 1.72 | 20 | 5 | 358 | FAMILY DOLLAR (9782) | 0.85 | 0 | 3.03 | 2.58 | 1.3 | 0.85 | 0.45 | 2.58
780 | HOSPITAL (9872) | 70 | 63 | 196 | 56 | 89 | 94.8 | HOSPITAL (9872) | 161724 | 222824 | 35840481 | 252280 | 1123506 | 7520163 | HOSPITAL (9872) | 1847 | 2205 | 5298 | 2624 | 3613 | 3117.4 | 9641.2346 | 2412.3189 | 3.9967 | 624 | 156 | 22745 | HOSPITAL (9872) | 29.94 | 2.76 | 6.87 | 3.08 | 36.49 | 29.94 | 6.55 | 3.08
600 | RAILROAD (9512) | 38 | 33 | 189 | 30 | 35 | 65 | RAILROAD (9512) | 65279 | 201262 | 7918924 | 41602 | 78760 | 1661165.4 | RAILROAD (9512) | 771 | 1780 | 4189 | 319 | 414 | 1494.6 | 2768.609 | 1111.4448 | 2.491 | 480 | 120 | 4039023 | RAILROAD (9512) | 6.99 | 1.16 | 9.85 | 7.94 | 10.07 | 6.99 | 3.07 | 7.94
1947 | SOUTH STREET (9854) | 185 | 210 | 608 | 193 | 139 | 267 | SOUTH STREET (9854) | 649676 | 2487682 | 84101397 | 680888 | 966152 | 17777159 | SOUTH STREET (9854) | 9072 | 17532 | 9815 | 9404 | 4392 | 10043 | 9130.5388 | 1770.1045 | 5.1582 | 1557.6 | 389.4 | 3988432 | SOUTH STREET (9854) | 85.49 | 4.02 | 17.84 | 7.33 | 100.02 | 85.49 | 14.53 | 7.33
[33 empty] | Total | 432.8 | 141.75 | 140.65
[33 empty] | 10YrTot | 185.54 | 45.03 | 38.3
[34 empty] | 42.87% | 31.77% | 27.23%

## 10YrPlan
Mileage %
[6 empty] | 32% | 100% | 100%
| OH Backbone vs. Lateral Mileage |  | Mileage |  |  | Target Miles |  |  | Target Cost |  |  |  | Miles per phase |  |  | UG cost/phase |  | Lat cost/phase |  | Fdr cost/phase
Top 5 Risk Feeders | Backbone | Lateral | 1 Phase | 2 Phase | 3 Phase | Lat UG | Lat Hard | Fdr Hard | Lat UG | Lat Hard | Fdr Hard | # Phases | Lat UG | Lat Hard | Fdr Hard | Design | Const | Design | Const | Design | Const
BRISTOL (9882) | 11.36 | 42.57 | 34.41 | 3.39 | 16.14 | 11.0112 | 8.17 | 11.36 | 12112320 | 4085000 | 4544000 | 3 | 3.6704 | 2.7233 | 3.7867 | 403744 | 3633696 | 136166.6667 | 1225500 | 151466.6667 | 1363200
SOUTH STREET (9854) | 7.33 | 100.02 | 85.49 | 4.02 | 17.84 | 27.3568 | 14.53 | 7.33 | 30092480 | 7265000 | 2932000 | 2 | 13.6784 | 7.265 | 3.665 | 1504624 | 13541616 | 363250 | 3269250 | 146600 | 1319400
COTTONDALE (9866) | 11.72 | 67.73 | 53.99 | 2.89 | 22.57 | 17.2768 | 13.74 | 11.72 | 19004480 | 6870000 | 4688000 | 4 | 4.3192 | 3.435 | 2.93 | 475112 | 4276008 | 171750 | 1545750 | 117200 | 1054800
JASMINE STREET (211) | 2.65 | 11.55 | 5.27 | 3.37 | 5.56 | 1.6864 | 6.28 | 2.65 | 1855040 | 3140000 | 1060000 | 1 | 1.6864 | 6.28 | 2.65 | 185504 | 1669536 | 314000 | 2826000 | 106000 | 954000
BAILEY (311) | 5.24 | 8.69 | 6.38 | 0.21 | 7.34 | 2.0416 | 2.31 | 5.24 | 2245760 | 1155000 | 2096000 | 2 | 1.0208 | 1.155 | 2.62 | 112288 | 1010592 | 57750 | 519750 | 104800 | 943200
South Fletcher | [5 empty] | 0 | 0 | 1.91 | 0 | 0 | 764000 | 1 | 0 | 0 | 1.91 | 0 | 0 | 0 | 0 | 76400 | 687600
Placeholder (Balance Investment) | [5 empty] | 0 | 6 | 3.75 | 0 | 3000000 | 1500000 | 1 | 0 | 6 | 3.75 | 0 | 0 | 300000 | 2700000 | 150000 | 1350000
Totals | 38.3 | 230.56 | 185.54 | 13.88 | 69.45 | 59.3728 | 51.03 | 43.96 | 65310080 | 25515000 | 17584000 |  | 24.3752 | 20.8583 | 17.5617 | 2681272 | 24131448 | 1042916.6667 | 9386250 | 702466.6667 | 6322200
108409080
Assumptions
% of single phase mileage in 1StdDev |  | 32%
Feeder Hardening $/mile |  | 400000
Lateral Undergrounding $/mile |  | 1100000
Lateral Hardening $/mile |  | 500000
Design costs as % of total costs |  | 10%
[12 empty] | Lateral Hardening | [9 empty] | Lateral Undergrounding
Feeder Hardening | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
Bailey Phase 1 Design | 104800 | [10 empty] | 57750 | [9 empty] | 112288
Bailey Phase 1 Construct |  | 943200 | [10 empty] | 519750 | [9 empty] | 1010592
Bailey Phase 2 Design |  | 104800 | [10 empty] | 57750 | [9 empty] | 112288
Bailey Phase 2 Construct |  |  | 943200 | [10 empty] | 519750 | [9 empty] | 1010592
Cottondale Phase 1 Design | 117200 | [12 empty] | 171750 | [9 empty] | 475112
Cottondale Phase 1 Construct |  | 1054800 | [12 empty] | 1545750 | [9 empty] | 4276008
Cottondale Phase 2 Design |  | 117200 | [12 empty] | 171750 | [9 empty] | 475112
Cottondale Phase 2 Construct |  |  | 1054800 | [12 empty] | 1545750 | [9 empty] | 4276008
Cottondale Phase 3 Design |  |  | 117200 | [12 empty] | 171750 | [9 empty] | 475112
Cottondale Phase 3 Construct |  |  |  | 1054800 | [12 empty] | 1545750 | [9 empty] | 4276008
Cottondale Phase 4 Design |  |  |  | 117200 | [12 empty] | 171750 | [9 empty] | 475112
Cottondale Phase 4 Construct |  |  |  |  | 1054800 | [12 empty] | 1545750 | [9 empty] | 4276008
Bristol Phase 1 Design |  |  |  | 151466.6667 | [11 empty] | 136166.6667 | [9 empty] | 403744
Bristol Phase 1 Construct |  |  |  |  | 1363200 | [11 empty] | 1225500 | [9 empty] | 3633696
Bristol Phase 2 Design |  |  |  |  | 151466.6667 | [11 empty] | 136166.6667 | [9 empty] | 403744
Bristol Phase 2 Construct | [5 empty] | 1363200 | [11 empty] | 1225500 | [9 empty] | 3633696
Bristol Phase 3 Design | [5 empty] | 151466.6667 | [11 empty] | 136166.6667 | [9 empty] | 403744
Bristol Phase 3 Construct | [6 empty] | 1363200 | [11 empty] | 1225500 | [9 empty] | 3633696
Jasmine Phase 1 Design |  | 106000 | [11 empty] | 314000 | [9 empty] | 185504
Jasmine Phase 1 Construct |  |  | 954000 | [11 empty] | 2826000 | [9 empty] | 1669536
SouthStreet Phase 1 Design | [6 empty] | 146600 | [10 empty] | 363250 | [10 empty] | 1504624
SouthStreet Phase 1 Construct | [7 empty] | 1319400 | [10 empty] | 3269250 | [10 empty] | 13541616
SouthStreet Phase 2 Design | [7 empty] | 146600 | [10 empty] | 363250 | [9 empty] | 1504624
SouthStreet Phase 2 Construct | [8 empty] | 1319400 | [10 empty] | 3269250 | [10 empty] | 13541616
South Fletcher A1A Design | 76400
South Fletcher A1A Construct |  | 687600
Placeholder for future project | [8 empty] | 150000 | 1350000 | [9 empty] | 300000 | 2700000
Fdr Hard | 298400 | 3013600 | 3069200 | 1323466.6667 | 2569466.6667 | 1514666.6667 | 1509800 | 1466000 | 1469400 | 1350000 | 17584000 | 57750 | 577500 | 1005500 | 4543500 | 1853666.6667 | 3079166.6667 | 3270666.6667 | 4858000 | 3569250 | 2700000 | 112288 | 1122880 | 1671208 | 6420656 | 5154864 | 8788560 | 8313448 | 6642944 | 13541616 | 13541616
Lat Hard | 57750 | 577500 | 1005500 | 4543500 | 1853666.6667 | 3079166.6667 | 3270666.6667 | 4858000 | 3569250 | 2700000 | 25515000
Lat UG | 112288 | 1122880 | 1671208 | 6420656 | 5154864 | 8788560 | 8313448 | 6642944 | 13541616 | 13541616 | 65310080
Total | 468438 | 4713980 | 5745908 | 12287622.6667 | 9577997.3333 | 13382393.3333 | 13093914.6667 | 12966944 | 18580266 | 17591616 | 108409080
Fdr Hard | 1.697% | 17.14% | 17.45% | 7.527% | 14.61% | 8.614% | 8.586% | 8.337% | 8.356% | 7.677% | 16.22%
Lat Hard | 0.2263% | 2.263% | 3.941% | 17.81% | 7.265% | 12.07% | 12.82% | 19.04% | 13.99% | 10.58% | 23.54%
Lat UG | 0.1719% | 1.719% | 2.559% | 9.831% | 7.893% | 13.46% | 12.73% | 10.17% | 20.73% | 20.73% | 60.24%

## TotalPlan
| 1Ph | 2Ph | 3Ph | BB | Lat
NE | 40.31 | 9.63 | 50.04 | 34.75 | 65.25
NW | 392.49 | 29.21 | 193.52 | 105.9 | 509.32
Total | 432.8 | 38.84 | 243.56 | 140.65 | 574.57
100/100/45% | Miles | Total Invest
FdrHard | 140.65 | 56260000
Lat Hard | 141.75 | 70875000
Lat UG | 194.76 | 214236000 | Assumes target 45% of single phase lateral mileage
341371000
100/100/45%
FdrHard | 11252000 | 5626000 | 3750666.6667 | 2813000 | 2250400 | 1875333.3333 | 1607428.5714 | 1406500 | 1250222.2222 | 1125200
LatHard | 14175000 | 7087500 | 4725000 | 3543750 | 2835000 | 2362500 | 2025000 | 1771875 | 1575000 | 1417500
LatUG | 42847200 | 21423600 | 14282400 | 10711800 | 8569440 | 7141200 | 6121028.5714 | 5355900 | 4760800 | 4284720
Years | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50
Annual Total | 68274200 | 34137100 | 22758066.6667 | 17068550 | 13654840 | 11379033.3333 | 9753457.1429 | 8534275 | 7586022.2222 | 6827420

## Targets
| Devices in Circuit |  | Devices w/Outage
Top 5 Risk Feeders | Fuses | Reclosers | Fuses | Reclosers
BRISTOL (9882) | 138 | 7 | 66 | 8
SOUTH STREET (9854) | 277 | 14 | 231 | 13
COTTONDALE (9866) | 225 | 9 | 180 | 9
JASMINE STREET (211) | 93 | 1 | 36 | 1
BAILEY (311) | 133 | 2 | 44 | 2
Totals | 866 | 33 | 557 | 33
Outage Table |  |  | OMS Table |  |  |  |  | Lateral Hardening Targets |  |  |  |  | Lateral UG Targets
Fuse ID | Fuse Out |  | Dev ID | Phase | #Outages | Proj. Type |  | Dev ID | Phase | #Outages | Proj. Type | Dist | Dev ID | Phase | #Outages | Proj. Type | Dist
FS.2107 | 16 |  | FS.1894 | B | 4 | UG |  | FS.2107 | ABC | 16 | Hard | 4574 | FS.1894 | B | 4 | UG | 457
FS.1873 | 4 |  | FS.1873 | C | 4 | UG |  | FS.2764 | ABC | 4 | Hard | 493 | FS.1873 | C | 4 | UG | Note 3
FS.1894 | 4 |  | FS.2130 | B | 4 | UG |  | FS.2074 | ABC | 3 | Hard | Note1 | FS.2130 | B | 4 | UG | 4484
FS.2130 | 4 |  | FS.2204 | B | 4 | UG |  | FS.2752 | AC | 2 | Hard | Note2 | FS.2204 | B | 4 | UG | 925
FS.2204 | 4 |  | FS.8908 | C | 4 | UG |  | FS.1888 | AC | 1 | Hard | 327 | FS.8908 | C | 4 | UG | 2226
FS.2764 | 4 |  | FS.1895 | A | 3 | UG |  | FS.1892 | AB | 1 | Hard | 425 | FS.1895 | A | 3 | UG | 600
FS.8908 | 4 |  | FS.2038 | C | 3 | UG |  | FS.2132 | ABC | 1 | Hard | 409 | FS.2038 | C | 3 | UG | Note 3
FS.1895 | 3 |  | FS.2028 | B | 3 | UG |  | FS.2442 | AB | 1 | Hard |  | FS.2028 | B | 3 | UG | Note 3
FS.2028 | 3 |  | FS.2184 | A | 3 | UG |  | FS.2590 | ABC | 1 | Hard | 5169 | FS.2184 | A | 3 | UG | 629
FS.2038 | 3 |  | FS.2060 | A | 3 | UG |  | FS.2747 | ABC | 1 | Hard |  | FS.2060 | A | 3 | UG | 376
FS.2060 | 3 |  | FS.1889 | A | 2 | UG |  | FS.2057 | ABC | 1 | Hard | Note1 | FS.1889 | A | 2 | UG | 401
FS.2074 | 3 |  | FS.43587 | C | 2 | UG |  | FS.64012 | ABC | 0 | Hard |  | FS.43587 | C | 2 | UG | Note 3
FS.2184 | 3 |  | FS.2294 | A | 2 | UG |  | FS.2217 | ABC | 0 | Hard |  | FS.2294 | A | 2 | UG | 1284
FS.1889 | 2 |  | FS.2218 | C | 2 | UG |  | FS.2192 | AB | 0 | Hard |  | FS.2218 | C | 2 | UG | 1301
FS.2106 | 2 |  | FS.2178 | B | 2 | UG |  | FS.2716 | ABC | 0 | Hard |  | FS.2178 | B | 2 | UG | 2361
FS.2131 | 2 | fdr312 | FS.2106 | C | 2 | UG |  | FS.8828 | ABC | 0 | Hard |  | FS.2106 | C | 2 | UG | 619
FS.2178 | 2 |  | FS.8803 | B | 2 | UG | Already UG | FS.2093 | ABC | 0 | Hard | Note1 | FS.8803 | B | 2 | UG | Note 3
FS.2218 | 2 |  | FS.8909 | C | 1 | UG |  | FS.2108 | ABC | 0 | Hard | Note1 | FS.8909 | C | 1 | UG
FS.2294 | 2 |  | FS.63614 | C | 1 | UG |  | FS.1973 | ABC | 0 | Hard | Note1 | FS.63614 | C | 1 | UG
FS.2752 | 2 |  | FS.2216 | A | 1 | UG | [6 empty] | FS.2216 | A | 1 | UG
FS.43587 | 2 |  | FS.2223 | A | 1 | UG |  | Note1 - Downstream of FS.2107 |  |  |  |  | FS.2223 | A | 1 | UG
FS.8803 | 2 |  | FS.2021 | B | 1 | UG |  | Note2 - Downstream of FS.2764 |  |  |  |  | FS.2021 | B | 1 | UG | Note 4
FS.1888 | 1 |  | FS.2563 | A | 1 | UG | [6 empty] | FS.2563 | A | 1 | UG
FS.1892 | 1 |  | FS.8825 | B | 1 | UG | [6 empty] | FS.8825 | B | 1 | UG
FS.2021 | 1 |  | FS.8826 | B | 1 | UG | [6 empty] | FS.8826 | B | 1 | UG
FS.2040 | 1 |  | FS.2612 | A | 1 | UG | [6 empty] | FS.2612 | A | 1 | UG
FS.2057 | 1 |  | FS.2726 | A | 1 | UG | [6 empty] | FS.2726 | A | 1 | UG
FS.2132 | 1 |  | FS.2583 | A | 1 | UG | [6 empty] | FS.2583 | A | 1 | UG
FS.2216 | 1 |  | FS.2040 | B | 1 | UG | [6 empty] | FS.2040 | B | 1 | UG | 2162
FS.2223 | 1 |  | FS.8812 | B | 1 | UG | [6 empty] | FS.8812 | B | 1 | UG
FS.2442 | 1 |  | FS.2470 | A | 1 | UG | [6 empty] | FS.2470 | A | 1 | UG
FS.2470 | 1 |  | FS.8813 | B | 1 | UG | [6 empty] | FS.8813 | B | 1 | UG
FS.2563 | 1 |  | FS.2759 | A | 1 | UG | Already UG | [5 empty] | FS.2759 | A | 1 | UG | Note 3
FS.2583 | 1 |  | FS.8800 | C | 1 | UG | [6 empty] | FS.8800 | C | 1 | UG
FS.2590 | 1 |  | FS.1881 | B | 0 | UG | [6 empty] | FS.1881 | B | 0 | UG
FS.2612 | 1 |  | FS.1890 | A | 0 | UG | [6 empty] | FS.1890 | A | 0 | UG
FS.2726 | 1 |  | FS.9983 | C | 0 | UG | [6 empty] | FS.9983 | C | 0 | UG
FS.2747 | 1 |  | FS.1893 | A | 0 | UG | [6 empty] | FS.1893 | A | 0 | UG
FS.2759 | 1 |  | FS.1898 | C | 0 | UG | N.O. UG | [5 empty] | FS.1898 | C | 0 | UG | Note 3
FS.63614 | 1 |  | FS.2018 | A | 0 | UG | [6 empty] | FS.2018 | A | 0 | UG
FS.8812 | 1 |  | FS.8381 | A | 0 | UG | [6 empty] | FS.8381 | A | 0 | UG
FS.8813 | 1 |  | FS.1876 | C | 0 | UG | N.O. UG | [5 empty] | FS.1876 | C | 0 | UG | Note 3
FS.8825 | 1 |  | FS.24787 | B | 0 | UG | [6 empty] | FS.24787 | B | 0 | UG
FS.8826 | 1 |  | FS.63613 | C | 0 | UG | [6 empty] | FS.63613 | C | 0 | UG
FS.8909 | 1 |  | FS.48787 | B | 0 | UG | [6 empty] | FS.48787 | B | 0 | UG
FS.8800 | 1 |  | FS.48788 | B | 0 | UG | [6 empty] | FS.48788 | B | 0 | UG
|  |  | FS.2110 | B | 0 | UG | Already UG | [5 empty] | FS.2110 | B | 0 | UG | Note 3
|  |  | FS.26791 | A | 0 | UG | [6 empty] | FS.26791 | A | 0 | UG
|  |  | FS.63213 | C | 0 | UG | [6 empty] | FS.63213 | C | 0 | UG
|  |  | FS.2295 | A | 0 | UG | [6 empty] | FS.2295 | A | 0 | UG
|  |  | FS.26786 | A | 0 | UG | [6 empty] | FS.26786 | A | 0 | UG
|  |  | FS.2385 | A | 0 | UG | [6 empty] | FS.2385 | A | 0 | UG
|  |  | FS.2205 | B | 0 | UG | [6 empty] | FS.2205 | B | 0 | UG
|  |  | FS.2224 | C | 0 | UG | [6 empty] | FS.2224 | C | 0 | UG
|  |  | FS.2041 | B | 0 | UG | Already UG | [5 empty] | FS.2041 | B | 0 | UG | Note 3
|  |  | FS.2215 | A | 0 | UG | [6 empty] | FS.2215 | A | 0 | UG
|  |  | FS.26792 | A | 0 | UG | [6 empty] | FS.26792 | A | 0 | UG
|  |  | FS.2136 | B | 0 | UG | N.O. UG | [5 empty] | FS.2136 | B | 0 | UG | Note 3
|  |  | FS.22384 | B | 0 | UG | N.O. UG | [5 empty] | FS.22384 | B | 0 | UG | Note 3
|  |  | FS.2191 | C | 0 | UG | [6 empty] | FS.2191 | C | 0 | UG
|  |  | FS.1975 | B | 0 | UG | N.O. UG | [5 empty] | FS.1975 | B | 0 | UG | Note 3
|  |  | FS.76024 | C | 0 | UG | [6 empty] | FS.76024 | C | 0 | UG
|  |  | FS.2655 | C | 0 | UG | [6 empty] | FS.2655 | C | 0 | UG
|  |  | FS.76025 | C | 0 | UG | [6 empty] | FS.76025 | C | 0 | UG
|  |  | FS.2662 | C | 0 | UG | [6 empty] | FS.2662 | C | 0 | UG
|  |  | FS.2593 | A | 0 | UG | [6 empty] | FS.2593 | A | 0 | UG
|  |  | FS.2250 | A | 0 | UG | [6 empty] | FS.2250 | A | 0 | UG
|  |  | FS.2548 | B | 0 | UG | [6 empty] | FS.2548 | B | 0 | UG
|  |  | FS.76026 | C | 0 | UG | [6 empty] | FS.76026 | C | 0 | UG
|  |  | FS.8820 | B | 0 | UG | [6 empty] | FS.8820 | B | 0 | UG
|  |  | FS.2688 | A | 0 | UG | [6 empty] | FS.2688 | A | 0 | UG
|  |  | FS.8821 | C | 0 | UG | [6 empty] | FS.8821 | C | 0 | UG
|  |  | FS.8824 | B | 0 | UG | [6 empty] | FS.8824 | B | 0 | UG
|  |  | FS.2706 | A | 0 | UG | [6 empty] | FS.2706 | A | 0 | UG
|  |  | FS.2711 | A | 0 | UG | [6 empty] | FS.2711 | A | 0 | UG
|  |  | FS.2647 | C | 0 | UG | [6 empty] | FS.2647 | C | 0 | UG
|  |  | FS.2574 | A | 0 | UG | [6 empty] | FS.2574 | A | 0 | UG
|  |  | FS.8827 | B | 0 | UG | [6 empty] | FS.8827 | B | 0 | UG
|  |  | FS.2723 | C | 0 | UG | [6 empty] | FS.2723 | C | 0 | UG
|  |  | FS.2101 | A | 0 | UG | [6 empty] | FS.2101 | A | 0 | UG | 186
|  |  | FS.2721 | B | 0 | UG | [6 empty] | FS.2721 | B | 0 | UG
|  |  | FS.8805 | C | 0 | UG | [6 empty] | FS.8805 | C | 0 | UG
|  |  | FS.2710 | B | 0 | UG | [6 empty] | FS.2710 | B | 0 | UG
|  |  | FS.2719 | A | 0 | UG | [6 empty] | FS.2719 | A | 0 | UG
|  |  | FS.2530 | B | 0 | UG | [6 empty] | FS.2530 | B | 0 | UG
|  |  | FS.2084 | A | 0 | UG | [6 empty] | FS.2084 | A | 0 | UG | 169
|  |  | FS.2516 | A | 0 | UG | [6 empty] | FS.2516 | A | 0 | UG
|  |  | FS.2461 | A | 0 | UG | [6 empty] | FS.2461 | A | 0 | UG
|  |  | FS.70421 | A | 0 | UG | [6 empty] | FS.70421 | A | 0 | UG
|  |  | FS.2490 | A | 0 | UG | [6 empty] | FS.2490 | A | 0 | UG
|  |  | FS.2082 | C | 0 | UG | [6 empty] | FS.2082 | C | 0 | UG | 148
|  |  | FS.69619 | A | 0 | UG | [6 empty] | FS.69619 | A | 0 | UG
|  |  | FS.2448 | B | 0 | UG | [6 empty] | FS.2448 | B | 0 | UG
|  |  | FS.2486 | A | 0 | UG | [6 empty] | FS.2486 | A | 0 | UG
|  |  | FS.51190 | C | 0 | UG | [6 empty] | FS.51190 | C | 0 | UG | 735
|  |  | FS.2712 | A | 0 | UG | [6 empty] | FS.2712 | A | 0 | UG
|  |  | FS.81227 | B | 0 | UG | [6 empty] | FS.81227 | B | 0 | UG
|  |  | FS.2052 | B | 0 | UG | [6 empty] | FS.2052 | B | 0 | UG | 388
|  |  | FS.2480 | B | 0 | UG | [6 empty] | FS.2480 | B | 0 | UG
|  |  | FS.2477 | A | 0 | UG | [6 empty] | FS.2477 | A | 0 | UG
|  |  | FS.8811 | C | 0 | UG | [6 empty] | FS.8811 | C | 0 | UG
|  |  | FS.2539 | A | 0 | UG | [6 empty] | FS.2539 | A | 0 | UG
|  |  | FS.2462 | A | 0 | UG | [6 empty] | FS.2462 | A | 0 | UG
|  |  | FS.8814 | C | 0 | UG | [6 empty] | FS.8814 | C | 0 | UG
|  |  | FS.2457 | A | 0 | UG | [6 empty] | FS.2457 | A | 0 | UG
|  |  | FS.2453 | C | 0 | UG | [6 empty] | FS.2453 | C | 0 | UG
|  |  | FS.2551 | A | 0 | UG | [6 empty] | FS.2551 | A | 0 | UG
|  |  | FS.2702 | B | 0 | UG | [6 empty] | FS.2702 | B | 0 | UG
|  |  | FS.2302 | B | 0 | UG | [6 empty] | FS.2302 | B | 0 | UG
|  |  | FS.2749 | C | 0 | UG | [6 empty] | FS.2749 | C | 0 | UG
|  |  | FS.2544 | A | 0 | UG | [6 empty] | FS.2544 | A | 0 | UG
|  |  | FS.2303 | C | 0 | UG | [6 empty] | FS.2303 | C | 0 | UG
|  |  | FS.2746 | B | 0 | UG | Already UG | [5 empty] | FS.2746 | B | 0 | UG | Note 3
|  |  | FS.2729 | B | 0 | UG | N.O. UG | [5 empty] | FS.2729 | B | 0 | UG | Note 3
|  |  | FS.2757 | A | 0 | UG | Already UG | [5 empty] | FS.2757 | A | 0 | UG | Note 3
|  |  | FS.2718 | A | 0 | UG | N.O. UG | [5 empty] | FS.2718 | A | 0 | UG | Note 3
|  |  | FS.2107 | ABC | 16 | Hard | [6 empty] | Average |  | 0.56897
|  |  | FS.2764 | ABC | 4 | Hard | [6 empty] | StdDev |  | 1.0685
|  |  | FS.2074 | ABC | 3 | Hard | [6 empty] | Threshold |  | 1.6
|  |  | FS.2752 | AC | 2 | Hard
|  |  | FS.1888 | AC | 1 | Hard | [6 empty] | Note 3 - Already UG
|  |  | FS.1892 | AB | 1 | Hard | [6 empty] | Note 4 - Downstream of FS.2130
|  |  | FS.2132 | ABC | 1 | Hard
|  |  | FS.2442 | AB | 1 | Hard
|  |  | FS.2590 | ABC | 1 | Hard
|  |  | FS.2747 | ABC | 1 | Hard
|  |  | FS.2057 | ABC | 1 | Hard
|  |  | FS.64012 | ABC | 0 | Hard
|  |  | FS.2217 | ABC | 0 | Hard
|  |  | FS.2192 | AB | 0 | Hard
|  |  | FS.2716 | ABC | 0 | Hard
|  |  | FS.8828 | ABC | 0 | Hard
|  |  | FS.2093 | ABC | 0 | Hard | Already UG
|  |  | FS.2108 | ABC | 0 | Hard | N.O. UG
|  |  | FS.1973 | ABC | 0 | Hard